## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'AA': 225.0 ton, 2.23 COP liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 0d92de87-13de-4fa4-a6f5-c092ded36fa1 |  | ✓
| data_timestamp | 2022-12-01T11:35Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'AA' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 369313.4068 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.033905 | 277.0389 | 0.053304 | 285.9278 | 1 | 107768.9247 | 198295.1327 | 306064.0574 | 278.4289 | 287.2986 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.053304 | 285.9278 | 2 | 142848.3337 | 396590.2654 | 539438.599 | 279.8189 | 288.3439 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.053304 | 285.9278 | 3 | 199053.1148 | 594885.398 | 793938.5128 | 281.2088 | 289.4837 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.053304 | 285.9278 | 4 | 276383.2681 | 793180.5307 | 1069563.7988 | 282.5988 | 290.7182 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.053304 | 295.0019 | 1 | 128340.5287 | 189751.5752 | 318092.1039 | 278.369 | 296.4316 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.053304 | 295.0019 | 2 | 170116.1139 | 379503.1504 | 549619.2643 | 279.6991 | 297.4723 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.053304 | 295.0019 | 3 | 237049.6139 | 569254.7256 | 806304.3395 | 281.0292 | 298.6261 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.053304 | 295.0019 | 4 | 329141.0288 | 759006.3008 | 1088147.3296 | 282.3593 | 299.893 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.053304 | 304.0759 | 1 | 130462.0144 | 176060.8478 | 306522.8622 | 278.273 | 305.4582 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.053304 | 304.0759 | 2 | 172928.1554 | 352121.6956 | 525049.851 | 279.5072 | 306.4436 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.053304 | 304.0759 | 3 | 240968.0749 | 528182.5434 | 769150.6183 | 280.7413 | 307.5443 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.053304 | 304.0759 | 4 | 334581.7728 | 704243.3912 | 1038825.164 | 281.9754 | 308.7604 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.053304 | 313.15 | 1 | 115937.8962 | 157222.9505 | 273160.8467 | 278.141 | 314.3858 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.053304 | 313.15 | 2 | 153676.3527 | 314445.9009 | 468122.2536 | 279.2431 | 315.2678 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.053304 | 313.15 | 3 | 214141.5016 | 471668.8514 | 685810.353 | 280.3451 | 316.2526 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.053304 | 313.15 | 4 | 297333.343 | 628891.8018 | 926225.1448 | 281.4472 | 317.3402 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 285.9278 | 1 | 104139.1616 | 215062.2805 | 319201.4421 | 282.4386 | 287.3574 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 285.9278 | 2 | 138037.0617 | 430124.5609 | 568161.6226 | 283.9494 | 288.4725 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 285.9278 | 3 | 192348.8107 | 645186.8414 | 837535.652 | 285.4602 | 289.679 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 285.9278 | 4 | 267074.4085 | 860249.1218 | 1127323.5303 | 286.971 | 290.9769 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 295.0019 | 1 | 131680.5312 | 211042.2756 | 342722.8067 | 282.4103 | 296.5424 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 295.0019 | 2 | 174543.3064 | 422084.5512 | 596627.8576 | 283.8929 | 297.6836 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 295.0019 | 3 | 243218.7196 | 633126.8267 | 876345.5463 | 285.3755 | 298.9409 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 295.0019 | 4 | 337706.7706 | 844169.1023 | 1181875.873 | 286.858 | 300.3143 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 304.0759 | 1 | 140391.9784 | 201875.1008 | 342267.0791 | 282.3459 | 305.6193 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 304.0759 | 2 | 186090.3802 | 403750.2015 | 589840.5817 | 283.7641 | 306.7358 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 304.0759 | 3 | 259309.0787 | 605625.3023 | 864934.3811 | 285.1823 | 307.9763 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 304.0759 | 4 | 360048.0741 | 807500.4031 | 1167548.4772 | 286.6005 | 309.3409 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 313.15 | 1 | 131046.3195 | 187560.756 | 318607.0755 | 282.2454 | 314.5914 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 313.15 | 2 | 173702.6552 | 375121.5121 | 548824.1673 | 283.563 | 315.6329 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 313.15 | 3 | 242047.3076 | 562682.2681 | 804729.5757 | 284.8806 | 316.7906 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.053304 | 313.15 | 4 | 336080.2768 | 750243.0241 | 1086323.3009 | 286.1982 | 318.0645 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 285.9278 | 1 | 97153.0967 | 220574.3985 | 317727.4952 | 286.3691 | 287.3508 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 285.9278 | 2 | 128776.9921 | 441148.7971 | 569925.7892 | 287.9215 | 288.4804 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 285.9278 | 3 | 179445.2952 | 661723.1956 | 841168.4908 | 289.4739 | 289.6953 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 285.9278 | 4 | 249158.0058 | 882297.5942 | 1131455.5999 | 291.0264 | 290.9954 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 295.0019 | 1 | 129777.7103 | 221077.9463 | 350855.6565 | 286.3726 | 296.5789 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 295.0019 | 2 | 172021.1063 | 442155.8925 | 614176.9989 | 287.9286 | 297.7625 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 295.0019 | 3 | 239704.1404 | 663233.8388 | 902937.9792 | 289.4846 | 299.0605 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 295.0019 | 4 | 332826.8124 | 884311.7851 | 1217138.5975 | 291.0406 | 300.4728 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 304.0759 | 1 | 144004.7692 | 216434.3241 | 360439.0933 | 286.34 | 305.7013 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 304.0759 | 2 | 190879.1554 | 432868.6481 | 623747.8035 | 287.8632 | 306.8887 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 304.0759 | 3 | 265982.0346 | 649302.9722 | 915285.0068 | 289.3865 | 308.2033 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 304.0759 | 4 | 369313.4068 | 865737.2963 | 1235050.7031 | 290.9098 | 309.6453 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 313.15 | 1 | 139575.3914 | 206643.5319 | 346218.9233 | 286.271 | 314.7163 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 313.15 | 2 | 185007.9894 | 413287.0638 | 598295.0533 | 287.7254 | 315.8567 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 313.15 | 3 | 257800.813 | 619930.5958 | 877731.4088 | 289.1798 | 317.1208 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.053304 | 313.15 | 4 | 357953.8621 | 826574.1277 | 1184527.9898 | 290.6342 | 318.5088 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 285.9278 | 1 | 88544.6524 | 214831.487 | 303376.1394 | 290.2201 | 287.2866 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 285.9278 | 2 | 117366.4494 | 429662.9739 | 547029.4233 | 291.7346 | 288.3779 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 285.9278 | 3 | 163545.1862 | 644494.4609 | 808039.6471 | 293.2491 | 289.5469 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 285.9278 | 4 | 227080.8628 | 859325.9478 | 1086406.8106 | 294.7636 | 290.7937 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 295.0019 | 1 | 124344.9947 | 219858.5873 | 344203.582 | 290.2555 | 296.549 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 295.0019 | 2 | 164820.0104 | 439717.1746 | 604537.1849 | 291.8055 | 297.7192 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 295.0019 | 3 | 229669.7175 | 659575.7618 | 889245.4794 | 293.3554 | 298.9989 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 295.0019 | 4 | 318894.1162 | 879434.3491 | 1198328.4653 | 294.9054 | 300.3882 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 304.0759 | 1 | 142992.3216 | 219738.5177 | 362730.8393 | 290.2547 | 305.7116 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 304.0759 | 2 | 189537.1502 | 439477.0353 | 629014.1856 | 291.8038 | 306.9124 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 304.0759 | 3 | 264112.0071 | 659215.553 | 923327.5601 | 293.3529 | 308.2396 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 304.0759 | 4 | 366716.8924 | 878954.0707 | 1245670.963 | 294.902 | 309.6932 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 313.15 | 1 | 143196.0528 | 214471.2781 | 357667.3309 | 290.2175 | 314.7681 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 313.15 | 2 | 189807.197 | 428942.5563 | 618749.7533 | 291.7295 | 315.9492 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 313.15 | 3 | 264488.3059 | 643413.8344 | 907902.1403 | 293.2415 | 317.2573 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.053304 | 313.15 | 4 | 367239.3795 | 857885.1125 | 1225124.492 | 294.7534 | 318.6924 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation