## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'AA': 300.0 ton, 2.03 COP liquid-cooled, centrifugal compressor chiller |  | ✓
| id | c2a84c29-9241-47cd-a2e5-b1f83f5ed79a |  | ✓
| data_timestamp | 2022-12-01T11:35Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'AA' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 541181.4219 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.045206 | 277.0389 | 0.073252 | 285.9278 | 1 | 157921.5345 | 264393.5102 | 422315.0447 | 278.4289 | 287.3042 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.073252 | 285.9278 | 2 | 209325.9083 | 528787.0205 | 738112.9287 | 279.8189 | 288.3334 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.073252 | 285.9278 | 3 | 291686.805 | 793180.5307 | 1084867.3357 | 281.2088 | 289.4636 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.073252 | 285.9278 | 4 | 405004.2247 | 1057574.0409 | 1462578.2656 | 282.5988 | 290.6946 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.073252 | 295.0019 | 1 | 188066.5812 | 253002.1003 | 441068.6815 | 278.369 | 296.4445 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.073252 | 295.0019 | 2 | 249283.3422 | 506004.2005 | 755287.5428 | 279.6991 | 297.4723 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.073252 | 295.0019 | 3 | 347365.8002 | 759006.3008 | 1106372.101 | 281.0292 | 298.6206 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.073252 | 295.0019 | 4 | 482313.9552 | 1012008.4011 | 1494322.3562 | 282.3593 | 299.8896 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.073252 | 304.0759 | 1 | 191175.3463 | 234747.7971 | 425923.1433 | 278.273 | 305.4736 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.073252 | 304.0759 | 2 | 253404.0283 | 469495.5941 | 722899.6225 | 279.5072 | 306.4481 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.073252 | 304.0759 | 3 | 353107.8021 | 704243.3912 | 1057351.1933 | 280.7413 | 307.5455 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.073252 | 304.0759 | 4 | 490286.6677 | 938991.1883 | 1429277.8559 | 281.9754 | 308.766 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.073252 | 313.15 | 1 | 169892.1143 | 209630.6006 | 379522.7149 | 278.141 | 314.3994 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.073252 | 313.15 | 2 | 225192.9811 | 419261.2012 | 644454.1824 | 279.2431 | 315.2715 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.073252 | 313.15 | 3 | 313796.9003 | 628891.8018 | 942688.7022 | 280.3451 | 316.2533 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.073252 | 313.15 | 4 | 435703.8719 | 838522.4024 | 1274226.2744 | 281.4472 | 317.3448 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 285.9278 | 1 | 152602.5823 | 286749.7073 | 439352.2896 | 282.4386 | 287.3597 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 285.9278 | 2 | 202275.6064 | 573499.4145 | 775775.0209 | 283.9494 | 288.4562 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 285.9278 | 3 | 281862.5074 | 860249.1218 | 1142111.6292 | 285.4602 | 289.6501 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 285.9278 | 4 | 391363.2852 | 1146998.8291 | 1538362.1143 | 286.971 | 290.9416 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 295.0019 | 1 | 192960.9263 | 281389.7008 | 474350.6271 | 282.4103 | 296.5534 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 295.0019 | 2 | 255770.825 | 562779.4015 | 818550.2266 | 283.8929 | 297.6792 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 295.0019 | 3 | 356405.8333 | 844169.1023 | 1200574.9356 | 285.3755 | 298.9288 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 295.0019 | 4 | 494865.9511 | 1125558.8031 | 1620424.7541 | 286.858 | 300.302 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 304.0759 | 1 | 205726.4347 | 269166.801 | 474893.2357 | 282.3459 | 305.6342 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 304.0759 | 2 | 272691.5803 | 538333.6021 | 811025.1823 | 283.7641 | 306.7372 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 304.0759 | 3 | 379984.1905 | 807500.4031 | 1187484.5936 | 285.1823 | 307.9725 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 304.0759 | 4 | 527604.2653 | 1076667.2041 | 1604271.4694 | 286.6005 | 309.3402 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 313.15 | 1 | 192031.5705 | 250081.008 | 442112.5785 | 282.2454 | 314.6054 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 313.15 | 2 | 254538.9585 | 500162.0161 | 754700.9745 | 283.563 | 315.6345 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 313.15 | 3 | 354689.2793 | 750243.0241 | 1104932.3034 | 284.8806 | 316.7874 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.073252 | 313.15 | 4 | 492482.5329 | 1000324.0322 | 1492806.5651 | 286.1982 | 318.0643 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 285.9278 | 1 | 142365.4003 | 294099.1981 | 436464.5984 | 286.3691 | 287.3503 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 285.9278 | 2 | 188706.1624 | 588198.3961 | 776904.5585 | 287.9215 | 288.4599 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 285.9278 | 3 | 262954.0607 | 882297.5942 | 1145251.6548 | 289.4739 | 289.6604 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 285.9278 | 4 | 365109.0952 | 1176396.7922 | 1541505.8875 | 291.0264 | 290.9519 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 295.0019 | 1 | 190172.5864 | 294770.595 | 484943.1814 | 286.3726 | 296.588 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 295.0019 | 2 | 252074.8643 | 589541.1901 | 841616.0544 | 287.9286 | 297.7547 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 295.0019 | 3 | 351255.6683 | 884311.7851 | 1235567.4534 | 289.4846 | 299.0432 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 295.0019 | 4 | 487714.9982 | 1179082.3801 | 1666797.3783 | 291.0406 | 300.4537 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 304.0759 | 1 | 211020.5162 | 288579.0988 | 499599.615 | 286.34 | 305.7153 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 304.0759 | 2 | 279708.916 | 577158.1975 | 856867.1135 | 287.8632 | 306.8877 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 304.0759 | 3 | 389762.5512 | 865737.2963 | 1255499.8475 | 289.3865 | 308.1957 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 304.0759 | 4 | 541181.4219 | 1154316.395 | 1695497.8169 | 290.9098 | 309.6395 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 313.15 | 1 | 204529.8313 | 275524.7092 | 480054.5405 | 286.271 | 314.7303 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 313.15 | 2 | 271105.4755 | 551049.4185 | 822154.894 | 287.7254 | 315.8565 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 313.15 | 3 | 377774.0205 | 826574.1277 | 1204348.1482 | 289.1798 | 317.1147 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.073252 | 313.15 | 4 | 524535.4663 | 1102098.8369 | 1626634.3032 | 290.6342 | 318.5049 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 285.9278 | 1 | 129750.8295 | 286441.9826 | 416192.8121 | 290.2201 | 287.2842 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 285.9278 | 2 | 171985.4758 | 572883.9652 | 744869.441 | 291.7346 | 288.3555 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 285.9278 | 3 | 239654.4907 | 859325.9478 | 1098980.4385 | 293.2491 | 289.5096 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 285.9278 | 4 | 332757.8742 | 1145767.9304 | 1478525.8046 | 294.7636 | 290.7466 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 295.0019 | 1 | 182211.6386 | 293144.783 | 475356.4217 | 290.2555 | 296.5567 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 295.0019 | 2 | 241522.582 | 586289.5661 | 827812.148 | 291.8055 | 297.7095 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 295.0019 | 3 | 336551.5088 | 879434.3491 | 1215985.858 | 293.3554 | 298.9792 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 295.0019 | 4 | 467298.4193 | 1172579.1322 | 1639877.5514 | 294.9054 | 300.3657 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 304.0759 | 1 | 209536.9042 | 292984.6902 | 502521.5944 | 290.2547 | 305.7249 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 304.0759 | 2 | 277742.3797 | 585969.3805 | 863711.7601 | 291.8038 | 306.9101 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 304.0759 | 3 | 387022.2659 | 878954.0707 | 1265976.3366 | 293.3529 | 308.2301 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 304.0759 | 4 | 537376.563 | 1171938.7609 | 1709315.3239 | 294.902 | 309.6849 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 313.15 | 1 | 209835.446 | 285961.7042 | 495797.1502 | 290.2175 | 314.7822 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 313.15 | 2 | 278138.0986 | 571923.4084 | 850061.507 | 291.7295 | 315.9484 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 313.15 | 3 | 387573.6836 | 857885.1125 | 1245458.7961 | 293.2415 | 317.2501 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.073252 | 313.15 | 4 | 538142.2009 | 1143846.8167 | 1681989.0176 | 294.7534 | 318.6871 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation