## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'D': 112.5 ton, 2.53 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 40edea78-3bde-417d-b3d4-f4fda4cf54c2 |  | ✓
| data_timestamp | 2022-12-01T11:35Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'D' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 187290.0926 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.016952 | 277.0389 | 0.025662 | 285.9278 | 1 | 35397.3514 | 100489.3949 | 135886.7462 | 278.4477 | 287.192 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025662 | 285.9278 | 2 | 54421.9435 | 200978.7897 | 255400.7333 | 279.8565 | 288.3038 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025662 | 285.9278 | 3 | 81725.6702 | 301468.1846 | 383193.8547 | 281.2653 | 289.4927 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025662 | 285.9278 | 4 | 117308.5312 | 401957.5794 | 519266.1107 | 282.6741 | 290.7586 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025662 | 295.0019 | 1 | 40346.6951 | 95153.5109 | 135500.206 | 278.3729 | 296.2669 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025662 | 295.0019 | 2 | 62031.352 | 190307.0218 | 252338.3738 | 279.7069 | 297.3578 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025662 | 295.0019 | 3 | 93152.7521 | 285460.5326 | 378613.2847 | 281.0409 | 298.5367 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025662 | 295.0019 | 4 | 133710.8953 | 380614.0435 | 514324.9388 | 282.3749 | 299.8038 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025662 | 304.0759 | 1 | 46276.6418 | 87602.3892 | 133879.031 | 278.267 | 305.3299 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025662 | 304.0759 | 2 | 71148.3964 | 175204.7784 | 246353.1748 | 279.4951 | 306.3834 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025662 | 304.0759 | 3 | 106843.8574 | 262807.1676 | 369651.025 | 280.7233 | 307.5383 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025662 | 304.0759 | 4 | 153363.0248 | 350409.5568 | 503772.5816 | 281.9514 | 308.7945 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025662 | 313.15 | 1 | 51758.7998 | 77836.0298 | 129594.8296 | 278.1301 | 314.3678 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025662 | 313.15 | 2 | 79576.9844 | 155672.0597 | 235249.0441 | 279.2213 | 315.3606 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025662 | 313.15 | 3 | 119501.1048 | 233508.0895 | 353009.1943 | 280.3125 | 316.4672 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025662 | 313.15 | 4 | 171531.161 | 311344.1193 | 482875.2803 | 281.4037 | 317.6875 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 285.9278 | 1 | 36106.2294 | 113195.1327 | 149301.3621 | 282.5182 | 287.3168 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 285.9278 | 2 | 55511.8138 | 226390.2653 | 281902.0791 | 284.1086 | 288.5504 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 285.9278 | 3 | 83362.3331 | 339585.398 | 422947.7311 | 285.6989 | 289.8625 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 285.9278 | 4 | 119657.7873 | 452780.5306 | 572438.318 | 287.2893 | 291.2533 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 295.0019 | 1 | 41469.6954 | 107998.8645 | 149468.5599 | 282.4452 | 296.3974 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 295.0019 | 2 | 63757.9179 | 215997.729 | 279755.6469 | 283.9625 | 297.6138 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 295.0019 | 3 | 95745.5436 | 323996.5935 | 419742.137 | 285.4799 | 298.9207 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 295.0019 | 4 | 137432.5725 | 431995.4579 | 569428.0304 | 286.9973 | 300.3183 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 304.0759 | 1 | 48429.3602 | 100587.3586 | 149016.7188 | 282.341 | 305.4717 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 304.0759 | 2 | 74458.1107 | 201174.7173 | 275632.828 | 283.7543 | 306.6576 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 304.0759 | 3 | 111814.0698 | 301762.0759 | 413576.1457 | 285.1675 | 307.9497 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 304.0759 | 4 | 160497.2376 | 402349.4345 | 562846.6721 | 286.5808 | 309.3478 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 313.15 | 1 | 55615.3448 | 90960.6151 | 146575.9599 | 282.2058 | 314.5273 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 313.15 | 2 | 85506.2607 | 181921.2302 | 267427.4909 | 283.4838 | 315.663 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 313.15 | 3 | 128405.125 | 272881.8452 | 401286.9702 | 284.7618 | 316.9208 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025662 | 313.15 | 4 | 184311.9375 | 363842.4603 | 548154.3978 | 286.0397 | 318.3009 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 285.9278 | 1 | 36646.8657 | 119408.7348 | 156055.6004 | 286.4975 | 287.3796 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 285.9278 | 2 | 56343.0194 | 238817.4695 | 295160.4889 | 288.1783 | 288.6737 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 285.9278 | 3 | 84610.5581 | 358226.2043 | 442836.7624 | 289.8591 | 290.0476 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 285.9278 | 4 | 121449.4819 | 477634.9391 | 599084.4209 | 291.54 | 291.5011 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 295.0019 | 1 | 41756.1408 | 114352.0824 | 156108.2232 | 286.4263 | 296.4593 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 295.0019 | 2 | 64198.3156 | 228704.1648 | 292902.4804 | 288.036 | 297.7365 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 295.0019 | 3 | 96406.8907 | 343056.2473 | 439463.138 | 289.6456 | 299.1049 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 295.0019 | 4 | 138381.8662 | 457408.3297 | 595790.1958 | 291.2552 | 300.5644 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 304.0759 | 1 | 48815.6378 | 107080.1924 | 155895.8302 | 286.324 | 305.5361 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 304.0759 | 2 | 75051.9964 | 214160.3848 | 289212.3811 | 287.8312 | 306.7848 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 304.0759 | 3 | 112705.9105 | 321240.5772 | 433946.4877 | 289.3385 | 308.1405 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 304.0759 | 4 | 161777.3803 | 428320.7695 | 590098.1498 | 290.8458 | 309.6031 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 313.15 | 1 | 56513.9905 | 97593.0647 | 154107.0551 | 286.1904 | 314.5981 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 313.15 | 2 | 86887.8908 | 195186.1293 | 282074.0201 | 287.5642 | 315.8006 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 313.15 | 3 | 130479.9248 | 292779.194 | 423259.1188 | 288.9379 | 317.1273 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025662 | 313.15 | 4 | 187290.0926 | 390372.2586 | 577662.3512 | 290.3116 | 318.5782 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 285.9278 | 1 | 37649.643 | 119130.2012 | 156779.8442 | 290.3852 | 287.3863 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 285.9278 | 2 | 57884.7475 | 238260.4024 | 296145.1499 | 292.0649 | 288.6829 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 285.9278 | 3 | 86925.7779 | 357390.6036 | 444316.3815 | 293.7446 | 290.0613 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 285.9278 | 4 | 124772.7344 | 476520.8048 | 601293.5392 | 295.4243 | 291.5217 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 295.0019 | 1 | 41976.9157 | 114213.1647 | 156190.0804 | 290.3159 | 296.4601 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 295.0019 | 2 | 64537.7478 | 228426.3294 | 292964.0771 | 291.9263 | 297.7371 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 295.0019 | 3 | 96916.6175 | 342639.494 | 439556.1116 | 293.5366 | 299.1057 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 295.0019 | 4 | 139113.5249 | 456852.6587 | 595966.1836 | 295.147 | 300.5661 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 304.0759 | 1 | 48346.8608 | 107080.8905 | 155427.7513 | 290.2153 | 305.5317 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 304.0759 | 2 | 74331.2713 | 214161.7809 | 288493.0522 | 291.7251 | 306.7781 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 304.0759 | 3 | 111623.5946 | 321242.6714 | 432866.266 | 293.2349 | 308.1304 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 304.0759 | 4 | 160223.8306 | 428323.5619 | 588547.3924 | 294.7447 | 309.5886 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 313.15 | 1 | 55506.6245 | 97733.3786 | 153240.003 | 290.0836 | 314.59 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 313.15 | 2 | 85339.1078 | 195466.7571 | 280805.8649 | 291.4615 | 315.7887 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 313.15 | 3 | 128154.1106 | 293200.1357 | 421354.2463 | 292.8395 | 317.1094 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025662 | 313.15 | 4 | 183951.633 | 390933.5142 | 574885.1472 | 294.2175 | 318.5521 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation