## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'F': 600.0 ton, 1.97 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 24b01636-b001-43f8-8d09-0218be5aba33 |  | ✓
| data_timestamp | 2022-12-01T11:35Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'F' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 1169486.4985 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.090412 | 277.0389 | 0.14794 | 285.9278 | 1 | 270011.1344 | 518894.9392 | 788906.0736 | 278.4029 | 287.2009 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14794 | 285.9278 | 2 | 395427.3963 | 1037789.8783 | 1433217.2746 | 279.7669 | 288.2407 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14794 | 285.9278 | 3 | 574869.9296 | 1556684.8175 | 2131554.747 | 281.1308 | 289.3677 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14794 | 285.9278 | 4 | 808338.7342 | 2075579.7566 | 2883918.4908 | 282.4948 | 290.5818 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14794 | 295.0019 | 1 | 324212.1122 | 514946.6924 | 839158.8045 | 278.3925 | 296.3609 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14794 | 295.0019 | 2 | 474803.9433 | 1029893.3848 | 1504697.3281 | 279.7461 | 297.4388 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14794 | 295.0019 | 3 | 690267.068 | 1544840.0771 | 2235107.1451 | 281.0997 | 298.6218 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14794 | 295.0019 | 4 | 970601.4861 | 2059786.7695 | 3030388.2556 | 282.4533 | 299.9098 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14794 | 304.0759 | 1 | 365345.9386 | 493884.6485 | 859230.5871 | 278.3371 | 305.472 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14794 | 304.0759 | 2 | 535043.8364 | 987769.2971 | 1522813.1335 | 279.6354 | 306.5502 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14794 | 304.0759 | 3 | 777843.456 | 1481653.9456 | 2259497.4016 | 280.9336 | 307.7471 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14794 | 304.0759 | 4 | 1093744.7974 | 1975538.5941 | 3069283.3915 | 282.2319 | 309.0629 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14794 | 313.15 | 1 | 387701.777 | 455708.8076 | 843410.5846 | 278.2368 | 314.5248 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14794 | 313.15 | 2 | 567783.638 | 911417.6152 | 1479201.2532 | 279.4347 | 315.5612 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14794 | 313.15 | 3 | 825440.3793 | 1367126.4228 | 2192566.8021 | 280.6326 | 316.724 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14794 | 313.15 | 4 | 1160672.0008 | 1822835.2304 | 2983507.2312 | 281.8304 | 318.0133 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 285.9278 | 1 | 260335.8899 | 547898.5588 | 808234.4487 | 282.3711 | 287.2321 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 285.9278 | 2 | 381258.1408 | 1095797.1177 | 1477055.2585 | 283.8145 | 288.3114 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 285.9278 | 3 | 554270.7526 | 1643695.6765 | 2197966.4291 | 285.2579 | 289.4749 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 285.9278 | 4 | 779373.7252 | 2191594.2354 | 2970967.9606 | 286.7012 | 290.7223 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 295.0019 | 1 | 316450.2864 | 548939.2507 | 865389.5372 | 282.3739 | 296.4034 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 295.0019 | 2 | 463436.8619 | 1097878.5015 | 1561315.3634 | 283.82 | 297.5305 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 295.0019 | 3 | 673741.6746 | 1646817.7522 | 2320559.4268 | 285.2661 | 298.7602 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 295.0019 | 4 | 947364.7244 | 2195757.003 | 3143121.7274 | 286.7122 | 300.0924 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 304.0759 | 1 | 361650.6036 | 532866.1456 | 894516.7492 | 282.3315 | 305.5293 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 304.0759 | 2 | 529632.0719 | 1065732.2911 | 1595364.363 | 283.7353 | 306.6681 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 304.0759 | 3 | 769975.8658 | 1598598.4367 | 2368574.3025 | 285.1391 | 307.9244 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 304.0759 | 4 | 1082681.9854 | 2131464.5822 | 3214146.5677 | 286.5428 | 309.2983 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 313.15 | 1 | 390646.1027 | 499679.2433 | 890325.346 | 282.2441 | 314.6013 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 313.15 | 2 | 572095.5604 | 999358.4866 | 1571454.047 | 283.5605 | 315.7115 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 313.15 | 3 | 831709.0257 | 1499037.7299 | 2330746.7556 | 284.8768 | 316.9492 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14794 | 313.15 | 4 | 1169486.4985 | 1998716.9732 | 3168203.4718 | 286.1931 | 318.3143 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 285.9278 | 1 | 256219.4928 | 558792.012 | 815011.5048 | 286.2915 | 287.243 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 285.9278 | 2 | 375229.7368 | 1117584.0241 | 1492813.7609 | 287.7663 | 288.3369 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 285.9278 | 3 | 545506.6957 | 1676376.0361 | 2221882.7318 | 289.2411 | 289.5135 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 285.9278 | 4 | 767050.3695 | 2235168.0482 | 3002218.4177 | 290.7159 | 290.7728 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 295.0019 | 1 | 311738.4459 | 564821.6426 | 876560.0885 | 286.3074 | 296.4215 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 295.0019 | 2 | 456536.4397 | 1129643.2852 | 1586179.725 | 287.7981 | 297.5708 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 295.0019 | 3 | 663709.883 | 1694464.9278 | 2358174.8109 | 289.2889 | 298.8211 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 295.0019 | 4 | 933258.7758 | 2259286.5705 | 3192545.3462 | 290.7796 | 300.1724 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 304.0759 | 1 | 357833.1263 | 553737.4761 | 911570.6024 | 286.2781 | 305.557 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 304.0759 | 2 | 524041.4316 | 1107474.9522 | 1631516.3838 | 287.7396 | 306.7268 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 304.0759 | 3 | 761848.2272 | 1661212.4283 | 2423060.6555 | 289.2011 | 308.0129 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 304.0759 | 4 | 1071253.5131 | 2214949.9044 | 3286203.4175 | 290.6626 | 309.4153 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 313.15 | 1 | 389632.8931 | 525539.5125 | 915172.4056 | 286.2037 | 314.6418 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 313.15 | 2 | 570611.7297 | 1051079.025 | 1621690.7547 | 287.5908 | 315.7934 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 313.15 | 3 | 829551.8416 | 1576618.5375 | 2406170.3792 | 288.9778 | 317.0722 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14794 | 313.15 | 4 | 1166453.229 | 2102158.05 | 3268611.279 | 290.3649 | 318.478 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 285.9278 | 1 | 259499.2762 | 551575.2988 | 811074.5749 | 290.1637 | 287.2367 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 285.9278 | 2 | 380032.9321 | 1103150.5975 | 1483183.5296 | 291.6219 | 288.3213 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 285.9278 | 3 | 552489.5517 | 1654725.8963 | 2207215.448 | 293.0801 | 289.4898 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 285.9278 | 4 | 776869.1349 | 2206301.195 | 2983170.3299 | 294.5383 | 290.742 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 295.0019 | 1 | 312772.0465 | 562593.868 | 875365.9145 | 290.1929 | 296.4196 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 295.0019 | 2 | 458050.1328 | 1125187.736 | 1583237.8687 | 291.6802 | 297.566 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 295.0019 | 3 | 665910.4807 | 1687781.604 | 2353692.0847 | 293.1675 | 298.8138 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 295.0019 | 4 | 936353.0902 | 2250375.472 | 3186728.5622 | 294.6548 | 300.163 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 304.0759 | 1 | 357447.0851 | 556498.6401 | 913945.7253 | 290.1768 | 305.5609 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 304.0759 | 2 | 523476.0799 | 1112997.2803 | 1636473.3602 | 291.6479 | 306.7349 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 304.0759 | 3 | 761026.3224 | 1669495.9204 | 2430522.2428 | 293.1191 | 308.025 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 304.0759 | 4 | 1070097.8125 | 2225994.5606 | 3296092.3731 | 294.5903 | 309.4314 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 313.15 | 1 | 389073.8494 | 533289.6152 | 922363.4646 | 290.1154 | 314.6535 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 313.15 | 2 | 569793.0182 | 1066579.2305 | 1636372.2486 | 291.5252 | 315.8174 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 313.15 | 3 | 828361.6039 | 1599868.8457 | 2428230.4496 | 292.9351 | 317.1081 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14794 | 313.15 | 4 | 1164779.6064 | 2133158.4609 | 3297938.0674 | 294.3449 | 318.5258 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation