## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'I': 350.0 ton, 1.97 COP liquid-cooled, centrifugal compressor chiller |  | ✓
| id | a8e91e7d-0a1a-4282-9bd3-11f390474874 |  | ✓
| data_timestamp | 2022-12-01T11:35Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'I' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 641446.7969 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.052741 | 277.0389 | 0.086297 | 285.9278 | 1 | 200016.5791 | 335171.6098 | 535188.1889 | 278.5492 | 287.4084 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.086297 | 285.9278 | 2 | 283219.3333 | 670343.2197 | 953562.553 | 280.0596 | 288.5658 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.086297 | 285.9278 | 3 | 411950.4682 | 1005514.8295 | 1417465.2977 | 281.57 | 289.8492 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.086297 | 285.9278 | 4 | 586209.9837 | 1340686.4394 | 1926896.4231 | 283.0803 | 291.2586 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.086297 | 295.0019 | 1 | 208040.768 | 302451.1426 | 510491.9106 | 278.4018 | 296.4192 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.086297 | 295.0019 | 2 | 294581.4186 | 604902.2852 | 899483.7038 | 279.7647 | 297.4992 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.086297 | 295.0019 | 3 | 428476.9401 | 907353.4279 | 1335830.368 | 281.1276 | 298.7107 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.086297 | 295.0019 | 4 | 609727.3325 | 1209804.5705 | 1819531.9029 | 282.4905 | 300.0536 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.086297 | 304.0759 | 1 | 204625.2274 | 279967.1006 | 484592.328 | 278.3005 | 305.4257 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.086297 | 304.0759 | 2 | 289745.0839 | 559934.2011 | 849679.285 | 279.5621 | 306.4426 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.086297 | 304.0759 | 3 | 421442.3556 | 839901.3017 | 1261343.6573 | 280.8237 | 307.5892 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.086297 | 304.0759 | 4 | 599717.0425 | 1119868.4022 | 1719585.4447 | 282.0853 | 308.8656 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.086297 | 313.15 | 1 | 194332.7501 | 267719.4836 | 462052.2338 | 278.2453 | 314.4411 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.086297 | 313.15 | 2 | 275171.1492 | 535438.9673 | 810610.1165 | 279.4517 | 315.4151 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.086297 | 313.15 | 3 | 400244.1586 | 803158.4509 | 1203402.6095 | 280.6581 | 316.5127 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.086297 | 313.15 | 4 | 569551.7783 | 1070877.9346 | 1640429.7128 | 281.8645 | 317.734 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 285.9278 | 1 | 196154.1085 | 358720.6769 | 554874.7854 | 282.5478 | 287.4628 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 285.9278 | 2 | 277750.155 | 717441.3537 | 995191.5087 | 284.1678 | 288.681 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 285.9278 | 3 | 403995.3948 | 1076162.0306 | 1480157.4254 | 285.7878 | 290.0227 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 285.9278 | 4 | 574889.8281 | 1434882.7074 | 2009772.5355 | 287.4078 | 291.4878 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 295.0019 | 1 | 211899.3062 | 331201.6746 | 543100.9808 | 282.4235 | 296.5097 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 295.0019 | 2 | 300045.0289 | 662403.3492 | 962448.3781 | 283.9192 | 297.674 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 295.0019 | 3 | 436423.9146 | 993605.0238 | 1430028.9384 | 285.415 | 298.9722 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 295.0019 | 4 | 621035.9633 | 1324806.6984 | 1945842.6618 | 286.9107 | 300.4043 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 304.0759 | 1 | 214944.6805 | 313919.0975 | 528863.778 | 282.3455 | 305.549 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 304.0759 | 2 | 304357.2158 | 627838.195 | 932195.4108 | 283.7631 | 306.6724 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 304.0759 | 3 | 442696.1114 | 941757.2925 | 1384453.404 | 285.1808 | 307.9321 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 304.0759 | 4 | 629961.3675 | 1255676.39 | 1885637.7576 | 286.5985 | 309.3281 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 313.15 | 1 | 209161.0735 | 306872.9456 | 516034.0191 | 282.3136 | 314.592 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 313.15 | 2 | 296167.748 | 613745.8911 | 909913.6392 | 283.6995 | 315.6926 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 313.15 | 3 | 430784.3008 | 920618.8367 | 1351403.1375 | 285.0853 | 316.9263 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.086297 | 313.15 | 4 | 613010.7318 | 1227491.7823 | 1840502.5141 | 286.4712 | 318.293 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 285.9278 | 1 | 187948.5269 | 371584.4797 | 559533.0066 | 286.4979 | 287.4757 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 285.9278 | 2 | 266131.2214 | 743168.9594 | 1009300.1808 | 288.1791 | 288.72 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 285.9278 | 3 | 387095.3299 | 1114753.4391 | 1501848.769 | 289.8604 | 290.0827 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 285.9278 | 4 | 550840.8524 | 1486337.9188 | 2037178.7712 | 291.5416 | 291.5637 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 295.0019 | 1 | 209790.5942 | 349266.9424 | 559057.5366 | 286.3969 | 296.554 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 295.0019 | 2 | 297059.1363 | 698533.8848 | 995593.0212 | 287.9772 | 297.766 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 295.0019 | 3 | 432080.85 | 1047800.8273 | 1479881.6773 | 289.5574 | 299.1106 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 295.0019 | 4 | 614855.7354 | 1397067.7697 | 2011923.5051 | 291.1377 | 300.5878 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 304.0759 | 1 | 218316.7586 | 337185.8303 | 555502.5889 | 286.3423 | 305.6232 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 304.0759 | 2 | 309132.0085 | 674371.6606 | 983503.6691 | 287.8679 | 306.8153 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 304.0759 | 3 | 449641.1814 | 1011557.4909 | 1461198.6723 | 289.3935 | 308.1459 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 304.0759 | 4 | 639844.2773 | 1348743.3212 | 1988587.5986 | 290.9191 | 309.6149 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 313.15 | 1 | 216705.9117 | 335341.1433 | 552047.055 | 286.3339 | 314.6926 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 313.15 | 2 | 306851.0826 | 670682.2867 | 977533.3693 | 287.8512 | 315.8816 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 313.15 | 3 | 446323.5107 | 1006023.43 | 1452346.9407 | 289.3684 | 317.2084 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.086297 | 313.15 | 4 | 635123.196 | 1341364.5734 | 1976487.7694 | 290.8857 | 318.673 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 285.9278 | 1 | 177059.1607 | 373763.0184 | 550822.1791 | 290.3994 | 287.4516 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 285.9278 | 2 | 250712.1044 | 747526.0368 | 998238.1412 | 292.0933 | 288.6894 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 285.9278 | 3 | 364667.7916 | 1121289.0551 | 1485956.8467 | 293.7872 | 290.0387 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 285.9278 | 4 | 518926.2221 | 1495052.0735 | 2013978.2956 | 295.4811 | 291.4995 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 295.0019 | 1 | 203452.9422 | 356646.9461 | 560099.8883 | 290.3219 | 296.5569 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 295.0019 | 2 | 288085.1524 | 713293.8922 | 1001379.0445 | 291.9382 | 297.7821 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 295.0019 | 3 | 419027.9386 | 1069940.8382 | 1488968.7768 | 293.5545 | 299.1358 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 295.0019 | 4 | 596281.3009 | 1426587.7843 | 2022869.0852 | 295.1708 | 300.6182 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 304.0759 | 1 | 216558.7559 | 349767.2989 | 566326.0549 | 290.2907 | 305.6533 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 304.0759 | 2 | 306642.7131 | 699534.5979 | 1006177.311 | 291.8758 | 306.8785 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 304.0759 | 3 | 446020.4315 | 1049301.8968 | 1495322.3283 | 293.461 | 308.2409 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 304.0759 | 4 | 634691.911 | 1399069.1957 | 2033761.1067 | 295.0461 | 309.7407 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 313.15 | 1 | 218863.543 | 353124.0769 | 571987.6199 | 290.3059 | 314.7483 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 313.15 | 2 | 309906.2438 | 706248.1539 | 1016154.3977 | 291.9063 | 315.9895 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 313.15 | 3 | 450767.3285 | 1059372.2308 | 1510139.5593 | 293.5066 | 317.3699 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.086297 | 313.15 | 4 | 641446.7969 | 1412496.3078 | 2053943.1047 | 295.107 | 318.8895 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation