## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'I': 400.0 ton, 1.97 COP liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 44e27932-97a8-47df-b59b-55ce265d741a |  | ✓
| data_timestamp | 2022-12-01T11:35Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'I' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 733082.0536 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.060275 | 277.0389 | 0.098625 | 285.9278 | 1 | 228590.3761 | 383053.2684 | 611643.6445 | 278.5492 | 287.4084 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.098625 | 285.9278 | 2 | 323679.238 | 766106.5368 | 1089785.7748 | 280.0596 | 288.5658 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.098625 | 285.9278 | 3 | 470800.535 | 1149159.8052 | 1619960.3402 | 281.57 | 289.8492 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.098625 | 285.9278 | 4 | 669954.2671 | 1532213.0736 | 2202167.3407 | 283.0803 | 291.2586 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.098625 | 295.0019 | 1 | 237760.8777 | 345658.4487 | 583419.3264 | 278.4018 | 296.4192 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.098625 | 295.0019 | 2 | 336664.4784 | 691316.8974 | 1027981.3758 | 279.7647 | 297.4992 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.098625 | 295.0019 | 3 | 489687.9315 | 1036975.3461 | 1526663.2777 | 281.1276 | 298.7107 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.098625 | 295.0019 | 4 | 696831.2371 | 1382633.7948 | 2079465.0319 | 282.4905 | 300.0536 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.098625 | 304.0759 | 1 | 233857.4028 | 319962.4006 | 553819.8034 | 278.3005 | 305.4257 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.098625 | 304.0759 | 2 | 331137.2388 | 639924.8013 | 971062.04 | 279.5621 | 306.4426 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.098625 | 304.0759 | 3 | 481648.4064 | 959887.2019 | 1441535.6083 | 280.8237 | 307.5892 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.098625 | 304.0759 | 4 | 685390.9057 | 1279849.6025 | 1965240.5082 | 282.0853 | 308.8656 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.098625 | 313.15 | 1 | 222094.5716 | 305965.1242 | 528059.6957 | 278.2453 | 314.4411 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.098625 | 313.15 | 2 | 314481.3134 | 611930.2483 | 926411.5617 | 279.4517 | 315.4151 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.098625 | 313.15 | 3 | 457421.8956 | 917895.3725 | 1375317.268 | 280.6581 | 316.5127 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.098625 | 313.15 | 4 | 650916.318 | 1223860.4966 | 1874776.8146 | 281.8645 | 317.734 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 285.9278 | 1 | 224176.124 | 409966.4878 | 634142.6118 | 282.5478 | 287.4628 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 285.9278 | 2 | 317428.7486 | 819932.9757 | 1137361.7242 | 284.1678 | 288.681 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 285.9278 | 3 | 461709.0227 | 1229899.4635 | 1691608.4862 | 285.7878 | 290.0227 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 285.9278 | 4 | 657016.9464 | 1639865.9513 | 2296882.8977 | 287.4078 | 291.4878 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 295.0019 | 1 | 242170.6357 | 378516.1995 | 620686.8353 | 282.4235 | 296.5097 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 295.0019 | 2 | 342908.6044 | 757032.3991 | 1099941.0035 | 283.9192 | 297.674 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 295.0019 | 3 | 498770.1881 | 1135548.5986 | 1634318.7867 | 285.415 | 298.9722 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 295.0019 | 4 | 709755.3867 | 1514064.7982 | 2223820.1849 | 286.9107 | 300.4043 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 304.0759 | 1 | 245651.0635 | 358764.6829 | 604415.7463 | 282.3455 | 305.549 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 304.0759 | 2 | 347836.818 | 717529.3657 | 1065366.1838 | 283.7631 | 306.6724 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 304.0759 | 3 | 505938.4131 | 1076294.0486 | 1582232.4617 | 285.1808 | 307.9321 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 304.0759 | 4 | 719955.8486 | 1435058.7315 | 2155014.5801 | 286.5985 | 309.3281 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 313.15 | 1 | 239041.2269 | 350711.9378 | 589753.1647 | 282.3136 | 314.592 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 313.15 | 2 | 338477.4263 | 701423.8756 | 1039901.3019 | 283.6995 | 315.6926 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 313.15 | 3 | 492324.9152 | 1052135.8134 | 1544460.7286 | 285.0853 | 316.9263 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.098625 | 313.15 | 4 | 700583.6934 | 1402847.7512 | 2103431.4446 | 286.4712 | 318.293 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 285.9278 | 1 | 214798.3165 | 424667.9768 | 639466.2933 | 286.4979 | 287.4757 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 285.9278 | 2 | 304149.9674 | 849335.9536 | 1153485.921 | 288.1791 | 288.72 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 285.9278 | 3 | 442394.6628 | 1274003.9304 | 1716398.5932 | 289.8604 | 290.0827 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 285.9278 | 4 | 629532.4028 | 1698671.9072 | 2328204.31 | 291.5416 | 291.5637 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 295.0019 | 1 | 239760.6791 | 399162.2199 | 638922.899 | 286.3969 | 296.554 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 295.0019 | 2 | 339496.1558 | 798324.4398 | 1137820.5956 | 287.9772 | 297.766 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 295.0019 | 3 | 493806.6858 | 1197486.6597 | 1691293.3455 | 289.5574 | 299.1106 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 295.0019 | 4 | 702692.269 | 1596648.8797 | 2299341.1487 | 291.1377 | 300.5878 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 304.0759 | 1 | 249504.8669 | 385355.2346 | 634860.1016 | 286.3423 | 305.6232 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 304.0759 | 2 | 353293.7239 | 770710.4693 | 1124004.1932 | 287.8679 | 306.8153 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 304.0759 | 3 | 513875.6359 | 1156065.7039 | 1669941.3398 | 289.3935 | 308.1459 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 304.0759 | 4 | 731250.6027 | 1541420.9385 | 2272671.5412 | 290.9191 | 309.6149 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 313.15 | 1 | 247663.899 | 383247.021 | 630910.92 | 286.3339 | 314.6926 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 313.15 | 2 | 350686.9515 | 766494.0419 | 1117180.9935 | 287.8512 | 315.8816 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 313.15 | 3 | 510084.0122 | 1149741.0629 | 1659825.0751 | 289.3684 | 317.2084 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.098625 | 313.15 | 4 | 725855.0811 | 1532988.0839 | 2258843.165 | 290.8857 | 318.673 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 285.9278 | 1 | 202353.3266 | 427157.7353 | 629511.0618 | 290.3994 | 287.4516 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 285.9278 | 2 | 286528.1194 | 854315.4706 | 1140843.5899 | 292.0933 | 288.6894 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 285.9278 | 3 | 416763.1904 | 1281473.2059 | 1698236.3962 | 293.7872 | 290.0387 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 285.9278 | 4 | 593058.5396 | 1708630.9412 | 2301689.4807 | 295.4811 | 291.4995 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 295.0019 | 1 | 232517.6483 | 407596.5098 | 640114.1581 | 290.3219 | 296.5569 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 295.0019 | 2 | 329240.1742 | 815193.0196 | 1144433.1938 | 291.9382 | 297.7821 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 295.0019 | 3 | 478889.0727 | 1222789.5294 | 1701678.6021 | 293.5545 | 299.1358 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 295.0019 | 4 | 681464.3438 | 1630386.0392 | 2311850.383 | 295.1708 | 300.6182 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 304.0759 | 1 | 247495.7211 | 399734.0559 | 647229.777 | 290.2907 | 305.6533 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 304.0759 | 2 | 350448.815 | 799468.1118 | 1149916.9269 | 291.8758 | 306.8785 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 304.0759 | 3 | 509737.636 | 1199202.1678 | 1708939.8038 | 293.461 | 308.2409 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 304.0759 | 4 | 725362.184 | 1598936.2237 | 2324298.4077 | 295.0461 | 309.7407 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 313.15 | 1 | 250129.7634 | 403570.3737 | 653700.137 | 290.3059 | 314.7483 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 313.15 | 2 | 354178.5644 | 807140.7473 | 1161319.3117 | 291.9063 | 315.9895 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 313.15 | 3 | 515162.6611 | 1210711.121 | 1725873.7821 | 293.5066 | 317.3699 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.098625 | 313.15 | 4 | 733082.0536 | 1614281.4946 | 2347363.5482 | 295.107 | 318.8895 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation