## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'M': 37.5 ton, 2.74 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 8a5c95f4-cd8c-459d-bdf4-02077b5790a7 |  | ✓
| data_timestamp | 2022-12-01T11:35Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'M' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 57921.0346 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.0056508 | 277.0389 | 0.0083679 | 285.9278 | 1 | 7369.2516 | 33280.139 | 40649.3906 | 278.4386 | 287.0875 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0083679 | 285.9278 | 2 | 14025.5431 | 66560.278 | 80585.821 | 279.8383 | 288.227 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0083679 | 285.9278 | 3 | 23980.4385 | 99840.417 | 123820.8555 | 281.238 | 289.4605 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0083679 | 285.9278 | 4 | 37233.9379 | 133120.556 | 170354.4939 | 282.6377 | 290.7881 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0083679 | 295.0019 | 1 | 8207.7262 | 31748.9745 | 39956.7007 | 278.3742 | 296.1459 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0083679 | 295.0019 | 2 | 15621.3717 | 63497.949 | 79119.3207 | 279.7095 | 297.2673 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0083679 | 295.0019 | 3 | 26708.9368 | 95246.9235 | 121955.8603 | 281.0448 | 298.4938 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0083679 | 295.0019 | 4 | 41470.4216 | 126995.898 | 168466.3196 | 282.3801 | 299.8255 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0083679 | 304.0759 | 1 | 9404.2865 | 29262.2173 | 38666.5037 | 278.2696 | 305.1866 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0083679 | 304.0759 | 2 | 17898.7274 | 58524.4346 | 76423.1619 | 279.5003 | 306.2712 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0083679 | 304.0759 | 3 | 30602.6889 | 87786.6518 | 118389.3407 | 280.731 | 307.4767 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0083679 | 304.0759 | 4 | 47516.1711 | 117048.8691 | 164565.0402 | 281.9617 | 308.8031 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0083679 | 313.15 | 1 | 10586.4598 | 25819.8673 | 36406.3272 | 278.1248 | 314.1992 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0083679 | 313.15 | 2 | 20148.7013 | 51639.7346 | 71788.4359 | 279.2108 | 315.2188 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0083679 | 313.15 | 3 | 34449.6245 | 77459.602 | 111909.2264 | 280.2967 | 316.375 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0083679 | 313.15 | 4 | 53489.2295 | 103279.4693 | 156768.6988 | 281.3826 | 317.6678 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 285.9278 | 1 | 7486.3801 | 37457.2592 | 44943.6393 | 282.5066 | 287.2101 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 285.9278 | 2 | 14248.4682 | 74914.5183 | 89162.9865 | 284.0854 | 288.4717 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 285.9278 | 3 | 24361.589 | 112371.7775 | 136733.3664 | 285.6642 | 289.8289 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 285.9278 | 4 | 37825.7425 | 149829.0366 | 187654.7791 | 287.2431 | 291.2817 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 295.0019 | 1 | 8371.6019 | 35948.2005 | 44319.8024 | 282.443 | 296.2709 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 295.0019 | 2 | 15933.2684 | 71896.401 | 87829.6694 | 283.9582 | 297.5167 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 295.0019 | 3 | 27242.2081 | 107844.6015 | 135086.8096 | 285.4734 | 298.8698 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 295.0019 | 4 | 42298.4211 | 143792.802 | 186091.223 | 286.9886 | 300.3302 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 304.0759 | 1 | 9766.029 | 33483.5491 | 43249.5782 | 282.3391 | 305.3183 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 304.0759 | 2 | 18587.2147 | 66967.0982 | 85554.3129 | 283.7504 | 306.5335 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 304.0759 | 3 | 31779.8431 | 100450.6473 | 132230.4905 | 285.1618 | 307.8743 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 304.0759 | 4 | 49343.9145 | 133934.1964 | 183278.1109 | 286.5731 | 309.3406 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 313.15 | 1 | 11310.5761 | 30063.305 | 41373.8811 | 282.1949 | 314.3423 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 313.15 | 2 | 21526.877 | 60126.61 | 81653.487 | 283.4621 | 315.5031 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 313.15 | 3 | 36805.9867 | 90189.915 | 126995.9016 | 284.7293 | 316.8098 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0083679 | 313.15 | 4 | 57147.905 | 120253.22 | 177401.125 | 285.9964 | 318.2623 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 285.9278 | 1 | 7585.8271 | 39521.1941 | 47107.0212 | 286.4856 | 287.2718 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 285.9278 | 2 | 14437.7408 | 79042.3883 | 93480.1291 | 288.1545 | 288.5948 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 285.9278 | 3 | 24685.2014 | 118563.5824 | 143248.7838 | 289.8234 | 290.0148 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 285.9278 | 4 | 38328.2089 | 158084.7765 | 196412.9855 | 291.4924 | 291.5316 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 295.0019 | 1 | 8401.1832 | 38034.2413 | 46435.4245 | 286.4228 | 296.3314 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 295.0019 | 2 | 15989.569 | 76068.4826 | 92058.0516 | 288.0289 | 297.6377 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 295.0019 | 3 | 27338.4691 | 114102.724 | 141441.193 | 289.6351 | 299.0517 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 295.0019 | 4 | 42447.8835 | 152136.9653 | 194584.8488 | 291.2412 | 300.5734 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 304.0759 | 1 | 9809.0043 | 35591.6958 | 45400.7001 | 286.3197 | 305.3801 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 304.0759 | 2 | 18669.0074 | 71183.3915 | 89852.3989 | 287.8226 | 306.657 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 304.0759 | 3 | 31919.6898 | 106775.0873 | 138694.7771 | 289.3256 | 308.06 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 304.0759 | 4 | 49561.0515 | 142366.7831 | 191927.8346 | 290.8286 | 309.5891 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 313.15 | 1 | 11463.5921 | 32193.5575 | 43657.1496 | 286.1762 | 314.4081 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 313.15 | 2 | 21818.1049 | 64387.115 | 86205.2199 | 287.5356 | 315.6343 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 313.15 | 3 | 37303.9191 | 96580.6725 | 133884.5916 | 288.8951 | 317.0083 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0083679 | 313.15 | 4 | 57921.0346 | 128774.23 | 186695.2646 | 290.2546 | 318.5302 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 285.9278 | 1 | 7802.2972 | 39471.9439 | 47274.2412 | 290.3752 | 287.2765 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 285.9278 | 2 | 14849.7381 | 78943.8879 | 93793.6259 | 292.0448 | 288.6038 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 285.9278 | 3 | 25389.6216 | 118415.8318 | 143805.4534 | 293.7144 | 290.0307 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 285.9278 | 4 | 39421.9477 | 157887.7758 | 197309.7235 | 295.384 | 291.5572 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 295.0019 | 1 | 8457.904 | 38007.097 | 46465.0009 | 290.3132 | 296.3323 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 295.0019 | 2 | 16097.5229 | 76014.1939 | 92111.7169 | 291.9209 | 297.6393 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 295.0019 | 3 | 27523.0454 | 114021.2909 | 141544.3363 | 293.5285 | 299.0547 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 295.0019 | 4 | 42734.4715 | 152028.3878 | 194762.8593 | 295.1361 | 300.5785 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 304.0759 | 1 | 9721.3754 | 35586.6573 | 45308.0326 | 290.2108 | 305.3774 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 304.0759 | 2 | 18502.2275 | 71173.3145 | 89675.542 | 291.7161 | 306.6519 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 304.0759 | 3 | 31634.5347 | 106759.9718 | 138394.5064 | 293.2214 | 308.0513 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 304.0759 | 4 | 49118.297 | 142346.629 | 191464.926 | 294.7266 | 309.5758 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 313.15 | 1 | 11260.4001 | 32210.6248 | 43471.0249 | 290.068 | 314.4027 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 313.15 | 2 | 21431.3793 | 64421.2496 | 85852.629 | 291.4305 | 315.6241 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 313.15 | 3 | 36642.7077 | 96631.8744 | 133274.5821 | 292.793 | 316.9907 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0083679 | 313.15 | 4 | 56894.3851 | 128842.4993 | 185736.8843 | 294.1554 | 318.5026 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation