## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'O': 225.0 ton, 2.39 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 5f1cd888-7227-4807-8f81-d4ce0701d1fc |  | ✓
| data_timestamp | 2022-12-01T11:35Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'O' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 381062.0331 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.033905 | 277.0389 | 0.05218 | 285.9278 | 1 | 44566.3585 | 193713.0171 | 238279.3757 | 278.3968 | 287.018 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05218 | 285.9278 | 2 | 88213.7978 | 387426.0343 | 475639.8321 | 279.7546 | 288.104 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05218 | 285.9278 | 3 | 152680.1231 | 581139.0514 | 733819.1746 | 281.1125 | 289.2853 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05218 | 285.9278 | 4 | 237965.3346 | 774852.0686 | 1012817.4031 | 282.4704 | 290.5618 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05218 | 295.0019 | 1 | 53443.4673 | 190437.7629 | 243881.2302 | 278.3738 | 296.1217 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05218 | 295.0019 | 2 | 105784.9772 | 380875.5259 | 486660.503 | 279.7087 | 297.2365 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05218 | 295.0019 | 3 | 183092.257 | 571313.2888 | 754405.5459 | 281.0436 | 298.4659 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05218 | 295.0019 | 4 | 285365.3069 | 761751.0518 | 1047116.3587 | 282.3785 | 299.8099 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05218 | 304.0759 | 1 | 61559.8785 | 181038.0281 | 242597.9066 | 278.3079 | 305.1935 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05218 | 304.0759 | 2 | 121850.4463 | 362076.0561 | 483926.5024 | 279.5769 | 306.3052 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05218 | 304.0759 | 3 | 210898.3131 | 543114.0842 | 754012.3973 | 280.8459 | 307.5493 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05218 | 304.0759 | 4 | 328703.4789 | 724152.1123 | 1052855.5912 | 282.115 | 308.926 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05218 | 313.15 | 1 | 67575.0727 | 165513.8125 | 233088.8852 | 278.1991 | 314.2272 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05218 | 313.15 | 2 | 133756.8066 | 331027.625 | 464784.4316 | 279.3593 | 315.298 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05218 | 313.15 | 3 | 231505.7985 | 496541.4376 | 728047.2361 | 280.5195 | 316.5146 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05218 | 313.15 | 4 | 360822.0485 | 662055.2501 | 1022877.2986 | 281.6797 | 317.8772 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 285.9278 | 1 | 45481.0651 | 211050.9087 | 256531.9738 | 282.4104 | 287.1015 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 285.9278 | 2 | 90024.3505 | 422101.8174 | 512126.1679 | 283.893 | 288.2709 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 285.9278 | 3 | 155813.8212 | 633152.7261 | 788966.5473 | 285.3757 | 289.5376 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 285.9278 | 4 | 242849.4773 | 844203.6348 | 1087053.1121 | 286.8583 | 290.9015 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 295.0019 | 1 | 54578.0365 | 208920.5042 | 263498.5407 | 282.3954 | 296.2118 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 295.0019 | 2 | 108030.7217 | 417841.0085 | 525871.7302 | 283.8631 | 297.4165 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 295.0019 | 3 | 186979.1837 | 626761.5127 | 813740.6964 | 285.3308 | 298.7383 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 295.0019 | 4 | 291423.4223 | 835682.0169 | 1127105.4392 | 286.7984 | 300.1772 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 304.0759 | 1 | 63372.4275 | 200665.6191 | 264038.0466 | 282.3374 | 305.2922 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 304.0759 | 2 | 125438.171 | 401331.2382 | 526769.4092 | 283.7471 | 306.5025 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 304.0759 | 3 | 217107.9341 | 601996.8573 | 819104.7914 | 285.1568 | 307.8492 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 304.0759 | 4 | 338381.7167 | 802662.4764 | 1141044.1931 | 286.5665 | 309.3322 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 313.15 | 1 | 70642.8123 | 186286.2533 | 256929.0656 | 282.2364 | 314.3374 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 313.15 | 2 | 139829.0317 | 372572.5065 | 512401.5383 | 283.5451 | 315.518 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 313.15 | 3 | 242015.5839 | 558858.7598 | 800874.3437 | 284.8537 | 316.8512 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05218 | 313.15 | 4 | 377202.4689 | 745145.0131 | 1122347.482 | 286.1624 | 318.3369 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 285.9278 | 1 | 46407.3078 | 218886.9464 | 265294.2542 | 286.3572 | 287.1416 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 285.9278 | 2 | 91857.7377 | 437773.8927 | 529631.6304 | 287.8978 | 288.351 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 285.9278 | 3 | 158987.0412 | 656660.8391 | 815647.8803 | 289.4383 | 289.6597 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 285.9278 | 4 | 247795.2183 | 875547.7855 | 1123343.0038 | 290.9789 | 291.0675 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 295.0019 | 1 | 55112.5807 | 217901.3916 | 273013.9724 | 286.3503 | 296.2555 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 295.0019 | 2 | 109088.7884 | 435802.7833 | 544891.5717 | 287.8839 | 297.5039 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 295.0019 | 3 | 188810.4816 | 653704.1749 | 842514.6565 | 289.4175 | 298.8705 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 295.0019 | 4 | 294277.6603 | 871605.5666 | 1165883.2269 | 290.9511 | 300.3553 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 304.0759 | 1 | 63799.467 | 210791.3562 | 274590.8233 | 286.3002 | 305.3408 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 304.0759 | 2 | 126283.445 | 421582.7125 | 547866.1574 | 287.7838 | 306.5997 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 304.0759 | 3 | 218570.9312 | 632374.0687 | 850944.9999 | 289.2674 | 307.9958 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 304.0759 | 4 | 340661.9258 | 843165.4249 | 1183827.3507 | 290.751 | 309.5293 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 313.15 | 1 | 71365.6349 | 197556.8401 | 268922.475 | 286.2071 | 314.3928 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 313.15 | 2 | 141259.7729 | 395113.6803 | 536373.4532 | 287.5975 | 315.6288 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 313.15 | 3 | 244491.9057 | 592670.5204 | 837162.4261 | 288.9879 | 317.0189 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05218 | 313.15 | 4 | 381062.0331 | 790227.3606 | 1171289.3937 | 290.3784 | 318.563 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 285.9278 | 1 | 47704.9068 | 217221.1302 | 264926.037 | 290.2369 | 287.1399 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 285.9278 | 2 | 94426.1802 | 434442.2604 | 528868.4406 | 291.7683 | 288.3476 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 285.9278 | 3 | 163432.4922 | 651663.3905 | 815095.8828 | 293.2996 | 289.6571 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 285.9278 | 4 | 254723.8429 | 868884.5207 | 1123608.3636 | 294.831 | 291.0687 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 295.0019 | 1 | 55582.6877 | 217380.4252 | 272963.1129 | 290.238 | 296.2552 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 295.0019 | 2 | 110019.3092 | 434760.8504 | 544780.1596 | 291.7705 | 297.5033 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 295.0019 | 3 | 190421.0237 | 652141.2755 | 842562.2992 | 293.303 | 298.8707 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 295.0019 | 4 | 296787.8311 | 869521.7007 | 1166309.5318 | 294.8355 | 300.3572 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 304.0759 | 1 | 63552.3527 | 211415.2395 | 274967.5922 | 290.196 | 305.3426 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 304.0759 | 2 | 125794.3116 | 422830.479 | 548624.7907 | 291.6864 | 306.6032 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 304.0759 | 3 | 217724.341 | 634245.7185 | 851970.0595 | 293.1768 | 308.0006 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 304.0759 | 4 | 339342.4408 | 845660.958 | 1185003.3989 | 294.6673 | 309.5347 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 313.15 | 1 | 70630.6637 | 199325.5731 | 269956.2368 | 290.1108 | 314.3976 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 313.15 | 2 | 139804.985 | 398651.1463 | 538456.1313 | 291.516 | 315.6384 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 313.15 | 3 | 241973.964 | 597976.7194 | 839950.6834 | 292.9212 | 317.0318 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05218 | 313.15 | 4 | 377137.6006 | 797302.2926 | 1174439.8931 | 294.3264 | 318.5776 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation