## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'P': 600.0 ton, 2.06 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 0b28764a-f376-4018-8fa9-6ddb944783b5 |  | ✓
| data_timestamp | 2022-12-01T11:35Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'P' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 1127059.3806 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.090412 | 277.0389 | 0.14581 | 285.9278 | 1 | 147359.5944 | 523756.3246 | 671115.919 | 278.4157 | 287.0266 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14581 | 285.9278 | 2 | 286412.3941 | 1047512.6492 | 1333925.0432 | 279.7924 | 288.1119 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14581 | 285.9278 | 3 | 498749.6132 | 1571268.9738 | 2070018.5869 | 281.1692 | 289.3172 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14581 | 285.9278 | 4 | 784371.2517 | 2095025.2984 | 2879396.5501 | 282.5459 | 290.6424 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14581 | 295.0019 | 1 | 174051.8962 | 514631.0345 | 688682.9307 | 278.3917 | 296.1335 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14581 | 295.0019 | 2 | 338292.3283 | 1029262.0691 | 1367554.3973 | 279.7444 | 297.249 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14581 | 295.0019 | 3 | 589091.7131 | 1543893.1036 | 2132984.8167 | 281.0972 | 298.5068 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14581 | 295.0019 | 4 | 926450.0506 | 2058524.1381 | 2984974.1887 | 282.45 | 299.9068 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14581 | 304.0759 | 1 | 195381.0762 | 490390.0049 | 685771.0811 | 278.3279 | 305.2064 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14581 | 304.0759 | 2 | 379748.343 | 980780.0098 | 1360528.3528 | 279.617 | 306.3188 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14581 | 304.0759 | 3 | 661281.9245 | 1471170.0148 | 2132451.9393 | 280.9061 | 307.5913 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14581 | 304.0759 | 4 | 1039981.8209 | 1961560.0197 | 3001541.8406 | 282.1951 | 309.024 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14581 | 313.15 | 1 | 208372.5344 | 451033.2358 | 659405.7702 | 278.2245 | 314.2406 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14581 | 313.15 | 2 | 404998.9191 | 902066.4715 | 1307065.3906 | 279.4101 | 315.3117 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14581 | 313.15 | 3 | 705252.4905 | 1353099.7073 | 2058352.1978 | 280.5957 | 316.5542 | 15000 | 15000 | 0 | 0
0.090412 | 277.0389 | 0.14581 | 313.15 | 4 | 1109133.2487 | 1804132.943 | 2913266.1917 | 281.7813 | 317.9681 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 285.9278 | 1 | 143827.0679 | 558000.8373 | 701827.9051 | 282.3978 | 287.0769 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 285.9278 | 2 | 279546.4728 | 1116001.6746 | 1395548.1473 | 283.8677 | 288.2128 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 285.9278 | 3 | 486793.5119 | 1674002.5118 | 2160796.0237 | 285.3377 | 289.4658 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 285.9278 | 4 | 765568.1853 | 2232003.3491 | 2997571.5344 | 286.8077 | 290.8359 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 295.0019 | 1 | 171567.5557 | 553194.3299 | 724761.8857 | 282.3851 | 296.1928 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 295.0019 | 2 | 333463.6919 | 1106388.6599 | 1439852.3518 | 283.8424 | 297.3678 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 295.0019 | 3 | 580683.2762 | 1659582.9898 | 2240266.266 | 285.2997 | 298.6831 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 295.0019 | 4 | 913226.3087 | 2212777.3198 | 3126003.6284 | 286.757 | 300.1386 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 304.0759 | 1 | 195114.7692 | 533272.0831 | 728386.8523 | 282.3326 | 305.2767 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 304.0759 | 2 | 379230.7409 | 1066544.1661 | 1445774.9071 | 283.7374 | 306.4593 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 304.0759 | 3 | 660380.5885 | 1599816.2492 | 2260196.8377 | 285.1423 | 307.8019 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 304.0759 | 4 | 1038564.3119 | 2133088.3322 | 3171652.6441 | 286.5471 | 309.3045 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 313.15 | 1 | 211740.3115 | 498234.0966 | 709974.4081 | 282.2403 | 314.3242 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 313.15 | 2 | 411544.6286 | 996468.1933 | 1408012.8218 | 283.5528 | 315.4786 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 313.15 | 3 | 716650.9849 | 1494702.2899 | 2211353.2748 | 284.8654 | 316.8072 | 15000 | 15000 | 0 | 0
0.090412 | 280.9278 | 0.14581 | 313.15 | 4 | 1127059.3806 | 1992936.3865 | 3119995.7671 | 286.1779 | 318.31 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 285.9278 | 1 | 142442.7855 | 572188.54 | 714631.3255 | 286.3268 | 287.0979 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 285.9278 | 2 | 276855.9413 | 1144377.08 | 1421233.0213 | 287.837 | 288.2549 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 285.9278 | 3 | 482108.3043 | 1716565.6201 | 2198673.9243 | 289.3472 | 289.5278 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 285.9278 | 4 | 758199.8744 | 2288754.1601 | 3046954.0345 | 290.8574 | 290.9168 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 295.0019 | 1 | 169714.6264 | 571700.8154 | 741415.4418 | 286.3256 | 296.2202 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 295.0019 | 2 | 329862.2845 | 1143401.6308 | 1473263.9153 | 287.8344 | 297.4228 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 295.0019 | 3 | 574411.8976 | 1715102.4463 | 2289514.3439 | 289.3433 | 298.764 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 295.0019 | 4 | 903363.4658 | 2286803.2617 | 3190166.7275 | 290.8522 | 300.244 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 304.0759 | 1 | 193594.9752 | 556097.3513 | 749692.3264 | 286.2844 | 305.3118 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 304.0759 | 2 | 376276.8251 | 1112194.7025 | 1488471.5276 | 287.7521 | 306.5297 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 304.0759 | 3 | 655236.7315 | 1668292.0538 | 2323528.7853 | 289.2198 | 307.9063 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 304.0759 | 4 | 1030474.6944 | 2224389.4051 | 3254864.0995 | 290.6875 | 309.4416 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 313.15 | 1 | 211601.6383 | 525378.1476 | 736979.7858 | 286.2033 | 314.3689 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 313.15 | 2 | 411275.0992 | 1050756.2951 | 1462031.3943 | 287.5899 | 315.568 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 313.15 | 3 | 716181.6349 | 1576134.4427 | 2292316.0776 | 288.9765 | 316.9411 | 15000 | 15000 | 0 | 0
0.090412 | 284.8167 | 0.14581 | 313.15 | 4 | 1126321.2454 | 2101512.5902 | 3227833.8356 | 290.3632 | 318.4883 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 285.9278 | 1 | 144366.2463 | 566319.4328 | 710685.6791 | 290.2027 | 287.0914 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 285.9278 | 2 | 280594.4356 | 1132638.8656 | 1413233.3013 | 291.6999 | 288.2418 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 285.9278 | 3 | 488618.4018 | 1698958.2985 | 2187576.7002 | 293.197 | 289.5096 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 285.9278 | 4 | 768438.1447 | 2265277.7313 | 3033715.8759 | 294.6942 | 290.8951 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 295.0019 | 1 | 170113.1622 | 570150.4909 | 740263.6532 | 290.2128 | 296.2183 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 295.0019 | 2 | 330636.8903 | 1140300.9819 | 1470937.8722 | 291.7201 | 297.4189 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 295.0019 | 3 | 575760.7721 | 1710451.4728 | 2286212.245 | 293.2274 | 298.7586 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 295.0019 | 4 | 905484.8076 | 2280601.9638 | 3186086.7714 | 294.7347 | 300.2373 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 304.0759 | 1 | 192902.3033 | 558865.8095 | 751768.1128 | 290.183 | 305.3152 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 304.0759 | 2 | 374930.5278 | 1117731.619 | 1492662.1468 | 291.6605 | 306.5366 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 304.0759 | 3 | 652892.3314 | 1676597.4286 | 2329489.76 | 293.1379 | 307.9161 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 304.0759 | 4 | 1026787.7141 | 2235463.2381 | 3262250.9522 | 294.6154 | 309.4538 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 313.15 | 1 | 210497.6789 | 532465.3885 | 742963.0675 | 290.1132 | 314.3787 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 313.15 | 2 | 409129.4118 | 1064930.7771 | 1474060.1889 | 291.5209 | 315.5879 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 313.15 | 3 | 712445.2017 | 1597396.1656 | 2309841.3673 | 292.9285 | 316.9701 | 15000 | 15000 | 0 | 0
0.090412 | 288.7056 | 0.14581 | 313.15 | 4 | 1120445.0487 | 2129861.5542 | 3250306.6029 | 294.3362 | 318.5255 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation