## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'R': 75.0 ton, 2.44 COP liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 5813ab96-0e75-4227-99b1-3ad492d0c671 |  | ✓
| data_timestamp | 2022-12-01T11:35Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'R' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 113923.3125 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.011302 | 277.0389 | 0.017283 | 285.9278 | 1 | 13725.6206 | 67122.1555 | 80847.7761 | 278.4504 | 287.0446 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017283 | 285.9278 | 2 | 30195.6789 | 134244.3111 | 164439.9899 | 279.8619 | 288.1994 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017283 | 285.9278 | 3 | 55994.0892 | 201366.4666 | 257360.5558 | 281.2734 | 289.483 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017283 | 285.9278 | 4 | 91120.8514 | 268488.6222 | 359609.4736 | 282.6849 | 290.8954 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017283 | 295.0019 | 1 | 15170.5543 | 63238.0877 | 78408.642 | 278.3687 | 296.0889 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017283 | 295.0019 | 2 | 33374.4609 | 126476.1755 | 159850.6363 | 279.6986 | 297.2179 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017283 | 295.0019 | 3 | 61888.7406 | 189714.2632 | 251603.0038 | 281.0284 | 298.4899 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017283 | 295.0019 | 4 | 100713.3936 | 252952.3509 | 353665.7445 | 282.3582 | 299.9049 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017283 | 304.0759 | 1 | 15534.8149 | 59495.187 | 75030.0019 | 278.29 | 305.1195 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017283 | 304.0759 | 2 | 34175.816 | 118990.374 | 153166.19 | 279.5411 | 306.2062 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017283 | 304.0759 | 3 | 63374.7529 | 178485.5611 | 241860.3139 | 280.7923 | 307.4398 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017283 | 304.0759 | 4 | 103131.6257 | 237980.7481 | 341112.3738 | 282.0434 | 308.8202 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017283 | 313.15 | 1 | 14986.7676 | 55893.4534 | 70880.221 | 278.2143 | 314.139 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017283 | 313.15 | 2 | 32970.1392 | 111786.9068 | 144757.046 | 279.3897 | 315.1698 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017283 | 313.15 | 3 | 61138.9769 | 167680.3602 | 228819.3372 | 280.565 | 316.3427 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017283 | 313.15 | 4 | 99493.2808 | 223573.8137 | 323067.0945 | 281.7404 | 317.6578 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 285.9278 | 1 | 13805.6197 | 73346.8557 | 87152.4754 | 282.4736 | 287.1317 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 285.9278 | 2 | 30371.673 | 146693.7114 | 177065.3844 | 284.0193 | 288.3738 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 285.9278 | 3 | 56320.4482 | 220040.5671 | 276361.0153 | 285.5651 | 289.7454 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 285.9278 | 4 | 91651.9453 | 293387.4228 | 385039.368 | 287.1109 | 291.2467 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 295.0019 | 1 | 15706.0343 | 70226.021 | 85932.0553 | 282.4078 | 296.1932 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 295.0019 | 2 | 34552.49 | 140452.0421 | 175004.5321 | 283.8878 | 297.428 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 295.0019 | 3 | 64073.2476 | 210678.0631 | 274751.3107 | 285.3678 | 298.8109 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 295.0019 | 4 | 104268.307 | 280904.0841 | 385172.3911 | 286.8478 | 300.3417 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 304.0759 | 1 | 16467.4059 | 67246.3535 | 83713.7594 | 282.345 | 305.2402 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 304.0759 | 2 | 36227.4695 | 134492.7069 | 170720.1765 | 283.7622 | 306.4503 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 304.0759 | 3 | 67179.2865 | 201739.0604 | 268918.3469 | 285.1794 | 307.8161 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 304.0759 | 4 | 109322.8566 | 268985.4139 | 378308.2705 | 286.5966 | 309.3375 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 313.15 | 1 | 16225.6071 | 64407.853 | 80633.4601 | 282.2852 | 314.2751 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 313.15 | 2 | 35695.5241 | 128815.7061 | 164511.2302 | 283.6426 | 315.4454 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 313.15 | 3 | 66192.8606 | 193223.5591 | 259416.4197 | 285 | 316.7697 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017283 | 313.15 | 4 | 107717.6164 | 257631.4121 | 365349.0285 | 286.3573 | 318.2478 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 285.9278 | 1 | 13653.8467 | 76019.3304 | 89673.1771 | 286.4218 | 287.1665 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 285.9278 | 2 | 30037.7799 | 152038.6609 | 182076.4408 | 288.0269 | 288.443 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 285.9278 | 3 | 55701.2853 | 228057.9913 | 283759.2767 | 289.632 | 289.8476 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 285.9278 | 4 | 90644.363 | 304077.3218 | 394721.6848 | 291.2371 | 291.3805 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 295.0019 | 1 | 15841.2209 | 73661.7289 | 89502.9499 | 286.372 | 296.2427 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 295.0019 | 2 | 34849.8939 | 147323.4579 | 182173.3518 | 287.9273 | 297.5274 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 295.0019 | 3 | 64624.7456 | 220985.1868 | 285609.9325 | 289.4826 | 298.9614 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 295.0019 | 4 | 105165.7762 | 294646.9158 | 399812.6919 | 291.0379 | 300.5446 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 304.0759 | 1 | 16882.7359 | 71445.2945 | 88328.0305 | 286.3252 | 305.3044 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 304.0759 | 2 | 37141.1748 | 142890.5891 | 180031.7639 | 287.8337 | 306.5798 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 304.0759 | 3 | 68873.638 | 214335.8836 | 283209.5216 | 289.3422 | 308.0148 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 304.0759 | 4 | 112080.1255 | 285781.1782 | 397861.3036 | 290.8507 | 309.6094 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 313.15 | 1 | 16881.7714 | 69370.0272 | 86251.7986 | 286.2814 | 314.3535 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 313.15 | 2 | 37139.0528 | 138740.0545 | 175879.1073 | 287.7461 | 315.6041 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 313.15 | 3 | 68869.703 | 208110.0817 | 276979.7848 | 289.2108 | 317.0147 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017283 | 313.15 | 4 | 112073.722 | 277480.109 | 389553.831 | 290.6755 | 318.5855 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 285.9278 | 1 | 13423.4256 | 75139.5798 | 88563.0054 | 290.2947 | 287.1512 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 285.9278 | 2 | 29530.865 | 150279.1596 | 179810.0246 | 291.8839 | 288.4117 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 285.9278 | 3 | 54761.2755 | 225418.7395 | 280180.0149 | 293.473 | 289.7982 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 285.9278 | 4 | 89114.6569 | 300558.3193 | 389672.9762 | 295.0622 | 291.3107 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 295.0019 | 1 | 15746.5692 | 73545.2115 | 89291.7807 | 290.261 | 296.2397 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 295.0019 | 2 | 34641.6648 | 147090.4229 | 181732.0878 | 291.8164 | 297.5213 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 295.0019 | 3 | 64238.611 | 220635.6344 | 284874.2454 | 293.3718 | 298.9512 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 295.0019 | 4 | 104537.4078 | 294180.8459 | 398718.2537 | 294.9273 | 300.5295 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 304.0759 | 1 | 16968.5907 | 72092.0102 | 89060.6009 | 290.2303 | 305.3146 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 304.0759 | 2 | 37330.051 | 144184.0204 | 181514.0714 | 291.7549 | 306.6005 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 304.0759 | 3 | 69223.8851 | 216276.0307 | 285499.9157 | 293.2796 | 308.0467 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 304.0759 | 4 | 112650.093 | 288368.0409 | 401018.1338 | 294.8043 | 309.6533 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 313.15 | 1 | 17160.377 | 70779.9761 | 87940.353 | 290.2025 | 314.377 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 313.15 | 2 | 37751.9712 | 141559.9522 | 179311.9234 | 291.6995 | 315.652 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 313.15 | 3 | 70006.283 | 212339.9282 | 282346.2113 | 293.1964 | 317.0896 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017283 | 313.15 | 4 | 113923.3125 | 283119.9043 | 397043.2168 | 294.6933 | 318.69 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation