## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'T': 400.0 ton, 2.06 COP liquid-cooled, centrifugal compressor chiller |  | ✓
| id | d1e081fb-cf86-4dcf-80cc-f3dd524cf6ff |  | ✓
| data_timestamp | 2022-12-01T11:35Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'T' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 706885.191 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.060275 | 277.0389 | 0.097206 | 285.9278 | 1 | 98172.6657 | 374117.1568 | 472289.8225 | 278.514 | 287.0877 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.097206 | 285.9278 | 2 | 203783.5588 | 748234.3136 | 952017.8725 | 279.9891 | 288.266 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.097206 | 285.9278 | 3 | 364990.4877 | 1122351.4705 | 1487341.9582 | 281.4643 | 289.5808 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.097206 | 285.9278 | 4 | 581793.4523 | 1496468.6273 | 2078262.0796 | 282.9394 | 291.0321 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.097206 | 295.0019 | 1 | 110325.474 | 347710.8853 | 458036.3593 | 278.4099 | 296.1308 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.097206 | 295.0019 | 2 | 229009.9546 | 695421.7706 | 924431.7252 | 279.7809 | 297.2804 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.097206 | 295.0019 | 3 | 410172.7122 | 1043132.6558 | 1453305.368 | 281.1519 | 298.584 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.097206 | 295.0019 | 4 | 653813.7467 | 1390843.5411 | 2044657.2878 | 282.5229 | 300.0416 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.097206 | 304.0759 | 1 | 109138.6425 | 312443.663 | 421582.3054 | 278.2708 | 305.1184 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.097206 | 304.0759 | 2 | 226546.3691 | 624887.3259 | 851433.695 | 279.5028 | 306.1813 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.097206 | 304.0759 | 3 | 405760.2597 | 937330.9889 | 1343091.2486 | 280.7347 | 307.3971 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.097206 | 304.0759 | 4 | 646780.3142 | 1249774.6519 | 1896554.966 | 281.9667 | 308.7657 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.097206 | 313.15 | 1 | 96180.0926 | 268315.4899 | 364495.5825 | 278.0968 | 314.0542 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.097206 | 313.15 | 2 | 199647.4417 | 536630.9798 | 736278.4215 | 279.1548 | 314.9765 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.097206 | 313.15 | 3 | 357582.4151 | 804946.4696 | 1162528.8847 | 280.2127 | 316.034 | 15000 | 15000 | 0 | 0
0.060275 | 277.0389 | 0.097206 | 313.15 | 4 | 569985.0127 | 1073261.9595 | 1643246.9722 | 281.2707 | 317.2265 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 285.9278 | 1 | 95969.2104 | 403033.7018 | 499002.9123 | 282.5204 | 287.1534 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 285.9278 | 2 | 199209.6995 | 806067.4037 | 1005277.1032 | 284.113 | 288.3968 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 285.9278 | 3 | 356798.3885 | 1209101.1055 | 1565899.494 | 285.7056 | 289.7737 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 285.9278 | 4 | 568735.2772 | 1612134.8073 | 2180870.0846 | 287.2982 | 291.2841 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 295.0019 | 1 | 112865.914 | 384483.1472 | 497349.0611 | 282.4471 | 296.2277 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 295.0019 | 2 | 234283.3156 | 768966.2943 | 1003249.6099 | 283.9664 | 297.4747 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 295.0019 | 3 | 419617.6674 | 1153449.4415 | 1573067.1089 | 285.4857 | 298.8792 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 295.0019 | 4 | 668868.9695 | 1537932.5886 | 2206801.5581 | 287.005 | 300.4413 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 304.0759 | 1 | 116449.6527 | 357071.6417 | 473521.2944 | 282.3388 | 305.2468 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 304.0759 | 2 | 241722.3213 | 714143.2834 | 955865.6047 | 283.7498 | 306.4396 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 304.0759 | 3 | 432941.4426 | 1071214.9251 | 1504156.3677 | 285.1607 | 307.7954 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 304.0759 | 4 | 690107.0166 | 1428286.5668 | 2118393.5834 | 286.5717 | 309.3142 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 313.15 | 1 | 107734.7425 | 320799.1855 | 428533.9279 | 282.1954 | 314.2131 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 313.15 | 2 | 223632.2001 | 641598.3709 | 865230.5711 | 283.4631 | 315.2964 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 313.15 | 3 | 400540.7809 | 962397.5564 | 1362938.3373 | 284.7307 | 316.5311 | 15000 | 15000 | 0 | 0
0.060275 | 280.9278 | 0.097206 | 313.15 | 4 | 638460.4848 | 1283196.7419 | 1921657.2267 | 285.9984 | 317.9172 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 285.9278 | 1 | 91854.3482 | 413419.9032 | 505274.2514 | 286.4534 | 287.1688 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 285.9278 | 2 | 190668.2052 | 826839.8064 | 1017508.0116 | 288.0901 | 288.4268 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 285.9278 | 3 | 341499.9797 | 1240259.7096 | 1581759.6894 | 289.7268 | 289.8127 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 285.9278 | 4 | 544349.6717 | 1653679.6129 | 2198029.2846 | 291.3635 | 291.3262 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 295.0019 | 1 | 112027.1982 | 402725.0654 | 514752.2636 | 286.411 | 296.2706 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 295.0019 | 2 | 232542.3372 | 805450.1308 | 1037992.468 | 288.0054 | 297.5603 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 295.0019 | 3 | 416499.4544 | 1208175.1962 | 1624674.6506 | 289.5998 | 299.0064 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 295.0019 | 4 | 663898.5498 | 1610900.2616 | 2274798.8114 | 291.1941 | 300.6089 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 304.0759 | 1 | 119280.826 | 383169.2768 | 502450.1028 | 286.3336 | 305.3184 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 304.0759 | 2 | 247599.1769 | 766338.5536 | 1013937.7305 | 287.8506 | 306.5832 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 304.0759 | 3 | 443467.2986 | 1149507.8304 | 1592975.129 | 289.3675 | 308.015 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 304.0759 | 4 | 706885.191 | 1532677.1072 | 2239562.2982 | 290.8844 | 309.6139 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 313.15 | 1 | 114075.9421 | 354752.5374 | 468828.4795 | 286.2211 | 314.3131 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 313.15 | 2 | 236795.0518 | 709505.0749 | 946300.1266 | 287.6256 | 315.4976 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 313.15 | 3 | 424116.3611 | 1064257.6123 | 1488373.9734 | 289.03 | 316.8423 | 15000 | 15000 | 0 | 0
0.060275 | 284.8167 | 0.097206 | 313.15 | 4 | 676039.8702 | 1419010.1497 | 2095050.0199 | 290.4344 | 318.3473 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 285.9278 | 1 | 86974.4004 | 405275.761 | 492250.1613 | 290.3127 | 287.1368 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 285.9278 | 2 | 180538.5715 | 810551.5219 | 991090.0935 | 291.9198 | 288.3619 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 285.9278 | 3 | 323357.1033 | 1215827.2829 | 1539184.3862 | 293.5269 | 289.7081 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 285.9278 | 4 | 515429.9955 | 1621103.0438 | 2136533.0394 | 295.134 | 291.1752 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 295.0019 | 1 | 109121.7426 | 402436.64 | 511558.3826 | 290.3014 | 296.2628 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 295.0019 | 2 | 226511.2889 | 804873.28 | 1031384.5689 | 291.8973 | 297.544 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 295.0019 | 3 | 405697.4286 | 1207309.92 | 1613007.3486 | 293.4931 | 298.9776 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 295.0019 | 4 | 646680.1617 | 1609746.56 | 2256426.7217 | 295.089 | 300.5636 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 304.0759 | 1 | 119110.673 | 390736.5683 | 509847.2413 | 290.255 | 305.3367 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 304.0759 | 2 | 247245.979 | 781473.1365 | 1028719.1155 | 291.8045 | 306.6197 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 304.0759 | 3 | 442834.6966 | 1172209.7048 | 1615044.4014 | 293.3539 | 308.0696 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 304.0759 | 4 | 705876.826 | 1562946.2731 | 2268823.099 | 294.9034 | 309.6862 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 313.15 | 1 | 116848.2967 | 370175.5458 | 487023.8425 | 290.1735 | 314.3582 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 313.15 | 2 | 242549.8134 | 740351.0915 | 982900.9049 | 291.6414 | 315.5884 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 313.15 | 3 | 434423.5384 | 1110526.6373 | 1544950.1757 | 293.1093 | 316.9827 | 15000 | 15000 | 0 | 0
0.060275 | 288.7056 | 0.097206 | 313.15 | 4 | 692469.4716 | 1480702.183 | 2173171.6547 | 294.5773 | 318.5411 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation