## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'V': 75.0 ton, 2.78 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | bcc86e2e-7cf6-4771-aeb3-f666b5ca64e7 |  | ✓
| data_timestamp | 2022-12-01T11:35Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'V' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 115326.3634 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.011302 | 277.0389 | 0.016677 | 285.9278 | 1 | 26645.2857 | 67088.7666 | 93734.0523 | 278.4497 | 287.2696 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.016677 | 285.9278 | 2 | 37549.4902 | 134177.5332 | 171727.0234 | 279.8605 | 288.3861 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.016677 | 285.9278 | 3 | 52667.8972 | 201266.2998 | 253934.197 | 281.2713 | 289.5629 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.016677 | 285.9278 | 4 | 72000.5066 | 268355.0664 | 340355.573 | 282.6821 | 290.8 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.016677 | 295.0019 | 1 | 30041.466 | 63679.592 | 93721.058 | 278.378 | 296.3483 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.016677 | 295.0019 | 2 | 42335.5091 | 127359.1841 | 169694.6931 | 279.7171 | 297.4398 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.016677 | 295.0019 | 3 | 59380.8924 | 191038.7761 | 250419.6685 | 281.0563 | 298.5995 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.016677 | 295.0019 | 4 | 81177.616 | 254718.3681 | 335895.9842 | 282.3954 | 299.8275 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.016677 | 304.0759 | 1 | 34692.5966 | 58228.9239 | 92921.5205 | 278.2634 | 305.4152 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.016677 | 304.0759 | 2 | 48890.0488 | 116457.8478 | 165347.8966 | 279.4879 | 306.459 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.016677 | 304.0759 | 3 | 68574.4614 | 174686.7717 | 243261.233 | 280.7124 | 307.582 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.016677 | 304.0759 | 4 | 93745.8342 | 232915.6956 | 326661.5297 | 281.9369 | 308.784 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.016677 | 313.15 | 1 | 39030.5426 | 50736.7622 | 89767.3048 | 278.1058 | 314.448 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.016677 | 313.15 | 2 | 55003.2376 | 101473.5244 | 156476.762 | 279.1728 | 315.4126 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.016677 | 313.15 | 3 | 77148.9798 | 152210.2866 | 229359.2664 | 280.2397 | 316.4664 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.016677 | 313.15 | 4 | 105467.7693 | 202947.0488 | 308414.8181 | 281.3067 | 317.6095 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 285.9278 | 1 | 26928.8815 | 75694.8568 | 102623.7382 | 282.523 | 287.3969 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 285.9278 | 2 | 37949.1436 | 151389.7135 | 189338.8571 | 284.1183 | 288.6382 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 285.9278 | 3 | 53228.4615 | 227084.5703 | 280313.0318 | 285.7136 | 289.9405 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 285.9278 | 4 | 72766.8351 | 302779.4271 | 375546.2622 | 287.3088 | 291.3038 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 295.0019 | 1 | 30601.5444 | 72332.2208 | 102933.7652 | 282.4522 | 296.4806 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 295.0019 | 2 | 43124.7917 | 144664.4416 | 187789.2333 | 283.9766 | 297.6997 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 295.0019 | 3 | 60487.9609 | 216996.6624 | 277484.6233 | 285.501 | 298.9883 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 295.0019 | 4 | 82691.052 | 289328.8832 | 372019.9352 | 287.0254 | 300.3465 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 304.0759 | 1 | 36129.44 | 66928.0913 | 103057.5313 | 282.3383 | 305.5613 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 304.0759 | 2 | 50914.9 | 133856.1825 | 184771.0826 | 283.7488 | 306.739 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 304.0759 | 3 | 71414.5706 | 200784.2738 | 272198.8444 | 285.1593 | 307.9991 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 304.0759 | 4 | 97628.4517 | 267712.3651 | 365340.8168 | 286.5698 | 309.3415 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 313.15 | 1 | 41995.9316 | 59482.4682 | 101478.3997 | 282.1814 | 314.6173 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 313.15 | 2 | 59182.1699 | 118964.9364 | 178147.1062 | 283.435 | 315.7259 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 313.15 | 3 | 83010.4595 | 178447.4045 | 261457.8641 | 284.6885 | 316.9305 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.016677 | 313.15 | 4 | 113480.8006 | 237929.8727 | 351410.6733 | 285.9421 | 318.2312 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 285.9278 | 1 | 27203.6028 | 79863.1583 | 107066.7611 | 286.5029 | 287.4605 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 285.9278 | 2 | 38336.2907 | 159726.3167 | 198062.6074 | 288.1892 | 288.7631 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 285.9278 | 3 | 53771.4842 | 239589.475 | 293360.9592 | 289.8754 | 290.1273 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 285.9278 | 4 | 73509.1832 | 319452.6333 | 392961.8165 | 291.5617 | 291.5531 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 295.0019 | 1 | 30669.3266 | 76547.061 | 107216.3876 | 286.4329 | 296.5422 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 295.0019 | 2 | 43220.3127 | 153094.1219 | 196314.4347 | 288.0491 | 297.8222 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 295.0019 | 3 | 60621.9412 | 229641.1829 | 290263.1241 | 289.6654 | 299.1719 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 295.0019 | 4 | 82874.212 | 306188.2439 | 389062.4559 | 291.2816 | 300.5913 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 304.0759 | 1 | 36316.1453 | 71189.4701 | 107505.6153 | 286.3198 | 305.6254 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 304.0759 | 2 | 51178.0118 | 142378.9401 | 193556.9519 | 287.8229 | 306.8656 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 304.0759 | 3 | 71783.618 | 213568.4102 | 285352.0282 | 289.326 | 308.1886 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 304.0759 | 4 | 98132.964 | 284757.8802 | 382890.8442 | 290.8291 | 309.5944 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 313.15 | 1 | 42678.9205 | 63790.3856 | 106469.3061 | 286.1636 | 314.6895 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 313.15 | 2 | 60144.6623 | 127580.7711 | 187725.4335 | 287.5105 | 315.8644 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 313.15 | 3 | 84360.4766 | 191371.1567 | 275731.6334 | 288.8573 | 317.1369 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.016677 | 313.15 | 4 | 115326.3634 | 255161.5423 | 370487.9057 | 290.2042 | 318.507 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 285.9278 | 1 | 27999.4941 | 79593.6713 | 107593.1655 | 290.3889 | 287.468 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 285.9278 | 2 | 39457.8893 | 159187.3426 | 198645.2319 | 292.0723 | 288.7714 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 285.9278 | 3 | 55344.6677 | 238781.0139 | 294125.6816 | 293.7556 | 290.1383 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 285.9278 | 4 | 75659.8292 | 318374.6852 | 394034.5145 | 295.439 | 291.5685 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 295.0019 | 1 | 30875.4675 | 76324.1126 | 107199.58 | 290.3198 | 296.5419 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 295.0019 | 2 | 43510.8138 | 152648.2251 | 196159.0389 | 291.934 | 297.82 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 295.0019 | 3 | 61029.4056 | 228972.3377 | 290001.7433 | 293.5482 | 299.1681 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 295.0019 | 4 | 83431.2429 | 305296.4502 | 388727.6931 | 295.1624 | 300.5865 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 304.0759 | 1 | 35983.978 | 71013.0602 | 106997.0382 | 290.2074 | 305.618 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 304.0759 | 2 | 50709.9097 | 142026.1205 | 192736.0301 | 291.7093 | 306.8538 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 304.0759 | 3 | 71127.0458 | 213039.1807 | 284166.2265 | 293.2112 | 308.1715 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 304.0759 | 4 | 97235.3862 | 284052.241 | 381287.6272 | 294.7131 | 309.5713 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 313.15 | 1 | 41911.3855 | 63660.5144 | 105571.8999 | 290.0519 | 314.6765 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 313.15 | 2 | 59063.0246 | 127321.0287 | 186384.0533 | 291.3983 | 315.845 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 313.15 | 3 | 82843.3432 | 190981.5431 | 273824.8863 | 292.7447 | 317.1093 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.016677 | 313.15 | 4 | 113252.3415 | 254642.0575 | 367894.399 | 294.0911 | 318.4695 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation