## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'X': 225.0 ton, 2.52 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 109ceed9-dc6e-4551-bb45-bf3cc6ea5495 |  | ✓
| data_timestamp | 2022-12-01T11:35Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'X' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 374807.669 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.033905 | 277.0389 | 0.051369 | 285.9278 | 1 | 81634.1685 | 198476.1651 | 280110.3336 | 278.4301 | 287.2296 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.051369 | 285.9278 | 2 | 117989.9075 | 396952.3303 | 514942.2377 | 279.8214 | 288.321 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.051369 | 285.9278 | 3 | 165589.7696 | 595428.4954 | 761018.265 | 281.2127 | 289.4646 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.051369 | 285.9278 | 4 | 224433.7548 | 793904.6606 | 1018338.4154 | 282.6039 | 290.6605 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.051369 | 295.0019 | 1 | 95883.4088 | 190379.5777 | 286262.9865 | 278.3734 | 296.337 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.051369 | 295.0019 | 2 | 138585.0403 | 380759.1555 | 519344.1958 | 279.7079 | 297.4242 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.051369 | 295.0019 | 3 | 194493.4561 | 571138.7332 | 765632.1894 | 281.0424 | 298.5729 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.051369 | 295.0019 | 4 | 263608.6562 | 761518.311 | 1025126.9672 | 282.3769 | 299.7832 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.051369 | 304.0759 | 1 | 111050.2676 | 177038.0893 | 288088.3569 | 278.2799 | 305.424 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.051369 | 304.0759 | 2 | 160506.4526 | 354076.1787 | 514582.6313 | 279.5209 | 306.4838 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.051369 | 304.0759 | 3 | 225258.474 | 531114.268 | 756372.742 | 280.7618 | 307.6151 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.051369 | 304.0759 | 4 | 305306.3317 | 708152.3574 | 1013458.6891 | 282.0028 | 308.8181 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.051369 | 313.15 | 1 | 123937.3639 | 158451.6999 | 282389.0638 | 278.1496 | 314.4756 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.051369 | 313.15 | 2 | 179132.8112 | 316903.3999 | 496036.2111 | 279.2603 | 315.4786 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.051369 | 313.15 | 3 | 251399.1372 | 475355.0998 | 726754.237 | 280.371 | 316.5616 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.051369 | 313.15 | 4 | 340736.3418 | 633806.7997 | 974543.1415 | 281.4817 | 317.7248 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 285.9278 | 1 | 85985.6284 | 220770.9027 | 306756.5312 | 282.4787 | 287.3534 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 285.9278 | 2 | 124279.2881 | 441541.8054 | 565821.0935 | 284.0296 | 288.5575 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 285.9278 | 3 | 174416.432 | 662312.7082 | 836729.1402 | 285.5805 | 289.8165 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 285.9278 | 4 | 236397.0603 | 883083.6109 | 1119480.6712 | 287.1314 | 291.1306 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 295.0019 | 1 | 100640.1869 | 213498.0487 | 314138.2355 | 282.4276 | 296.467 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 295.0019 | 2 | 145460.2473 | 426996.0973 | 572456.3447 | 283.9274 | 297.6719 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 295.0019 | 3 | 204142.2809 | 640494.146 | 844636.4269 | 285.4272 | 298.9414 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 295.0019 | 4 | 276686.2877 | 853992.1947 | 1130678.4824 | 286.9271 | 300.2755 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 304.0759 | 1 | 117489.1483 | 200980.2936 | 318469.4419 | 282.3397 | 305.5661 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 304.0759 | 2 | 169812.8858 | 401960.5872 | 571773.473 | 283.7515 | 306.7514 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 304.0759 | 3 | 238319.3379 | 602940.8808 | 841260.2188 | 285.1634 | 308.0124 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 304.0759 | 4 | 323008.5047 | 803921.1745 | 1126929.6792 | 286.5753 | 309.3491 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 313.15 | 1 | 133576.5698 | 183217.6375 | 316794.2074 | 282.2149 | 314.6371 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 313.15 | 2 | 193064.8331 | 366435.2751 | 559500.1082 | 283.502 | 315.7765 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 313.15 | 3 | 270951.6594 | 549652.9126 | 820604.572 | 284.7891 | 317.0022 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.051369 | 313.15 | 4 | 367237.0488 | 732870.5502 | 1100107.599 | 286.0762 | 318.3143 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 285.9278 | 1 | 89358.1813 | 231391.7632 | 320749.9445 | 286.4452 | 287.4185 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 285.9278 | 2 | 129153.8058 | 462783.5263 | 591937.3321 | 288.0738 | 288.6788 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 285.9278 | 3 | 181257.4432 | 694175.2895 | 875432.7326 | 289.7024 | 289.9964 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 285.9278 | 4 | 245669.0933 | 925567.0526 | 1171236.146 | 291.3309 | 291.3711 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 295.0019 | 1 | 102945.9365 | 224942.6424 | 327888.579 | 286.3998 | 296.5312 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 295.0019 | 2 | 148792.8615 | 449885.2849 | 598678.1464 | 287.983 | 297.7942 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 295.0019 | 3 | 208819.3489 | 674827.9273 | 883647.2762 | 289.5662 | 299.1233 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 295.0019 | 4 | 283025.3987 | 899770.5698 | 1182795.9684 | 291.1494 | 300.5186 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 304.0759 | 1 | 119508.1313 | 213248.6207 | 332756.752 | 286.3175 | 305.633 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 304.0759 | 2 | 172731.022 | 426497.2415 | 599228.2635 | 287.8184 | 306.8798 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 304.0759 | 3 | 242414.7179 | 639745.8622 | 882160.5801 | 289.3193 | 308.2037 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 304.0759 | 4 | 328559.219 | 852994.4829 | 1181553.7019 | 290.8201 | 309.6047 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 313.15 | 1 | 136330.2611 | 196309.698 | 332639.9591 | 286.1983 | 314.7115 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 313.15 | 2 | 197044.8795 | 392619.396 | 589664.2755 | 287.58 | 315.9181 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 313.15 | 3 | 276537.3488 | 588929.094 | 865466.4428 | 288.9616 | 317.2128 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.051369 | 313.15 | 4 | 374807.669 | 785238.792 | 1160046.461 | 290.3433 | 318.5956 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 285.9278 | 1 | 92457.6799 | 230338.7464 | 322796.4263 | 290.3294 | 287.428 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 285.9278 | 2 | 133633.6646 | 460677.4929 | 594311.1575 | 291.9532 | 288.6899 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 285.9278 | 3 | 187544.5807 | 691016.2393 | 878560.8201 | 293.5771 | 290.0109 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 285.9278 | 4 | 254190.4283 | 921354.9858 | 1175545.4141 | 295.2009 | 291.3912 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 295.0019 | 1 | 103917.5892 | 224713.3591 | 328630.9483 | 290.2897 | 296.5346 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 295.0019 | 2 | 150197.2393 | 449426.7182 | 599623.9574 | 291.8739 | 297.7986 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 295.0019 | 3 | 210790.2852 | 674140.0772 | 884930.3624 | 293.4581 | 299.1293 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 295.0019 | 4 | 285696.7269 | 898853.4363 | 1184550.1632 | 295.0423 | 300.5268 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 304.0759 | 1 | 118635.227 | 213843.0707 | 332478.2977 | 290.2131 | 305.6317 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 304.0759 | 2 | 171469.3701 | 427686.1414 | 599155.5115 | 291.7206 | 306.8795 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 304.0759 | 3 | 240644.0864 | 641529.2121 | 882173.2985 | 293.2282 | 308.2038 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 304.0759 | 4 | 326159.3758 | 855372.2828 | 1181531.6587 | 294.7357 | 309.6046 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 313.15 | 1 | 134137.5268 | 197727.8813 | 331865.4081 | 290.0995 | 314.7079 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 313.15 | 2 | 193875.6119 | 395455.7627 | 589331.3746 | 291.4934 | 315.9165 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 313.15 | 3 | 272089.5253 | 593183.644 | 865273.1693 | 292.8874 | 317.2119 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.051369 | 313.15 | 4 | 368779.2668 | 790911.5253 | 1159690.7921 | 294.2813 | 318.594 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation