## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'X': 300.0 ton, 2.25 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | c9f3bf45-6502-4409-b94e-461e2b3b4195 |  | ✓
| data_timestamp | 2022-12-01T11:35Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'X' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 560931.8632 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.045206 | 277.0389 | 0.070872 | 285.9278 | 1 | 122172.5434 | 264634.8869 | 386807.4303 | 278.4301 | 287.2308 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.070872 | 285.9278 | 2 | 176582.0289 | 529269.7737 | 705851.8026 | 279.8214 | 288.3055 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.070872 | 285.9278 | 3 | 247819.3101 | 793904.6606 | 1041723.9707 | 281.2127 | 289.437 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.070872 | 285.9278 | 4 | 335884.3873 | 1058539.5474 | 1394423.9347 | 282.6039 | 290.6251 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.070872 | 295.0019 | 1 | 143497.7552 | 253839.437 | 397337.1922 | 278.3734 | 296.3451 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.070872 | 295.0019 | 2 | 207404.4138 | 507678.874 | 715083.2878 | 279.7079 | 297.4193 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.070872 | 295.0019 | 3 | 291076.1592 | 761518.311 | 1052594.4702 | 281.0424 | 298.5603 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.070872 | 295.0019 | 4 | 394512.9914 | 1015357.748 | 1409870.7394 | 282.3769 | 299.7682 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.070872 | 304.0759 | 1 | 166196.2618 | 236050.7858 | 402247.0476 | 278.2799 | 305.4402 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.070872 | 304.0759 | 2 | 240211.6898 | 472101.5716 | 712313.2614 | 279.5209 | 306.4918 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.070872 | 304.0759 | 3 | 337118.6503 | 708152.3574 | 1045271.0077 | 280.7618 | 307.621 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.070872 | 304.0759 | 4 | 456917.1436 | 944203.1432 | 1401120.2867 | 282.0028 | 308.8279 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.070872 | 313.15 | 1 | 185482.9081 | 211268.9332 | 396751.8413 | 278.1496 | 314.5 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.070872 | 313.15 | 2 | 268087.635 | 422537.8665 | 690625.5015 | 279.2603 | 315.4999 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.070872 | 313.15 | 3 | 376240.3977 | 633806.7997 | 1010047.1974 | 280.371 | 316.5867 | 15000 | 15000 | 0 | 0
0.045206 | 277.0389 | 0.070872 | 313.15 | 4 | 509941.1961 | 845075.733 | 1355016.9291 | 281.4817 | 317.7605 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 285.9278 | 1 | 128684.877 | 294361.2036 | 423046.0806 | 282.4787 | 287.3529 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 285.9278 | 2 | 185994.6271 | 588722.4073 | 774717.0343 | 284.0296 | 288.5375 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 285.9278 | 3 | 261029.1685 | 883083.6109 | 1144112.7794 | 285.5805 | 289.7819 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 285.9278 | 4 | 353788.5013 | 1177444.8145 | 1531233.3158 | 287.1314 | 291.0859 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 295.0019 | 1 | 150616.6821 | 284664.0649 | 435280.747 | 282.4276 | 296.4734 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 295.0019 | 2 | 217693.7515 | 569328.1298 | 787021.8813 | 283.9274 | 297.6625 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 295.0019 | 3 | 305516.4541 | 853992.1947 | 1159508.6487 | 285.4272 | 298.9218 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 295.0019 | 4 | 414084.7899 | 1138656.2596 | 1552741.0495 | 286.9271 | 300.2512 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 304.0759 | 1 | 175832.5997 | 267973.7248 | 443806.3245 | 282.3397 | 305.5811 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 304.0759 | 2 | 254139.5662 | 535947.4496 | 790087.0159 | 283.7515 | 306.7556 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 304.0759 | 3 | 356665.3549 | 803921.1745 | 1160586.5293 | 285.1634 | 308.0121 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 304.0759 | 4 | 483409.9656 | 1071894.8993 | 1555304.8648 | 286.5753 | 309.3509 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 313.15 | 1 | 199908.8076 | 244290.1834 | 444198.991 | 282.2149 | 314.6614 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 313.15 | 2 | 288938.1021 | 488580.3668 | 777518.4689 | 283.502 | 315.7955 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 313.15 | 3 | 405502.4262 | 732870.5502 | 1138372.9764 | 284.7891 | 317.0234 | 15000 | 15000 | 0 | 0
0.045206 | 280.9278 | 0.070872 | 313.15 | 4 | 549601.78 | 977160.7336 | 1526762.5136 | 286.0762 | 318.3449 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 285.9278 | 1 | 133732.1919 | 308522.3509 | 442254.5428 | 286.4452 | 287.4176 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 285.9278 | 2 | 193289.7615 | 617044.7017 | 810334.4632 | 288.0738 | 288.6575 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 285.9278 | 3 | 271267.3291 | 925567.0526 | 1196834.3817 | 289.7024 | 289.9595 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 285.9278 | 4 | 367664.895 | 1234089.4035 | 1601754.2984 | 291.3309 | 291.3235 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 295.0019 | 1 | 154067.4345 | 299923.5233 | 453990.9577 | 286.3998 | 296.5367 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 295.0019 | 2 | 222681.2948 | 599847.0465 | 822528.3413 | 287.983 | 297.7826 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 295.0019 | 3 | 312516.0879 | 899770.5698 | 1212286.6577 | 289.5662 | 299.1002 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 295.0019 | 4 | 423571.8138 | 1199694.0931 | 1623265.9069 | 291.1494 | 300.4896 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 304.0759 | 1 | 178854.1812 | 284331.4943 | 463185.6755 | 286.3175 | 305.6469 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 304.0759 | 2 | 258506.8077 | 568662.9886 | 827169.7963 | 287.8184 | 306.8813 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 304.0759 | 3 | 362794.4427 | 852994.4829 | 1215788.9256 | 289.3193 | 308.1994 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 304.0759 | 4 | 491717.0862 | 1137325.9772 | 1629043.0634 | 290.8201 | 309.601 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 313.15 | 1 | 204029.9431 | 261746.264 | 465776.2071 | 286.1983 | 314.7348 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 313.15 | 2 | 294894.5834 | 523492.528 | 818387.1114 | 287.58 | 315.9346 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 313.15 | 3 | 413861.8901 | 785238.792 | 1199100.6821 | 288.9616 | 317.23 | 15000 | 15000 | 0 | 0
0.045206 | 284.8167 | 0.070872 | 313.15 | 4 | 560931.8632 | 1046985.0561 | 1607916.9192 | 290.3433 | 318.621 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 285.9278 | 1 | 138370.8577 | 307118.3286 | 445489.1863 | 290.3294 | 287.4285 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 285.9278 | 2 | 199994.2548 | 614236.6572 | 814230.912 | 291.9532 | 288.6706 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 285.9278 | 3 | 280676.5704 | 921354.9858 | 1202031.5562 | 293.5771 | 289.977 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 285.9278 | 4 | 380417.8045 | 1228473.3144 | 1608891.1189 | 295.2009 | 291.3475 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 295.0019 | 1 | 155521.5962 | 299617.8121 | 455139.4083 | 290.2897 | 296.5405 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 295.0019 | 2 | 224783.0667 | 599235.6242 | 824018.6909 | 291.8739 | 297.7876 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 295.0019 | 3 | 315465.7633 | 898853.4363 | 1214319.1996 | 293.4581 | 299.1071 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 295.0019 | 4 | 427569.686 | 1198471.2484 | 1626040.9344 | 295.0423 | 300.499 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 304.0759 | 1 | 177547.8049 | 285124.0943 | 462671.8992 | 290.2131 | 305.6451 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 304.0759 | 2 | 256618.6373 | 570248.1886 | 826866.8258 | 291.7206 | 306.8803 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 304.0759 | 3 | 360144.5406 | 855372.2828 | 1215516.8234 | 293.2282 | 308.1984 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 304.0759 | 4 | 488125.5148 | 1140496.3771 | 1628621.8919 | 294.7357 | 309.5995 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 313.15 | 1 | 200748.3278 | 263637.1751 | 464385.5029 | 290.0995 | 314.7301 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 313.15 | 2 | 290151.5023 | 527274.3502 | 817425.8525 | 291.4934 | 315.9313 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 313.15 | 3 | 407205.3402 | 790911.5253 | 1198116.8655 | 292.8874 | 317.2266 | 15000 | 15000 | 0 | 0
0.045206 | 288.7056 | 0.070872 | 313.15 | 4 | 551909.8415 | 1054548.7004 | 1606458.542 | 294.2813 | 318.616 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation