## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | Water-Cooled Chiller with Constant Efficiency |  | ✓
| id | 123e4567-e89b-12d3-a456-426614174000 |  | ✓
| data_timestamp | 2020-05-07T00:00Z |  | ✓
| data_version | 1 |  | ✓
| disclaimer | Example data not to be used for simulation
| notes | An example representation that applies a constant COP of 5.9
description
description.product_information
| manufacturer | ABC Chillers
| model_number | Chiller A1B2
| nominal_voltage | 460 | V
| nominal_frequency | 60 | Hz
| compressor_type | CENTRIFUGAL
| liquid_data_source | AHRI_550_590_2015
| refrigerant | R-134A
| hot_gas_bypass_installed | FALSE
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0.01761 | m2-K/W | ✓
| condenser_fouling_factor | 0.04403 | m2-K/W | ✓
| compressor_speed_control_type | DISCRETE |  | ✓
| maximum_power | 31400 | W
| cycling_degradation_coefficient | 0.25 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Characterization of accuracy, limitations, and applicability of this data
Note on B12: Additional Information
Note on A13: Data group describing product and rating information
Note on A14: Data group describing product information
Note on B15: Manufacturer name
Note on B16: Model number
Note on B17: Unit nominal voltage
Note on B18: Unit nominal frequency
Note on B19: Type of compressor
Note on B20: Source of the liquid properties data
Note on B21: Refrigerant used in the chiller
Note on B22: Indicates if a hot-gas bypass valve is installed on the chiller
Note on A23: Data group containing performance information
Note on A24: Type of liquid in evaporator
Note on A25: An array of all liquid components within the liquid mixture
Note on B26: Defines whether concentration is defined on a volume or mass basis
Note on A27: Type of liquid in condenser
Note on A28: An array of all liquid components within the liquid mixture
Note on B29: Defines whether concentration is defined on a volume or mass basis
Note on B30: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B32: Type of compressor speed control
Note on B33: Maximum input power at which the chiller operates reliably and continuously
Note on B34: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A35: Data group describing cooling performance over a range of conditions
Note on A36: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.0755 | 279.82 | 0.0957 | 294.15 | 1 | 59593.2203 | 351600 | 411193.2203 | 280.93 | 295.1799 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 294.15 | 2 | 119186.4407 | 703200 | 822386.4407 | 282.05 | 296.2098 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 294.15 | 3 | 178779.661 | 1054800 | 1233579.661 | 283.16 | 297.2397 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 294.15 | 4 | 238372.8814 | 1406400 | 1644772.8814 | 284.28 | 298.2695 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 294.15 | 5 | 297966.1017 | 1758000 | 2055966.1017 | 285.39 | 299.2994 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 297.15 | 1 | 59593.2203 | 351600 | 411193.2203 | 280.93 | 298.1799 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 297.15 | 2 | 119186.4407 | 703200 | 822386.4407 | 282.05 | 299.2098 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 297.15 | 3 | 178779.661 | 1054800 | 1233579.661 | 283.16 | 300.2397 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 297.15 | 4 | 238372.8814 | 1406400 | 1644772.8814 | 284.28 | 301.2695 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 297.15 | 5 | 297966.1017 | 1758000 | 2055966.1017 | 285.39 | 302.2994 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 300.15 | 1 | 59593.2203 | 351600 | 411193.2203 | 280.93 | 301.1799 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 300.15 | 2 | 119186.4407 | 703200 | 822386.4407 | 282.05 | 302.2098 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 300.15 | 3 | 178779.661 | 1054800 | 1233579.661 | 283.16 | 303.2397 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 300.15 | 4 | 238372.8814 | 1406400 | 1644772.8814 | 284.28 | 304.2695 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 300.15 | 5 | 297966.1017 | 1758000 | 2055966.1017 | 285.39 | 305.2994 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 302.59 | 1 | 59593.2203 | 351600 | 411193.2203 | 280.93 | 303.6199 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 302.59 | 2 | 119186.4407 | 703200 | 822386.4407 | 282.05 | 304.6498 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 302.59 | 3 | 178779.661 | 1054800 | 1233579.661 | 283.16 | 305.6797 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 302.59 | 4 | 238372.8814 | 1406400 | 1644772.8814 | 284.28 | 306.7095 | 74400 | 23600 | 0 | 0
0.0755 | 279.82 | 0.0957 | 302.59 | 5 | 297966.1017 | 1758000 | 2055966.1017 | 285.39 | 307.7394 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 294.15 | 1 | 59593.2203 | 351600 | 411193.2203 | 282.93 | 295.1799 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 294.15 | 2 | 119186.4407 | 703200 | 822386.4407 | 284.05 | 296.2098 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 294.15 | 3 | 178779.661 | 1054800 | 1233579.661 | 285.16 | 297.2397 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 294.15 | 4 | 238372.8814 | 1406400 | 1644772.8814 | 286.28 | 298.2695 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 294.15 | 5 | 297966.1017 | 1758000 | 2055966.1017 | 287.39 | 299.2994 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 297.15 | 1 | 59593.2203 | 351600 | 411193.2203 | 282.93 | 298.1799 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 297.15 | 2 | 119186.4407 | 703200 | 822386.4407 | 284.05 | 299.2098 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 297.15 | 3 | 178779.661 | 1054800 | 1233579.661 | 285.16 | 300.2397 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 297.15 | 4 | 238372.8814 | 1406400 | 1644772.8814 | 286.28 | 301.2695 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 297.15 | 5 | 297966.1017 | 1758000 | 2055966.1017 | 287.39 | 302.2994 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 300.15 | 1 | 59593.2203 | 351600 | 411193.2203 | 282.93 | 301.1799 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 300.15 | 2 | 119186.4407 | 703200 | 822386.4407 | 284.05 | 302.2098 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 300.15 | 3 | 178779.661 | 1054800 | 1233579.661 | 285.16 | 303.2397 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 300.15 | 4 | 238372.8814 | 1406400 | 1644772.8814 | 286.28 | 304.2695 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 300.15 | 5 | 297966.1017 | 1758000 | 2055966.1017 | 287.39 | 305.2994 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 302.59 | 1 | 59593.2203 | 351600 | 411193.2203 | 282.93 | 303.6199 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 302.59 | 2 | 119186.4407 | 703200 | 822386.4407 | 284.05 | 304.6498 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 302.59 | 3 | 178779.661 | 1054800 | 1233579.661 | 285.16 | 305.6797 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 302.59 | 4 | 238372.8814 | 1406400 | 1644772.8814 | 286.28 | 306.7095 | 74400 | 23600 | 0 | 0
0.0755 | 281.82 | 0.0957 | 302.59 | 5 | 297966.1017 | 1758000 | 2055966.1017 | 287.39 | 307.7394 | 74400 | 23600 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
273.15 | 2200
311.15 | 2200
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation