## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model |  |  | ✓
| schema |  |  | ✓
| schema_version | 1.0.0 |  | ✓
| id |  |  | ✓
| description |  |  | ✓
| data_timestamp |  |  | ✓
| data_version |  |  | ✓
data_source
disclaimer
notes
description
description.product_information
manufacturer
model_number
| nominal_voltage |  | V
| nominal_frequency |  | Hz
compressor_type
liquid_data_source
refrigerant
hot_gas_bypass_installed
description.rating_ahri_550_590
| certified_reference_number |  |  | ✓
| test_standard_year |  |  | ✓
rating_source
| net_refrigerating_capacity |  | Btu/h | ✓
| input_power |  | kW | ✓
| cop |  | - | ✓
| part_load_value |  | - | ✓
description.rating_ahri_550_590.part_load_rating_points |  | $part_load_rating_points
| full_load_evaporator_liquid_volumetric_flow_rate |  | gpm | ✓
| full_load_evaporator_liquid_entering_temperature |  | F | ✓
| full_load_evaporator_liquid_leaving_temperature |  | F | ✓
| full_load_evaporator_liquid_differential_pressure |  | ft of water | ✓
| full_load_evaporator_fouling_factor |  | h-ft2-F/Btu | ✓
| full_load_condenser_liquid_volumetric_flow_rate |  | gpm | ✓
| full_load_condenser_liquid_entering_temperature |  | F | ✓
| full_load_condenser_liquid_leaving_temperature |  | F | ✓
| full_load_condenser_liquid_differential_pressure |  | ft of water | ✓
| full_load_condenser_fouling_factor |  | h-ft2-F/Btu | ✓
| rating_recalculatable_from_performance_data |  |  | ✓
rating_recalculatable_explanation
description.rating_ahri_551_591
| certified_reference_number |  |  | ✓
| test_standard_year |  |  | ✓
rating_source
| net_refrigerating_capacity |  | kW | ✓
| input_power |  | kW | ✓
| cop |  | - | ✓
| part_load_value |  | - | ✓
description.rating_ahri_551_591.part_load_rating_points |  | $part_load_rating_points0
| full_load_evaporator_liquid_volumetric_flow_rate |  | l/s | ✓
| full_load_evaporator_liquid_entering_temperature |  | C | ✓
| full_load_evaporator_liquid_leaving_temperature |  | C | ✓
| full_load_evaporator_liquid_differential_pressure |  | kPa | ✓
| full_load_evaporator_fouling_factor |  | m2-K/kW | ✓
| full_load_condenser_liquid_volumetric_flow_rate |  | l/s | ✓
| full_load_condenser_liquid_entering_temperature |  | C | ✓
| full_load_condenser_liquid_leaving_temperature |  | C | ✓
| full_load_condenser_liquid_differential_pressure |  | kPa | ✓
| full_load_condenser_fouling_factor |  | m2-K/kW | ✓
| rating_recalculatable_from_performance_data |  |  | ✓
rating_recalculatable_explanation
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type |  |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type |  |  | ✓
| evaporator_fouling_factor |  | m2-K/W | ✓
| condenser_fouling_factor |  | m2-K/W | ✓
| compressor_speed_control_type |  |  | ✓
| maximum_power |  | W
| cycling_degradation_coefficient |  | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Unique equipment identifier
Note on B8: Description of data (suitable for display)
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Manufacturer name
Note on B17: Model number
Note on B18: Unit nominal voltage
Note on B19: Unit nominal frequency
Note on B20: Type of compressor
Note on B21: Source of the liquid properties data
Note on B22: Refrigerant used in the chiller
Note on B23: Indicates if a hot-gas bypass valve is installed on the chiller
Note on A24: Data group containing information relevant to products rated under AHRI 550/590
Note on B25: AHRI certified reference number
Note on B26: Year of the AHRI test standard
Note on B27: Source of this rating data
Note on B28: Rated net refrigeration capacity
Note on B29: Combined power input of all components of the unit, including auxiliary power and excluding integral pumps
Note on B30: Ratio of the net refrigerating capacity to the total input power at the rating conditions
Note on B31: Rated part-load efficiency on the basis of weighted operation at various partial load capacities
Note on A32: The four measured data points used to calculate the part load rating value
Note on B33: Evaporator liquid volumetric flow rate at the full load design point rating condition
Note on B34: Liquid temperature at the entry flange of the evaporator at the full load design rating conditions
Note on B35: Liquid temperature at the exit flange of the evaporator at the full load design rating conditions
Note on B36: Pressure difference across the evaporator at the full load design rating conditions
Note on B37: Factor of heat transfer inhibition due to evaporator heat exchanger fouling layer at the full load design rating condition
Note on B38: Condenser liquid volumetric flow rate at the full load design rating conditions
Note on B39: Liquid temperature at the entry flange of the condenser at the full load design rating conditions
Note on B40: Liquid temperature at the exit flange of the condenser at the full load design rating conditions
Note on B41: Pressure difference across the condenser at the full load design rating conditions
Note on B42: Factor of heat transfer inhibition due to condenser heat exchanger fouling layer at the full load design rating conditions
Note on B43: Whether this rating can be recalculated using the performance data in the representation
Note on B44: An explanation of the value for `rating_recalculatable_from_performance_data`
Note on A45: Data group containing information relevant to products rated under AHRI 551/591
Note on B46: AHRI certified reference number
Note on B47: Year of the AHRI test standard
Note on B48: Source of this rating data
Note on B49: Rated net refrigeration capacity
Note on B50: Combined power input of all components of the unit, including auxiliary power and excluding integral pumps
Note on B51: Ratio of the net refrigerating capacity to the total input power at the rating conditions
Note on B52: Rated part-load efficiency on the basis of weighted operation at various partial load capacities
Note on A53: The four measured data points used to calculate the part load rating value
Note on B54: Evaporator liquid volumetric flow rate at the full load design rating conditions
Note on B55: Liquid temperature at the entry flange of the evaporator at the full load design rating conditions
Note on B56: Liquid temperature at the exit flange of the evaporator at the full load design rating conditions
Note on B57: Pressure difference across the evaporator at the full load design rating conditions
Note on B58: Factor of heat transfer inhibition due to evaporator heat exchanger fouling layer at the full load design rating conditions
Note on B59: Condenser liquid volumetric flow rate at the full load design rating conditions
Note on B60: Liquid temperature at the entry flange of the condenser at the full load design rating conditions
Note on B61: Liquid temperature at the exit flange of the condenser at the full load design rating conditions
Note on B62: Pressure difference across the condenser at the full load design rating conditions
Note on B63: Factor of heat transfer inhibition due to condenser heat exchanger fouling layer at the full load design rating conditions
Note on B64: Whether this rating can be recalculated using the performance data in the representation
Note on B65: An explanation of the value for `rating_recalculatable_from_performance_data`
Note on A66: Data group containing performance information
Note on A67: Type of liquid in evaporator
Note on A68: An array of all liquid components within the liquid mixture
Note on B69: Defines whether concentration is defined on a volume or mass basis
Note on A70: Type of liquid in condenser
Note on A71: An array of all liquid components within the liquid mixture
Note on B72: Defines whether concentration is defined on a volume or mass basis
Note on B73: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B74: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B75: Type of compressor speed control
Note on B76: Maximum input power at which the chiller operates reliably and continuously
Note on B77: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A78: Data group describing cooling performance over a range of conditions
Note on A79: Data group describing standby performance

## part_load_rating_points
description.rating_ahri_550_590.part_load_rating_points
percent_full_load_capacity | cooling_capacity | input_power | evaporator_liquid_volumetric_flow_rate | evaporator_liquid_entering_temperature | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure | evaporator_fouling_factor | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_leaving_temperature | condenser_liquid_differential_pressure | condenser_fouling_factor
% | Btu/h | kW | gpm | F | F | ft of water | h-ft2-F/Btu | gpm | F | F | ft of water | h-ft2-F/Btu
Note on A2: Percent full load cooling capacity
Note on B2: The actual cooling capacity
Note on C2: Combined power input of all components of the unit, including auxiliary power and excluding integral pumps
Note on D2: Evaporator liquid volumetric flow rate
Note on E2: Liquid temperature at the entry flange of the evaporator
Note on F2: Liquid temperature at the exit flange of the evaporator
Note on G2: Pressure difference across the evaporator
Note on H2: Factor of heat transfer inhibition due to evaporator heat exchanger fouling layer
Note on I2: Condenser liquid volumetric flow rate
Note on J2: Liquid temperature at the entry flange of the condenser
Note on K2: Liquid temperature at the exit flange of the condenser
Note on L2: Pressure difference across the condenser
Note on M2: Factor of heat transfer inhibition due to condenser heat exchanger fouling layer

## part_load_rating_points0
description.rating_ahri_551_591.part_load_rating_points
percent_full_load_capacity | cooling_capacity | input_power | evaporator_liquid_volumetric_flow_rate | evaporator_liquid_entering_temperature | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure | evaporator_fouling_factor | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_leaving_temperature | condenser_liquid_differential_pressure | condenser_fouling_factor
% | kW | kW | l/s | C | C | kPa | m2-K/kW | l/s | C | C | kPa | m2-K/kW
Note on A2: Percent full load cooling capacity
Note on B2: The actual cooling capacity
Note on C2: Combined power input of all components of the unit, including auxiliary power and excluding integral pumps
Note on D2: Evaporator liquid volumetric flow rate
Note on E2: Liquid temperature at the entry flange of the evaporator
Note on F2: Liquid temperature at the exit flange of the evaporator
Note on G2: Pressure difference across the evaporator
Note on H2: Factor of heat transfer inhibition due to evaporator heat exchanger fouling layer
Note on I2: Condenser liquid volumetric flow rate
Note on J2: Liquid temperature at the entry flange of the condenser
Note on K2: Liquid temperature at the exit flange of the condenser
Note on L2: Pressure difference across the condenser
Note on M2: Factor of heat transfer inhibition due to condenser heat exchanger fouling layer

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation