## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'M': 0.0-75.0 ton, 4.51 COP, 7.03 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 745707fc-bfae-4b6b-ac57-c54be90c541a |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'M' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| maximum | 2 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.0056508 | 277.0389 | 0.0074924 | 285.9278 | 1 | 4483.452 | 33280.139 | 37763.591 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074924 | 285.9278 | 2 | 8533.1392 | 66560.278 | 75093.4172 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074924 | 285.9278 | 3 | 14589.6967 | 99840.417 | 114430.1137 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074924 | 285.9278 | 4 | 22653.1247 | 133120.556 | 155773.6806 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074924 | 295.0019 | 1 | 4993.5799 | 31748.9745 | 36742.5544 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074924 | 295.0019 | 2 | 9504.0412 | 63497.949 | 73001.9902 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074924 | 295.0019 | 3 | 16249.7149 | 95246.9235 | 111496.6384 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074924 | 295.0019 | 4 | 25230.6009 | 126995.898 | 152226.4989 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074924 | 304.0759 | 1 | 5721.5671 | 29262.2173 | 34983.7844 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074924 | 304.0759 | 2 | 10889.5842 | 58524.4346 | 69414.0188 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074924 | 304.0759 | 3 | 18618.6733 | 87786.6518 | 106405.3251 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074924 | 304.0759 | 4 | 28908.8344 | 117048.8691 | 145957.7035 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074924 | 313.15 | 1 | 6440.8013 | 25819.8673 | 32260.6686 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074924 | 313.15 | 2 | 12258.4681 | 51639.7346 | 63898.2028 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074924 | 313.15 | 3 | 20959.1486 | 77459.602 | 98418.7506 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074924 | 313.15 | 4 | 32542.8427 | 103279.4693 | 135822.3119 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 285.9278 | 1 | 4554.713 | 37457.2592 | 42011.9722 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 285.9278 | 2 | 8668.7668 | 74914.5183 | 83583.2851 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 285.9278 | 3 | 14821.5887 | 112371.7775 | 127193.3661 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 285.9278 | 4 | 23013.1785 | 149829.0366 | 172842.2151 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 295.0019 | 1 | 5093.2819 | 35948.2005 | 41041.4824 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 295.0019 | 2 | 9693.7991 | 71896.401 | 81590.2001 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 295.0019 | 3 | 16574.1571 | 107844.6015 | 124418.7586 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 295.0019 | 4 | 25734.3558 | 143792.802 | 169527.1577 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 304.0759 | 1 | 5941.6512 | 33483.5491 | 39425.2003 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 304.0759 | 2 | 11308.4598 | 66967.0982 | 78275.558 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 304.0759 | 3 | 19334.8539 | 100450.6473 | 119785.5012 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 304.0759 | 4 | 30020.8333 | 133934.1964 | 163955.0298 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 313.15 | 1 | 6881.3535 | 30063.305 | 36944.6585 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 313.15 | 2 | 13096.9501 | 60126.61 | 73223.5601 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 313.15 | 3 | 22392.7591 | 90189.915 | 112582.6741 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074924 | 313.15 | 4 | 34768.7805 | 120253.22 | 155022.0005 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 285.9278 | 1 | 4615.2165 | 39521.1941 | 44136.4107 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 285.9278 | 2 | 8783.9203 | 79042.3883 | 87826.3085 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 285.9278 | 3 | 15018.4744 | 118563.5824 | 133582.0568 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 285.9278 | 4 | 23318.879 | 158084.7765 | 181403.6556 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 295.0019 | 1 | 5111.2791 | 38034.2413 | 43145.5204 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 295.0019 | 2 | 9728.0524 | 76068.4826 | 85796.535 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 295.0019 | 3 | 16632.7222 | 114102.724 | 130735.4462 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 295.0019 | 4 | 25825.2887 | 152136.9653 | 177962.254 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 304.0759 | 1 | 5967.7974 | 35591.6958 | 41559.4931 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 304.0759 | 2 | 11358.2225 | 71183.3915 | 82541.614 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 304.0759 | 3 | 19419.9366 | 106775.0873 | 126195.0239 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 304.0759 | 4 | 30152.9395 | 142366.7831 | 172519.7226 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 313.15 | 1 | 6974.4484 | 32193.5575 | 39168.0059 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 313.15 | 2 | 13274.1332 | 64387.115 | 77661.2482 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 313.15 | 3 | 22695.7012 | 96580.6725 | 119276.3737 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074924 | 313.15 | 4 | 35239.1525 | 128774.23 | 164013.3825 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 285.9278 | 1 | 4746.917 | 39471.9439 | 44218.8609 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 285.9278 | 2 | 9034.5794 | 78943.8879 | 87978.4673 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 285.9278 | 3 | 15447.0436 | 118415.8318 | 133862.8754 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 285.9278 | 4 | 23984.3096 | 157887.7758 | 181872.0854 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 295.0019 | 1 | 5145.788 | 38007.097 | 43152.885 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 295.0019 | 2 | 9793.7316 | 76014.1939 | 85807.9255 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 295.0019 | 3 | 16745.0185 | 114021.2909 | 130766.3094 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 295.0019 | 4 | 25999.6488 | 152028.3878 | 178028.0366 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 304.0759 | 1 | 5914.4839 | 35586.6573 | 41501.1412 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 304.0759 | 2 | 11256.7536 | 71173.3145 | 82430.0681 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 304.0759 | 3 | 19246.4482 | 106759.9718 | 126006.42 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 304.0759 | 4 | 29883.5677 | 142346.629 | 172230.1967 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 313.15 | 1 | 6850.8264 | 32210.6248 | 39061.4512 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 313.15 | 2 | 13038.8494 | 64421.2496 | 77460.099 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 313.15 | 3 | 22293.4202 | 96631.8744 | 118925.2947 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074924 | 313.15 | 4 | 34614.539 | 128842.4993 | 163457.0383 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.0056508 | 277.0389 | 15000
0.0056508 | 280.9278 | 15000
0.0056508 | 284.8167 | 15000
0.0056508 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.0074924 | 285.9278 | 15000
0.0074924 | 295.0019 | 15000
0.0074924 | 304.0759 | 15000
0.0074924 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser