## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'O': 150.0-300.0 ton, 5.17 COP, 7.99 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | c72c5598-9cea-4f23-a182-968c79e2b922 |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'O' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Minimum scaling factor
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.033905 | 277.0389 | 0.043908 | 285.9278 | 1 | 20607.4813 | 193713.0171 | 214320.4984 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043908 | 285.9278 | 2 | 40790.0544 | 387426.0343 | 428216.0887 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043908 | 285.9278 | 3 | 70599.279 | 581139.0514 | 651738.3305 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043908 | 285.9278 | 4 | 110035.1553 | 774852.0686 | 884887.2238 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043908 | 295.0019 | 1 | 24712.2558 | 190437.7629 | 215150.0188 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043908 | 295.0019 | 2 | 48914.9666 | 380875.5259 | 429790.4925 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043908 | 295.0019 | 3 | 84661.8478 | 571313.2888 | 655975.1366 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043908 | 295.0019 | 4 | 131952.8994 | 761751.0518 | 893703.9512 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043908 | 304.0759 | 1 | 28465.2838 | 181038.0281 | 209503.3119 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043908 | 304.0759 | 2 | 56343.6385 | 362076.0561 | 418419.6946 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043908 | 304.0759 | 3 | 97519.3663 | 543114.0842 | 640633.4505 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043908 | 304.0759 | 4 | 151992.4673 | 724152.1123 | 876144.5796 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043908 | 313.15 | 1 | 31246.7092 | 165513.8125 | 196760.5217 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043908 | 313.15 | 2 | 61849.1387 | 331027.625 | 392876.7637 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043908 | 313.15 | 3 | 107048.2662 | 496541.4376 | 603589.7038 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043908 | 313.15 | 4 | 166844.0918 | 662055.2501 | 828899.3419 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 285.9278 | 1 | 21030.4416 | 211050.9087 | 232081.3502 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 285.9278 | 2 | 41627.2538 | 422101.8174 | 463729.0712 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 285.9278 | 3 | 72048.3008 | 633152.7261 | 705201.0269 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 285.9278 | 4 | 112293.5826 | 844203.6348 | 956497.2173 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 295.0019 | 1 | 25236.8805 | 208920.5042 | 234157.3848 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 295.0019 | 2 | 49953.3987 | 417841.0085 | 467794.4072 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 295.0019 | 3 | 86459.1624 | 626761.5127 | 713220.6751 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 295.0019 | 4 | 134754.1715 | 835682.0169 | 970436.1885 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 304.0759 | 1 | 29303.4063 | 200665.6191 | 229969.0254 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 304.0759 | 2 | 58002.6021 | 401331.2382 | 459333.8403 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 304.0759 | 3 | 100390.6946 | 601996.8573 | 702387.5519 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 304.0759 | 4 | 156467.6839 | 802662.4764 | 959130.1602 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 313.15 | 1 | 32665.2318 | 186286.2533 | 218951.4851 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 313.15 | 2 | 64656.9352 | 372572.5065 | 437229.4417 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 313.15 | 3 | 111907.9903 | 558858.7598 | 670766.7501 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043908 | 313.15 | 4 | 174418.3971 | 745145.0131 | 919563.4102 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 285.9278 | 1 | 21458.7361 | 218886.9464 | 240345.6825 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 285.9278 | 2 | 42475.0119 | 437773.8927 | 480248.9047 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 285.9278 | 3 | 73515.5975 | 656660.8391 | 730176.4366 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 285.9278 | 4 | 114580.4929 | 875547.7855 | 990128.2784 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 295.0019 | 1 | 25484.0538 | 217901.3916 | 243385.4454 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 295.0019 | 2 | 50442.6487 | 435802.7833 | 486245.4319 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 295.0019 | 3 | 87305.9544 | 653704.1749 | 741010.1293 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 295.0019 | 4 | 136073.971 | 871605.5666 | 1007679.5376 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 304.0759 | 1 | 29500.8694 | 210791.3562 | 240292.2256 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 304.0759 | 2 | 58393.4568 | 421582.7125 | 479976.1692 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 304.0759 | 3 | 101067.1844 | 632374.0687 | 733441.2531 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 304.0759 | 4 | 157522.0524 | 843165.4249 | 1000687.4773 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 313.15 | 1 | 32999.4649 | 197556.8401 | 230556.3051 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 313.15 | 2 | 65318.5098 | 395113.6803 | 460432.1901 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 313.15 | 3 | 113053.0413 | 592670.5204 | 705723.5617 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043908 | 313.15 | 4 | 176203.0594 | 790227.3606 | 966430.4199 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 285.9278 | 1 | 22058.7458 | 217221.1302 | 239279.876 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 285.9278 | 2 | 43662.6596 | 434442.2604 | 478104.92 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 285.9278 | 3 | 75571.1738 | 651663.3905 | 727234.5643 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 285.9278 | 4 | 117784.2884 | 868884.5207 | 986668.8091 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 295.0019 | 1 | 25701.4312 | 217380.4252 | 243081.8564 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 295.0019 | 2 | 50872.9214 | 434760.8504 | 485633.7718 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 295.0019 | 3 | 88050.669 | 652141.2755 | 740191.9445 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 295.0019 | 4 | 137234.6739 | 869521.7007 | 1006756.3746 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 304.0759 | 1 | 29386.6038 | 211415.2395 | 240801.8433 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 304.0759 | 2 | 58167.2815 | 422830.479 | 480997.7605 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 304.0759 | 3 | 100675.7212 | 634245.7185 | 734921.4397 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 304.0759 | 4 | 156911.9226 | 845660.958 | 1002572.8806 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 313.15 | 1 | 32659.6143 | 199325.5731 | 231985.1875 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 313.15 | 2 | 64645.816 | 398651.1463 | 463296.9623 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 313.15 | 3 | 111888.7452 | 597976.7194 | 709865.4647 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043908 | 313.15 | 4 | 174388.402 | 797302.2926 | 971690.6946 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.033905 | 277.0389 | 15000
0.033905 | 280.9278 | 15000
0.033905 | 284.8167 | 15000
0.033905 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.043908 | 285.9278 | 15000
0.043908 | 295.0019 | 15000
0.043908 | 304.0759 | 15000
0.043908 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser