## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'AA': 150.0-300.0 ton, 5.55 COP, 5.90 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 5adc5b62-8a68-4774-8610-7b157625a90b |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'AA' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Minimum scaling factor
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.033905 | 277.0389 | 0.043424 | 285.9278 | 1 | 43277.3742 | 198295.1327 | 241572.5069 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043424 | 285.9278 | 2 | 57364.4101 | 396590.2654 | 453954.6755 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043424 | 285.9278 | 3 | 79934.8807 | 594885.398 | 674820.2787 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043424 | 285.9278 | 4 | 110988.786 | 793180.5307 | 904169.3167 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043424 | 295.0019 | 1 | 51538.4291 | 189751.5752 | 241290.0044 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043424 | 295.0019 | 2 | 68314.4862 | 379503.1504 | 447817.6366 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043424 | 295.0019 | 3 | 95193.3489 | 569254.7256 | 664448.0745 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043424 | 295.0019 | 4 | 132175.0172 | 759006.3008 | 891181.318 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043424 | 304.0759 | 1 | 52390.3661 | 176060.8478 | 228451.2139 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043424 | 304.0759 | 2 | 69443.7336 | 352121.6956 | 421565.4292 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043424 | 304.0759 | 3 | 96766.9074 | 528182.5434 | 624949.4508 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043424 | 304.0759 | 4 | 134359.8875 | 704243.3912 | 838603.2786 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043424 | 313.15 | 1 | 46557.8341 | 157222.9505 | 203780.7846 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043424 | 313.15 | 2 | 61712.6787 | 314445.9009 | 376158.5796 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043424 | 313.15 | 3 | 85994.0092 | 471668.8514 | 557662.8606 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043424 | 313.15 | 4 | 119401.8256 | 628891.8018 | 748293.6275 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 285.9278 | 1 | 41819.7498 | 215062.2805 | 256882.0303 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 285.9278 | 2 | 55432.3205 | 430124.5609 | 485556.8814 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 285.9278 | 3 | 77242.5955 | 645186.8414 | 722429.4369 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 285.9278 | 4 | 107250.5749 | 860249.1218 | 967499.6967 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 295.0019 | 1 | 52879.6927 | 211042.2756 | 263921.9683 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 295.0019 | 2 | 70092.3389 | 422084.5512 | 492176.8901 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 295.0019 | 3 | 97670.7115 | 633126.8267 | 730797.5382 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 295.0019 | 4 | 135614.8104 | 844169.1023 | 979783.9127 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 304.0759 | 1 | 56377.9977 | 201875.1008 | 258253.0985 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 304.0759 | 2 | 74729.3623 | 403750.2015 | 478479.5639 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 304.0759 | 3 | 104132.2076 | 605625.3023 | 709757.5099 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 304.0759 | 4 | 144586.5335 | 807500.4031 | 952086.9366 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 313.15 | 1 | 52625.0088 | 187560.756 | 240185.7648 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 313.15 | 2 | 69754.7538 | 375121.5121 | 444876.2659 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 313.15 | 3 | 97200.3009 | 562682.2681 | 659882.569 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043424 | 313.15 | 4 | 134961.6501 | 750243.0241 | 885204.6743 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 285.9278 | 1 | 39014.3164 | 220574.3985 | 259588.7149 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 285.9278 | 2 | 51713.7022 | 441148.7971 | 492862.4993 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 285.9278 | 3 | 72060.8581 | 661723.1956 | 733784.0538 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 285.9278 | 4 | 100055.7841 | 882297.5942 | 982353.3782 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 295.0019 | 1 | 52115.5662 | 221077.9463 | 273193.5125 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 295.0019 | 2 | 69079.4848 | 442155.8925 | 511235.3773 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 295.0019 | 3 | 96259.3421 | 663233.8388 | 759493.1809 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 295.0019 | 4 | 133655.1381 | 884311.7851 | 1017966.9232 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 304.0759 | 1 | 57828.8065 | 216434.3241 | 274263.1305 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 304.0759 | 2 | 76652.4178 | 432868.6481 | 509521.0659 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 304.0759 | 3 | 106811.9041 | 649302.9722 | 756114.8763 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 304.0759 | 4 | 148307.2654 | 865737.2963 | 1014044.5616 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 313.15 | 1 | 56050.0763 | 206643.5319 | 262693.6082 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 313.15 | 2 | 74294.7006 | 413287.0638 | 487581.7644 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 313.15 | 3 | 103526.5248 | 619930.5958 | 723457.1206 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043424 | 313.15 | 4 | 143745.549 | 826574.1277 | 970319.6767 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 285.9278 | 1 | 35557.3749 | 214831.487 | 250388.8619 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 285.9278 | 2 | 47131.5063 | 429662.9739 | 476794.4802 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 285.9278 | 3 | 65675.7618 | 644494.4609 | 710170.2226 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 285.9278 | 4 | 91190.1414 | 859325.9478 | 950516.0892 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 295.0019 | 1 | 49933.92 | 219858.5873 | 269792.5073 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 295.0019 | 2 | 66187.7001 | 439717.1746 | 505904.8747 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 295.0019 | 3 | 92229.7624 | 659575.7618 | 751805.5242 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 295.0019 | 4 | 128060.1068 | 879434.3491 | 1007494.4559 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 304.0759 | 1 | 57422.2322 | 219738.5177 | 277160.7499 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 304.0759 | 2 | 76113.5012 | 439477.0353 | 515590.5366 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 304.0759 | 3 | 106060.9466 | 659215.553 | 765276.4997 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 304.0759 | 4 | 147264.5684 | 878954.0707 | 1026218.6391 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 313.15 | 1 | 57504.0456 | 214471.2781 | 271975.3238 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 313.15 | 2 | 76221.9454 | 428942.5563 | 505164.5017 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 313.15 | 3 | 106212.0591 | 643413.8344 | 749625.8935 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043424 | 313.15 | 4 | 147474.3866 | 857885.1125 | 1005359.4991 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.033905 | 277.0389 | 15000
0.033905 | 280.9278 | 15000
0.033905 | 284.8167 | 15000
0.033905 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.043424 | 285.9278 | 15000
0.043424 | 295.0019 | 15000
0.043424 | 304.0759 | 15000
0.043424 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser