## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'Q': 600.0+ ton, 6.01 COP, 9.25 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 138dd29b-1fe6-431a-b926-b856bc2281fa |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'Q' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.92308 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Minimum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.097947 | 277.0389 | 0.12398 | 285.9278 | 1 | 47153.0735 | 553665.0499 | 600818.1234 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12398 | 285.9278 | 2 | 100684.5396 | 1107330.0998 | 1208014.6394 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12398 | 285.9278 | 3 | 177765.6802 | 1660995.1497 | 1838760.8299 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12398 | 285.9278 | 4 | 278396.4952 | 2214660.1996 | 2493056.6948 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12398 | 295.0019 | 1 | 59092.9487 | 559421.0187 | 618513.9674 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12398 | 295.0019 | 2 | 126179.3961 | 1118842.0374 | 1245021.4335 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12398 | 295.0019 | 3 | 222778.6537 | 1678263.0561 | 1901041.7098 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12398 | 295.0019 | 4 | 348890.7213 | 2237684.0748 | 2586574.7961 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12398 | 304.0759 | 1 | 66507.7395 | 539578.6852 | 606086.4248 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12398 | 304.0759 | 2 | 142011.9759 | 1079157.3705 | 1221169.3464 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12398 | 304.0759 | 3 | 250732.1936 | 1618736.0557 | 1869468.2494 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12398 | 304.0759 | 4 | 392668.3928 | 2158314.741 | 2550983.1338 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12398 | 313.15 | 1 | 68212.9319 | 494138.0496 | 562350.9815 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12398 | 313.15 | 2 | 145653.0219 | 988276.0991 | 1133929.121 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12398 | 313.15 | 3 | 257160.718 | 1482414.1487 | 1739574.8667 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12398 | 313.15 | 4 | 402736.0204 | 1976552.1983 | 2379288.2187 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 285.9278 | 1 | 44431.4493 | 575077.9189 | 619509.3682 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 285.9278 | 2 | 94873.1373 | 1150155.8378 | 1245028.9751 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 285.9278 | 3 | 167505.2382 | 1725233.7566 | 1892738.9948 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 285.9278 | 4 | 262327.7519 | 2300311.6755 | 2562639.4274 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 295.0019 | 1 | 56744.2954 | 588416.578 | 645160.8735 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 295.0019 | 2 | 121164.3874 | 1176833.1561 | 1297997.5434 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 295.0019 | 3 | 213924.3007 | 1765249.7341 | 1979174.0348 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 295.0019 | 4 | 335024.0356 | 2353666.3121 | 2688690.3477 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 304.0759 | 1 | 64972.5658 | 576156.9349 | 641129.5007 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 304.0759 | 2 | 138733.9655 | 1152313.8699 | 1291047.8354 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 304.0759 | 3 | 244944.6344 | 1728470.8048 | 1973415.4392 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 304.0759 | 4 | 383604.5724 | 2304627.7398 | 2688232.3122 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 313.15 | 1 | 67966.4243 | 538298.9896 | 606265.4139 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 313.15 | 2 | 145126.6616 | 1076597.9793 | 1221724.6408 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 313.15 | 3 | 256231.3917 | 1614896.9689 | 1871128.3606 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12398 | 313.15 | 4 | 401280.6146 | 2153195.9585 | 2554476.5732 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 285.9278 | 1 | 43053.7251 | 580449.5948 | 623503.32 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 285.9278 | 2 | 91931.3243 | 1160899.1897 | 1252830.514 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 285.9278 | 3 | 162311.2591 | 1741348.7845 | 1903660.0437 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 285.9278 | 4 | 254193.5295 | 2321798.3794 | 2575991.9089 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 295.0019 | 1 | 55358.6034 | 601370.9444 | 656729.5477 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 295.0019 | 2 | 118205.5608 | 1202741.8887 | 1320947.4495 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 295.0019 | 3 | 208700.283 | 1804112.8331 | 2012813.1161 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 295.0019 | 4 | 326842.7701 | 2405483.7775 | 2732326.5475 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 304.0759 | 1 | 63902.5036 | 596693.9917 | 660596.4953 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 304.0759 | 2 | 136449.0941 | 1193387.9833 | 1329837.0774 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 304.0759 | 3 | 240910.5321 | 1790081.975 | 2030992.5071 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 304.0759 | 4 | 377286.8178 | 2386775.9666 | 2764062.7845 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 313.15 | 1 | 67570.2678 | 566418.7367 | 633989.0045 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 313.15 | 2 | 144280.7605 | 1132837.4734 | 1277118.234 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 313.15 | 3 | 254737.8935 | 1699256.2101 | 1953994.1037 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12398 | 313.15 | 4 | 398941.6668 | 2265674.9468 | 2664616.6137 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 285.9278 | 1 | 43246.1298 | 569780.0778 | 613026.2076 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 285.9278 | 2 | 92342.1602 | 1139560.1557 | 1231902.3158 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 285.9278 | 3 | 163036.6189 | 1709340.2335 | 1872376.8524 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 285.9278 | 4 | 255329.5059 | 2279120.3113 | 2534449.8172 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 295.0019 | 1 | 55333.8624 | 598284.1177 | 653617.9801 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 295.0019 | 2 | 118152.7321 | 1196568.2354 | 1314720.9676 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 295.0019 | 3 | 208607.0103 | 1794852.3531 | 2003459.3634 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 295.0019 | 4 | 326696.6969 | 2393136.4708 | 2719833.1678 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 304.0759 | 1 | 63867.304 | 601189.8554 | 665057.1594 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 304.0759 | 2 | 136373.9333 | 1202379.7107 | 1338753.6441 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 304.0759 | 3 | 240777.8306 | 1803569.5661 | 2044347.3967 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 304.0759 | 4 | 377078.9957 | 2404759.4215 | 2781838.4171 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 313.15 | 1 | 67765.9743 | 578497.2908 | 646263.2651 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 313.15 | 2 | 144698.6468 | 1156994.5816 | 1301693.2283 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 313.15 | 3 | 255475.7012 | 1735491.8724 | 1990967.5736 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12398 | 313.15 | 4 | 400097.1378 | 2313989.1632 | 2714086.3009 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.097947 | 277.0389 | 15000
0.097947 | 280.9278 | 15000
0.097947 | 284.8167 | 15000
0.097947 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.12398 | 285.9278 | 15000
0.12398 | 295.0019 | 15000
0.12398 | 304.0759 | 15000
0.12398 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser