## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'U': 400.0+ ton, 6.01 COP, 9.25 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 557efc07-0375-48f2-acf0-9fd166db98d9 |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'U' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.88889 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Minimum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.067809 | 277.0389 | 0.085829 | 285.9278 | 1 | 34717.6788 | 411645.8754 | 446363.5542 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085829 | 285.9278 | 2 | 76883.0253 | 823291.7508 | 900174.7761 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085829 | 285.9278 | 3 | 139535.6414 | 1234937.6262 | 1374473.2676 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085829 | 285.9278 | 4 | 222675.5272 | 1646583.5016 | 1869259.0288 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085829 | 295.0019 | 1 | 38051.8853 | 380113.3098 | 418165.1952 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085829 | 295.0019 | 2 | 84266.6953 | 760226.6196 | 844493.3149 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085829 | 295.0019 | 3 | 152936.3255 | 1140339.9294 | 1293276.2549 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085829 | 295.0019 | 4 | 244060.7759 | 1520453.2392 | 1764514.0151 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085829 | 304.0759 | 1 | 37217.2956 | 341804.723 | 379022.0186 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085829 | 304.0759 | 2 | 82418.4788 | 683609.4461 | 766027.9249 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085829 | 304.0759 | 3 | 149581.982 | 1025414.1691 | 1174996.1511 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085829 | 304.0759 | 4 | 238707.8051 | 1367218.8922 | 1605926.6973 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085829 | 313.15 | 1 | 32838.8018 | 296720.1151 | 329558.9168 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085829 | 313.15 | 2 | 72722.2127 | 593440.2302 | 666162.4429 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085829 | 313.15 | 3 | 131984.1481 | 890160.3453 | 1022144.4934 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085829 | 313.15 | 4 | 210624.608 | 1186880.4604 | 1397505.0683 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 285.9278 | 1 | 36021.4704 | 460386.8982 | 496408.3686 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 285.9278 | 2 | 79770.299 | 920773.7964 | 1000544.0955 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 285.9278 | 3 | 144775.7785 | 1381160.6947 | 1525936.4731 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 285.9278 | 4 | 231037.9088 | 1841547.5929 | 2072585.5017 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 295.0019 | 1 | 41124.7735 | 435974.7395 | 477099.513 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 295.0019 | 2 | 91071.6703 | 871949.479 | 963021.1493 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 295.0019 | 3 | 165286.7312 | 1307924.2185 | 1473210.9497 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 295.0019 | 4 | 263769.956 | 1743898.958 | 2007668.9141 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 304.0759 | 1 | 41865.025 | 404786.5596 | 446651.5846 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 304.0759 | 2 | 92710.9727 | 809573.1192 | 902284.092 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 304.0759 | 3 | 168261.9147 | 1214359.6788 | 1382621.5936 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 304.0759 | 4 | 268517.851 | 1619146.2384 | 1887664.0894 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 313.15 | 1 | 38711.3253 | 366822.3585 | 405533.6838 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 313.15 | 2 | 85727.0389 | 733644.7171 | 819371.7559 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 313.15 | 3 | 155586.7151 | 1100467.0756 | 1256053.7907 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085829 | 313.15 | 4 | 248290.3541 | 1467289.4341 | 1715579.7882 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 285.9278 | 1 | 35766.7659 | 480562.5241 | 516329.29 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 285.9278 | 2 | 79206.2507 | 961125.0482 | 1040331.2988 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 285.9278 | 3 | 143752.0824 | 1441687.5722 | 1585439.6546 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 285.9278 | 4 | 229404.2613 | 1922250.0963 | 2151654.3576 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 295.0019 | 1 | 42079.8533 | 463270.7722 | 505350.6256 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 295.0019 | 2 | 93186.7146 | 926541.5445 | 1019728.259 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 295.0019 | 3 | 169125.3425 | 1389812.3167 | 1558937.6592 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 295.0019 | 4 | 269895.7373 | 1853083.0889 | 2122978.8262 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 304.0759 | 1 | 44028.9172 | 439202.9992 | 483231.9164 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 304.0759 | 2 | 97502.9573 | 878405.9984 | 975908.9557 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 304.0759 | 3 | 176958.9274 | 1317608.9976 | 1494567.925 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 304.0759 | 4 | 282396.8274 | 1756811.9968 | 2039208.8242 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 313.15 | 1 | 41927.2662 | 408359.205 | 450286.4712 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 313.15 | 2 | 92848.8071 | 816718.41 | 909567.2171 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 313.15 | 3 | 168512.0715 | 1225077.615 | 1393589.6865 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085829 | 313.15 | 4 | 268917.0594 | 1633436.82 | 1902353.8793 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 285.9278 | 1 | 34418.6132 | 472172.753 | 506591.3662 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 285.9278 | 2 | 76220.7382 | 944345.5059 | 1020566.2442 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 285.9278 | 3 | 138333.6511 | 1416518.2589 | 1554851.91 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 285.9278 | 4 | 220757.3519 | 1888691.0118 | 2109448.3637 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 295.0019 | 1 | 41403.617 | 462001.408 | 503405.025 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 295.0019 | 2 | 91689.1751 | 924002.816 | 1015691.991 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 295.0019 | 3 | 166407.4457 | 1386004.2239 | 1552411.6696 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 295.0019 | 4 | 265558.4288 | 1848005.6319 | 2113564.0607 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 304.0759 | 1 | 44216.9088 | 445054.0418 | 489270.9506 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 304.0759 | 2 | 97919.2685 | 890108.0836 | 988027.3522 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 304.0759 | 3 | 177714.494 | 1335162.1255 | 1512876.6195 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 304.0759 | 4 | 283602.5853 | 1780216.1673 | 2063818.7526 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 313.15 | 1 | 43016.0052 | 421330.6545 | 464346.6597 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 313.15 | 2 | 95259.8425 | 842661.309 | 937921.1515 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 313.15 | 3 | 172887.8797 | 1263991.9635 | 1436879.8431 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085829 | 313.15 | 4 | 275900.1167 | 1685322.6179 | 1961222.7347 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.067809 | 277.0389 | 15000
0.067809 | 280.9278 | 15000
0.067809 | 284.8167 | 15000
0.067809 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.085829 | 285.9278 | 15000
0.085829 | 295.0019 | 15000
0.085829 | 304.0759 | 15000
0.085829 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser