## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'Y': 300.0+ ton, 5.50 COP, 6.15 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | e1cea60c-a591-4c7c-8427-8b3b7fafccda |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'Y' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.85714 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Minimum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.052741 | 277.0389 | 0.067643 | 285.9278 | 1 | 65196.9676 | 303191.1415 | 368388.1091 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.067643 | 285.9278 | 2 | 88000.4037 | 606382.283 | 694382.6867 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.067643 | 285.9278 | 3 | 123859.3995 | 909573.4245 | 1033432.8241 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.067643 | 285.9278 | 4 | 172773.9553 | 1212764.566 | 1385538.5213 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.067643 | 295.0019 | 1 | 76251.4079 | 296784.0164 | 373035.4243 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.067643 | 295.0019 | 2 | 102921.2695 | 593568.0327 | 696489.3022 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.067643 | 295.0019 | 3 | 144860.3201 | 890352.0491 | 1035212.3691 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.067643 | 295.0019 | 4 | 202068.5596 | 1187136.0654 | 1389204.625 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.067643 | 304.0759 | 1 | 85145.4498 | 284599.8988 | 369745.3485 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.067643 | 304.0759 | 2 | 114926.1112 | 569199.7976 | 684125.9087 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.067643 | 304.0759 | 3 | 161756.9753 | 853799.6964 | 1015556.6716 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.067643 | 304.0759 | 4 | 225638.0421 | 1138399.5951 | 1364037.6372 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.067643 | 313.15 | 1 | 91133.6702 | 266638.7888 | 357772.459 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.067643 | 313.15 | 2 | 123008.7849 | 533277.5776 | 656286.3625 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.067643 | 313.15 | 3 | 173133.2312 | 799916.3664 | 973049.5976 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.067643 | 313.15 | 4 | 241507.0092 | 1066555.1552 | 1308062.1644 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 285.9278 | 1 | 64180.4705 | 326700.5842 | 390881.0547 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 285.9278 | 2 | 86628.3742 | 653401.1684 | 740029.5426 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 285.9278 | 3 | 121928.2863 | 980101.7527 | 1102030.0389 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 285.9278 | 4 | 170080.2067 | 1306802.3369 | 1476882.5436 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 295.0019 | 1 | 75809.6155 | 322226.3625 | 398035.978 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 295.0019 | 2 | 102324.9548 | 644452.7251 | 746777.6799 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 295.0019 | 3 | 144021.015 | 966679.0876 | 1110700.1027 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 295.0019 | 4 | 200897.7962 | 1288905.4502 | 1489803.2464 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 304.0759 | 1 | 85620.5231 | 311975.1484 | 397595.6716 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 304.0759 | 2 | 115567.3473 | 623950.2969 | 739517.6442 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 304.0759 | 3 | 162659.5066 | 935925.4453 | 1098584.9519 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 304.0759 | 4 | 226897.001 | 1247900.5938 | 1474797.5948 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 313.15 | 1 | 92923.1018 | 295946.9419 | 388870.0438 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 313.15 | 2 | 125424.0921 | 591893.8839 | 717317.976 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 313.15 | 3 | 176532.744 | 887840.8258 | 1064373.5698 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.067643 | 313.15 | 4 | 246249.0576 | 1183787.7678 | 1430036.8254 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 285.9278 | 1 | 63726.5892 | 337262.9865 | 400989.5757 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 285.9278 | 2 | 86015.7424 | 674525.9729 | 760541.7153 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 285.9278 | 3 | 121066.0152 | 1011788.9594 | 1132854.9746 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 285.9278 | 4 | 168877.4075 | 1349051.9458 | 1517929.3534 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 295.0019 | 1 | 75211.297 | 334721.6683 | 409932.9652 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 295.0019 | 2 | 101517.3671 | 669443.3365 | 770960.7036 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 295.0019 | 3 | 142884.346 | 1004165.0048 | 1147049.3508 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 295.0019 | 4 | 199312.2338 | 1338886.673 | 1538198.9069 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 304.0759 | 1 | 85127.457 | 326403.3576 | 411530.8147 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 304.0759 | 2 | 114901.8253 | 652806.7153 | 767708.5406 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 304.0759 | 3 | 161722.7932 | 979210.0729 | 1140932.8661 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 304.0759 | 4 | 225590.3608 | 1305613.4306 | 1531203.7914 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 313.15 | 1 | 92840.3093 | 312308.0546 | 405148.3639 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 313.15 | 2 | 125312.3418 | 624616.1092 | 749928.451 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 313.15 | 3 | 176375.457 | 936924.1639 | 1113299.6208 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.067643 | 313.15 | 4 | 246029.6548 | 1249232.2185 | 1495261.8732 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 285.9278 | 1 | 64477.8858 | 334878.3482 | 399356.234 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 285.9278 | 2 | 87029.8141 | 669756.6965 | 756786.5106 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 285.9278 | 3 | 122493.3077 | 1004635.0447 | 1127128.3524 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 285.9278 | 4 | 170868.3663 | 1339513.393 | 1510381.7593 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 295.0019 | 1 | 75282.6242 | 334269.9335 | 409552.5577 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 295.0019 | 2 | 101613.6419 | 668539.867 | 770153.5089 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 295.0019 | 3 | 143019.8515 | 1002809.8006 | 1145829.6521 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 295.0019 | 4 | 199501.2532 | 1337079.7341 | 1536580.9872 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 304.0759 | 1 | 84676.0333 | 327884.5264 | 412560.5597 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 304.0759 | 2 | 114292.5106 | 655769.0528 | 770061.5634 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 304.0759 | 3 | 160865.1909 | 983653.5791 | 1144518.77 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 304.0759 | 4 | 224394.0742 | 1311538.1055 | 1535932.1797 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 313.15 | 1 | 92078.6844 | 315722.1268 | 407800.8112 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 313.15 | 2 | 124284.3293 | 631444.2537 | 755728.583 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 313.15 | 3 | 174928.5431 | 947166.3805 | 1122094.9235 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.067643 | 313.15 | 4 | 244011.3256 | 1262888.5073 | 1506899.8329 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.052741 | 277.0389 | 15000
0.052741 | 280.9278 | 15000
0.052741 | 284.8167 | 15000
0.052741 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.067643 | 285.9278 | 15000
0.067643 | 295.0019 | 15000
0.067643 | 304.0759 | 15000
0.067643 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser