## Instructions
This spreadsheet serves as a template for ASHRAE Standard 205 compliant representations corresponding to RS0001 "Liquid-Cooled Chiller".
General Instructions:
Only the names and values are read out of this sheet using the SI-unit system defined in the standard. Any other columns are for user-information only.
Do not change Data Group, Data Element, or sheet names. These are used to translate the spreadsheet into simulation data.
If data group is not required, it's required elements are only required if the data group is present
RSID, RSVersion, and RSTitle should not be changed (they are set by the schema associated with this template).
Performance maps and array data groups each have separate sheets to enable an extensible number of entries in consecutive rows.
Performance map grid variables are colored in blue and must be entered in the order defined by the standard (with the rightmost column varying with the highest frequency)
The structure of the data here does not necessarily reflect the actual hierarchical data structure as defined in the standard. It has been modified for user readability, but contains all necessary data elements for simulation purposes.
This instruction sheet is informative only. It may be removed once data entry is complete.

## RS0001
Data Group | Data Element | Value | Units | Required?
ASHRAE205 |  |  |  | Yes
| RSID | RS0001 |  | Yes
| RSVersion | 0.1.0 |  | Yes
| RSTitle | Liquid-Cooled Chillers |  | Yes
| ID | UID123456789 |  | Yes
| dataTimeStamp | 2019-02-04 14:20 |  | Yes
| dataVersion | A205DV-1
| description | Water Cooled Centrifugal Chiller
| dataSource | CWI-ChilSelect
notes
Description/ProductInformation
| manufacturer | ColdWaterInc |  | Yes
| manufacturerSoftwareVersion | CW.2019.01 |  | Yes
| modelNumber | CC-500-VS |  | Yes
| nominalVoltage | 460 | V | Yes
| nominalFrequency | 60 | Hz | Yes
| toleranceStandard | AHRI 551/591-2015
| compressorType | Centrifugal |  | Yes
| driveType | variableSpeed |  | Yes
| liquidDataSource | AHRI 551/591-2015
| refrigerantType | R134a |  | Yes
| hotgasBypassInstalled | 0
Description/RatingAHRI
| certificationReferenceNumber | 987654 |  | Yes
| standardRatingVersion | AHRI_551_591_2015 |  | Yes
| designNetRefrigeratingCapacity | 1758000 | W | Yes
| designInputPower | 284900 | W | Yes
| designCOP | 6.171 |  | Yes
| designPartLoadValue | 10.36 |  | Yes
| designEvaporatorLiquidVolumetricFlowRate | 0.008385 | m3/s | Yes
| designEvaporatorLiquidLeavingTemperature | 7 | C | Yes
| designEvaporatorLiquidEnteringTemperature | 12 | C | Yes
| designEvaporatorLiquidDifferentialPressure | 53100 | Pa | Yes
| designCondenserLiquidVolumetricFlowRate | 0.009737 | m3/s | Yes
| designCondenserLiquidEnteringTemperature | 30 | C | Yes
| designCondenserLiquidLeavingTemperature | 35 | C | Yes
| designCondenserLiquidDifferentialPressure | 36400 | Pa | Yes
Performance |  |  |  | Yes
| evaporatorLiquidType | water |  | Yes
| condenserLiquidType | water |  | Yes
| evaporatorFoulingFactor | 1.8e-05 | m2-K/W | Yes
| condenserFoulingFactor | 4.4e-05 | m2-K/W | Yes
| unitPowerLimit | 315000 | W

## PerformanceMapCooling
evaporatorLiquidVolumetricFlowRate | evaporatorLiquidLeavingTemperature | condenserLiquidVolumetricFlowRate | condenserLiquidEnteringTemperature | netEvaporatorCapacityFraction | inputPower | netEvaporatorCapacity | netCondenserCapacity | evaporatorLiquidEnteringTemperature | condenserLiquidLeavingTemperature | evaporatorLiquidDifferentialPressure | condenserLiquidDifferentialPressure | oilCoolerHeat | motorControllerHeat
m3/s | C | m3/s | C |  | W | W | W | C | C | Pa | Pa | W | W
0.05737 | 5 | 0.09437 | 30 | 1 | 306000 | 1758000 | 2055000 | 12 | 35.2325 | 27.3 | 34.4 | 0 | 9177
0.05737 | 5 | 0.09437 | 30 | 0.9 | 267000 | 1582000 | 1841000 | 12 | 34.6881 | 27.3 | 34.4 | 0 | 8002
0.05737 | 5 | 0.09437 | 30 | 0.8 | 230000 | 1406000 | 1630000 | 12 | 34.1508 | 27.3 | 34.4 | 0 | 6913
0.05737 | 5 | 0.09437 | 30 | 0.7 | 200000 | 1231000 | 1425000 | 12 | 33.628 | 27.3 | 34.4 | 0 | 6001
0.05737 | 5 | 0.09437 | 30 | 0.6 | 174000 | 1055000 | 1223000 | 12 | 33.1154 | 27.3 | 34.4 | 0 | 5213
0.05737 | 5 | 0.09437 | 30 | 0.5 | 153000 | 879000 | 1027000 | 12 | 32.6161 | 27.3 | 34.4 | 0 | 4586
0.05737 | 5 | 0.09437 | 30 | 0.4 | 127000 | 703000 | 827000 | 12 | 32.1052 | 27.3 | 34.4 | 0 | 3819
0.05737 | 5 | 0.09437 | 30 | 0.3 | 105000 | 527000 | 630000 | 12 | 31.6032 | 27.3 | 34.4 | 0 | 3159
0.05737 | 5 | 0.09437 | 30 | 0.2 | 83000 | 352000 | 432000 | 12 | 31.1009 | 27.3 | 34.4 | 0 | 2496
0.05737 | 5 | 0.09437 | 30 | 0.15 | 71000 | 264000 | 333000 | 12 | 30.8481 | 27.3 | 34.4 | 0 | 2144
0.05737 | 5 | 0.09437 | 27 | 1 | 275000 | 1758000 | 2024000 | 12 | 32.1502 | 27.3 | 34.4 | 0 | 8242
0.05737 | 5 | 0.09437 | 27 | 0.9 | 238000 | 1582000 | 1813000 | 12 | 31.613 | 27.3 | 34.4 | 0 | 7147
0.05737 | 5 | 0.09437 | 27 | 0.8 | 204000 | 1406000 | 1605000 | 12 | 31.0821 | 27.3 | 34.4 | 0 | 6130
0.05737 | 5 | 0.09437 | 27 | 0.7 | 175000 | 1231000 | 1401000 | 12 | 30.5634 | 27.3 | 34.4 | 0 | 5261
0.05737 | 5 | 0.09437 | 27 | 0.6 | 150000 | 1055000 | 1201000 | 12 | 30.0542 | 27.3 | 34.4 | 0 | 4508
0.05737 | 5 | 0.09437 | 27 | 0.5 | 131000 | 879000 | 1006000 | 12 | 29.5588 | 27.3 | 34.4 | 0 | 3922
0.05737 | 5 | 0.09437 | 27 | 0.4 | 109000 | 703000 | 809000 | 12 | 29.0587 | 27.3 | 34.4 | 0 | 3279
0.05737 | 5 | 0.09437 | 27 | 0.3 | 90000 | 527000 | 615000 | 12 | 28.5643 | 27.3 | 34.4 | 0 | 2706
0.05737 | 5 | 0.09437 | 27 | 0.2 | 71000 | 352000 | 421000 | 12 | 28.0704 | 27.3 | 34.4 | 0 | 2140
0.05737 | 5 | 0.09437 | 27 | 0.15 | 61000 | 264000 | 323000 | 12 | 27.8222 | 27.3 | 34.4 | 0 | 1841
0.05737 | 5 | 0.09437 | 24 | 1 | 246000 | 1758000 | 1996000 | 12 | 29.0734 | 27.3 | 34.4 | 0 | 7372
0.05737 | 5 | 0.09437 | 24 | 0.9 | 210000 | 1582000 | 1786000 | 12 | 28.5397 | 27.3 | 34.4 | 0 | 6314
0.05737 | 5 | 0.09437 | 24 | 0.8 | 181000 | 1406000 | 1582000 | 12 | 28.0193 | 27.3 | 34.4 | 0 | 5418
0.05737 | 5 | 0.09437 | 24 | 0.7 | 153000 | 1231000 | 1379000 | 12 | 27.5044 | 27.3 | 34.4 | 0 | 4588
0.05737 | 5 | 0.09437 | 24 | 0.6 | 129000 | 1055000 | 1180000 | 12 | 26.9993 | 27.3 | 34.4 | 0 | 3879
0.05737 | 5 | 0.09437 | 24 | 0.5 | 110000 | 879000 | 985000 | 12 | 26.5039 | 27.3 | 34.4 | 0 | 3287
0.05737 | 5 | 0.09437 | 24 | 0.4 | 95000 | 703000 | 795000 | 12 | 26.0211 | 27.3 | 34.4 | 0 | 2849
0.05737 | 5 | 0.09437 | 24 | 0.3 | 77000 | 527000 | 602000 | 12 | 25.5295 | 27.3 | 34.4 | 0 | 2303
0.05737 | 5 | 0.09437 | 24 | 0.2 | 61000 | 352000 | 411000 | 12 | 25.0434 | 27.3 | 34.4 | 0 | 1824
0.05737 | 5 | 0.09437 | 24 | 0.15 | 52000 | 264000 | 315000 | 12 | 24.7995 | 27.3 | 34.4 | 0 | 1574
0.05737 | 5 | 0.09437 | 21 | 1 | 218000 | 1758000 | 1970000 | 12 | 26 | 27.3 | 34.4 | 0 | 6543
0.05737 | 5 | 0.09437 | 21 | 0.9 | 186000 | 1582000 | 1763000 | 12 | 25.4752 | 27.3 | 34.4 | 0 | 5588
0.05737 | 5 | 0.09437 | 21 | 0.8 | 157000 | 1406000 | 1559000 | 12 | 24.9579 | 27.3 | 34.4 | 0 | 4723
0.05737 | 5 | 0.09437 | 21 | 0.7 | 132000 | 1231000 | 1359000 | 12 | 24.4503 | 27.3 | 34.4 | 0 | 3975
0.05737 | 5 | 0.09437 | 21 | 0.6 | 110000 | 1055000 | 1162000 | 12 | 23.9494 | 27.3 | 34.4 | 0 | 3310
0.05737 | 5 | 0.09437 | 21 | 0.5 | 92000 | 879000 | 968000 | 12 | 23.4584 | 27.3 | 34.4 | 0 | 2765
0.05737 | 5 | 0.09437 | 21 | 0.4 | 76000 | 703000 | 777000 | 12 | 22.9728 | 27.3 | 34.4 | 0 | 2286
0.05737 | 5 | 0.09437 | 21 | 0.3 | 64000 | 527000 | 590000 | 12 | 22.4966 | 27.3 | 34.4 | 0 | 1922
0.05737 | 5 | 0.09437 | 21 | 0.2 | 51000 | 352000 | 401000 | 12 | 22.0176 | 27.3 | 34.4 | 0 | 1523
0.05737 | 5 | 0.09437 | 21 | 0.15 | 44000 | 264000 | 306000 | 12 | 21.7777 | 27.3 | 34.4 | 0 | 1319
0.05737 | 5 | 0.09437 | 18 | 1 | 195000 | 1758000 | 1947000 | 12 | 22.938 | 27.3 | 34.4 | 0 | 5855
0.05737 | 5 | 0.09437 | 18 | 0.9 | 163000 | 1582000 | 1740000 | 12 | 22.4134 | 27.3 | 34.4 | 0 | 4895
0.05737 | 5 | 0.09437 | 18 | 0.8 | 136000 | 1406000 | 1539000 | 12 | 21.9018 | 27.3 | 34.4 | 0 | 4092
0.05737 | 5 | 0.09437 | 18 | 0.7 | 113000 | 1231000 | 1341000 | 12 | 21.3995 | 27.3 | 34.4 | 0 | 3403
0.05737 | 5 | 0.09437 | 18 | 0.6 | 93000 | 1055000 | 1145000 | 12 | 20.9035 | 27.3 | 34.4 | 0 | 2790
0.05737 | 5 | 0.09437 | 18 | 0.5 | 77000 | 879000 | 953000 | 12 | 20.4176 | 27.3 | 34.4 | 0 | 2301
0.05737 | 5 | 0.09437 | 18 | 0.4 | 63000 | 703000 | 764000 | 12 | 19.9376 | 27.3 | 34.4 | 0 | 1884
0.05737 | 5 | 0.09437 | 18 | 0.3 | 54000 | 527000 | 580000 | 12 | 19.4704 | 27.3 | 34.4 | 0 | 1623
0.05737 | 5 | 0.09437 | 18 | 0.2 | 42000 | 352000 | 392000 | 12 | 18.9938 | 27.3 | 34.4 | 0 | 1247
0.05737 | 5 | 0.09437 | 18 | 0.15 | 36000 | 264000 | 299000 | 12 | 18.7577 | 27.3 | 34.4 | 0 | 1085
0.05737 | 5 | 0.09437 | 17.5 | 1 | 191000 | 1758000 | 1944000 | 12 | 22.4274 | 27.3 | 34.4 | 0 | 5738
0.05737 | 5 | 0.09437 | 17.5 | 0.9 | 160000 | 1582000 | 1737000 | 12 | 21.9037 | 27.3 | 34.4 | 0 | 4786
0.05737 | 5 | 0.09437 | 17.5 | 0.8 | 133000 | 1406000 | 1535000 | 12 | 21.3928 | 27.3 | 34.4 | 0 | 3992
0.05737 | 5 | 0.09437 | 17.5 | 0.7 | 110000 | 1231000 | 1338000 | 12 | 20.8913 | 27.3 | 34.4 | 0 | 3311
0.05737 | 5 | 0.09437 | 17.5 | 0.6 | 90000 | 1055000 | 1142000 | 12 | 20.3961 | 27.3 | 34.4 | 0 | 2707
0.05737 | 5 | 0.09437 | 17.5 | 0.5 | 74000 | 879000 | 951000 | 12 | 19.9111 | 27.3 | 34.4 | 0 | 2227
0.05737 | 5 | 0.09437 | 17.5 | 0.4 | 61000 | 703000 | 762000 | 12 | 19.4322 | 27.3 | 34.4 | 0 | 1822
0.05737 | 5 | 0.09437 | 17.5 | 0.3 | 52000 | 527000 | 578000 | 12 | 18.9646 | 27.3 | 34.4 | 0 | 1556
0.05737 | 5 | 0.09437 | 17.5 | 0.2 | 40000 | 352000 | 391000 | 12 | 18.4903 | 27.3 | 34.4 | 0 | 1206
0.05737 | 5 | 0.09437 | 17.5 | 0.15 | 35000 | 264000 | 298000 | 12 | 18.2545 | 27.3 | 34.4 | 0 | 1049
0.05737 | 5 | 0.09437 | 17 | 1 | 187000 | 1758000 | 1939000 | 12 | 21.9161 | 27.3 | 34.4 | 0 | 5611
0.05737 | 5 | 0.09437 | 17 | 0.9 | 156000 | 1582000 | 1733000 | 12 | 21.3938 | 27.3 | 34.4 | 0 | 4676
0.05737 | 5 | 0.09437 | 17 | 0.8 | 130000 | 1406000 | 1532000 | 12 | 20.8842 | 27.3 | 34.4 | 0 | 3896
0.05737 | 5 | 0.09437 | 17 | 0.7 | 107000 | 1231000 | 1335000 | 12 | 20.3834 | 27.3 | 34.4 | 0 | 3221
0.05737 | 5 | 0.09437 | 17 | 0.6 | 88000 | 1055000 | 1140000 | 12 | 19.8889 | 27.3 | 34.4 | 0 | 2626
0.05737 | 5 | 0.09437 | 17 | 0.5 | 72000 | 879000 | 949000 | 12 | 19.4048 | 27.3 | 34.4 | 0 | 2156
0.05737 | 5 | 0.09437 | 17 | 0.4 | 59000 | 703000 | 760000 | 12 | 18.9267 | 27.3 | 34.4 | 0 | 1759
0.05737 | 5 | 0.09437 | 17 | 0.3 | 50000 | 527000 | 576000 | 12 | 18.4598 | 27.3 | 34.4 | 0 | 1500
0.05737 | 5 | 0.09437 | 17 | 0.2 | 39000 | 352000 | 389000 | 12 | 17.9865 | 27.3 | 34.4 | 0 | 1162
0.05737 | 5 | 0.09437 | 17 | 0.15 | 34000 | 264000 | 296000 | 12 | 17.7514 | 27.3 | 34.4 | 0 | 1012
0.05737 | 5 | 0.09437 | 16.5 | 1 | 183000 | 1758000 | 1935000 | 12 | 21.4048 | 27.3 | 34.4 | 0 | 5485
0.05737 | 5 | 0.09437 | 16.5 | 0.9 | 152000 | 1582000 | 1730000 | 12 | 20.8845 | 27.3 | 34.4 | 0 | 4573
0.05737 | 5 | 0.09437 | 16.5 | 0.8 | 127000 | 1406000 | 1529000 | 12 | 20.376 | 27.3 | 34.4 | 0 | 3805
0.05737 | 5 | 0.09437 | 16.5 | 0.7 | 104000 | 1231000 | 1332000 | 12 | 19.8755 | 27.3 | 34.4 | 0 | 3134
0.05737 | 5 | 0.09437 | 16.5 | 0.6 | 85000 | 1055000 | 1137000 | 12 | 19.382 | 27.3 | 34.4 | 0 | 2548
0.05737 | 5 | 0.09437 | 16.5 | 0.5 | 69000 | 879000 | 946000 | 12 | 18.8985 | 27.3 | 34.4 | 0 | 2085
0.05737 | 5 | 0.09437 | 16.5 | 0.4 | 57000 | 703000 | 758000 | 12 | 18.4214 | 27.3 | 34.4 | 0 | 1700
0.05737 | 5 | 0.09437 | 16.5 | 0.3 | 45000 | 527000 | 572000 | 12 | 17.9484 | 27.3 | 34.4 | 0 | 1364
0.05737 | 5 | 0.09437 | 16.5 | 0.2 | 37000 | 352000 | 388000 | 12 | 17.4829 | 27.3 | 34.4 | 0 | 1121
0.05737 | 5 | 0.09437 | 16.5 | 0.15 | 33000 | 264000 | 295000 | 12 | 17.2484 | 27.3 | 34.4 | 0 | 977
0.05737 | 5 | 0.09437 | 16 | 1 | 179000 | 1758000 | 1931000 | 12 | 20.8937 | 27.3 | 34.4 | 0 | 5361
0.05737 | 5 | 0.09437 | 16 | 0.9 | 149000 | 1582000 | 1727000 | 12 | 20.3755 | 27.3 | 34.4 | 0 | 4474
0.05737 | 5 | 0.09437 | 16 | 0.8 | 124000 | 1406000 | 1526000 | 12 | 19.8676 | 27.3 | 34.4 | 0 | 3711
0.05737 | 5 | 0.09437 | 16 | 0.7 | 102000 | 1231000 | 1329000 | 12 | 19.3676 | 27.3 | 34.4 | 0 | 3046
0.05737 | 5 | 0.09437 | 16 | 0.6 | 82000 | 1055000 | 1135000 | 12 | 18.8749 | 27.3 | 34.4 | 0 | 2468
0.05737 | 5 | 0.09437 | 16 | 0.5 | 67000 | 879000 | 944000 | 12 | 18.3924 | 27.3 | 34.4 | 0 | 2016
0.05737 | 5 | 0.09437 | 16 | 0.4 | 55000 | 703000 | 756000 | 12 | 17.9163 | 27.3 | 34.4 | 0 | 1642
0.05737 | 5 | 0.09437 | 16 | 0.3 | 44000 | 527000 | 570000 | 12 | 17.4441 | 27.3 | 34.4 | 0 | 1315
0.05737 | 5 | 0.09437 | 16 | 0.2 | 36000 | 352000 | 387000 | 12 | 16.9794 | 27.3 | 34.4 | 0 | 1080
0.05737 | 5 | 0.09437 | 16 | 0.15 | 31000 | 264000 | 294000 | 12 | 16.7454 | 27.3 | 34.4 | 0 | 942
0.05737 | 5 | 0.09437 | 15.5 | 1 | 175000 | 1758000 | 1928000 | 12 | 20.383 | 27.3 | 34.4 | 0 | 5243
0.05737 | 5 | 0.09437 | 15.5 | 0.9 | 146000 | 1582000 | 1724000 | 12 | 19.8665 | 27.3 | 34.4 | 0 | 4375
0.05737 | 5 | 0.09437 | 15.5 | 0.8 | 121000 | 1406000 | 1523000 | 12 | 19.3595 | 27.3 | 34.4 | 0 | 3622
0.05737 | 5 | 0.09437 | 15.5 | 0.7 | 99000 | 1231000 | 1326000 | 12 | 18.86 | 27.3 | 34.4 | 0 | 2961
0.05737 | 5 | 0.09437 | 15.5 | 0.6 | 80000 | 1055000 | 1132000 | 12 | 18.368 | 27.3 | 34.4 | 0 | 2392
0.05737 | 5 | 0.09437 | 15.5 | 0.5 | 65000 | 879000 | 942000 | 12 | 17.8864 | 27.3 | 34.4 | 0 | 1949
0.05737 | 5 | 0.09437 | 15.5 | 0.4 | 53000 | 703000 | 754000 | 12 | 17.4111 | 27.3 | 34.4 | 0 | 1584
0.05737 | 5 | 0.09437 | 15.5 | 0.3 | 45000 | 527000 | 571000 | 12 | 16.946 | 27.3 | 34.4 | 0 | 1342
0.05737 | 5 | 0.09437 | 15.5 | 0.2 | 36000 | 352000 | 387000 | 12 | 16.4793 | 27.3 | 34.4 | 0 | 1082
0.05737 | 5 | 0.09437 | 15.5 | 0.15 | 30000 | 264000 | 293000 | 12 | 16.2424 | 27.3 | 34.4 | 0 | 908
0.05737 | 5 | 0.09437 | 15 | 1 | 171000 | 1758000 | 1924000 | 12 | 19.8732 | 27.3 | 34.4 | 0 | 5135
0.05737 | 5 | 0.09437 | 15 | 0.9 | 143000 | 1582000 | 1720000 | 12 | 19.3576 | 27.3 | 34.4 | 0 | 4276
0.05737 | 5 | 0.09437 | 15 | 0.8 | 118000 | 1406000 | 1521000 | 12 | 18.8512 | 27.3 | 34.4 | 0 | 3531
0.05737 | 5 | 0.09437 | 15 | 0.7 | 96000 | 1231000 | 1324000 | 12 | 18.3525 | 27.3 | 34.4 | 0 | 2877
0.05737 | 5 | 0.09437 | 15 | 0.6 | 78000 | 1055000 | 1130000 | 12 | 17.8623 | 27.3 | 34.4 | 0 | 2328
0.05737 | 5 | 0.09437 | 15 | 0.5 | 63000 | 879000 | 940000 | 12 | 17.3805 | 27.3 | 34.4 | 0 | 1882
0.05737 | 5 | 0.09437 | 15 | 0.4 | 51000 | 703000 | 753000 | 12 | 16.9061 | 27.3 | 34.4 | 0 | 1526
0.05737 | 5 | 0.09437 | 15 | 0.3 | 43000 | 527000 | 569000 | 12 | 16.4415 | 27.3 | 34.4 | 0 | 1291
0.05737 | 5 | 0.09437 | 15 | 0.2 | 34000 | 352000 | 385000 | 12 | 15.975 | 27.3 | 34.4 | 0 | 1032
0.05737 | 5 | 0.09437 | 15 | 0.15 | 29000 | 264000 | 292000 | 12 | 15.7394 | 27.3 | 34.4 | 0 | 873
0.05737 | 5 | 0.09437 | 14.5 | 1 | 169000 | 1758000 | 1921000 | 12 | 19.3657 | 27.3 | 34.4 | 0 | 5057
0.05737 | 5 | 0.09437 | 14.5 | 0.9 | 140000 | 1582000 | 1718000 | 12 | 18.8493 | 27.3 | 34.4 | 0 | 4186
0.05737 | 5 | 0.09437 | 14.5 | 0.8 | 115000 | 1406000 | 1518000 | 12 | 18.3434 | 27.3 | 34.4 | 0 | 3444
0.05737 | 5 | 0.09437 | 14.5 | 0.7 | 93000 | 1231000 | 1321000 | 12 | 17.8452 | 27.3 | 34.4 | 0 | 2797
0.05737 | 5 | 0.09437 | 14.5 | 0.6 | 75000 | 1055000 | 1128000 | 12 | 17.3556 | 27.3 | 34.4 | 0 | 2254
0.05737 | 5 | 0.09437 | 14.5 | 0.5 | 61000 | 879000 | 938000 | 12 | 16.8747 | 27.3 | 34.4 | 0 | 1817
0.05737 | 5 | 0.09437 | 14.5 | 0.4 | 50000 | 703000 | 752000 | 12 | 16.4034 | 27.3 | 34.4 | 0 | 1498
0.05737 | 5 | 0.09437 | 14.5 | 0.3 | 41000 | 527000 | 567000 | 12 | 15.9357 | 27.3 | 34.4 | 0 | 1224
0.05737 | 5 | 0.09437 | 14.5 | 0.2 | 33000 | 352000 | 384000 | 12 | 15.4712 | 27.3 | 34.4 | 0 | 988
0.05737 | 5 | 0.09437 | 14.5 | 0.15 | 28000 | 264000 | 291000 | 12 | 15.2368 | 27.3 | 34.4 | 0 | 843
0.05737 | 5 | 0.09437 | 14 | 1 | 165000 | 1758000 | 1918000 | 12 | 18.8566 | 27.3 | 34.4 | 0 | 4957
0.05737 | 5 | 0.09437 | 14 | 0.9 | 137000 | 1582000 | 1715000 | 12 | 18.341 | 27.3 | 34.4 | 0 | 4095
0.05737 | 5 | 0.09437 | 14 | 0.8 | 112000 | 1406000 | 1515000 | 12 | 17.8354 | 27.3 | 34.4 | 0 | 3357
0.05737 | 5 | 0.09437 | 14 | 0.7 | 91000 | 1231000 | 1319000 | 12 | 17.3381 | 27.3 | 34.4 | 0 | 2719
0.05737 | 5 | 0.09437 | 14 | 0.6 | 73000 | 1055000 | 1125000 | 12 | 16.8491 | 27.3 | 34.4 | 0 | 2182
0.05737 | 5 | 0.09437 | 14 | 0.5 | 58000 | 879000 | 936000 | 12 | 16.3688 | 27.3 | 34.4 | 0 | 1752
0.05737 | 5 | 0.09437 | 14 | 0.4 | 48000 | 703000 | 750000 | 12 | 15.898 | 27.3 | 34.4 | 0 | 1438
0.05737 | 5 | 0.09437 | 14 | 0.3 | 39000 | 527000 | 565000 | 12 | 15.4313 | 27.3 | 34.4 | 0 | 1173
0.05737 | 5 | 0.09437 | 14 | 0.2 | 32000 | 352000 | 382000 | 12 | 14.9679 | 27.3 | 34.4 | 0 | 950
0.05737 | 5 | 0.09437 | 14 | 0.15 | 27000 | 264000 | 290000 | 12 | 14.7346 | 27.3 | 34.4 | 0 | 819
0.05737 | 5 | 0.09437 | 13.5 | 1 | 169000 | 1758000 | 1921000 | 12 | 18.3637 | 27.3 | 34.4 | 0 | 5057
0.05737 | 5 | 0.09437 | 13.5 | 0.9 | 134000 | 1582000 | 1712000 | 12 | 17.8333 | 27.3 | 34.4 | 0 | 4012
0.05737 | 5 | 0.09437 | 13.5 | 0.8 | 109000 | 1406000 | 1512000 | 12 | 17.3278 | 27.3 | 34.4 | 0 | 3273
0.05737 | 5 | 0.09437 | 13.5 | 0.7 | 88000 | 1231000 | 1316000 | 12 | 16.831 | 27.3 | 34.4 | 0 | 2641
0.05737 | 5 | 0.09437 | 13.5 | 0.6 | 70000 | 1055000 | 1123000 | 12 | 16.3427 | 27.3 | 34.4 | 0 | 2111
0.05737 | 5 | 0.09437 | 13.5 | 0.5 | 56000 | 879000 | 934000 | 12 | 15.8632 | 27.3 | 34.4 | 0 | 1689
0.05737 | 5 | 0.09437 | 13.5 | 0.4 | 46000 | 703000 | 748000 | 12 | 15.3929 | 27.3 | 34.4 | 0 | 1381
0.05737 | 5 | 0.09437 | 13.5 | 0.3 | 38000 | 527000 | 564000 | 12 | 14.9277 | 27.3 | 34.4 | 0 | 1133
0.05737 | 5 | 0.09437 | 13.5 | 0.2 | 31000 | 352000 | 381000 | 12 | 14.4653 | 27.3 | 34.4 | 0 | 920
0.05737 | 5 | 0.09437 | 13.5 | 0.15 | 27000 | 264000 | 290000 | 12 | 14.2347 | 27.3 | 34.4 | 0 | 822
0.05737 | 5 | 0.09437 | 13 | 1 | 173000 | 1758000 | 1926000 | 12 | 17.8728 | 27.3 | 34.4 | 0 | 5181
0.05737 | 5 | 0.09437 | 13 | 0.9 | 131000 | 1582000 | 1709000 | 12 | 17.3258 | 27.3 | 34.4 | 0 | 3933
0.05737 | 5 | 0.09437 | 13 | 0.8 | 106000 | 1406000 | 1510000 | 12 | 16.8201 | 27.3 | 34.4 | 0 | 3189
0.05737 | 5 | 0.09437 | 13 | 0.7 | 86000 | 1231000 | 1314000 | 12 | 16.3243 | 27.3 | 34.4 | 0 | 2567
0.05737 | 5 | 0.09437 | 13 | 0.6 | 68000 | 1055000 | 1121000 | 12 | 15.8364 | 27.3 | 34.4 | 0 | 2042
0.05737 | 5 | 0.09437 | 13 | 0.5 | 54000 | 879000 | 932000 | 12 | 15.3576 | 27.3 | 34.4 | 0 | 1627
0.05737 | 5 | 0.09437 | 13 | 0.4 | 44000 | 703000 | 746000 | 12 | 14.8887 | 27.3 | 34.4 | 0 | 1334
0.05737 | 5 | 0.09437 | 13 | 0.3 | 37000 | 527000 | 563000 | 12 | 14.4246 | 27.3 | 34.4 | 0 | 1100
0.05737 | 5 | 0.09437 | 13 | 0.2 | 30000 | 352000 | 381000 | 12 | 13.9629 | 27.3 | 34.4 | 0 | 894
0.05737 | 5 | 0.09437 | 13 | 0.15 | 27000 | 264000 | 290000 | 12 | 13.7327 | 27.3 | 34.4 | 0 | 799
0.05737 | 5 | 0.09437 | 12.5 | 1 | 174000 | 1758000 | 1927000 | 12 | 17.3751 | 27.3 | 34.4 | 0 | 5222
0.05737 | 5 | 0.09437 | 12.5 | 0.9 | 128000 | 1582000 | 1706000 | 12 | 16.8173 | 27.3 | 34.4 | 0 | 3840
0.05737 | 5 | 0.09437 | 12.5 | 0.8 | 104000 | 1406000 | 1507000 | 12 | 16.3127 | 27.3 | 34.4 | 0 | 3109
0.05737 | 5 | 0.09437 | 12.5 | 0.7 | 83000 | 1231000 | 1311000 | 12 | 15.8176 | 27.3 | 34.4 | 0 | 2494
0.05737 | 5 | 0.09437 | 12.5 | 0.6 | 66000 | 1055000 | 1119000 | 12 | 15.3303 | 27.3 | 34.4 | 0 | 1974
0.05737 | 5 | 0.09437 | 12.5 | 0.5 | 52000 | 879000 | 930000 | 12 | 14.8524 | 27.3 | 34.4 | 0 | 1570
0.05737 | 5 | 0.09437 | 12.5 | 0.4 | 43000 | 703000 | 745000 | 12 | 14.3849 | 27.3 | 34.4 | 0 | 1292
0.05737 | 5 | 0.09437 | 12.5 | 0.3 | 36000 | 527000 | 562000 | 12 | 13.9221 | 27.3 | 34.4 | 0 | 1072
0.05737 | 5 | 0.09437 | 12.5 | 0.2 | 29000 | 352000 | 380000 | 12 | 13.4609 | 27.3 | 34.4 | 0 | 872
0.05737 | 5 | 0.09437 | 12.5 | 0.15 | 26000 | 264000 | 289000 | 12 | 13.2309 | 27.3 | 34.4 | 0 | 779
0.05737 | 5 | 0.09437 | 12 | 1 | 166000 | 1758000 | 1919000 | 12 | 16.8555 | 27.3 | 34.4 | 0 | 4994
0.05737 | 5 | 0.09437 | 12 | 0.9 | 126000 | 1582000 | 1704000 | 12 | 16.3109 | 27.3 | 34.4 | 0 | 3773
0.05737 | 5 | 0.09437 | 12 | 0.8 | 101000 | 1406000 | 1504000 | 12 | 15.8057 | 27.3 | 34.4 | 0 | 3033
0.05737 | 5 | 0.09437 | 12 | 0.7 | 81000 | 1231000 | 1309000 | 12 | 15.311 | 27.3 | 34.4 | 0 | 2422
0.05737 | 5 | 0.09437 | 12 | 0.6 | 64000 | 1055000 | 1116000 | 12 | 14.8241 | 27.3 | 34.4 | 0 | 1906
0.05737 | 5 | 0.09437 | 12 | 0.5 | 51000 | 879000 | 928000 | 12 | 14.3474 | 27.3 | 34.4 | 0 | 1516
0.05737 | 5 | 0.09437 | 12 | 0.4 | 42000 | 703000 | 744000 | 12 | 13.8815 | 27.3 | 34.4 | 0 | 1256
0.05737 | 5 | 0.09437 | 12 | 0.3 | 35000 | 527000 | 561000 | 12 | 13.4191 | 27.3 | 34.4 | 0 | 1040
0.05737 | 5 | 0.09437 | 12 | 0.2 | 28000 | 352000 | 379000 | 12 | 12.959 | 27.3 | 34.4 | 0 | 851
0.05737 | 5 | 0.09437 | 12 | 0.15 | 25000 | 264000 | 288000 | 12 | 12.7293 | 27.3 | 34.4 | 0 | 761
0.05737 | 5 | 0.09437 | 11.5 | 1 | 167000 | 1758000 | 1920000 | 12 | 16.3548 | 27.3 | 34.4 | 0 | 4999
0.05737 | 5 | 0.09437 | 11.5 | 0.9 | 124000 | 1582000 | 1703000 | 12 | 15.8068 | 27.3 | 34.4 | 0 | 3735
0.05737 | 5 | 0.09437 | 11.5 | 0.8 | 99000 | 1406000 | 1502000 | 12 | 15.2986 | 27.3 | 34.4 | 0 | 2957
0.05737 | 5 | 0.09437 | 11.5 | 0.7 | 78000 | 1231000 | 1307000 | 12 | 14.8046 | 27.3 | 34.4 | 0 | 2353
0.05737 | 5 | 0.09437 | 11.5 | 0.6 | 61000 | 1055000 | 1114000 | 12 | 14.3179 | 27.3 | 34.4 | 0 | 1839
0.05737 | 5 | 0.09437 | 11.5 | 0.5 | 49000 | 879000 | 927000 | 12 | 13.8436 | 27.3 | 34.4 | 0 | 1475
0.05737 | 5 | 0.09437 | 11.5 | 0.4 | 41000 | 703000 | 743000 | 12 | 13.3792 | 27.3 | 34.4 | 0 | 1232
0.05737 | 5 | 0.09437 | 11.5 | 0.3 | 34000 | 527000 | 560000 | 12 | 12.917 | 27.3 | 34.4 | 0 | 1017
0.05737 | 5 | 0.09437 | 11.5 | 0.2 | 28000 | 352000 | 378000 | 12 | 12.457 | 27.3 | 34.4 | 0 | 829
0.05737 | 5 | 0.09437 | 11.5 | 0.15 | 25000 | 264000 | 288000 | 12 | 12.2277 | 27.3 | 34.4 | 0 | 744
0.05737 | 5 | 0.09437 | 11 | 1 | 167000 | 1758000 | 1920000 | 12 | 15.8556 | 27.3 | 34.4 | 0 | 5023
0.05737 | 5 | 0.09437 | 11 | 0.9 | 124000 | 1582000 | 1702000 | 12 | 15.3034 | 27.3 | 34.4 | 0 | 3705
0.05737 | 5 | 0.09437 | 11 | 0.8 | 96000 | 1406000 | 1500000 | 12 | 14.7919 | 27.3 | 34.4 | 0 | 2886
0.05737 | 5 | 0.09437 | 11 | 0.7 | 76000 | 1231000 | 1304000 | 12 | 14.2981 | 27.3 | 34.4 | 0 | 2283
0.05737 | 5 | 0.09437 | 11 | 0.6 | 59000 | 1055000 | 1112000 | 12 | 13.8119 | 27.3 | 34.4 | 0 | 1773
0.05737 | 5 | 0.09437 | 11 | 0.5 | 48000 | 879000 | 926000 | 12 | 13.3402 | 27.3 | 34.4 | 0 | 1439
0.05737 | 5 | 0.09437 | 11 | 0.4 | 40000 | 703000 | 742000 | 12 | 12.8762 | 27.3 | 34.4 | 0 | 1201
0.05737 | 5 | 0.09437 | 11 | 0.3 | 33000 | 527000 | 560000 | 12 | 12.415 | 27.3 | 34.4 | 0 | 997
0.05737 | 5 | 0.09437 | 11 | 0.2 | 27000 | 352000 | 378000 | 12 | 11.9554 | 27.3 | 34.4 | 0 | 813
0.05737 | 5 | 0.09437 | 11 | 0.15 | 24000 | 264000 | 287000 | 12 | 11.7264 | 27.3 | 34.4 | 0 | 729
0.05737 | 5 | 0.09437 | 10.5 | 1 | 169000 | 1758000 | 1922000 | 12 | 15.3576 | 27.3 | 34.4 | 0 | 5061
0.05737 | 5 | 0.09437 | 10.5 | 0.9 | 123000 | 1582000 | 1701000 | 12 | 14.8001 | 27.3 | 34.4 | 0 | 3677
0.05737 | 5 | 0.09437 | 10.5 | 0.8 | 94000 | 1406000 | 1498000 | 12 | 14.2855 | 27.3 | 34.4 | 0 | 2818
0.05737 | 5 | 0.09437 | 10.5 | 0.7 | 74000 | 1231000 | 1302000 | 12 | 13.7918 | 27.3 | 34.4 | 0 | 2215
0.05737 | 5 | 0.09437 | 10.5 | 0.6 | 57000 | 1055000 | 1110000 | 12 | 13.306 | 27.3 | 34.4 | 0 | 1708
0.05737 | 5 | 0.09437 | 10.5 | 0.5 | 47000 | 879000 | 925000 | 12 | 12.8371 | 27.3 | 34.4 | 0 | 1408
0.05737 | 5 | 0.09437 | 10.5 | 0.4 | 39000 | 703000 | 741000 | 12 | 12.3743 | 27.3 | 34.4 | 0 | 1184
0.05737 | 5 | 0.09437 | 10.5 | 0.3 | 33000 | 527000 | 559000 | 12 | 11.9131 | 27.3 | 34.4 | 0 | 977
0.05737 | 5 | 0.09437 | 10.5 | 0.2 | 27000 | 352000 | 377000 | 12 | 11.454 | 27.3 | 34.4 | 0 | 798
0.05737 | 5 | 0.09437 | 10.5 | 0.15 | 24000 | 264000 | 287000 | 12 | 11.2251 | 27.3 | 34.4 | 0 | 716
0.08385 | 7 | 0.09737 | 30 | 1 | 306000 | 1758000 | 2055000 | 12 | 35.0713 | 53.1 | 36.4 | 0 | 9177
0.08385 | 7 | 0.09737 | 30 | 0.9 | 267000 | 1582000 | 1841000 | 12 | 34.5436 | 53.1 | 36.4 | 0 | 8002
0.08385 | 7 | 0.09737 | 30 | 0.8 | 230000 | 1406000 | 1630000 | 12 | 34.0229 | 53.1 | 36.4 | 0 | 6913
0.08385 | 7 | 0.09737 | 30 | 0.7 | 200000 | 1231000 | 1425000 | 12 | 33.5162 | 53.1 | 36.4 | 0 | 6001
0.08385 | 7 | 0.09737 | 30 | 0.6 | 174000 | 1055000 | 1223000 | 12 | 33.0194 | 53.1 | 36.4 | 0 | 5213
0.08385 | 7 | 0.09737 | 30 | 0.5 | 153000 | 879000 | 1027000 | 12 | 32.5355 | 53.1 | 36.4 | 0 | 4586
0.08385 | 7 | 0.09737 | 30 | 0.4 | 127000 | 703000 | 827000 | 12 | 32.0404 | 53.1 | 36.4 | 0 | 3819
0.08385 | 7 | 0.09737 | 30 | 0.3 | 105000 | 527000 | 630000 | 12 | 31.5538 | 53.1 | 36.4 | 0 | 3159
0.08385 | 7 | 0.09737 | 30 | 0.2 | 83000 | 352000 | 432000 | 12 | 31.067 | 53.1 | 36.4 | 0 | 2496
0.08385 | 7 | 0.09737 | 30 | 0.15 | 71000 | 264000 | 333000 | 12 | 30.822 | 53.1 | 36.4 | 0 | 2144
0.08385 | 7 | 0.09737 | 27 | 1 | 275000 | 1758000 | 2024000 | 12 | 31.9916 | 53.1 | 36.4 | 0 | 8242
0.08385 | 7 | 0.09737 | 27 | 0.9 | 238000 | 1582000 | 1813000 | 12 | 31.4709 | 53.1 | 36.4 | 0 | 7147
0.08385 | 7 | 0.09737 | 27 | 0.8 | 204000 | 1406000 | 1605000 | 12 | 30.9563 | 53.1 | 36.4 | 0 | 6130
0.08385 | 7 | 0.09737 | 27 | 0.7 | 175000 | 1231000 | 1401000 | 12 | 30.4536 | 53.1 | 36.4 | 0 | 5261
0.08385 | 7 | 0.09737 | 27 | 0.6 | 150000 | 1055000 | 1201000 | 12 | 29.9601 | 53.1 | 36.4 | 0 | 4508
0.08385 | 7 | 0.09737 | 27 | 0.5 | 131000 | 879000 | 1006000 | 12 | 29.4799 | 53.1 | 36.4 | 0 | 3922
0.08385 | 7 | 0.09737 | 27 | 0.4 | 109000 | 703000 | 809000 | 12 | 28.9952 | 53.1 | 36.4 | 0 | 3279
0.08385 | 7 | 0.09737 | 27 | 0.3 | 90000 | 527000 | 615000 | 12 | 28.5161 | 53.1 | 36.4 | 0 | 2706
0.08385 | 7 | 0.09737 | 27 | 0.2 | 71000 | 352000 | 421000 | 12 | 28.0375 | 53.1 | 36.4 | 0 | 2140
0.08385 | 7 | 0.09737 | 27 | 0.15 | 61000 | 264000 | 323000 | 12 | 27.7969 | 53.1 | 36.4 | 0 | 1841
0.08385 | 7 | 0.09737 | 24 | 1 | 246000 | 1758000 | 1996000 | 12 | 28.9171 | 53.1 | 36.4 | 0 | 7372
0.08385 | 7 | 0.09737 | 24 | 0.9 | 210000 | 1582000 | 1786000 | 12 | 28.3999 | 53.1 | 36.4 | 0 | 6314
0.08385 | 7 | 0.09737 | 24 | 0.8 | 181000 | 1406000 | 1582000 | 12 | 27.8954 | 53.1 | 36.4 | 0 | 5418
0.08385 | 7 | 0.09737 | 24 | 0.7 | 153000 | 1231000 | 1379000 | 12 | 27.3964 | 53.1 | 36.4 | 0 | 4588
0.08385 | 7 | 0.09737 | 24 | 0.6 | 129000 | 1055000 | 1180000 | 12 | 26.9069 | 53.1 | 36.4 | 0 | 3879
0.08385 | 7 | 0.09737 | 24 | 0.5 | 110000 | 879000 | 985000 | 12 | 26.4268 | 53.1 | 36.4 | 0 | 3287
0.08385 | 7 | 0.09737 | 24 | 0.4 | 95000 | 703000 | 795000 | 12 | 25.9589 | 53.1 | 36.4 | 0 | 2849
0.08385 | 7 | 0.09737 | 24 | 0.3 | 77000 | 527000 | 602000 | 12 | 25.4824 | 53.1 | 36.4 | 0 | 2303
0.08385 | 7 | 0.09737 | 24 | 0.2 | 61000 | 352000 | 411000 | 12 | 25.0113 | 53.1 | 36.4 | 0 | 1824
0.08385 | 7 | 0.09737 | 24 | 0.15 | 52000 | 264000 | 315000 | 12 | 24.7749 | 53.1 | 36.4 | 0 | 1574
0.08385 | 7 | 0.09737 | 21 | 1 | 218000 | 1758000 | 1970000 | 12 | 25.8459 | 53.1 | 36.4 | 0 | 6543
0.08385 | 7 | 0.09737 | 21 | 0.9 | 186000 | 1582000 | 1763000 | 12 | 25.3373 | 53.1 | 36.4 | 0 | 5588
0.08385 | 7 | 0.09737 | 21 | 0.8 | 157000 | 1406000 | 1559000 | 12 | 24.836 | 53.1 | 36.4 | 0 | 4723
0.08385 | 7 | 0.09737 | 21 | 0.7 | 132000 | 1231000 | 1359000 | 12 | 24.344 | 53.1 | 36.4 | 0 | 3975
0.08385 | 7 | 0.09737 | 21 | 0.6 | 110000 | 1055000 | 1162000 | 12 | 23.8586 | 53.1 | 36.4 | 0 | 3310
0.08385 | 7 | 0.09737 | 21 | 0.5 | 92000 | 879000 | 968000 | 12 | 23.3827 | 53.1 | 36.4 | 0 | 2765
0.08385 | 7 | 0.09737 | 21 | 0.4 | 76000 | 703000 | 777000 | 12 | 22.912 | 53.1 | 36.4 | 0 | 2286
0.08385 | 7 | 0.09737 | 21 | 0.3 | 64000 | 527000 | 590000 | 12 | 22.4505 | 53.1 | 36.4 | 0 | 1922
0.08385 | 7 | 0.09737 | 21 | 0.2 | 51000 | 352000 | 401000 | 12 | 21.9862 | 53.1 | 36.4 | 0 | 1523
0.08385 | 7 | 0.09737 | 21 | 0.15 | 44000 | 264000 | 306000 | 12 | 21.7538 | 53.1 | 36.4 | 0 | 1319
0.08385 | 7 | 0.09737 | 18 | 1 | 195000 | 1758000 | 1947000 | 12 | 22.7858 | 53.1 | 36.4 | 0 | 5855
0.08385 | 7 | 0.09737 | 18 | 0.9 | 163000 | 1582000 | 1740000 | 12 | 22.2775 | 53.1 | 36.4 | 0 | 4895
0.08385 | 7 | 0.09737 | 18 | 0.8 | 136000 | 1406000 | 1539000 | 12 | 21.7816 | 53.1 | 36.4 | 0 | 4092
0.08385 | 7 | 0.09737 | 18 | 0.7 | 113000 | 1231000 | 1341000 | 12 | 21.2948 | 53.1 | 36.4 | 0 | 3403
0.08385 | 7 | 0.09737 | 18 | 0.6 | 93000 | 1055000 | 1145000 | 12 | 20.8141 | 53.1 | 36.4 | 0 | 2790
0.08385 | 7 | 0.09737 | 18 | 0.5 | 77000 | 879000 | 953000 | 12 | 20.3431 | 53.1 | 36.4 | 0 | 2301
0.08385 | 7 | 0.09737 | 18 | 0.4 | 63000 | 703000 | 764000 | 12 | 19.8779 | 53.1 | 36.4 | 0 | 1884
0.08385 | 7 | 0.09737 | 18 | 0.3 | 54000 | 527000 | 580000 | 12 | 19.4251 | 53.1 | 36.4 | 0 | 1623
0.08385 | 7 | 0.09737 | 18 | 0.2 | 42000 | 352000 | 392000 | 12 | 18.9632 | 53.1 | 36.4 | 0 | 1247
0.08385 | 7 | 0.09737 | 18 | 0.15 | 36000 | 264000 | 299000 | 12 | 18.7343 | 53.1 | 36.4 | 0 | 1085
0.08385 | 7 | 0.09737 | 17.5 | 1 | 191000 | 1758000 | 1944000 | 12 | 22.2756 | 53.1 | 36.4 | 0 | 5738
0.08385 | 7 | 0.09737 | 17.5 | 0.9 | 160000 | 1582000 | 1737000 | 12 | 21.768 | 53.1 | 36.4 | 0 | 4786
0.08385 | 7 | 0.09737 | 17.5 | 0.8 | 133000 | 1406000 | 1535000 | 12 | 21.2729 | 53.1 | 36.4 | 0 | 3992
0.08385 | 7 | 0.09737 | 17.5 | 0.7 | 110000 | 1231000 | 1338000 | 12 | 20.7869 | 53.1 | 36.4 | 0 | 3311
0.08385 | 7 | 0.09737 | 17.5 | 0.6 | 90000 | 1055000 | 1142000 | 12 | 20.3069 | 53.1 | 36.4 | 0 | 2707
0.08385 | 7 | 0.09737 | 17.5 | 0.5 | 74000 | 879000 | 951000 | 12 | 19.8368 | 53.1 | 36.4 | 0 | 2227
0.08385 | 7 | 0.09737 | 17.5 | 0.4 | 61000 | 703000 | 762000 | 12 | 19.3726 | 53.1 | 36.4 | 0 | 1822
0.08385 | 7 | 0.09737 | 17.5 | 0.3 | 52000 | 527000 | 578000 | 12 | 18.9195 | 53.1 | 36.4 | 0 | 1556
0.08385 | 7 | 0.09737 | 17.5 | 0.2 | 40000 | 352000 | 391000 | 12 | 18.4597 | 53.1 | 36.4 | 0 | 1206
0.08385 | 7 | 0.09737 | 17.5 | 0.15 | 35000 | 264000 | 298000 | 12 | 18.2313 | 53.1 | 36.4 | 0 | 1049
0.08385 | 7 | 0.09737 | 17 | 1 | 187000 | 1758000 | 1939000 | 12 | 21.7646 | 53.1 | 36.4 | 0 | 5611
0.08385 | 7 | 0.09737 | 17 | 0.9 | 156000 | 1582000 | 1733000 | 12 | 21.2585 | 53.1 | 36.4 | 0 | 4676
0.08385 | 7 | 0.09737 | 17 | 0.8 | 130000 | 1406000 | 1532000 | 12 | 20.7646 | 53.1 | 36.4 | 0 | 3896
0.08385 | 7 | 0.09737 | 17 | 0.7 | 107000 | 1231000 | 1335000 | 12 | 20.2791 | 53.1 | 36.4 | 0 | 3221
0.08385 | 7 | 0.09737 | 17 | 0.6 | 88000 | 1055000 | 1140000 | 12 | 19.7999 | 53.1 | 36.4 | 0 | 2626
0.08385 | 7 | 0.09737 | 17 | 0.5 | 72000 | 879000 | 949000 | 12 | 19.3307 | 53.1 | 36.4 | 0 | 2156
0.08385 | 7 | 0.09737 | 17 | 0.4 | 59000 | 703000 | 760000 | 12 | 18.8673 | 53.1 | 36.4 | 0 | 1759
0.08385 | 7 | 0.09737 | 17 | 0.3 | 50000 | 527000 | 576000 | 12 | 18.4148 | 53.1 | 36.4 | 0 | 1500
0.08385 | 7 | 0.09737 | 17 | 0.2 | 39000 | 352000 | 389000 | 12 | 17.9561 | 53.1 | 36.4 | 0 | 1162
0.08385 | 7 | 0.09737 | 17 | 0.15 | 34000 | 264000 | 296000 | 12 | 17.7283 | 53.1 | 36.4 | 0 | 1012
0.08385 | 7 | 0.09737 | 16.5 | 1 | 183000 | 1758000 | 1935000 | 12 | 21.2537 | 53.1 | 36.4 | 0 | 5485
0.08385 | 7 | 0.09737 | 16.5 | 0.9 | 152000 | 1582000 | 1730000 | 12 | 20.7494 | 53.1 | 36.4 | 0 | 4573
0.08385 | 7 | 0.09737 | 16.5 | 0.8 | 127000 | 1406000 | 1529000 | 12 | 20.2566 | 53.1 | 36.4 | 0 | 3805
0.08385 | 7 | 0.09737 | 16.5 | 0.7 | 104000 | 1231000 | 1332000 | 12 | 19.7715 | 53.1 | 36.4 | 0 | 3134
0.08385 | 7 | 0.09737 | 16.5 | 0.6 | 85000 | 1055000 | 1137000 | 12 | 19.2932 | 53.1 | 36.4 | 0 | 2548
0.08385 | 7 | 0.09737 | 16.5 | 0.5 | 69000 | 879000 | 946000 | 12 | 18.8246 | 53.1 | 36.4 | 0 | 2085
0.08385 | 7 | 0.09737 | 16.5 | 0.4 | 57000 | 703000 | 758000 | 12 | 18.3622 | 53.1 | 36.4 | 0 | 1700
0.08385 | 7 | 0.09737 | 16.5 | 0.3 | 45000 | 527000 | 572000 | 12 | 17.9037 | 53.1 | 36.4 | 0 | 1364
0.08385 | 7 | 0.09737 | 16.5 | 0.2 | 37000 | 352000 | 388000 | 12 | 17.4526 | 53.1 | 36.4 | 0 | 1121
0.08385 | 7 | 0.09737 | 16.5 | 0.15 | 33000 | 264000 | 295000 | 12 | 17.2253 | 53.1 | 36.4 | 0 | 977
0.08385 | 7 | 0.09737 | 16 | 1 | 179000 | 1758000 | 1931000 | 12 | 20.7429 | 53.1 | 36.4 | 0 | 5361
0.08385 | 7 | 0.09737 | 16 | 0.9 | 149000 | 1582000 | 1727000 | 12 | 20.2407 | 53.1 | 36.4 | 0 | 4474
0.08385 | 7 | 0.09737 | 16 | 0.8 | 124000 | 1406000 | 1526000 | 12 | 19.7484 | 53.1 | 36.4 | 0 | 3711
0.08385 | 7 | 0.09737 | 16 | 0.7 | 102000 | 1231000 | 1329000 | 12 | 19.2639 | 53.1 | 36.4 | 0 | 3046
0.08385 | 7 | 0.09737 | 16 | 0.6 | 82000 | 1055000 | 1135000 | 12 | 18.7863 | 53.1 | 36.4 | 0 | 2468
0.08385 | 7 | 0.09737 | 16 | 0.5 | 67000 | 879000 | 944000 | 12 | 18.3187 | 53.1 | 36.4 | 0 | 2016
0.08385 | 7 | 0.09737 | 16 | 0.4 | 55000 | 703000 | 756000 | 12 | 17.8572 | 53.1 | 36.4 | 0 | 1642
0.08385 | 7 | 0.09737 | 16 | 0.3 | 44000 | 527000 | 570000 | 12 | 17.3996 | 53.1 | 36.4 | 0 | 1315
0.08385 | 7 | 0.09737 | 16 | 0.2 | 36000 | 352000 | 387000 | 12 | 16.9492 | 53.1 | 36.4 | 0 | 1080
0.08385 | 7 | 0.09737 | 16 | 0.15 | 31000 | 264000 | 294000 | 12 | 16.7224 | 53.1 | 36.4 | 0 | 942
0.08385 | 7 | 0.09737 | 15.5 | 1 | 175000 | 1758000 | 1928000 | 12 | 20.2325 | 53.1 | 36.4 | 0 | 5243
0.08385 | 7 | 0.09737 | 15.5 | 0.9 | 146000 | 1582000 | 1724000 | 12 | 19.732 | 53.1 | 36.4 | 0 | 4375
0.08385 | 7 | 0.09737 | 15.5 | 0.8 | 121000 | 1406000 | 1523000 | 12 | 19.2406 | 53.1 | 36.4 | 0 | 3622
0.08385 | 7 | 0.09737 | 15.5 | 0.7 | 99000 | 1231000 | 1326000 | 12 | 18.7565 | 53.1 | 36.4 | 0 | 2961
0.08385 | 7 | 0.09737 | 15.5 | 0.6 | 80000 | 1055000 | 1132000 | 12 | 18.2797 | 53.1 | 36.4 | 0 | 2392
0.08385 | 7 | 0.09737 | 15.5 | 0.5 | 65000 | 879000 | 942000 | 12 | 17.8129 | 53.1 | 36.4 | 0 | 1949
0.08385 | 7 | 0.09737 | 15.5 | 0.4 | 53000 | 703000 | 754000 | 12 | 17.3523 | 53.1 | 36.4 | 0 | 1584
0.08385 | 7 | 0.09737 | 15.5 | 0.3 | 45000 | 527000 | 571000 | 12 | 16.9014 | 53.1 | 36.4 | 0 | 1342
0.08385 | 7 | 0.09737 | 15.5 | 0.2 | 36000 | 352000 | 387000 | 12 | 16.4491 | 53.1 | 36.4 | 0 | 1082
0.08385 | 7 | 0.09737 | 15.5 | 0.15 | 30000 | 264000 | 293000 | 12 | 16.2195 | 53.1 | 36.4 | 0 | 908
0.08385 | 7 | 0.09737 | 15 | 1 | 171000 | 1758000 | 1924000 | 12 | 19.723 | 53.1 | 36.4 | 0 | 5135
0.08385 | 7 | 0.09737 | 15 | 0.9 | 143000 | 1582000 | 1720000 | 12 | 19.2233 | 53.1 | 36.4 | 0 | 4276
0.08385 | 7 | 0.09737 | 15 | 0.8 | 118000 | 1406000 | 1521000 | 12 | 18.7326 | 53.1 | 36.4 | 0 | 3531
0.08385 | 7 | 0.09737 | 15 | 0.7 | 96000 | 1231000 | 1324000 | 12 | 18.2492 | 53.1 | 36.4 | 0 | 2877
0.08385 | 7 | 0.09737 | 15 | 0.6 | 78000 | 1055000 | 1130000 | 12 | 17.7741 | 53.1 | 36.4 | 0 | 2328
0.08385 | 7 | 0.09737 | 15 | 0.5 | 63000 | 879000 | 940000 | 12 | 17.3071 | 53.1 | 36.4 | 0 | 1882
0.08385 | 7 | 0.09737 | 15 | 0.4 | 51000 | 703000 | 753000 | 12 | 16.8473 | 53.1 | 36.4 | 0 | 1526
0.08385 | 7 | 0.09737 | 15 | 0.3 | 43000 | 527000 | 569000 | 12 | 16.3971 | 53.1 | 36.4 | 0 | 1291
0.08385 | 7 | 0.09737 | 15 | 0.2 | 34000 | 352000 | 385000 | 12 | 15.945 | 53.1 | 36.4 | 0 | 1032
0.08385 | 7 | 0.09737 | 15 | 0.15 | 29000 | 264000 | 292000 | 12 | 15.7166 | 53.1 | 36.4 | 0 | 873
0.08385 | 7 | 0.09737 | 14.5 | 1 | 169000 | 1758000 | 1921000 | 12 | 19.2158 | 53.1 | 36.4 | 0 | 5057
0.08385 | 7 | 0.09737 | 14.5 | 0.9 | 140000 | 1582000 | 1718000 | 12 | 18.7153 | 53.1 | 36.4 | 0 | 4186
0.08385 | 7 | 0.09737 | 14.5 | 0.8 | 115000 | 1406000 | 1518000 | 12 | 18.225 | 53.1 | 36.4 | 0 | 3444
0.08385 | 7 | 0.09737 | 14.5 | 0.7 | 93000 | 1231000 | 1321000 | 12 | 17.7421 | 53.1 | 36.4 | 0 | 2797
0.08385 | 7 | 0.09737 | 14.5 | 0.6 | 75000 | 1055000 | 1128000 | 12 | 17.2676 | 53.1 | 36.4 | 0 | 2254
0.08385 | 7 | 0.09737 | 14.5 | 0.5 | 61000 | 879000 | 938000 | 12 | 16.8015 | 53.1 | 36.4 | 0 | 1817
0.08385 | 7 | 0.09737 | 14.5 | 0.4 | 50000 | 703000 | 752000 | 12 | 16.3447 | 53.1 | 36.4 | 0 | 1498
0.08385 | 7 | 0.09737 | 14.5 | 0.3 | 41000 | 527000 | 567000 | 12 | 15.8915 | 53.1 | 36.4 | 0 | 1224
0.08385 | 7 | 0.09737 | 14.5 | 0.2 | 33000 | 352000 | 384000 | 12 | 15.4413 | 53.1 | 36.4 | 0 | 988
0.08385 | 7 | 0.09737 | 14.5 | 0.15 | 28000 | 264000 | 291000 | 12 | 15.2141 | 53.1 | 36.4 | 0 | 843
0.08385 | 7 | 0.09737 | 14 | 1 | 165000 | 1758000 | 1918000 | 12 | 18.7069 | 53.1 | 36.4 | 0 | 4957
0.08385 | 7 | 0.09737 | 14 | 0.9 | 137000 | 1582000 | 1715000 | 12 | 18.2072 | 53.1 | 36.4 | 0 | 4095
0.08385 | 7 | 0.09737 | 14 | 0.8 | 112000 | 1406000 | 1515000 | 12 | 17.7172 | 53.1 | 36.4 | 0 | 3357
0.08385 | 7 | 0.09737 | 14 | 0.7 | 91000 | 1231000 | 1319000 | 12 | 17.2353 | 53.1 | 36.4 | 0 | 2719
0.08385 | 7 | 0.09737 | 14 | 0.6 | 73000 | 1055000 | 1125000 | 12 | 16.7613 | 53.1 | 36.4 | 0 | 2182
0.08385 | 7 | 0.09737 | 14 | 0.5 | 58000 | 879000 | 936000 | 12 | 16.2958 | 53.1 | 36.4 | 0 | 1752
0.08385 | 7 | 0.09737 | 14 | 0.4 | 48000 | 703000 | 750000 | 12 | 15.8396 | 53.1 | 36.4 | 0 | 1438
0.08385 | 7 | 0.09737 | 14 | 0.3 | 39000 | 527000 | 565000 | 12 | 15.3872 | 53.1 | 36.4 | 0 | 1173
0.08385 | 7 | 0.09737 | 14 | 0.2 | 32000 | 352000 | 382000 | 12 | 14.9381 | 53.1 | 36.4 | 0 | 950
0.08385 | 7 | 0.09737 | 14 | 0.15 | 27000 | 264000 | 290000 | 12 | 14.712 | 53.1 | 36.4 | 0 | 819
0.08385 | 7 | 0.09737 | 13.5 | 1 | 169000 | 1758000 | 1921000 | 12 | 18.2139 | 53.1 | 36.4 | 0 | 5057
0.08385 | 7 | 0.09737 | 13.5 | 0.9 | 134000 | 1582000 | 1712000 | 12 | 17.6997 | 53.1 | 36.4 | 0 | 4012
0.08385 | 7 | 0.09737 | 13.5 | 0.8 | 109000 | 1406000 | 1512000 | 12 | 17.2098 | 53.1 | 36.4 | 0 | 3273
0.08385 | 7 | 0.09737 | 13.5 | 0.7 | 88000 | 1231000 | 1316000 | 12 | 16.7284 | 53.1 | 36.4 | 0 | 2641
0.08385 | 7 | 0.09737 | 13.5 | 0.6 | 70000 | 1055000 | 1123000 | 12 | 16.2551 | 53.1 | 36.4 | 0 | 2111
0.08385 | 7 | 0.09737 | 13.5 | 0.5 | 56000 | 879000 | 934000 | 12 | 15.7904 | 53.1 | 36.4 | 0 | 1689
0.08385 | 7 | 0.09737 | 13.5 | 0.4 | 46000 | 703000 | 748000 | 12 | 15.3346 | 53.1 | 36.4 | 0 | 1381
0.08385 | 7 | 0.09737 | 13.5 | 0.3 | 38000 | 527000 | 564000 | 12 | 14.8837 | 53.1 | 36.4 | 0 | 1133
0.08385 | 7 | 0.09737 | 13.5 | 0.2 | 31000 | 352000 | 381000 | 12 | 14.4356 | 53.1 | 36.4 | 0 | 920
0.08385 | 7 | 0.09737 | 13.5 | 0.15 | 27000 | 264000 | 290000 | 12 | 14.2121 | 53.1 | 36.4 | 0 | 822
0.08385 | 7 | 0.09737 | 13 | 1 | 173000 | 1758000 | 1926000 | 12 | 17.7227 | 53.1 | 36.4 | 0 | 5181
0.08385 | 7 | 0.09737 | 13 | 0.9 | 131000 | 1582000 | 1709000 | 12 | 17.1925 | 53.1 | 36.4 | 0 | 3933
0.08385 | 7 | 0.09737 | 13 | 0.8 | 106000 | 1406000 | 1510000 | 12 | 16.7024 | 53.1 | 36.4 | 0 | 3189
0.08385 | 7 | 0.09737 | 13 | 0.7 | 86000 | 1231000 | 1314000 | 12 | 16.2219 | 53.1 | 36.4 | 0 | 2567
0.08385 | 7 | 0.09737 | 13 | 0.6 | 68000 | 1055000 | 1121000 | 12 | 15.749 | 53.1 | 36.4 | 0 | 2042
0.08385 | 7 | 0.09737 | 13 | 0.5 | 54000 | 879000 | 932000 | 12 | 15.2849 | 53.1 | 36.4 | 0 | 1627
0.08385 | 7 | 0.09737 | 13 | 0.4 | 44000 | 703000 | 746000 | 12 | 14.8305 | 53.1 | 36.4 | 0 | 1334
0.08385 | 7 | 0.09737 | 13 | 0.3 | 37000 | 527000 | 563000 | 12 | 14.3807 | 53.1 | 36.4 | 0 | 1100
0.08385 | 7 | 0.09737 | 13 | 0.2 | 30000 | 352000 | 381000 | 12 | 13.9333 | 53.1 | 36.4 | 0 | 894
0.08385 | 7 | 0.09737 | 13 | 0.15 | 27000 | 264000 | 290000 | 12 | 13.7101 | 53.1 | 36.4 | 0 | 799
0.08385 | 7 | 0.09737 | 12.5 | 1 | 174000 | 1758000 | 1927000 | 12 | 17.2249 | 53.1 | 36.4 | 0 | 5222
0.08385 | 7 | 0.09737 | 12.5 | 0.9 | 128000 | 1582000 | 1706000 | 12 | 16.6843 | 53.1 | 36.4 | 0 | 3840
0.08385 | 7 | 0.09737 | 12.5 | 0.8 | 104000 | 1406000 | 1507000 | 12 | 16.1952 | 53.1 | 36.4 | 0 | 3109
0.08385 | 7 | 0.09737 | 12.5 | 0.7 | 83000 | 1231000 | 1311000 | 12 | 15.7154 | 53.1 | 36.4 | 0 | 2494
0.08385 | 7 | 0.09737 | 12.5 | 0.6 | 66000 | 1055000 | 1119000 | 12 | 15.2431 | 53.1 | 36.4 | 0 | 1974
0.08385 | 7 | 0.09737 | 12.5 | 0.5 | 52000 | 879000 | 930000 | 12 | 14.7799 | 53.1 | 36.4 | 0 | 1570
0.08385 | 7 | 0.09737 | 12.5 | 0.4 | 43000 | 703000 | 745000 | 12 | 14.3268 | 53.1 | 36.4 | 0 | 1292
0.08385 | 7 | 0.09737 | 12.5 | 0.3 | 36000 | 527000 | 562000 | 12 | 13.8783 | 53.1 | 36.4 | 0 | 1072
0.08385 | 7 | 0.09737 | 12.5 | 0.2 | 29000 | 352000 | 380000 | 12 | 13.4313 | 53.1 | 36.4 | 0 | 872
0.08385 | 7 | 0.09737 | 12.5 | 0.15 | 26000 | 264000 | 289000 | 12 | 13.2084 | 53.1 | 36.4 | 0 | 779
0.08385 | 7 | 0.09737 | 12 | 1 | 166000 | 1758000 | 1919000 | 12 | 16.7059 | 53.1 | 36.4 | 0 | 4994
0.08385 | 7 | 0.09737 | 12 | 0.9 | 126000 | 1582000 | 1704000 | 12 | 16.1781 | 53.1 | 36.4 | 0 | 3773
0.08385 | 7 | 0.09737 | 12 | 0.8 | 101000 | 1406000 | 1504000 | 12 | 15.6884 | 53.1 | 36.4 | 0 | 3033
0.08385 | 7 | 0.09737 | 12 | 0.7 | 81000 | 1231000 | 1309000 | 12 | 15.209 | 53.1 | 36.4 | 0 | 2422
0.08385 | 7 | 0.09737 | 12 | 0.6 | 64000 | 1055000 | 1116000 | 12 | 14.7371 | 53.1 | 36.4 | 0 | 1906
0.08385 | 7 | 0.09737 | 12 | 0.5 | 51000 | 879000 | 928000 | 12 | 14.2751 | 53.1 | 36.4 | 0 | 1516
0.08385 | 7 | 0.09737 | 12 | 0.4 | 42000 | 703000 | 744000 | 12 | 13.8235 | 53.1 | 36.4 | 0 | 1256
0.08385 | 7 | 0.09737 | 12 | 0.3 | 35000 | 527000 | 561000 | 12 | 13.3754 | 53.1 | 36.4 | 0 | 1040
0.08385 | 7 | 0.09737 | 12 | 0.2 | 28000 | 352000 | 379000 | 12 | 12.9294 | 53.1 | 36.4 | 0 | 851
0.08385 | 7 | 0.09737 | 12 | 0.15 | 25000 | 264000 | 288000 | 12 | 12.7068 | 53.1 | 36.4 | 0 | 761
0.08385 | 7 | 0.09737 | 11.5 | 1 | 167000 | 1758000 | 1920000 | 12 | 16.2052 | 53.1 | 36.4 | 0 | 4999
0.08385 | 7 | 0.09737 | 11.5 | 0.9 | 124000 | 1582000 | 1703000 | 12 | 15.6741 | 53.1 | 36.4 | 0 | 3735
0.08385 | 7 | 0.09737 | 11.5 | 0.8 | 99000 | 1406000 | 1502000 | 12 | 15.1815 | 53.1 | 36.4 | 0 | 2957
0.08385 | 7 | 0.09737 | 11.5 | 0.7 | 78000 | 1231000 | 1307000 | 12 | 14.7028 | 53.1 | 36.4 | 0 | 2353
0.08385 | 7 | 0.09737 | 11.5 | 0.6 | 61000 | 1055000 | 1114000 | 12 | 14.2311 | 53.1 | 36.4 | 0 | 1839
0.08385 | 7 | 0.09737 | 11.5 | 0.5 | 49000 | 879000 | 927000 | 12 | 13.7714 | 53.1 | 36.4 | 0 | 1475
0.08385 | 7 | 0.09737 | 11.5 | 0.4 | 41000 | 703000 | 743000 | 12 | 13.3213 | 53.1 | 36.4 | 0 | 1232
0.08385 | 7 | 0.09737 | 11.5 | 0.3 | 34000 | 527000 | 560000 | 12 | 12.8733 | 53.1 | 36.4 | 0 | 1017
0.08385 | 7 | 0.09737 | 11.5 | 0.2 | 28000 | 352000 | 378000 | 12 | 12.4275 | 53.1 | 36.4 | 0 | 829
0.08385 | 7 | 0.09737 | 11.5 | 0.15 | 25000 | 264000 | 288000 | 12 | 12.2053 | 53.1 | 36.4 | 0 | 744
0.08385 | 7 | 0.09737 | 11 | 1 | 167000 | 1758000 | 1920000 | 12 | 15.706 | 53.1 | 36.4 | 0 | 5023
0.08385 | 7 | 0.09737 | 11 | 0.9 | 124000 | 1582000 | 1702000 | 12 | 15.1708 | 53.1 | 36.4 | 0 | 3705
0.08385 | 7 | 0.09737 | 11 | 0.8 | 96000 | 1406000 | 1500000 | 12 | 14.6751 | 53.1 | 36.4 | 0 | 2886
0.08385 | 7 | 0.09737 | 11 | 0.7 | 76000 | 1231000 | 1304000 | 12 | 14.1965 | 53.1 | 36.4 | 0 | 2283
0.08385 | 7 | 0.09737 | 11 | 0.6 | 59000 | 1055000 | 1112000 | 12 | 13.7253 | 53.1 | 36.4 | 0 | 1773
0.08385 | 7 | 0.09737 | 11 | 0.5 | 48000 | 879000 | 926000 | 12 | 13.2681 | 53.1 | 36.4 | 0 | 1439
0.08385 | 7 | 0.09737 | 11 | 0.4 | 40000 | 703000 | 742000 | 12 | 12.8184 | 53.1 | 36.4 | 0 | 1201
0.08385 | 7 | 0.09737 | 11 | 0.3 | 33000 | 527000 | 560000 | 12 | 12.3714 | 53.1 | 36.4 | 0 | 997
0.08385 | 7 | 0.09737 | 11 | 0.2 | 27000 | 352000 | 378000 | 12 | 11.926 | 53.1 | 36.4 | 0 | 813
0.08385 | 7 | 0.09737 | 11 | 0.15 | 24000 | 264000 | 287000 | 12 | 11.704 | 53.1 | 36.4 | 0 | 729
0.08385 | 7 | 0.09737 | 10.5 | 1 | 169000 | 1758000 | 1922000 | 12 | 15.208 | 53.1 | 36.4 | 0 | 5061
0.08385 | 7 | 0.09737 | 10.5 | 0.9 | 123000 | 1582000 | 1701000 | 12 | 14.6676 | 53.1 | 36.4 | 0 | 3677
0.08385 | 7 | 0.09737 | 10.5 | 0.8 | 94000 | 1406000 | 1498000 | 12 | 14.1689 | 53.1 | 36.4 | 0 | 2818
0.08385 | 7 | 0.09737 | 10.5 | 0.7 | 74000 | 1231000 | 1302000 | 12 | 13.6904 | 53.1 | 36.4 | 0 | 2215
0.08385 | 7 | 0.09737 | 10.5 | 0.6 | 57000 | 1055000 | 1110000 | 12 | 13.2195 | 53.1 | 36.4 | 0 | 1708
0.08385 | 7 | 0.09737 | 10.5 | 0.5 | 47000 | 879000 | 925000 | 12 | 12.765 | 53.1 | 36.4 | 0 | 1408
0.08385 | 7 | 0.09737 | 10.5 | 0.4 | 39000 | 703000 | 741000 | 12 | 12.3166 | 53.1 | 36.4 | 0 | 1184
0.08385 | 7 | 0.09737 | 10.5 | 0.3 | 33000 | 527000 | 559000 | 12 | 11.8695 | 53.1 | 36.4 | 0 | 977
0.08385 | 7 | 0.09737 | 10.5 | 0.2 | 27000 | 352000 | 377000 | 12 | 11.4246 | 53.1 | 36.4 | 0 | 798
0.08385 | 7 | 0.09737 | 10.5 | 0.15 | 24000 | 264000 | 287000 | 12 | 11.2028 | 53.1 | 36.4 | 0 | 716
0.1398 | 9 | 0.09644 | 30 | 1 | 263000 | 1758000 | 2013000 | 12 | 35.0168 | 131 | 35.8 | 0 | 7893
0.1398 | 9 | 0.09644 | 30 | 0.9 | 227000 | 1582000 | 1802000 | 12 | 34.4906 | 131 | 35.8 | 0 | 6800
0.1398 | 9 | 0.09644 | 30 | 0.8 | 195000 | 1406000 | 1596000 | 12 | 33.9767 | 131 | 35.8 | 0 | 5858
0.1398 | 9 | 0.09644 | 30 | 0.7 | 168000 | 1231000 | 1393000 | 12 | 33.4718 | 131 | 35.8 | 0 | 5030
0.1398 | 9 | 0.09644 | 30 | 0.6 | 144000 | 1055000 | 1194000 | 12 | 32.9754 | 131 | 35.8 | 0 | 4305
0.1398 | 9 | 0.09644 | 30 | 0.5 | 125000 | 879000 | 1000000 | 12 | 32.4931 | 131 | 35.8 | 0 | 3757
0.1398 | 9 | 0.09644 | 30 | 0.4 | 104000 | 703000 | 804000 | 12 | 32.0046 | 131 | 35.8 | 0 | 3131
0.1398 | 9 | 0.09644 | 30 | 0.3 | 86000 | 527000 | 611000 | 12 | 31.5219 | 131 | 35.8 | 0 | 2578
0.1398 | 9 | 0.09644 | 30 | 0.2 | 68000 | 352000 | 417000 | 12 | 31.0397 | 131 | 35.8 | 0 | 2029
0.1398 | 9 | 0.09644 | 30 | 0.15 | 58000 | 264000 | 320000 | 12 | 30.7974 | 131 | 35.8 | 0 | 1741
0.1398 | 9 | 0.09644 | 27 | 1 | 233000 | 1758000 | 1984000 | 12 | 31.9389 | 131 | 35.8 | 0 | 6989
0.1398 | 9 | 0.09644 | 27 | 0.9 | 201000 | 1582000 | 1777000 | 12 | 31.4233 | 131 | 35.8 | 0 | 6021
0.1398 | 9 | 0.09644 | 27 | 0.8 | 171000 | 1406000 | 1573000 | 12 | 30.9149 | 131 | 35.8 | 0 | 5142
0.1398 | 9 | 0.09644 | 27 | 0.7 | 145000 | 1231000 | 1371000 | 12 | 30.4141 | 131 | 35.8 | 0 | 4357
0.1398 | 9 | 0.09644 | 27 | 0.6 | 123000 | 1055000 | 1174000 | 12 | 29.9224 | 131 | 35.8 | 0 | 3685
0.1398 | 9 | 0.09644 | 27 | 0.5 | 104000 | 879000 | 979000 | 12 | 29.4383 | 131 | 35.8 | 0 | 3108
0.1398 | 9 | 0.09644 | 27 | 0.4 | 90000 | 703000 | 791000 | 12 | 28.9682 | 131 | 35.8 | 0 | 2705
0.1398 | 9 | 0.09644 | 27 | 0.3 | 72000 | 527000 | 598000 | 12 | 28.4879 | 131 | 35.8 | 0 | 2174
0.1398 | 9 | 0.09644 | 27 | 0.2 | 57000 | 352000 | 407000 | 12 | 28.0132 | 131 | 35.8 | 0 | 1714
0.1398 | 9 | 0.09644 | 27 | 0.15 | 49000 | 264000 | 311000 | 12 | 27.7752 | 131 | 35.8 | 0 | 1476
0.1398 | 9 | 0.09644 | 24 | 1 | 207000 | 1758000 | 1959000 | 12 | 28.8706 | 131 | 35.8 | 0 | 6204
0.1398 | 9 | 0.09644 | 24 | 0.9 | 176000 | 1582000 | 1753000 | 12 | 28.3583 | 131 | 35.8 | 0 | 5270
0.1398 | 9 | 0.09644 | 24 | 0.8 | 148000 | 1406000 | 1550000 | 12 | 27.8555 | 131 | 35.8 | 0 | 4454
0.1398 | 9 | 0.09644 | 24 | 0.7 | 125000 | 1231000 | 1351000 | 12 | 27.3608 | 131 | 35.8 | 0 | 3738
0.1398 | 9 | 0.09644 | 24 | 0.6 | 104000 | 1055000 | 1156000 | 12 | 26.874 | 131 | 35.8 | 0 | 3121
0.1398 | 9 | 0.09644 | 24 | 0.5 | 87000 | 879000 | 963000 | 12 | 26.395 | 131 | 35.8 | 0 | 2601
0.1398 | 9 | 0.09644 | 24 | 0.4 | 71000 | 703000 | 773000 | 12 | 25.9211 | 131 | 35.8 | 0 | 2145
0.1398 | 9 | 0.09644 | 24 | 0.3 | 60000 | 527000 | 586000 | 12 | 25.4566 | 131 | 35.8 | 0 | 1804
0.1398 | 9 | 0.09644 | 24 | 0.2 | 47000 | 352000 | 398000 | 12 | 24.9887 | 131 | 35.8 | 0 | 1422
0.1398 | 9 | 0.09644 | 24 | 0.15 | 41000 | 264000 | 303000 | 12 | 24.7546 | 131 | 35.8 | 0 | 1229
0.1398 | 9 | 0.09644 | 21 | 1 | 182000 | 1758000 | 1935000 | 12 | 25.8058 | 131 | 35.8 | 0 | 5462
0.1398 | 9 | 0.09644 | 21 | 0.9 | 153000 | 1582000 | 1730000 | 12 | 25.2984 | 131 | 35.8 | 0 | 4582
0.1398 | 9 | 0.09644 | 21 | 0.8 | 128000 | 1406000 | 1530000 | 12 | 24.8015 | 131 | 35.8 | 0 | 3832
0.1398 | 9 | 0.09644 | 21 | 0.7 | 106000 | 1231000 | 1333000 | 12 | 24.3124 | 131 | 35.8 | 0 | 3180
0.1398 | 9 | 0.09644 | 21 | 0.6 | 87000 | 1055000 | 1139000 | 12 | 23.8294 | 131 | 35.8 | 0 | 2604
0.1398 | 9 | 0.09644 | 21 | 0.5 | 72000 | 879000 | 948000 | 12 | 23.356 | 131 | 35.8 | 0 | 2147
0.1398 | 9 | 0.09644 | 21 | 0.4 | 59000 | 703000 | 760000 | 12 | 22.8879 | 131 | 35.8 | 0 | 1757
0.1398 | 9 | 0.09644 | 21 | 0.3 | 50000 | 527000 | 576000 | 12 | 22.431 | 131 | 35.8 | 0 | 1505
0.1398 | 9 | 0.09644 | 21 | 0.2 | 39000 | 352000 | 389000 | 12 | 21.9663 | 131 | 35.8 | 0 | 1157
0.1398 | 9 | 0.09644 | 21 | 0.15 | 34000 | 264000 | 296000 | 12 | 21.7359 | 131 | 35.8 | 0 | 1006
0.1398 | 9 | 0.09644 | 18 | 1 | 162000 | 1758000 | 1915000 | 12 | 22.7526 | 131 | 35.8 | 0 | 4865
0.1398 | 9 | 0.09644 | 18 | 0.9 | 133000 | 1582000 | 1711000 | 12 | 22.2463 | 131 | 35.8 | 0 | 3992
0.1398 | 9 | 0.09644 | 18 | 0.8 | 109000 | 1406000 | 1512000 | 12 | 21.7518 | 131 | 35.8 | 0 | 3266
0.1398 | 9 | 0.09644 | 18 | 0.7 | 88000 | 1231000 | 1316000 | 12 | 21.266 | 131 | 35.8 | 0 | 2648
0.1398 | 9 | 0.09644 | 18 | 0.6 | 71000 | 1055000 | 1124000 | 12 | 20.7891 | 131 | 35.8 | 0 | 2141
0.1398 | 9 | 0.09644 | 18 | 0.5 | 58000 | 879000 | 935000 | 12 | 20.3205 | 131 | 35.8 | 0 | 1737
0.1398 | 9 | 0.09644 | 18 | 0.4 | 48000 | 703000 | 750000 | 12 | 19.86 | 131 | 35.8 | 0 | 1435
0.1398 | 9 | 0.09644 | 18 | 0.3 | 39000 | 527000 | 565000 | 12 | 19.4029 | 131 | 35.8 | 0 | 1175
0.1398 | 9 | 0.09644 | 18 | 0.2 | 32000 | 352000 | 382000 | 12 | 18.9488 | 131 | 35.8 | 0 | 951
0.1398 | 9 | 0.09644 | 18 | 0.15 | 27000 | 264000 | 290000 | 12 | 18.7192 | 131 | 35.8 | 0 | 809
0.1398 | 9 | 0.09644 | 17.5 | 1 | 159000 | 1758000 | 1913000 | 12 | 22.2449 | 131 | 35.8 | 0 | 4782
0.1398 | 9 | 0.09644 | 17.5 | 0.9 | 130000 | 1582000 | 1708000 | 12 | 21.7384 | 131 | 35.8 | 0 | 3903
0.1398 | 9 | 0.09644 | 17.5 | 0.8 | 106000 | 1406000 | 1509000 | 12 | 21.2441 | 131 | 35.8 | 0 | 3180
0.1398 | 9 | 0.09644 | 17.5 | 0.7 | 86000 | 1231000 | 1314000 | 12 | 20.759 | 131 | 35.8 | 0 | 2569
0.1398 | 9 | 0.09644 | 17.5 | 0.6 | 69000 | 1055000 | 1122000 | 12 | 20.2827 | 131 | 35.8 | 0 | 2068
0.1398 | 9 | 0.09644 | 17.5 | 0.5 | 56000 | 879000 | 933000 | 12 | 19.8149 | 131 | 35.8 | 0 | 1673
0.1398 | 9 | 0.09644 | 17.5 | 0.4 | 46000 | 703000 | 748000 | 12 | 19.3551 | 131 | 35.8 | 0 | 1378
0.1398 | 9 | 0.09644 | 17.5 | 0.3 | 38000 | 527000 | 564000 | 12 | 18.8992 | 131 | 35.8 | 0 | 1132
0.1398 | 9 | 0.09644 | 17.5 | 0.2 | 31000 | 352000 | 381000 | 12 | 18.4462 | 131 | 35.8 | 0 | 921
0.1398 | 9 | 0.09644 | 17.5 | 0.15 | 26000 | 264000 | 289000 | 12 | 18.2174 | 131 | 35.8 | 0 | 788
0.1398 | 9 | 0.09644 | 17 | 1 | 157000 | 1758000 | 1910000 | 12 | 21.7378 | 131 | 35.8 | 0 | 4705
0.1398 | 9 | 0.09644 | 17 | 0.9 | 127000 | 1582000 | 1706000 | 12 | 21.2305 | 131 | 35.8 | 0 | 3816
0.1398 | 9 | 0.09644 | 17 | 0.8 | 103000 | 1406000 | 1506000 | 12 | 20.7365 | 131 | 35.8 | 0 | 3093
0.1398 | 9 | 0.09644 | 17 | 0.7 | 83000 | 1231000 | 1311000 | 12 | 20.252 | 131 | 35.8 | 0 | 2489
0.1398 | 9 | 0.09644 | 17 | 0.6 | 67000 | 1055000 | 1119000 | 12 | 19.7763 | 131 | 35.8 | 0 | 1995
0.1398 | 9 | 0.09644 | 17 | 0.5 | 54000 | 879000 | 931000 | 12 | 19.3097 | 131 | 35.8 | 0 | 1614
0.1398 | 9 | 0.09644 | 17 | 0.4 | 45000 | 703000 | 746000 | 12 | 18.8513 | 131 | 35.8 | 0 | 1335
0.1398 | 9 | 0.09644 | 17 | 0.3 | 37000 | 527000 | 563000 | 12 | 18.3962 | 131 | 35.8 | 0 | 1098
0.1398 | 9 | 0.09644 | 17 | 0.2 | 30000 | 352000 | 380000 | 12 | 17.9435 | 131 | 35.8 | 0 | 890
0.1398 | 9 | 0.09644 | 17 | 0.15 | 27000 | 264000 | 290000 | 12 | 17.7181 | 131 | 35.8 | 0 | 799
0.1398 | 9 | 0.09644 | 16.5 | 1 | 154000 | 1758000 | 1908000 | 12 | 21.2313 | 131 | 35.8 | 0 | 4634
0.1398 | 9 | 0.09644 | 16.5 | 0.9 | 124000 | 1582000 | 1703000 | 12 | 20.7227 | 131 | 35.8 | 0 | 3729
0.1398 | 9 | 0.09644 | 16.5 | 0.8 | 100000 | 1406000 | 1504000 | 12 | 20.2292 | 131 | 35.8 | 0 | 3012
0.1398 | 9 | 0.09644 | 16.5 | 0.7 | 80000 | 1231000 | 1309000 | 12 | 19.7453 | 131 | 35.8 | 0 | 2413
0.1398 | 9 | 0.09644 | 16.5 | 0.6 | 64000 | 1055000 | 1117000 | 12 | 19.2701 | 131 | 35.8 | 0 | 1925
0.1398 | 9 | 0.09644 | 16.5 | 0.5 | 52000 | 879000 | 929000 | 12 | 18.8044 | 131 | 35.8 | 0 | 1553
0.1398 | 9 | 0.09644 | 16.5 | 0.4 | 43000 | 703000 | 745000 | 12 | 18.3476 | 131 | 35.8 | 0 | 1293
0.1398 | 9 | 0.09644 | 16.5 | 0.3 | 36000 | 527000 | 562000 | 12 | 17.8937 | 131 | 35.8 | 0 | 1070
0.1398 | 9 | 0.09644 | 16.5 | 0.2 | 29000 | 352000 | 380000 | 12 | 17.4415 | 131 | 35.8 | 0 | 867
0.1398 | 9 | 0.09644 | 16.5 | 0.15 | 26000 | 264000 | 289000 | 12 | 17.2164 | 131 | 35.8 | 0 | 779
0.1398 | 9 | 0.09644 | 16 | 1 | 152000 | 1758000 | 1906000 | 12 | 20.7249 | 131 | 35.8 | 0 | 4566
0.1398 | 9 | 0.09644 | 16 | 0.9 | 121000 | 1582000 | 1700000 | 12 | 20.215 | 131 | 35.8 | 0 | 3643
0.1398 | 9 | 0.09644 | 16 | 0.8 | 98000 | 1406000 | 1501000 | 12 | 19.7219 | 131 | 35.8 | 0 | 2930
0.1398 | 9 | 0.09644 | 16 | 0.7 | 78000 | 1231000 | 1306000 | 12 | 19.2385 | 131 | 35.8 | 0 | 2337
0.1398 | 9 | 0.09644 | 16 | 0.6 | 62000 | 1055000 | 1115000 | 12 | 18.7648 | 131 | 35.8 | 0 | 1865
0.1398 | 9 | 0.09644 | 16 | 0.5 | 50000 | 879000 | 928000 | 12 | 18.3001 | 131 | 35.8 | 0 | 1506
0.1398 | 9 | 0.09644 | 16 | 0.4 | 42000 | 703000 | 744000 | 12 | 17.8443 | 131 | 35.8 | 0 | 1256
0.1398 | 9 | 0.09644 | 16 | 0.3 | 35000 | 527000 | 561000 | 12 | 17.3914 | 131 | 35.8 | 0 | 1045
0.1398 | 9 | 0.09644 | 16 | 0.2 | 28000 | 352000 | 379000 | 12 | 16.9396 | 131 | 35.8 | 0 | 847
0.1398 | 9 | 0.09644 | 16 | 0.15 | 25000 | 264000 | 288000 | 12 | 16.7149 | 131 | 35.8 | 0 | 761
0.1398 | 9 | 0.09644 | 15.5 | 1 | 150000 | 1758000 | 1904000 | 12 | 20.2186 | 131 | 35.8 | 0 | 4500
0.1398 | 9 | 0.09644 | 15.5 | 0.9 | 119000 | 1582000 | 1697000 | 12 | 19.7078 | 131 | 35.8 | 0 | 3564
0.1398 | 9 | 0.09644 | 15.5 | 0.8 | 95000 | 1406000 | 1499000 | 12 | 19.215 | 131 | 35.8 | 0 | 2853
0.1398 | 9 | 0.09644 | 15.5 | 0.7 | 75000 | 1231000 | 1304000 | 12 | 18.7319 | 131 | 35.8 | 0 | 2262
0.1398 | 9 | 0.09644 | 15.5 | 0.6 | 60000 | 1055000 | 1113000 | 12 | 18.2586 | 131 | 35.8 | 0 | 1795
0.1398 | 9 | 0.09644 | 15.5 | 0.5 | 49000 | 879000 | 926000 | 12 | 17.7964 | 131 | 35.8 | 0 | 1465
0.1398 | 9 | 0.09644 | 15.5 | 0.4 | 41000 | 703000 | 743000 | 12 | 17.3419 | 131 | 35.8 | 0 | 1232
0.1398 | 9 | 0.09644 | 15.5 | 0.3 | 34000 | 527000 | 560000 | 12 | 16.8893 | 131 | 35.8 | 0 | 1022
0.1398 | 9 | 0.09644 | 15.5 | 0.2 | 28000 | 352000 | 378000 | 12 | 16.4381 | 131 | 35.8 | 0 | 829
0.1398 | 9 | 0.09644 | 15.5 | 0.15 | 25000 | 264000 | 288000 | 12 | 16.2132 | 131 | 35.8 | 0 | 743
0.1398 | 9 | 0.09644 | 15 | 1 | 148000 | 1758000 | 1901000 | 12 | 19.7122 | 131 | 35.8 | 0 | 4432
0.1398 | 9 | 0.09644 | 15 | 0.9 | 116000 | 1582000 | 1695000 | 12 | 19.2006 | 131 | 35.8 | 0 | 3485
0.1398 | 9 | 0.09644 | 15 | 0.8 | 93000 | 1406000 | 1496000 | 12 | 18.7082 | 131 | 35.8 | 0 | 2778
0.1398 | 9 | 0.09644 | 15 | 0.7 | 73000 | 1231000 | 1301000 | 12 | 18.2254 | 131 | 35.8 | 0 | 2190
0.1398 | 9 | 0.09644 | 15 | 0.6 | 58000 | 1055000 | 1111000 | 12 | 17.7543 | 131 | 35.8 | 0 | 1748
0.1398 | 9 | 0.09644 | 15 | 0.5 | 48000 | 879000 | 926000 | 12 | 17.2939 | 131 | 35.8 | 0 | 1440
0.1398 | 9 | 0.09644 | 15 | 0.4 | 40000 | 703000 | 742000 | 12 | 16.839 | 131 | 35.8 | 0 | 1201
0.1398 | 9 | 0.09644 | 15 | 0.3 | 33000 | 527000 | 560000 | 12 | 16.387 | 131 | 35.8 | 0 | 996
0.1398 | 9 | 0.09644 | 15 | 0.2 | 27000 | 352000 | 378000 | 12 | 15.9365 | 131 | 35.8 | 0 | 812
0.1398 | 9 | 0.09644 | 15 | 0.15 | 24000 | 264000 | 287000 | 12 | 15.7119 | 131 | 35.8 | 0 | 728
0.1398 | 9 | 0.09644 | 14.5 | 1 | 152000 | 1758000 | 1906000 | 12 | 19.2223 | 131 | 35.8 | 0 | 4570
0.1398 | 9 | 0.09644 | 14.5 | 0.9 | 114000 | 1582000 | 1693000 | 12 | 18.6939 | 131 | 35.8 | 0 | 3412
0.1398 | 9 | 0.09644 | 14.5 | 0.8 | 90000 | 1406000 | 1494000 | 12 | 18.2018 | 131 | 35.8 | 0 | 2706
0.1398 | 9 | 0.09644 | 14.5 | 0.7 | 71000 | 1231000 | 1299000 | 12 | 17.719 | 131 | 35.8 | 0 | 2118
0.1398 | 9 | 0.09644 | 14.5 | 0.6 | 56000 | 1055000 | 1109000 | 12 | 17.2488 | 131 | 35.8 | 0 | 1687
0.1398 | 9 | 0.09644 | 14.5 | 0.5 | 47000 | 879000 | 925000 | 12 | 16.7909 | 131 | 35.8 | 0 | 1409
0.1398 | 9 | 0.09644 | 14.5 | 0.4 | 39000 | 703000 | 741000 | 12 | 16.3372 | 131 | 35.8 | 0 | 1182
0.1398 | 9 | 0.09644 | 14.5 | 0.3 | 33000 | 527000 | 559000 | 12 | 15.8851 | 131 | 35.8 | 0 | 977
0.1398 | 9 | 0.09644 | 14.5 | 0.2 | 27000 | 352000 | 377000 | 12 | 15.4351 | 131 | 35.8 | 0 | 797
0.1398 | 9 | 0.09644 | 14.5 | 0.15 | 24000 | 264000 | 287000 | 12 | 15.2106 | 131 | 35.8 | 0 | 714
0.1398 | 9 | 0.09644 | 14 | 1 | 154000 | 1758000 | 1907000 | 12 | 18.7252 | 131 | 35.8 | 0 | 4618
0.1398 | 9 | 0.09644 | 14 | 0.9 | 112000 | 1582000 | 1691000 | 12 | 18.1881 | 131 | 35.8 | 0 | 3350
0.1398 | 9 | 0.09644 | 14 | 0.8 | 88000 | 1406000 | 1492000 | 12 | 17.6953 | 131 | 35.8 | 0 | 2635
0.1398 | 9 | 0.09644 | 14 | 0.7 | 68000 | 1231000 | 1297000 | 12 | 17.2127 | 131 | 35.8 | 0 | 2048
0.1398 | 9 | 0.09644 | 14 | 0.6 | 55000 | 1055000 | 1108000 | 12 | 16.7453 | 131 | 35.8 | 0 | 1650
0.1398 | 9 | 0.09644 | 14 | 0.5 | 46000 | 879000 | 924000 | 12 | 16.2881 | 131 | 35.8 | 0 | 1379
0.1398 | 9 | 0.09644 | 14 | 0.4 | 39000 | 703000 | 741000 | 12 | 15.8354 | 131 | 35.8 | 0 | 1165
0.1398 | 9 | 0.09644 | 14 | 0.3 | 32000 | 527000 | 558000 | 12 | 15.3835 | 131 | 35.8 | 0 | 960
0.1398 | 9 | 0.09644 | 14 | 0.2 | 26000 | 352000 | 377000 | 12 | 14.9337 | 131 | 35.8 | 0 | 782
0.1398 | 9 | 0.09644 | 14 | 0.15 | 23000 | 264000 | 286000 | 12 | 14.7095 | 131 | 35.8 | 0 | 702
0.1398 | 9 | 0.09644 | 13.5 | 1 | 0 | 1758000 | 0 | 12 | 0 | 131 | 35.8 | 0 | 0
0.1398 | 9 | 0.09644 | 13.5 | 0.9 | 0 | 1582000 | 0 | 12 | 0 | 131 | 35.8 | 0 | 0
0.1398 | 9 | 0.09644 | 13.5 | 0.8 | 86000 | 1406000 | 1489000 | 12 | 17.1891 | 131 | 35.8 | 0 | 2568
0.1398 | 9 | 0.09644 | 13.5 | 0.7 | 66000 | 1231000 | 1295000 | 12 | 16.7065 | 131 | 35.8 | 0 | 1978
0.1398 | 9 | 0.09644 | 13.5 | 0.6 | 54000 | 1055000 | 1107000 | 12 | 16.242 | 131 | 35.8 | 0 | 1616
0.1398 | 9 | 0.09644 | 13.5 | 0.5 | 45000 | 879000 | 923000 | 12 | 15.7854 | 131 | 35.8 | 0 | 1351
0.1398 | 9 | 0.09644 | 13.5 | 0.4 | 38000 | 703000 | 740000 | 12 | 15.3329 | 131 | 35.8 | 0 | 1138
0.1398 | 9 | 0.09644 | 13.5 | 0.3 | 31000 | 527000 | 558000 | 12 | 14.8819 | 131 | 35.8 | 0 | 944
0.1398 | 9 | 0.09644 | 13.5 | 0.2 | 26000 | 352000 | 376000 | 12 | 14.4325 | 131 | 35.8 | 0 | 769
0.1398 | 9 | 0.09644 | 13.5 | 0.15 | 23000 | 264000 | 286000 | 12 | 14.2084 | 131 | 35.8 | 0 | 690
0.1398 | 9 | 0.09644 | 13 | 1 | 0 | 1758000 | 0 | 12 | 0 | 131 | 35.8 | 0 | 0
0.1398 | 9 | 0.09644 | 13 | 0.9 | 0 | 1582000 | 0 | 12 | 0 | 131 | 35.8 | 0 | 0
0.1398 | 9 | 0.09644 | 13 | 0.8 | 0 | 1406000 | 0 | 12 | 0 | 131 | 35.8 | 0 | 0
0.1398 | 9 | 0.09644 | 13 | 0.7 | 0 | 1231000 | 0 | 12 | 0 | 131 | 35.8 | 0 | 0
0.1398 | 9 | 0.09644 | 13 | 0.6 | 0 | 1055000 | 0 | 12 | 0 | 131 | 35.8 | 0 | 0
0.1398 | 9 | 0.09644 | 13 | 0.5 | 45000 | 879000 | 922000 | 12 | 15.2838 | 131 | 35.8 | 0 | 1337
0.1398 | 9 | 0.09644 | 13 | 0.4 | 37000 | 703000 | 739000 | 12 | 14.8311 | 131 | 35.8 | 0 | 1120
0.1398 | 9 | 0.09644 | 13 | 0.3 | 31000 | 527000 | 557000 | 12 | 14.3804 | 131 | 35.8 | 0 | 929
0.1398 | 9 | 0.09644 | 13 | 0.2 | 25000 | 352000 | 376000 | 12 | 13.9313 | 131 | 35.8 | 0 | 757
0.1398 | 9 | 0.09644 | 13 | 0.15 | 23000 | 264000 | 286000 | 12 | 13.7074 | 131 | 35.8 | 0 | 680
0.1398 | 9 | 0.09644 | 12.5 | 1 | 0 | 1758000 | 0 | 12 | 0 | 131 | 35.8 | 0 | 0
0.1398 | 9 | 0.09644 | 12.5 | 0.9 | 0 | 1582000 | 0 | 12 | 0 | 131 | 35.8 | 0 | 0
0.1398 | 9 | 0.09644 | 12.5 | 0.8 | 0 | 1406000 | 0 | 12 | 0 | 131 | 35.8 | 0 | 0
0.1398 | 9 | 0.09644 | 12.5 | 0.7 | 0 | 1231000 | 0 | 12 | 0 | 131 | 35.8 | 0 | 0
0.1398 | 9 | 0.09644 | 12.5 | 0.6 | 0 | 1055000 | 0 | 12 | 0 | 131 | 35.8 | 0 | 0
0.1398 | 9 | 0.09644 | 12.5 | 0.5 | 0 | 879000 | 0 | 12 | 0 | 131 | 35.8 | 0 | 0
0.1398 | 9 | 0.09644 | 12.5 | 0.4 | 0 | 703000 | 0 | 12 | 0 | 131 | 35.8 | 0 | 0
0.1398 | 9 | 0.09644 | 12.5 | 0.3 | 30000 | 527000 | 557000 | 12 | 13.879 | 131 | 35.8 | 0 | 915
0.1398 | 9 | 0.09644 | 12.5 | 0.2 | 25000 | 352000 | 376000 | 12 | 13.4302 | 131 | 35.8 | 0 | 745
0.1398 | 9 | 0.09644 | 12.5 | 0.15 | 22000 | 264000 | 285000 | 12 | 13.2064 | 131 | 35.8 | 0 | 669
0.08385 | 7 | 0.077 | 30 | 1 | 296000 | 1758000 | 2045000 | 12 | 36.3819 | 53.1 | 23.9 | 0 | 8870
0.08385 | 7 | 0.077 | 30 | 0.9 | 257000 | 1582000 | 1831000 | 12 | 35.7149 | 53.1 | 23.9 | 0 | 7697
0.08385 | 7 | 0.077 | 30 | 0.8 | 220000 | 1406000 | 1620000 | 12 | 35.0547 | 53.1 | 23.9 | 0 | 6593
0.08385 | 7 | 0.077 | 30 | 0.7 | 189000 | 1231000 | 1414000 | 12 | 34.4136 | 53.1 | 23.9 | 0 | 5676
0.08385 | 7 | 0.077 | 30 | 0.6 | 162000 | 1055000 | 1212000 | 12 | 33.7824 | 53.1 | 23.9 | 0 | 4859
0.08385 | 7 | 0.077 | 30 | 0.5 | 141000 | 879000 | 1016000 | 12 | 33.17 | 53.1 | 23.9 | 0 | 4227
0.08385 | 7 | 0.077 | 30 | 0.4 | 117000 | 703000 | 816000 | 12 | 32.5474 | 53.1 | 23.9 | 0 | 3495
0.08385 | 7 | 0.077 | 30 | 0.3 | 96000 | 527000 | 620000 | 12 | 31.9352 | 53.1 | 23.9 | 0 | 2865
0.08385 | 7 | 0.077 | 30 | 0.2 | 75000 | 352000 | 424000 | 12 | 31.324 | 53.1 | 23.9 | 0 | 2246
0.08385 | 7 | 0.077 | 30 | 0.15 | 64000 | 264000 | 326000 | 12 | 31.0168 | 53.1 | 23.9 | 0 | 1920
0.08385 | 7 | 0.077 | 27 | 1 | 265000 | 1758000 | 2015000 | 12 | 33.2839 | 53.1 | 23.9 | 0 | 7963
0.08385 | 7 | 0.077 | 27 | 0.9 | 228000 | 1582000 | 1803000 | 12 | 32.622 | 53.1 | 23.9 | 0 | 6834
0.08385 | 7 | 0.077 | 27 | 0.8 | 195000 | 1406000 | 1595000 | 12 | 31.9737 | 53.1 | 23.9 | 0 | 5841
0.08385 | 7 | 0.077 | 27 | 0.7 | 165000 | 1231000 | 1391000 | 12 | 31.3372 | 53.1 | 23.9 | 0 | 4963
0.08385 | 7 | 0.077 | 27 | 0.6 | 140000 | 1055000 | 1191000 | 12 | 30.7121 | 53.1 | 23.9 | 0 | 4200
0.08385 | 7 | 0.077 | 27 | 0.5 | 119000 | 879000 | 995000 | 12 | 30.1009 | 53.1 | 23.9 | 0 | 3575
0.08385 | 7 | 0.077 | 27 | 0.4 | 102000 | 703000 | 802000 | 12 | 29.5014 | 53.1 | 23.9 | 0 | 3064
0.08385 | 7 | 0.077 | 27 | 0.3 | 82000 | 527000 | 607000 | 12 | 28.8923 | 53.1 | 23.9 | 0 | 2459
0.08385 | 7 | 0.077 | 27 | 0.2 | 64000 | 352000 | 414000 | 12 | 28.2907 | 53.1 | 23.9 | 0 | 1929
0.08385 | 7 | 0.077 | 27 | 0.15 | 55000 | 264000 | 317000 | 12 | 27.9889 | 53.1 | 23.9 | 0 | 1654
0.08385 | 7 | 0.077 | 24 | 1 | 236000 | 1758000 | 1987000 | 12 | 30.1889 | 53.1 | 23.9 | 0 | 7084
0.08385 | 7 | 0.077 | 24 | 0.9 | 201000 | 1582000 | 1778000 | 12 | 29.5364 | 53.1 | 23.9 | 0 | 6042
0.08385 | 7 | 0.077 | 24 | 0.8 | 171000 | 1406000 | 1572000 | 12 | 28.8974 | 53.1 | 23.9 | 0 | 5134
0.08385 | 7 | 0.077 | 24 | 0.7 | 144000 | 1231000 | 1370000 | 12 | 28.2664 | 53.1 | 23.9 | 0 | 4305
0.08385 | 7 | 0.077 | 24 | 0.6 | 120000 | 1055000 | 1171000 | 12 | 27.6479 | 53.1 | 23.9 | 0 | 3601
0.08385 | 7 | 0.077 | 24 | 0.5 | 100000 | 879000 | 976000 | 12 | 27.0406 | 53.1 | 23.9 | 0 | 3008
0.08385 | 7 | 0.077 | 24 | 0.4 | 86000 | 703000 | 787000 | 12 | 26.4505 | 53.1 | 23.9 | 0 | 2585
0.08385 | 7 | 0.077 | 24 | 0.3 | 69000 | 527000 | 594000 | 12 | 25.8509 | 53.1 | 23.9 | 0 | 2068
0.08385 | 7 | 0.077 | 24 | 0.2 | 54000 | 352000 | 404000 | 12 | 25.2583 | 53.1 | 23.9 | 0 | 1621
0.08385 | 7 | 0.077 | 24 | 0.15 | 46000 | 264000 | 309000 | 12 | 24.9617 | 53.1 | 23.9 | 0 | 1394
0.08385 | 7 | 0.077 | 21 | 1 | 210000 | 1758000 | 1961000 | 12 | 27.1027 | 53.1 | 23.9 | 0 | 6294
0.08385 | 7 | 0.077 | 21 | 0.9 | 177000 | 1582000 | 1754000 | 12 | 26.4579 | 53.1 | 23.9 | 0 | 5321
0.08385 | 7 | 0.077 | 21 | 0.8 | 149000 | 1406000 | 1550000 | 12 | 25.824 | 53.1 | 23.9 | 0 | 4456
0.08385 | 7 | 0.077 | 21 | 0.7 | 124000 | 1231000 | 1351000 | 12 | 25.2026 | 53.1 | 23.9 | 0 | 3717
0.08385 | 7 | 0.077 | 21 | 0.6 | 102000 | 1055000 | 1154000 | 12 | 24.5893 | 53.1 | 23.9 | 0 | 3057
0.08385 | 7 | 0.077 | 21 | 0.5 | 84000 | 879000 | 961000 | 12 | 23.9884 | 53.1 | 23.9 | 0 | 2521
0.08385 | 7 | 0.077 | 21 | 0.4 | 69000 | 703000 | 770000 | 12 | 23.3947 | 53.1 | 23.9 | 0 | 2056
0.08385 | 7 | 0.077 | 21 | 0.3 | 59000 | 527000 | 584000 | 12 | 22.8175 | 53.1 | 23.9 | 0 | 1756
0.08385 | 7 | 0.077 | 21 | 0.2 | 45000 | 352000 | 395000 | 12 | 22.2287 | 53.1 | 23.9 | 0 | 1340
0.08385 | 7 | 0.077 | 21 | 0.15 | 38000 | 264000 | 301000 | 12 | 21.9366 | 53.1 | 23.9 | 0 | 1155
0.08385 | 7 | 0.077 | 18 | 1 | 186000 | 1758000 | 1939000 | 12 | 24.0254 | 53.1 | 23.9 | 0 | 5592
0.08385 | 7 | 0.077 | 18 | 0.9 | 155000 | 1582000 | 1733000 | 12 | 23.3848 | 53.1 | 23.9 | 0 | 4654
0.08385 | 7 | 0.077 | 18 | 0.8 | 129000 | 1406000 | 1531000 | 12 | 22.7584 | 53.1 | 23.9 | 0 | 3857
0.08385 | 7 | 0.077 | 18 | 0.7 | 106000 | 1231000 | 1333000 | 12 | 22.1426 | 53.1 | 23.9 | 0 | 3166
0.08385 | 7 | 0.077 | 18 | 0.6 | 85000 | 1055000 | 1138000 | 12 | 21.5354 | 53.1 | 23.9 | 0 | 2560
0.08385 | 7 | 0.077 | 18 | 0.5 | 69000 | 879000 | 946000 | 12 | 20.9409 | 53.1 | 23.9 | 0 | 2081
0.08385 | 7 | 0.077 | 18 | 0.4 | 56000 | 703000 | 758000 | 12 | 20.3545 | 53.1 | 23.9 | 0 | 1682
0.08385 | 7 | 0.077 | 18 | 0.3 | 44000 | 527000 | 571000 | 12 | 19.7731 | 53.1 | 23.9 | 0 | 1334
0.08385 | 7 | 0.077 | 18 | 0.2 | 36000 | 352000 | 387000 | 12 | 19.2016 | 53.1 | 23.9 | 0 | 1084
0.08385 | 7 | 0.077 | 18 | 0.15 | 31000 | 264000 | 294000 | 12 | 18.914 | 53.1 | 23.9 | 0 | 940
0.08385 | 7 | 0.077 | 17.5 | 1 | 182000 | 1758000 | 1935000 | 12 | 23.5113 | 53.1 | 23.9 | 0 | 5462
0.08385 | 7 | 0.077 | 17.5 | 0.9 | 152000 | 1582000 | 1729000 | 12 | 22.8734 | 53.1 | 23.9 | 0 | 4551
0.08385 | 7 | 0.077 | 17.5 | 0.8 | 125000 | 1406000 | 1528000 | 12 | 22.2481 | 53.1 | 23.9 | 0 | 3764
0.08385 | 7 | 0.077 | 17.5 | 0.7 | 103000 | 1231000 | 1330000 | 12 | 21.6331 | 53.1 | 23.9 | 0 | 3079
0.08385 | 7 | 0.077 | 17.5 | 0.6 | 83000 | 1055000 | 1135000 | 12 | 21.0268 | 53.1 | 23.9 | 0 | 2482
0.08385 | 7 | 0.077 | 17.5 | 0.5 | 67000 | 879000 | 944000 | 12 | 20.4335 | 53.1 | 23.9 | 0 | 2013
0.08385 | 7 | 0.077 | 17.5 | 0.4 | 54000 | 703000 | 756000 | 12 | 19.8482 | 53.1 | 23.9 | 0 | 1624
0.08385 | 7 | 0.077 | 17.5 | 0.3 | 43000 | 527000 | 569000 | 12 | 19.268 | 53.1 | 23.9 | 0 | 1286
0.08385 | 7 | 0.077 | 17.5 | 0.2 | 35000 | 352000 | 385000 | 12 | 18.6975 | 53.1 | 23.9 | 0 | 1045
0.08385 | 7 | 0.077 | 17.5 | 0.15 | 30000 | 264000 | 293000 | 12 | 18.4104 | 53.1 | 23.9 | 0 | 906
0.08385 | 7 | 0.077 | 17 | 1 | 178000 | 1758000 | 1931000 | 12 | 22.9978 | 53.1 | 23.9 | 0 | 5340
0.08385 | 7 | 0.077 | 17 | 0.9 | 148000 | 1582000 | 1726000 | 12 | 22.3621 | 53.1 | 23.9 | 0 | 4449
0.08385 | 7 | 0.077 | 17 | 0.8 | 122000 | 1406000 | 1525000 | 12 | 21.738 | 53.1 | 23.9 | 0 | 3672
0.08385 | 7 | 0.077 | 17 | 0.7 | 100000 | 1231000 | 1327000 | 12 | 21.1238 | 53.1 | 23.9 | 0 | 2994
0.08385 | 7 | 0.077 | 17 | 0.6 | 80000 | 1055000 | 1133000 | 12 | 20.5186 | 53.1 | 23.9 | 0 | 2406
0.08385 | 7 | 0.077 | 17 | 0.5 | 65000 | 879000 | 942000 | 12 | 19.9262 | 53.1 | 23.9 | 0 | 1946
0.08385 | 7 | 0.077 | 17 | 0.4 | 52000 | 703000 | 754000 | 12 | 19.3419 | 53.1 | 23.9 | 0 | 1566
0.08385 | 7 | 0.077 | 17 | 0.3 | 44000 | 527000 | 570000 | 12 | 18.7704 | 53.1 | 23.9 | 0 | 1314
0.08385 | 7 | 0.077 | 17 | 0.2 | 35000 | 352000 | 385000 | 12 | 18.1968 | 53.1 | 23.9 | 0 | 1040
0.08385 | 7 | 0.077 | 17 | 0.15 | 29000 | 264000 | 292000 | 12 | 17.9065 | 53.1 | 23.9 | 0 | 869
0.08385 | 7 | 0.077 | 16.5 | 1 | 173000 | 1758000 | 1926000 | 12 | 22.4822 | 53.1 | 23.9 | 0 | 5196
0.08385 | 7 | 0.077 | 16.5 | 0.9 | 145000 | 1582000 | 1723000 | 12 | 21.8512 | 53.1 | 23.9 | 0 | 4351
0.08385 | 7 | 0.077 | 16.5 | 0.8 | 119000 | 1406000 | 1522000 | 12 | 21.228 | 53.1 | 23.9 | 0 | 3582
0.08385 | 7 | 0.077 | 16.5 | 0.7 | 97000 | 1231000 | 1325000 | 12 | 20.6144 | 53.1 | 23.9 | 0 | 2909
0.08385 | 7 | 0.077 | 16.5 | 0.6 | 78000 | 1055000 | 1130000 | 12 | 20.0104 | 53.1 | 23.9 | 0 | 2332
0.08385 | 7 | 0.077 | 16.5 | 0.5 | 63000 | 879000 | 940000 | 12 | 19.4189 | 53.1 | 23.9 | 0 | 1880
0.08385 | 7 | 0.077 | 16.5 | 0.4 | 50000 | 703000 | 752000 | 12 | 18.8358 | 53.1 | 23.9 | 0 | 1510
0.08385 | 7 | 0.077 | 16.5 | 0.3 | 42000 | 527000 | 568000 | 12 | 18.2641 | 53.1 | 23.9 | 0 | 1255
0.08385 | 7 | 0.077 | 16.5 | 0.2 | 33000 | 352000 | 384000 | 12 | 17.6919 | 53.1 | 23.9 | 0 | 994
0.08385 | 7 | 0.077 | 16.5 | 0.15 | 28000 | 264000 | 291000 | 12 | 17.4032 | 53.1 | 23.9 | 0 | 838
0.08385 | 7 | 0.077 | 16 | 1 | 170000 | 1758000 | 1923000 | 12 | 21.9724 | 53.1 | 23.9 | 0 | 5110
0.08385 | 7 | 0.077 | 16 | 0.9 | 142000 | 1582000 | 1720000 | 12 | 21.3404 | 53.1 | 23.9 | 0 | 4253
0.08385 | 7 | 0.077 | 16 | 0.8 | 116000 | 1406000 | 1519000 | 12 | 20.7181 | 53.1 | 23.9 | 0 | 3493
0.08385 | 7 | 0.077 | 16 | 0.7 | 94000 | 1231000 | 1322000 | 12 | 20.1053 | 53.1 | 23.9 | 0 | 2827
0.08385 | 7 | 0.077 | 16 | 0.6 | 75000 | 1055000 | 1128000 | 12 | 19.5022 | 53.1 | 23.9 | 0 | 2257
0.08385 | 7 | 0.077 | 16 | 0.5 | 60000 | 879000 | 938000 | 12 | 18.9117 | 53.1 | 23.9 | 0 | 1814
0.08385 | 7 | 0.077 | 16 | 0.4 | 49000 | 703000 | 751000 | 12 | 18.3327 | 53.1 | 23.9 | 0 | 1484
0.08385 | 7 | 0.077 | 16 | 0.3 | 40000 | 527000 | 566000 | 12 | 17.7578 | 53.1 | 23.9 | 0 | 1195
0.08385 | 7 | 0.077 | 16 | 0.2 | 32000 | 352000 | 382000 | 12 | 17.1877 | 53.1 | 23.9 | 0 | 955
0.08385 | 7 | 0.077 | 16 | 0.15 | 27000 | 264000 | 290000 | 12 | 16.9004 | 53.1 | 23.9 | 0 | 812
0.08385 | 7 | 0.077 | 15.5 | 1 | 169000 | 1758000 | 1922000 | 12 | 21.4673 | 53.1 | 23.9 | 0 | 5071
0.08385 | 7 | 0.077 | 15.5 | 0.9 | 138000 | 1582000 | 1716000 | 12 | 20.8285 | 53.1 | 23.9 | 0 | 4146
0.08385 | 7 | 0.077 | 15.5 | 0.8 | 114000 | 1406000 | 1517000 | 12 | 20.2084 | 53.1 | 23.9 | 0 | 3405
0.08385 | 7 | 0.077 | 15.5 | 0.7 | 92000 | 1231000 | 1319000 | 12 | 19.5965 | 53.1 | 23.9 | 0 | 2747
0.08385 | 7 | 0.077 | 15.5 | 0.6 | 73000 | 1055000 | 1126000 | 12 | 18.9952 | 53.1 | 23.9 | 0 | 2194
0.08385 | 7 | 0.077 | 15.5 | 0.5 | 58000 | 879000 | 936000 | 12 | 18.4048 | 53.1 | 23.9 | 0 | 1750
0.08385 | 7 | 0.077 | 15.5 | 0.4 | 47000 | 703000 | 749000 | 12 | 17.8259 | 53.1 | 23.9 | 0 | 1421
0.08385 | 7 | 0.077 | 15.5 | 0.3 | 38000 | 527000 | 564000 | 12 | 17.2526 | 53.1 | 23.9 | 0 | 1147
0.08385 | 7 | 0.077 | 15.5 | 0.2 | 31000 | 352000 | 381000 | 12 | 16.6842 | 53.1 | 23.9 | 0 | 922
0.08385 | 7 | 0.077 | 15.5 | 0.15 | 27000 | 264000 | 290000 | 12 | 16.4011 | 53.1 | 23.9 | 0 | 821
0.08385 | 7 | 0.077 | 15 | 1 | 171000 | 1758000 | 1924000 | 12 | 20.971 | 53.1 | 23.9 | 0 | 5120
0.08385 | 7 | 0.077 | 15 | 0.9 | 135000 | 1582000 | 1713000 | 12 | 20.3179 | 53.1 | 23.9 | 0 | 4050
0.08385 | 7 | 0.077 | 15 | 0.8 | 111000 | 1406000 | 1514000 | 12 | 19.6986 | 53.1 | 23.9 | 0 | 3317
0.08385 | 7 | 0.077 | 15 | 0.7 | 89000 | 1231000 | 1317000 | 12 | 19.0879 | 53.1 | 23.9 | 0 | 2669
0.08385 | 7 | 0.077 | 15 | 0.6 | 71000 | 1055000 | 1123000 | 12 | 18.4873 | 53.1 | 23.9 | 0 | 2122
0.08385 | 7 | 0.077 | 15 | 0.5 | 56000 | 879000 | 934000 | 12 | 17.8978 | 53.1 | 23.9 | 0 | 1686
0.08385 | 7 | 0.077 | 15 | 0.4 | 45000 | 703000 | 747000 | 12 | 17.3198 | 53.1 | 23.9 | 0 | 1365
0.08385 | 7 | 0.077 | 15 | 0.3 | 37000 | 527000 | 563000 | 12 | 16.7485 | 53.1 | 23.9 | 0 | 1110
0.08385 | 7 | 0.077 | 15 | 0.2 | 30000 | 352000 | 381000 | 12 | 16.1813 | 53.1 | 23.9 | 0 | 895
0.08385 | 7 | 0.077 | 15 | 0.15 | 26000 | 264000 | 289000 | 12 | 15.8982 | 53.1 | 23.9 | 0 | 793
0.08385 | 7 | 0.077 | 14.5 | 1 | 173000 | 1758000 | 1925000 | 12 | 20.4753 | 53.1 | 23.9 | 0 | 5176
0.08385 | 7 | 0.077 | 14.5 | 0.9 | 132000 | 1582000 | 1711000 | 12 | 19.8086 | 53.1 | 23.9 | 0 | 3969
0.08385 | 7 | 0.077 | 14.5 | 0.8 | 108000 | 1406000 | 1511000 | 12 | 19.1892 | 53.1 | 23.9 | 0 | 3233
0.08385 | 7 | 0.077 | 14.5 | 0.7 | 86000 | 1231000 | 1314000 | 12 | 18.5793 | 53.1 | 23.9 | 0 | 2593
0.08385 | 7 | 0.077 | 14.5 | 0.6 | 68000 | 1055000 | 1121000 | 12 | 17.9796 | 53.1 | 23.9 | 0 | 2053
0.08385 | 7 | 0.077 | 14.5 | 0.5 | 54000 | 879000 | 932000 | 12 | 17.3909 | 53.1 | 23.9 | 0 | 1624
0.08385 | 7 | 0.077 | 14.5 | 0.4 | 44000 | 703000 | 746000 | 12 | 16.8146 | 53.1 | 23.9 | 0 | 1318
0.08385 | 7 | 0.077 | 14.5 | 0.3 | 36000 | 527000 | 562000 | 12 | 16.2451 | 53.1 | 23.9 | 0 | 1079
0.08385 | 7 | 0.077 | 14.5 | 0.2 | 29000 | 352000 | 380000 | 12 | 15.6787 | 53.1 | 23.9 | 0 | 872
0.08385 | 7 | 0.077 | 14.5 | 0.15 | 26000 | 264000 | 289000 | 12 | 15.3959 | 53.1 | 23.9 | 0 | 773
0.08385 | 7 | 0.077 | 14 | 1 | 174000 | 1758000 | 1927000 | 12 | 19.9787 | 53.1 | 23.9 | 0 | 5222
0.08385 | 7 | 0.077 | 14 | 0.9 | 130000 | 1582000 | 1708000 | 12 | 19.3003 | 53.1 | 23.9 | 0 | 3897
0.08385 | 7 | 0.077 | 14 | 0.8 | 105000 | 1406000 | 1508000 | 12 | 18.6798 | 53.1 | 23.9 | 0 | 3149
0.08385 | 7 | 0.077 | 14 | 0.7 | 84000 | 1231000 | 1312000 | 12 | 18.071 | 53.1 | 23.9 | 0 | 2518
0.08385 | 7 | 0.077 | 14 | 0.6 | 66000 | 1055000 | 1119000 | 12 | 17.4719 | 53.1 | 23.9 | 0 | 1984
0.08385 | 7 | 0.077 | 14 | 0.5 | 52000 | 879000 | 929000 | 12 | 16.8841 | 53.1 | 23.9 | 0 | 1561
0.08385 | 7 | 0.077 | 14 | 0.4 | 43000 | 703000 | 745000 | 12 | 16.3107 | 53.1 | 23.9 | 0 | 1284
0.08385 | 7 | 0.077 | 14 | 0.3 | 35000 | 527000 | 561000 | 12 | 15.7421 | 53.1 | 23.9 | 0 | 1053
0.08385 | 7 | 0.077 | 14 | 0.2 | 28000 | 352000 | 379000 | 12 | 15.1757 | 53.1 | 23.9 | 0 | 845
0.08385 | 7 | 0.077 | 14 | 0.15 | 25000 | 264000 | 288000 | 12 | 14.8939 | 53.1 | 23.9 | 0 | 754
0.08385 | 7 | 0.077 | 13.5 | 1 | 174000 | 1758000 | 1927000 | 12 | 19.4764 | 53.1 | 23.9 | 0 | 5211
0.08385 | 7 | 0.077 | 13.5 | 0.9 | 128000 | 1582000 | 1706000 | 12 | 18.7926 | 53.1 | 23.9 | 0 | 3831
0.08385 | 7 | 0.077 | 13.5 | 0.8 | 102000 | 1406000 | 1506000 | 12 | 18.1707 | 53.1 | 23.9 | 0 | 3069
0.08385 | 7 | 0.077 | 13.5 | 0.7 | 82000 | 1231000 | 1310000 | 12 | 17.563 | 53.1 | 23.9 | 0 | 2447
0.08385 | 7 | 0.077 | 13.5 | 0.6 | 64000 | 1055000 | 1117000 | 12 | 16.9643 | 53.1 | 23.9 | 0 | 1915
0.08385 | 7 | 0.077 | 13.5 | 0.5 | 50000 | 879000 | 928000 | 12 | 16.3784 | 53.1 | 23.9 | 0 | 1511
0.08385 | 7 | 0.077 | 13.5 | 0.4 | 42000 | 703000 | 744000 | 12 | 15.8068 | 53.1 | 23.9 | 0 | 1249
0.08385 | 7 | 0.077 | 13.5 | 0.3 | 34000 | 527000 | 560000 | 12 | 15.2386 | 53.1 | 23.9 | 0 | 1021
0.08385 | 7 | 0.077 | 13.5 | 0.2 | 28000 | 352000 | 378000 | 12 | 14.6742 | 53.1 | 23.9 | 0 | 832
0.08385 | 7 | 0.077 | 13.5 | 0.15 | 25000 | 264000 | 288000 | 12 | 14.3921 | 53.1 | 23.9 | 0 | 738
0.08385 | 7 | 0.077 | 13 | 1 | 172000 | 1758000 | 1925000 | 12 | 18.9705 | 53.1 | 23.9 | 0 | 5166
0.08385 | 7 | 0.077 | 13 | 0.9 | 126000 | 1582000 | 1704000 | 12 | 18.285 | 53.1 | 23.9 | 0 | 3767
0.08385 | 7 | 0.077 | 13 | 0.8 | 100000 | 1406000 | 1503000 | 12 | 17.6621 | 53.1 | 23.9 | 0 | 2992
0.08385 | 7 | 0.077 | 13 | 0.7 | 79000 | 1231000 | 1307000 | 12 | 17.0549 | 53.1 | 23.9 | 0 | 2374
0.08385 | 7 | 0.077 | 13 | 0.6 | 62000 | 1055000 | 1115000 | 12 | 16.4569 | 53.1 | 23.9 | 0 | 1848
0.08385 | 7 | 0.077 | 13 | 0.5 | 49000 | 879000 | 927000 | 12 | 15.8737 | 53.1 | 23.9 | 0 | 1471
0.08385 | 7 | 0.077 | 13 | 0.4 | 41000 | 703000 | 743000 | 12 | 15.3029 | 53.1 | 23.9 | 0 | 1216
0.08385 | 7 | 0.077 | 13 | 0.3 | 33000 | 527000 | 560000 | 12 | 14.7361 | 53.1 | 23.9 | 0 | 1000
0.08385 | 7 | 0.077 | 13 | 0.2 | 27000 | 352000 | 378000 | 12 | 14.1717 | 53.1 | 23.9 | 0 | 810
0.08385 | 7 | 0.077 | 13 | 0.15 | 24000 | 264000 | 287000 | 12 | 13.8904 | 53.1 | 23.9 | 0 | 723
0.08385 | 7 | 0.077 | 12.5 | 1 | 170000 | 1758000 | 1923000 | 12 | 18.4627 | 53.1 | 23.9 | 0 | 5101
0.08385 | 7 | 0.077 | 12.5 | 0.9 | 124000 | 1582000 | 1702000 | 12 | 17.7783 | 53.1 | 23.9 | 0 | 3711
0.08385 | 7 | 0.077 | 12.5 | 0.8 | 97000 | 1406000 | 1501000 | 12 | 17.1534 | 53.1 | 23.9 | 0 | 2916
0.08385 | 7 | 0.077 | 12.5 | 0.7 | 77000 | 1231000 | 1305000 | 12 | 16.5468 | 53.1 | 23.9 | 0 | 2303
0.08385 | 7 | 0.077 | 12.5 | 0.6 | 59000 | 1055000 | 1112000 | 12 | 15.9494 | 53.1 | 23.9 | 0 | 1782
0.08385 | 7 | 0.077 | 12.5 | 0.5 | 48000 | 879000 | 925000 | 12 | 15.3695 | 53.1 | 23.9 | 0 | 1435
0.08385 | 7 | 0.077 | 12.5 | 0.4 | 40000 | 703000 | 742000 | 12 | 14.8005 | 53.1 | 23.9 | 0 | 1197
0.08385 | 7 | 0.077 | 12.5 | 0.3 | 33000 | 527000 | 559000 | 12 | 14.2337 | 53.1 | 23.9 | 0 | 980
0.08385 | 7 | 0.077 | 12.5 | 0.2 | 26000 | 352000 | 377000 | 12 | 13.6698 | 53.1 | 23.9 | 0 | 794
0.08385 | 7 | 0.077 | 12.5 | 0.15 | 24000 | 264000 | 287000 | 12 | 13.3888 | 53.1 | 23.9 | 0 | 710
0.08385 | 7 | 0.077 | 12 | 1 | 164000 | 1758000 | 1917000 | 12 | 17.9424 | 53.1 | 23.9 | 0 | 4911
0.08385 | 7 | 0.077 | 12 | 0.9 | 122000 | 1582000 | 1701000 | 12 | 17.2723 | 53.1 | 23.9 | 0 | 3663
0.08385 | 7 | 0.077 | 12 | 0.8 | 95000 | 1406000 | 1498000 | 12 | 16.6451 | 53.1 | 23.9 | 0 | 2843
0.08385 | 7 | 0.077 | 12 | 0.7 | 74000 | 1231000 | 1303000 | 12 | 16.039 | 53.1 | 23.9 | 0 | 2233
0.08385 | 7 | 0.077 | 12 | 0.6 | 57000 | 1055000 | 1110000 | 12 | 15.4422 | 53.1 | 23.9 | 0 | 1717
0.08385 | 7 | 0.077 | 12 | 0.5 | 47000 | 879000 | 924000 | 12 | 14.8657 | 53.1 | 23.9 | 0 | 1403
0.08385 | 7 | 0.077 | 12 | 0.4 | 39000 | 703000 | 741000 | 12 | 14.2971 | 53.1 | 23.9 | 0 | 1168
0.08385 | 7 | 0.077 | 12 | 0.3 | 32000 | 527000 | 559000 | 12 | 13.7315 | 53.1 | 23.9 | 0 | 962
0.08385 | 7 | 0.077 | 12 | 0.2 | 26000 | 352000 | 377000 | 12 | 13.1682 | 53.1 | 23.9 | 0 | 780
0.08385 | 7 | 0.077 | 12 | 0.15 | 23000 | 264000 | 286000 | 12 | 12.8874 | 53.1 | 23.9 | 0 | 697
0.08385 | 7 | 0.077 | 11.5 | 1 | 165000 | 1758000 | 1918000 | 12 | 17.4443 | 53.1 | 23.9 | 0 | 4943
0.08385 | 7 | 0.077 | 11.5 | 0.9 | 121000 | 1582000 | 1699000 | 12 | 16.7666 | 53.1 | 23.9 | 0 | 3618
0.08385 | 7 | 0.077 | 11.5 | 0.8 | 93000 | 1406000 | 1496000 | 12 | 16.1373 | 53.1 | 23.9 | 0 | 2776
0.08385 | 7 | 0.077 | 11.5 | 0.7 | 72000 | 1231000 | 1301000 | 12 | 15.5313 | 53.1 | 23.9 | 0 | 2165
0.08385 | 7 | 0.077 | 11.5 | 0.6 | 56000 | 1055000 | 1109000 | 12 | 14.9382 | 53.1 | 23.9 | 0 | 1685
0.08385 | 7 | 0.077 | 11.5 | 0.5 | 46000 | 879000 | 923000 | 12 | 14.362 | 53.1 | 23.9 | 0 | 1373
0.08385 | 7 | 0.077 | 11.5 | 0.4 | 38000 | 703000 | 740000 | 12 | 13.795 | 53.1 | 23.9 | 0 | 1152
0.08385 | 7 | 0.077 | 11.5 | 0.3 | 32000 | 527000 | 558000 | 12 | 13.2295 | 53.1 | 23.9 | 0 | 946
0.08385 | 7 | 0.077 | 11.5 | 0.2 | 26000 | 352000 | 376000 | 12 | 12.6666 | 53.1 | 23.9 | 0 | 767
0.08385 | 7 | 0.077 | 11.5 | 0.15 | 23000 | 264000 | 286000 | 12 | 12.386 | 53.1 | 23.9 | 0 | 685
0.08385 | 7 | 0.077 | 11 | 1 | 168000 | 1758000 | 1921000 | 12 | 16.9539 | 53.1 | 23.9 | 0 | 5052
0.08385 | 7 | 0.077 | 11 | 0.9 | 119000 | 1582000 | 1698000 | 12 | 16.2613 | 53.1 | 23.9 | 0 | 3577
0.08385 | 7 | 0.077 | 11 | 0.8 | 91000 | 1406000 | 1494000 | 12 | 15.6302 | 53.1 | 23.9 | 0 | 2715
0.08385 | 7 | 0.077 | 11 | 0.7 | 70000 | 1231000 | 1298000 | 12 | 15.0237 | 53.1 | 23.9 | 0 | 2099
0.08385 | 7 | 0.077 | 11 | 0.6 | 55000 | 1055000 | 1108000 | 12 | 14.4337 | 53.1 | 23.9 | 0 | 1647
0.08385 | 7 | 0.077 | 11 | 0.5 | 45000 | 879000 | 923000 | 12 | 13.8599 | 53.1 | 23.9 | 0 | 1358
0.08385 | 7 | 0.077 | 11 | 0.4 | 38000 | 703000 | 740000 | 12 | 13.293 | 53.1 | 23.9 | 0 | 1137
0.08385 | 7 | 0.077 | 11 | 0.3 | 31000 | 527000 | 557000 | 12 | 12.7276 | 53.1 | 23.9 | 0 | 931
0.08385 | 7 | 0.077 | 11 | 0.2 | 25000 | 352000 | 376000 | 12 | 12.1651 | 53.1 | 23.9 | 0 | 754
0.08385 | 7 | 0.077 | 11 | 0.15 | 22000 | 264000 | 286000 | 12 | 11.8847 | 53.1 | 23.9 | 0 | 674
0.08385 | 7 | 0.077 | 10.5 | 1 | 168000 | 1758000 | 1921000 | 12 | 16.4506 | 53.1 | 23.9 | 0 | 5032
0.08385 | 7 | 0.077 | 10.5 | 0.9 | 125000 | 1582000 | 1703000 | 12 | 15.7771 | 53.1 | 23.9 | 0 | 3746
0.08385 | 7 | 0.077 | 10.5 | 0.8 | 89000 | 1406000 | 1492000 | 12 | 15.1233 | 53.1 | 23.9 | 0 | 2657
0.08385 | 7 | 0.077 | 10.5 | 0.7 | 68000 | 1231000 | 1296000 | 12 | 14.516 | 53.1 | 23.9 | 0 | 2032
0.08385 | 7 | 0.077 | 10.5 | 0.6 | 54000 | 1055000 | 1107000 | 12 | 13.9298 | 53.1 | 23.9 | 0 | 1616
0.08385 | 7 | 0.077 | 10.5 | 0.5 | 45000 | 879000 | 922000 | 12 | 13.3571 | 53.1 | 23.9 | 0 | 1337
0.08385 | 7 | 0.077 | 10.5 | 0.4 | 37000 | 703000 | 739000 | 12 | 12.7899 | 53.1 | 23.9 | 0 | 1111
0.08385 | 7 | 0.077 | 10.5 | 0.3 | 31000 | 527000 | 557000 | 12 | 12.2257 | 53.1 | 23.9 | 0 | 916
0.08385 | 7 | 0.077 | 10.5 | 0.2 | 25000 | 352000 | 376000 | 12 | 11.6636 | 53.1 | 23.9 | 0 | 742
0.08385 | 7 | 0.077 | 10.5 | 0.15 | 22000 | 264000 | 285000 | 12 | 11.3835 | 53.1 | 23.9 | 0 | 664
0.08385 | 7 | 0.115 | 30 | 1 | 279000 | 1758000 | 2029000 | 12 | 34.2394 | 53.1 | 49 | 0 | 8371
0.08385 | 7 | 0.115 | 30 | 0.9 | 243000 | 1582000 | 1818000 | 12 | 33.7982 | 53.1 | 49 | 0 | 7279
0.08385 | 7 | 0.115 | 30 | 0.8 | 208000 | 1406000 | 1608000 | 12 | 33.3607 | 53.1 | 49 | 0 | 6240
0.08385 | 7 | 0.115 | 30 | 0.7 | 180000 | 1231000 | 1405000 | 12 | 32.9357 | 53.1 | 49 | 0 | 5388
0.08385 | 7 | 0.115 | 30 | 0.6 | 154000 | 1055000 | 1204000 | 12 | 32.517 | 53.1 | 49 | 0 | 4629
0.08385 | 7 | 0.115 | 30 | 0.5 | 135000 | 879000 | 1010000 | 12 | 32.1098 | 53.1 | 49 | 0 | 4040
0.08385 | 7 | 0.115 | 30 | 0.4 | 113000 | 703000 | 812000 | 12 | 31.6978 | 53.1 | 49 | 0 | 3379
0.08385 | 7 | 0.115 | 30 | 0.3 | 93000 | 527000 | 618000 | 12 | 31.2909 | 53.1 | 49 | 0 | 2794
0.08385 | 7 | 0.115 | 30 | 0.2 | 74000 | 352000 | 423000 | 12 | 30.8839 | 53.1 | 49 | 0 | 2207
0.08385 | 7 | 0.115 | 30 | 0.15 | 63000 | 264000 | 325000 | 12 | 30.6791 | 53.1 | 49 | 0 | 1895
0.08385 | 7 | 0.115 | 27 | 1 | 250000 | 1758000 | 2000000 | 12 | 31.176 | 53.1 | 49 | 0 | 7496
0.08385 | 7 | 0.115 | 27 | 0.9 | 215000 | 1582000 | 1790000 | 12 | 30.7374 | 53.1 | 49 | 0 | 6436
0.08385 | 7 | 0.115 | 27 | 0.8 | 185000 | 1406000 | 1585000 | 12 | 30.3097 | 53.1 | 49 | 0 | 5536
0.08385 | 7 | 0.115 | 27 | 0.7 | 157000 | 1231000 | 1383000 | 12 | 29.8867 | 53.1 | 49 | 0 | 4706
0.08385 | 7 | 0.115 | 27 | 0.6 | 133000 | 1055000 | 1184000 | 12 | 29.4715 | 53.1 | 49 | 0 | 3993
0.08385 | 7 | 0.115 | 27 | 0.5 | 113000 | 879000 | 989000 | 12 | 29.0647 | 53.1 | 49 | 0 | 3403
0.08385 | 7 | 0.115 | 27 | 0.4 | 98000 | 703000 | 799000 | 12 | 28.6673 | 53.1 | 49 | 0 | 2952
0.08385 | 7 | 0.115 | 27 | 0.3 | 80000 | 527000 | 605000 | 12 | 28.2624 | 53.1 | 49 | 0 | 2391
0.08385 | 7 | 0.115 | 27 | 0.2 | 63000 | 352000 | 413000 | 12 | 27.8617 | 53.1 | 49 | 0 | 1892
0.08385 | 7 | 0.115 | 27 | 0.15 | 54000 | 264000 | 316000 | 12 | 27.6605 | 53.1 | 49 | 0 | 1629
0.08385 | 7 | 0.115 | 24 | 1 | 222000 | 1758000 | 1973000 | 12 | 28.1149 | 53.1 | 49 | 0 | 6654
0.08385 | 7 | 0.115 | 24 | 0.9 | 190000 | 1582000 | 1766000 | 12 | 27.6838 | 53.1 | 49 | 0 | 5699
0.08385 | 7 | 0.115 | 24 | 0.8 | 161000 | 1406000 | 1563000 | 12 | 27.2589 | 53.1 | 49 | 0 | 4834
0.08385 | 7 | 0.115 | 24 | 0.7 | 136000 | 1231000 | 1362000 | 12 | 26.8407 | 53.1 | 49 | 0 | 4069
0.08385 | 7 | 0.115 | 24 | 0.6 | 114000 | 1055000 | 1165000 | 12 | 26.43 | 53.1 | 49 | 0 | 3415
0.08385 | 7 | 0.115 | 24 | 0.5 | 95000 | 879000 | 972000 | 12 | 26.0262 | 53.1 | 49 | 0 | 2864
0.08385 | 7 | 0.115 | 24 | 0.4 | 83000 | 703000 | 783000 | 12 | 25.6337 | 53.1 | 49 | 0 | 2480
0.08385 | 7 | 0.115 | 24 | 0.3 | 67000 | 527000 | 592000 | 12 | 25.2349 | 53.1 | 49 | 0 | 2003
0.08385 | 7 | 0.115 | 24 | 0.2 | 53000 | 352000 | 403000 | 12 | 24.8403 | 53.1 | 49 | 0 | 1587
0.08385 | 7 | 0.115 | 24 | 0.15 | 46000 | 264000 | 308000 | 12 | 24.6425 | 53.1 | 49 | 0 | 1372
0.08385 | 7 | 0.115 | 21 | 1 | 198000 | 1758000 | 1950000 | 12 | 25.0629 | 53.1 | 49 | 0 | 5949
0.08385 | 7 | 0.115 | 21 | 0.9 | 166000 | 1582000 | 1744000 | 12 | 24.6324 | 53.1 | 49 | 0 | 4994
0.08385 | 7 | 0.115 | 21 | 0.8 | 140000 | 1406000 | 1542000 | 12 | 24.212 | 53.1 | 49 | 0 | 4190
0.08385 | 7 | 0.115 | 21 | 0.7 | 117000 | 1231000 | 1344000 | 12 | 23.7993 | 53.1 | 49 | 0 | 3499
0.08385 | 7 | 0.115 | 21 | 0.6 | 96000 | 1055000 | 1148000 | 12 | 23.3917 | 53.1 | 49 | 0 | 2885
0.08385 | 7 | 0.115 | 21 | 0.5 | 80000 | 879000 | 956000 | 12 | 22.9922 | 53.1 | 49 | 0 | 2391
0.08385 | 7 | 0.115 | 21 | 0.4 | 66000 | 703000 | 767000 | 12 | 22.5973 | 53.1 | 49 | 0 | 1966
0.08385 | 7 | 0.115 | 21 | 0.3 | 56000 | 527000 | 582000 | 12 | 22.2127 | 53.1 | 49 | 0 | 1693
0.08385 | 7 | 0.115 | 21 | 0.2 | 44000 | 352000 | 394000 | 12 | 21.8205 | 53.1 | 49 | 0 | 1307
0.08385 | 7 | 0.115 | 21 | 0.15 | 38000 | 264000 | 300000 | 12 | 21.6257 | 53.1 | 49 | 0 | 1134
0.08385 | 7 | 0.115 | 18 | 1 | 172000 | 1758000 | 1924000 | 12 | 22.0044 | 53.1 | 49 | 0 | 5145
0.08385 | 7 | 0.115 | 18 | 0.9 | 145000 | 1582000 | 1723000 | 12 | 21.5856 | 53.1 | 49 | 0 | 4359
0.08385 | 7 | 0.115 | 18 | 0.8 | 121000 | 1406000 | 1523000 | 12 | 21.1698 | 53.1 | 49 | 0 | 3615
0.08385 | 7 | 0.115 | 18 | 0.7 | 99000 | 1231000 | 1326000 | 12 | 20.7601 | 53.1 | 49 | 0 | 2963
0.08385 | 7 | 0.115 | 18 | 0.6 | 80000 | 1055000 | 1132000 | 12 | 20.3566 | 53.1 | 49 | 0 | 2403
0.08385 | 7 | 0.115 | 18 | 0.5 | 65000 | 879000 | 942000 | 12 | 19.9612 | 53.1 | 49 | 0 | 1964
0.08385 | 7 | 0.115 | 18 | 0.4 | 53000 | 703000 | 755000 | 12 | 19.5709 | 53.1 | 49 | 0 | 1599
0.08385 | 7 | 0.115 | 18 | 0.3 | 45000 | 527000 | 572000 | 12 | 19.1892 | 53.1 | 49 | 0 | 1364
0.08385 | 7 | 0.115 | 18 | 0.2 | 35000 | 352000 | 386000 | 12 | 18.8026 | 53.1 | 49 | 0 | 1055
0.08385 | 7 | 0.115 | 18 | 0.15 | 31000 | 264000 | 293000 | 12 | 18.6106 | 53.1 | 49 | 0 | 920
0.08385 | 7 | 0.115 | 17.5 | 1 | 169000 | 1758000 | 1922000 | 12 | 21.4986 | 53.1 | 49 | 0 | 5071
0.08385 | 7 | 0.115 | 17.5 | 0.9 | 142000 | 1582000 | 1720000 | 12 | 21.0786 | 53.1 | 49 | 0 | 4265
0.08385 | 7 | 0.115 | 17.5 | 0.8 | 117000 | 1406000 | 1520000 | 12 | 20.6631 | 53.1 | 49 | 0 | 3525
0.08385 | 7 | 0.115 | 17.5 | 0.7 | 96000 | 1231000 | 1324000 | 12 | 20.254 | 53.1 | 49 | 0 | 2880
0.08385 | 7 | 0.115 | 17.5 | 0.6 | 78000 | 1055000 | 1130000 | 12 | 19.851 | 53.1 | 49 | 0 | 2327
0.08385 | 7 | 0.115 | 17.5 | 0.5 | 63000 | 879000 | 940000 | 12 | 19.4563 | 53.1 | 49 | 0 | 1896
0.08385 | 7 | 0.115 | 17.5 | 0.4 | 51000 | 703000 | 753000 | 12 | 19.0668 | 53.1 | 49 | 0 | 1543
0.08385 | 7 | 0.115 | 17.5 | 0.3 | 44000 | 527000 | 570000 | 12 | 18.6855 | 53.1 | 49 | 0 | 1312
0.08385 | 7 | 0.115 | 17.5 | 0.2 | 35000 | 352000 | 386000 | 12 | 18.3026 | 53.1 | 49 | 0 | 1057
0.08385 | 7 | 0.115 | 17.5 | 0.15 | 29000 | 264000 | 292000 | 12 | 18.1081 | 53.1 | 49 | 0 | 885
0.08385 | 7 | 0.115 | 17 | 1 | 169000 | 1758000 | 1922000 | 12 | 20.9972 | 53.1 | 49 | 0 | 5061
0.08385 | 7 | 0.115 | 17 | 0.9 | 139000 | 1582000 | 1717000 | 12 | 20.5714 | 53.1 | 49 | 0 | 4167
0.08385 | 7 | 0.115 | 17 | 0.8 | 115000 | 1406000 | 1517000 | 12 | 20.1565 | 53.1 | 49 | 0 | 3436
0.08385 | 7 | 0.115 | 17 | 0.7 | 93000 | 1231000 | 1321000 | 12 | 19.7478 | 53.1 | 49 | 0 | 2797
0.08385 | 7 | 0.115 | 17 | 0.6 | 75000 | 1055000 | 1128000 | 12 | 19.3462 | 53.1 | 49 | 0 | 2262
0.08385 | 7 | 0.115 | 17 | 0.5 | 61000 | 879000 | 938000 | 12 | 18.9515 | 53.1 | 49 | 0 | 1830
0.08385 | 7 | 0.115 | 17 | 0.4 | 50000 | 703000 | 751000 | 12 | 18.5627 | 53.1 | 49 | 0 | 1487
0.08385 | 7 | 0.115 | 17 | 0.3 | 42000 | 527000 | 568000 | 12 | 18.1808 | 53.1 | 49 | 0 | 1246
0.08385 | 7 | 0.115 | 17 | 0.2 | 33000 | 352000 | 384000 | 12 | 17.7989 | 53.1 | 49 | 0 | 1005
0.08385 | 7 | 0.115 | 17 | 0.15 | 28000 | 264000 | 291000 | 12 | 17.6058 | 53.1 | 49 | 0 | 851
0.08385 | 7 | 0.115 | 16.5 | 1 | 172000 | 1758000 | 1924000 | 12 | 20.5021 | 53.1 | 49 | 0 | 5145
0.08385 | 7 | 0.115 | 16.5 | 0.9 | 135000 | 1582000 | 1713000 | 12 | 20.0635 | 53.1 | 49 | 0 | 4060
0.08385 | 7 | 0.115 | 16.5 | 0.8 | 112000 | 1406000 | 1515000 | 12 | 19.65 | 53.1 | 49 | 0 | 3349
0.08385 | 7 | 0.115 | 16.5 | 0.7 | 91000 | 1231000 | 1318000 | 12 | 19.2419 | 53.1 | 49 | 0 | 2717
0.08385 | 7 | 0.115 | 16.5 | 0.6 | 73000 | 1055000 | 1126000 | 12 | 18.8408 | 53.1 | 49 | 0 | 2188
0.08385 | 7 | 0.115 | 16.5 | 0.5 | 59000 | 879000 | 936000 | 12 | 18.4467 | 53.1 | 49 | 0 | 1765
0.08385 | 7 | 0.115 | 16.5 | 0.4 | 48000 | 703000 | 750000 | 12 | 18.0602 | 53.1 | 49 | 0 | 1454
0.08385 | 7 | 0.115 | 16.5 | 0.3 | 40000 | 527000 | 566000 | 12 | 17.6769 | 53.1 | 49 | 0 | 1191
0.08385 | 7 | 0.115 | 16.5 | 0.2 | 32000 | 352000 | 383000 | 12 | 17.296 | 53.1 | 49 | 0 | 964
0.08385 | 7 | 0.115 | 16.5 | 0.15 | 27000 | 264000 | 290000 | 12 | 17.1038 | 53.1 | 49 | 0 | 823
0.08385 | 7 | 0.115 | 16 | 1 | 174000 | 1758000 | 1927000 | 12 | 20.0071 | 53.1 | 49 | 0 | 5232
0.08385 | 7 | 0.115 | 16 | 0.9 | 132000 | 1582000 | 1711000 | 12 | 19.5566 | 53.1 | 49 | 0 | 3969
0.08385 | 7 | 0.115 | 16 | 0.8 | 109000 | 1406000 | 1512000 | 12 | 19.1435 | 53.1 | 49 | 0 | 3261
0.08385 | 7 | 0.115 | 16 | 0.7 | 88000 | 1231000 | 1316000 | 12 | 18.7363 | 53.1 | 49 | 0 | 2641
0.08385 | 7 | 0.115 | 16 | 0.6 | 71000 | 1055000 | 1123000 | 12 | 18.3355 | 53.1 | 49 | 0 | 2117
0.08385 | 7 | 0.115 | 16 | 0.5 | 57000 | 879000 | 934000 | 12 | 17.942 | 53.1 | 49 | 0 | 1700
0.08385 | 7 | 0.115 | 16 | 0.4 | 46000 | 703000 | 748000 | 12 | 17.5559 | 53.1 | 49 | 0 | 1394
0.08385 | 7 | 0.115 | 16 | 0.3 | 38000 | 527000 | 564000 | 12 | 17.1736 | 53.1 | 49 | 0 | 1145
0.08385 | 7 | 0.115 | 16 | 0.2 | 31000 | 352000 | 382000 | 12 | 16.7935 | 53.1 | 49 | 0 | 929
0.08385 | 7 | 0.115 | 16 | 0.15 | 27000 | 264000 | 290000 | 12 | 16.6021 | 53.1 | 49 | 0 | 800
0.08385 | 7 | 0.115 | 15.5 | 1 | 176000 | 1758000 | 1929000 | 12 | 19.5095 | 53.1 | 49 | 0 | 5280
0.08385 | 7 | 0.115 | 15.5 | 0.9 | 130000 | 1582000 | 1708000 | 12 | 19.0511 | 53.1 | 49 | 0 | 3897
0.08385 | 7 | 0.115 | 15.5 | 0.8 | 106000 | 1406000 | 1509000 | 12 | 18.6372 | 53.1 | 49 | 0 | 3177
0.08385 | 7 | 0.115 | 15.5 | 0.7 | 85000 | 1231000 | 1313000 | 12 | 18.2306 | 53.1 | 49 | 0 | 2564
0.08385 | 7 | 0.115 | 15.5 | 0.6 | 68000 | 1055000 | 1121000 | 12 | 17.8303 | 53.1 | 49 | 0 | 2047
0.08385 | 7 | 0.115 | 15.5 | 0.5 | 55000 | 879000 | 932000 | 12 | 17.4373 | 53.1 | 49 | 0 | 1637
0.08385 | 7 | 0.115 | 15.5 | 0.4 | 45000 | 703000 | 747000 | 12 | 17.0521 | 53.1 | 49 | 0 | 1343
0.08385 | 7 | 0.115 | 15.5 | 0.3 | 37000 | 527000 | 563000 | 12 | 16.6709 | 53.1 | 49 | 0 | 1109
0.08385 | 7 | 0.115 | 15.5 | 0.2 | 30000 | 352000 | 381000 | 12 | 16.2914 | 53.1 | 49 | 0 | 899
0.08385 | 7 | 0.115 | 15.5 | 0.15 | 27000 | 264000 | 290000 | 12 | 16.1022 | 53.1 | 49 | 0 | 804
0.08385 | 7 | 0.115 | 15 | 1 | 176000 | 1758000 | 1928000 | 12 | 19.0079 | 53.1 | 49 | 0 | 5269
0.08385 | 7 | 0.115 | 15 | 0.9 | 128000 | 1582000 | 1706000 | 12 | 18.5461 | 53.1 | 49 | 0 | 3834
0.08385 | 7 | 0.115 | 15 | 0.8 | 103000 | 1406000 | 1506000 | 12 | 18.1311 | 53.1 | 49 | 0 | 3096
0.08385 | 7 | 0.115 | 15 | 0.7 | 83000 | 1231000 | 1311000 | 12 | 17.7251 | 53.1 | 49 | 0 | 2491
0.08385 | 7 | 0.115 | 15 | 0.6 | 66000 | 1055000 | 1119000 | 12 | 17.3251 | 53.1 | 49 | 0 | 1977
0.08385 | 7 | 0.115 | 15 | 0.5 | 53000 | 879000 | 930000 | 12 | 16.9331 | 53.1 | 49 | 0 | 1579
0.08385 | 7 | 0.115 | 15 | 0.4 | 43000 | 703000 | 745000 | 12 | 16.5492 | 53.1 | 49 | 0 | 1305
0.08385 | 7 | 0.115 | 15 | 0.3 | 36000 | 527000 | 562000 | 12 | 16.1682 | 53.1 | 49 | 0 | 1073
0.08385 | 7 | 0.115 | 15 | 0.2 | 29000 | 352000 | 380000 | 12 | 15.7896 | 53.1 | 49 | 0 | 875
0.08385 | 7 | 0.115 | 15 | 0.15 | 26000 | 264000 | 289000 | 12 | 15.6006 | 53.1 | 49 | 0 | 782
0.08385 | 7 | 0.115 | 14.5 | 1 | 166000 | 1758000 | 1919000 | 12 | 18.4877 | 53.1 | 49 | 0 | 4980
0.08385 | 7 | 0.115 | 14.5 | 0.9 | 126000 | 1582000 | 1704000 | 12 | 18.0415 | 53.1 | 49 | 0 | 3776
0.08385 | 7 | 0.115 | 14.5 | 0.8 | 101000 | 1406000 | 1504000 | 12 | 17.6253 | 53.1 | 49 | 0 | 3018
0.08385 | 7 | 0.115 | 14.5 | 0.7 | 81000 | 1231000 | 1309000 | 12 | 17.2196 | 53.1 | 49 | 0 | 2418
0.08385 | 7 | 0.115 | 14.5 | 0.6 | 64000 | 1055000 | 1117000 | 12 | 16.8201 | 53.1 | 49 | 0 | 1909
0.08385 | 7 | 0.115 | 14.5 | 0.5 | 51000 | 879000 | 928000 | 12 | 16.4289 | 53.1 | 49 | 0 | 1523
0.08385 | 7 | 0.115 | 14.5 | 0.4 | 42000 | 703000 | 744000 | 12 | 16.0463 | 53.1 | 49 | 0 | 1266
0.08385 | 7 | 0.115 | 14.5 | 0.3 | 35000 | 527000 | 561000 | 12 | 15.6662 | 53.1 | 49 | 0 | 1046
0.08385 | 7 | 0.115 | 14.5 | 0.2 | 28000 | 352000 | 379000 | 12 | 15.2879 | 53.1 | 49 | 0 | 853
0.08385 | 7 | 0.115 | 14.5 | 0.15 | 25000 | 264000 | 288000 | 12 | 15.0992 | 53.1 | 49 | 0 | 762
0.08385 | 7 | 0.115 | 14 | 1 | 167000 | 1758000 | 1920000 | 12 | 17.9885 | 53.1 | 49 | 0 | 5004
0.08385 | 7 | 0.115 | 14 | 0.9 | 124000 | 1582000 | 1703000 | 12 | 17.5378 | 53.1 | 49 | 0 | 3732
0.08385 | 7 | 0.115 | 14 | 0.8 | 98000 | 1406000 | 1501000 | 12 | 17.1194 | 53.1 | 49 | 0 | 2940
0.08385 | 7 | 0.115 | 14 | 0.7 | 78000 | 1231000 | 1306000 | 12 | 16.7142 | 53.1 | 49 | 0 | 2345
0.08385 | 7 | 0.115 | 14 | 0.6 | 61000 | 1055000 | 1114000 | 12 | 16.315 | 53.1 | 49 | 0 | 1840
0.08385 | 7 | 0.115 | 14 | 0.5 | 49000 | 879000 | 927000 | 12 | 15.9256 | 53.1 | 49 | 0 | 1481
0.08385 | 7 | 0.115 | 14 | 0.4 | 41000 | 703000 | 743000 | 12 | 15.5437 | 53.1 | 49 | 0 | 1232
0.08385 | 7 | 0.115 | 14 | 0.3 | 34000 | 527000 | 560000 | 12 | 15.1644 | 53.1 | 49 | 0 | 1022
0.08385 | 7 | 0.115 | 14 | 0.2 | 28000 | 352000 | 379000 | 12 | 14.7864 | 53.1 | 49 | 0 | 833
0.08385 | 7 | 0.115 | 14 | 0.15 | 25000 | 264000 | 288000 | 12 | 14.5979 | 53.1 | 49 | 0 | 745
0.08385 | 7 | 0.115 | 13.5 | 1 | 170000 | 1758000 | 1923000 | 12 | 17.4945 | 53.1 | 49 | 0 | 5106
0.08385 | 7 | 0.115 | 13.5 | 0.9 | 123000 | 1582000 | 1702000 | 12 | 17.0345 | 53.1 | 49 | 0 | 3694
0.08385 | 7 | 0.115 | 13.5 | 0.8 | 96000 | 1406000 | 1499000 | 12 | 16.6138 | 53.1 | 49 | 0 | 2866
0.08385 | 7 | 0.115 | 13.5 | 0.7 | 76000 | 1231000 | 1304000 | 12 | 16.2089 | 53.1 | 49 | 0 | 2275
0.08385 | 7 | 0.115 | 13.5 | 0.6 | 59000 | 1055000 | 1112000 | 12 | 15.81 | 53.1 | 49 | 0 | 1773
0.08385 | 7 | 0.115 | 13.5 | 0.5 | 48000 | 879000 | 926000 | 12 | 15.4227 | 53.1 | 49 | 0 | 1443
0.08385 | 7 | 0.115 | 13.5 | 0.4 | 40000 | 703000 | 742000 | 12 | 15.0419 | 53.1 | 49 | 0 | 1210
0.08385 | 7 | 0.115 | 13.5 | 0.3 | 33000 | 527000 | 560000 | 12 | 14.6627 | 53.1 | 49 | 0 | 1001
0.08385 | 7 | 0.115 | 13.5 | 0.2 | 27000 | 352000 | 378000 | 12 | 14.285 | 53.1 | 49 | 0 | 814
0.08385 | 7 | 0.115 | 13.5 | 0.15 | 24000 | 264000 | 287000 | 12 | 14.0967 | 53.1 | 49 | 0 | 729
0.08385 | 7 | 0.115 | 13 | 1 | 172000 | 1758000 | 1924000 | 12 | 16.9963 | 53.1 | 49 | 0 | 5145
0.08385 | 7 | 0.115 | 13 | 0.9 | 122000 | 1582000 | 1700000 | 12 | 16.5313 | 53.1 | 49 | 0 | 3657
0.08385 | 7 | 0.115 | 13 | 0.8 | 93000 | 1406000 | 1497000 | 12 | 16.1085 | 53.1 | 49 | 0 | 2798
0.08385 | 7 | 0.115 | 13 | 0.7 | 73000 | 1231000 | 1302000 | 12 | 15.7036 | 53.1 | 49 | 0 | 2204
0.08385 | 7 | 0.115 | 13 | 0.6 | 58000 | 1055000 | 1111000 | 12 | 15.3074 | 53.1 | 49 | 0 | 1742
0.08385 | 7 | 0.115 | 13 | 0.5 | 47000 | 879000 | 925000 | 12 | 14.9201 | 53.1 | 49 | 0 | 1410
0.08385 | 7 | 0.115 | 13 | 0.4 | 39000 | 703000 | 741000 | 12 | 14.5396 | 53.1 | 49 | 0 | 1181
0.08385 | 7 | 0.115 | 13 | 0.3 | 33000 | 527000 | 559000 | 12 | 14.161 | 53.1 | 49 | 0 | 979
0.08385 | 7 | 0.115 | 13 | 0.2 | 27000 | 352000 | 377000 | 12 | 13.7837 | 53.1 | 49 | 0 | 798
0.08385 | 7 | 0.115 | 13 | 0.15 | 24000 | 264000 | 287000 | 12 | 13.5957 | 53.1 | 49 | 0 | 715
0.08385 | 7 | 0.115 | 12.5 | 1 | 170000 | 1758000 | 1923000 | 12 | 16.4924 | 53.1 | 49 | 0 | 5101
0.08385 | 7 | 0.115 | 12.5 | 0.9 | 127000 | 1582000 | 1705000 | 12 | 16.0401 | 53.1 | 49 | 0 | 3800
0.08385 | 7 | 0.115 | 12.5 | 0.8 | 91000 | 1406000 | 1495000 | 12 | 15.6036 | 53.1 | 49 | 0 | 2734
0.08385 | 7 | 0.115 | 12.5 | 0.7 | 71000 | 1231000 | 1300000 | 12 | 15.1984 | 53.1 | 49 | 0 | 2135
0.08385 | 7 | 0.115 | 12.5 | 0.6 | 56000 | 1055000 | 1109000 | 12 | 14.803 | 53.1 | 49 | 0 | 1683
0.08385 | 7 | 0.115 | 12.5 | 0.5 | 46000 | 879000 | 924000 | 12 | 14.4176 | 53.1 | 49 | 0 | 1380
0.08385 | 7 | 0.115 | 12.5 | 0.4 | 39000 | 703000 | 741000 | 12 | 14.0381 | 53.1 | 49 | 0 | 1164
0.08385 | 7 | 0.115 | 12.5 | 0.3 | 32000 | 527000 | 558000 | 12 | 13.6595 | 53.1 | 49 | 0 | 961
0.08385 | 7 | 0.115 | 12.5 | 0.2 | 26000 | 352000 | 377000 | 12 | 13.2826 | 53.1 | 49 | 0 | 783
0.08385 | 7 | 0.115 | 12.5 | 0.15 | 23000 | 264000 | 286000 | 12 | 13.0946 | 53.1 | 49 | 0 | 702
0.08385 | 7 | 0.115 | 12 | 1 | 0 | 1758000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 12 | 0.9 | 0 | 1582000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 12 | 0.8 | 89000 | 1406000 | 1493000 | 12 | 15.0992 | 53.1 | 49 | 0 | 2679
0.08385 | 7 | 0.115 | 12 | 0.7 | 69000 | 1231000 | 1297000 | 12 | 14.6933 | 53.1 | 49 | 0 | 2068
0.08385 | 7 | 0.115 | 12 | 0.6 | 55000 | 1055000 | 1108000 | 12 | 14.2995 | 53.1 | 49 | 0 | 1638
0.08385 | 7 | 0.115 | 12 | 0.5 | 45000 | 879000 | 923000 | 12 | 13.9162 | 53.1 | 49 | 0 | 1364
0.08385 | 7 | 0.115 | 12 | 0.4 | 38000 | 703000 | 740000 | 12 | 13.5367 | 53.1 | 49 | 0 | 1148
0.08385 | 7 | 0.115 | 12 | 0.3 | 31000 | 527000 | 558000 | 12 | 13.1582 | 53.1 | 49 | 0 | 945
0.08385 | 7 | 0.115 | 12 | 0.2 | 26000 | 352000 | 376000 | 12 | 12.7815 | 53.1 | 49 | 0 | 770
0.08385 | 7 | 0.115 | 12 | 0.15 | 23000 | 264000 | 286000 | 12 | 12.5937 | 53.1 | 49 | 0 | 690
0.08385 | 7 | 0.115 | 11.5 | 1 | 0 | 1758000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 11.5 | 0.9 | 0 | 1582000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 11.5 | 0.8 | 0 | 1406000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 11.5 | 0.7 | 0 | 1231000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 11.5 | 0.6 | 54000 | 1055000 | 1107000 | 12 | 13.7968 | 53.1 | 49 | 0 | 1605
0.08385 | 7 | 0.115 | 11.5 | 0.5 | 45000 | 879000 | 922000 | 12 | 13.4143 | 53.1 | 49 | 0 | 1342
0.08385 | 7 | 0.115 | 11.5 | 0.4 | 37000 | 703000 | 739000 | 12 | 13.0346 | 53.1 | 49 | 0 | 1121
0.08385 | 7 | 0.115 | 11.5 | 0.3 | 31000 | 527000 | 557000 | 12 | 12.6569 | 53.1 | 49 | 0 | 929
0.08385 | 7 | 0.115 | 11.5 | 0.2 | 25000 | 352000 | 376000 | 12 | 12.2805 | 53.1 | 49 | 0 | 757
0.08385 | 7 | 0.115 | 11.5 | 0.15 | 23000 | 264000 | 286000 | 12 | 12.0928 | 53.1 | 49 | 0 | 679
0.08385 | 7 | 0.115 | 11 | 1 | 0 | 1758000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 11 | 0.9 | 0 | 1582000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 11 | 0.8 | 0 | 1406000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 11 | 0.7 | 0 | 1231000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 11 | 0.6 | 0 | 1055000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 11 | 0.5 | 0 | 879000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 11 | 0.4 | 37000 | 703000 | 739000 | 12 | 12.5331 | 53.1 | 49 | 0 | 1104
0.08385 | 7 | 0.115 | 11 | 0.3 | 31000 | 527000 | 557000 | 12 | 12.1557 | 53.1 | 49 | 0 | 915
0.08385 | 7 | 0.115 | 11 | 0.2 | 25000 | 352000 | 376000 | 12 | 11.7795 | 53.1 | 49 | 0 | 745
0.08385 | 7 | 0.115 | 11 | 0.15 | 22000 | 264000 | 285000 | 12 | 11.592 | 53.1 | 49 | 0 | 669
0.08385 | 7 | 0.115 | 10.5 | 1 | 0 | 1758000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 10.5 | 0.9 | 0 | 1582000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 10.5 | 0.8 | 0 | 1406000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 10.5 | 0.7 | 0 | 1231000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 10.5 | 0.6 | 0 | 1055000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 10.5 | 0.5 | 0 | 879000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 10.5 | 0.4 | 0 | 703000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 10.5 | 0.3 | 0 | 527000 | 0 | 12 | 0 | 53.1 | 49 | 0 | 0
0.08385 | 7 | 0.115 | 10.5 | 0.2 | 24000 | 352000 | 375000 | 12 | 11.2786 | 53.1 | 49 | 0 | 734
0.08385 | 7 | 0.115 | 10.5 | 0.15 | 22000 | 264000 | 285000 | 12 | 11.0912 | 53.1 | 49 | 0 | 659
0.05856 | 5 | 0.00115 | 30 | 1 | 301000 | 1758000 | 2050000 | 12 | 458.4511 | 28.3 | 49 | 0 | 9039
0.05856 | 5 | 0.00115 | 30 | 0.9 | 262000 | 1582000 | 1837000 | 12 | 413.7933 | 28.3 | 49 | 0 | 7866
0.05856 | 5 | 0.00115 | 30 | 0.8 | 226000 | 1406000 | 1626000 | 12 | 369.7884 | 28.3 | 49 | 0 | 6791
0.05856 | 5 | 0.00115 | 30 | 0.7 | 196000 | 1231000 | 1420000 | 12 | 326.8486 | 28.3 | 49 | 0 | 5873
0.05856 | 5 | 0.00115 | 30 | 0.6 | 170000 | 1055000 | 1219000 | 12 | 284.8413 | 28.3 | 49 | 0 | 5093
0.05856 | 5 | 0.00115 | 30 | 0.5 | 150000 | 879000 | 1024000 | 12 | 244.0022 | 28.3 | 49 | 0 | 4486
0.05856 | 5 | 0.00115 | 30 | 0.4 | 125000 | 703000 | 824000 | 12 | 202.2027 | 28.3 | 49 | 0 | 3737
0.05856 | 5 | 0.00115 | 30 | 0.3 | 103000 | 527000 | 628000 | 12 | 161.1389 | 28.3 | 49 | 0 | 3097
0.05856 | 5 | 0.00115 | 30 | 0.2 | 82000 | 352000 | 431000 | 12 | 120.0428 | 28.3 | 49 | 0 | 2452
0.05856 | 5 | 0.00115 | 30 | 0.15 | 70000 | 264000 | 332000 | 12 | 99.3687 | 28.3 | 49 | 0 | 2111
0.05856 | 5 | 0.00115 | 27 | 1 | 271000 | 1758000 | 2020000 | 12 | 448.7854 | 28.3 | 49 | 0 | 8116
0.05856 | 5 | 0.00115 | 27 | 0.9 | 234000 | 1582000 | 1810000 | 12 | 404.752 | 28.3 | 49 | 0 | 7030
0.05856 | 5 | 0.00115 | 27 | 0.8 | 201000 | 1406000 | 1601000 | 12 | 361.2388 | 28.3 | 49 | 0 | 6021
0.05856 | 5 | 0.00115 | 27 | 0.7 | 172000 | 1231000 | 1397000 | 12 | 318.7284 | 28.3 | 49 | 0 | 5160
0.05856 | 5 | 0.00115 | 27 | 0.6 | 147000 | 1055000 | 1197000 | 12 | 276.9821 | 28.3 | 49 | 0 | 4412
0.05856 | 5 | 0.00115 | 27 | 0.5 | 126000 | 879000 | 1002000 | 12 | 236.0817 | 28.3 | 49 | 0 | 3790
0.05856 | 5 | 0.00115 | 27 | 0.4 | 107000 | 703000 | 807000 | 12 | 195.4674 | 28.3 | 49 | 0 | 3210
0.05856 | 5 | 0.00115 | 27 | 0.3 | 88000 | 527000 | 613000 | 12 | 155.0162 | 28.3 | 49 | 0 | 2654
0.05856 | 5 | 0.00115 | 27 | 0.2 | 70000 | 352000 | 420000 | 12 | 114.6 | 28.3 | 49 | 0 | 2104
0.05856 | 5 | 0.00115 | 27 | 0.15 | 60000 | 264000 | 322000 | 12 | 94.2807 | 28.3 | 49 | 0 | 1812
0.05856 | 5 | 0.00115 | 24 | 1 | 242000 | 1758000 | 1993000 | 12 | 439.5751 | 28.3 | 49 | 0 | 7260
0.05856 | 5 | 0.00115 | 24 | 0.9 | 207000 | 1582000 | 1783000 | 12 | 395.8546 | 28.3 | 49 | 0 | 6214
0.05856 | 5 | 0.00115 | 24 | 0.8 | 177000 | 1406000 | 1579000 | 12 | 353.1889 | 28.3 | 49 | 0 | 5323
0.05856 | 5 | 0.00115 | 24 | 0.7 | 150000 | 1231000 | 1376000 | 12 | 310.9723 | 28.3 | 49 | 0 | 4499
0.05856 | 5 | 0.00115 | 24 | 0.6 | 127000 | 1055000 | 1178000 | 12 | 269.6631 | 28.3 | 49 | 0 | 3810
0.05856 | 5 | 0.00115 | 24 | 0.5 | 107000 | 879000 | 983000 | 12 | 228.9644 | 28.3 | 49 | 0 | 3212
0.05856 | 5 | 0.00115 | 24 | 0.4 | 93000 | 703000 | 793000 | 12 | 189.4211 | 28.3 | 49 | 0 | 2784
0.05856 | 5 | 0.00115 | 24 | 0.3 | 75000 | 527000 | 600000 | 12 | 149.2025 | 28.3 | 49 | 0 | 2257
0.05856 | 5 | 0.00115 | 24 | 0.2 | 60000 | 352000 | 410000 | 12 | 109.3991 | 28.3 | 49 | 0 | 1791
0.05856 | 5 | 0.00115 | 24 | 0.15 | 52000 | 264000 | 314000 | 12 | 89.4317 | 28.3 | 49 | 0 | 1548
0.05856 | 5 | 0.00115 | 21 | 1 | 216000 | 1758000 | 1967000 | 12 | 430.7771 | 28.3 | 49 | 0 | 6466
0.05856 | 5 | 0.00115 | 21 | 0.9 | 183000 | 1582000 | 1760000 | 12 | 387.6769 | 28.3 | 49 | 0 | 5504
0.05856 | 5 | 0.00115 | 21 | 0.8 | 155000 | 1406000 | 1556000 | 12 | 345.2422 | 28.3 | 49 | 0 | 4641
0.05856 | 5 | 0.00115 | 21 | 0.7 | 130000 | 1231000 | 1357000 | 12 | 303.62 | 28.3 | 49 | 0 | 3899
0.05856 | 5 | 0.00115 | 21 | 0.6 | 108000 | 1055000 | 1160000 | 12 | 262.5657 | 28.3 | 49 | 0 | 3241
0.05856 | 5 | 0.00115 | 21 | 0.5 | 90000 | 879000 | 966000 | 12 | 222.3346 | 28.3 | 49 | 0 | 2705
0.05856 | 5 | 0.00115 | 21 | 0.4 | 75000 | 703000 | 776000 | 12 | 182.5528 | 28.3 | 49 | 0 | 2236
0.05856 | 5 | 0.00115 | 21 | 0.3 | 64000 | 527000 | 590000 | 12 | 143.8884 | 28.3 | 49 | 0 | 1933
0.05856 | 5 | 0.00115 | 21 | 0.2 | 50000 | 352000 | 400000 | 12 | 104.3102 | 28.3 | 49 | 0 | 1494
0.05856 | 5 | 0.00115 | 21 | 0.15 | 43000 | 264000 | 306000 | 12 | 84.6651 | 28.3 | 49 | 0 | 1296
0.05856 | 5 | 0.00115 | 18 | 1 | 194000 | 1758000 | 1946000 | 12 | 422.9719 | 28.3 | 49 | 0 | 5819
0.05856 | 5 | 0.00115 | 18 | 0.9 | 161000 | 1582000 | 1739000 | 12 | 379.765 | 28.3 | 49 | 0 | 4835
0.05856 | 5 | 0.00115 | 18 | 0.8 | 134000 | 1406000 | 1537000 | 12 | 337.7424 | 28.3 | 49 | 0 | 4026
0.05856 | 5 | 0.00115 | 18 | 0.7 | 111000 | 1231000 | 1339000 | 12 | 296.552 | 28.3 | 49 | 0 | 3341
0.05856 | 5 | 0.00115 | 18 | 0.6 | 91000 | 1055000 | 1143000 | 12 | 255.8612 | 28.3 | 49 | 0 | 2730
0.05856 | 5 | 0.00115 | 18 | 0.5 | 75000 | 879000 | 952000 | 12 | 216.0349 | 28.3 | 49 | 0 | 2248
0.05856 | 5 | 0.00115 | 18 | 0.4 | 61000 | 703000 | 763000 | 12 | 176.7238 | 28.3 | 49 | 0 | 1842
0.05856 | 5 | 0.00115 | 18 | 0.3 | 53000 | 527000 | 578000 | 12 | 138.3486 | 28.3 | 49 | 0 | 1576
0.05856 | 5 | 0.00115 | 18 | 0.2 | 41000 | 352000 | 391000 | 12 | 99.3892 | 28.3 | 49 | 0 | 1223
0.05856 | 5 | 0.00115 | 18 | 0.15 | 36000 | 264000 | 298000 | 12 | 80.0501 | 28.3 | 49 | 0 | 1067
0.05856 | 5 | 0.00115 | 17.5 | 1 | 190000 | 1758000 | 1943000 | 12 | 421.6861 | 28.3 | 49 | 0 | 5714
0.05856 | 5 | 0.00115 | 17.5 | 0.9 | 158000 | 1582000 | 1735000 | 12 | 378.5082 | 28.3 | 49 | 0 | 4732
0.05856 | 5 | 0.00115 | 17.5 | 0.8 | 131000 | 1406000 | 1534000 | 12 | 336.5502 | 28.3 | 49 | 0 | 3932
0.05856 | 5 | 0.00115 | 17.5 | 0.7 | 108000 | 1231000 | 1336000 | 12 | 295.4046 | 28.3 | 49 | 0 | 3253
0.05856 | 5 | 0.00115 | 17.5 | 0.6 | 88000 | 1055000 | 1140000 | 12 | 254.7772 | 28.3 | 49 | 0 | 2650
0.05856 | 5 | 0.00115 | 17.5 | 0.5 | 73000 | 879000 | 949000 | 12 | 215.0225 | 28.3 | 49 | 0 | 2178
0.05856 | 5 | 0.00115 | 17.5 | 0.4 | 59000 | 703000 | 761000 | 12 | 175.7751 | 28.3 | 49 | 0 | 1780
0.05856 | 5 | 0.00115 | 17.5 | 0.3 | 51000 | 527000 | 577000 | 12 | 137.4487 | 28.3 | 49 | 0 | 1520
0.05856 | 5 | 0.00115 | 17.5 | 0.2 | 39000 | 352000 | 390000 | 12 | 98.5884 | 28.3 | 49 | 0 | 1180
0.05856 | 5 | 0.00115 | 17.5 | 0.15 | 34000 | 264000 | 297000 | 12 | 79.2834 | 28.3 | 49 | 0 | 1029
0.05856 | 5 | 0.00115 | 17 | 1 | 187000 | 1758000 | 1939000 | 12 | 420.3327 | 28.3 | 49 | 0 | 5599
0.05856 | 5 | 0.00115 | 17 | 0.9 | 154000 | 1582000 | 1732000 | 12 | 377.2249 | 28.3 | 49 | 0 | 4626
0.05856 | 5 | 0.00115 | 17 | 0.8 | 128000 | 1406000 | 1531000 | 12 | 335.3628 | 28.3 | 49 | 0 | 3839
0.05856 | 5 | 0.00115 | 17 | 0.7 | 105000 | 1231000 | 1333000 | 12 | 294.251 | 28.3 | 49 | 0 | 3163
0.05856 | 5 | 0.00115 | 17 | 0.6 | 86000 | 1055000 | 1138000 | 12 | 253.6955 | 28.3 | 49 | 0 | 2571
0.05856 | 5 | 0.00115 | 17 | 0.5 | 70000 | 879000 | 947000 | 12 | 214.0046 | 28.3 | 49 | 0 | 2106
0.05856 | 5 | 0.00115 | 17 | 0.4 | 57000 | 703000 | 759000 | 12 | 174.844 | 28.3 | 49 | 0 | 1721
0.05856 | 5 | 0.00115 | 17 | 0.3 | 46000 | 527000 | 572000 | 12 | 136.0052 | 28.3 | 49 | 0 | 1383
0.05856 | 5 | 0.00115 | 17 | 0.2 | 38000 | 352000 | 388000 | 12 | 97.7925 | 28.3 | 49 | 0 | 1138
0.05856 | 5 | 0.00115 | 17 | 0.15 | 33000 | 264000 | 296000 | 12 | 78.5443 | 28.3 | 49 | 0 | 995
0.05856 | 5 | 0.00115 | 16.5 | 1 | 183000 | 1758000 | 1935000 | 12 | 419.0095 | 28.3 | 49 | 0 | 5488
0.05856 | 5 | 0.00115 | 16.5 | 0.9 | 151000 | 1582000 | 1729000 | 12 | 376.0014 | 28.3 | 49 | 0 | 4529
0.05856 | 5 | 0.00115 | 16.5 | 0.8 | 125000 | 1406000 | 1528000 | 12 | 334.1815 | 28.3 | 49 | 0 | 3747
0.05856 | 5 | 0.00115 | 16.5 | 0.7 | 103000 | 1231000 | 1330000 | 12 | 293.1118 | 28.3 | 49 | 0 | 3077
0.05856 | 5 | 0.00115 | 16.5 | 0.6 | 83000 | 1055000 | 1136000 | 12 | 252.698 | 28.3 | 49 | 0 | 2503
0.05856 | 5 | 0.00115 | 16.5 | 0.5 | 68000 | 879000 | 945000 | 12 | 213.0064 | 28.3 | 49 | 0 | 2038
0.05856 | 5 | 0.00115 | 16.5 | 0.4 | 55000 | 703000 | 757000 | 12 | 173.9123 | 28.3 | 49 | 0 | 1661
0.05856 | 5 | 0.00115 | 16.5 | 0.3 | 44000 | 527000 | 571000 | 12 | 135.1526 | 28.3 | 49 | 0 | 1334
0.05856 | 5 | 0.00115 | 16.5 | 0.2 | 37000 | 352000 | 387000 | 12 | 97.0019 | 28.3 | 49 | 0 | 1098
0.05856 | 5 | 0.00115 | 16.5 | 0.15 | 32000 | 264000 | 295000 | 12 | 77.785 | 28.3 | 49 | 0 | 958
0.05856 | 5 | 0.00115 | 16 | 1 | 180000 | 1758000 | 1932000 | 12 | 417.7923 | 28.3 | 49 | 0 | 5393
0.05856 | 5 | 0.00115 | 16 | 0.9 | 148000 | 1582000 | 1725000 | 12 | 374.7764 | 28.3 | 49 | 0 | 4432
0.05856 | 5 | 0.00115 | 16 | 0.8 | 122000 | 1406000 | 1525000 | 12 | 333.0288 | 28.3 | 49 | 0 | 3659
0.05856 | 5 | 0.00115 | 16 | 0.7 | 100000 | 1231000 | 1327000 | 12 | 291.9872 | 28.3 | 49 | 0 | 2992
0.05856 | 5 | 0.00115 | 16 | 0.6 | 81000 | 1055000 | 1133000 | 12 | 251.635 | 28.3 | 49 | 0 | 2427
0.05856 | 5 | 0.00115 | 16 | 0.5 | 66000 | 879000 | 943000 | 12 | 212.0071 | 28.3 | 49 | 0 | 1969
0.05856 | 5 | 0.00115 | 16 | 0.4 | 53000 | 703000 | 755000 | 12 | 172.9908 | 28.3 | 49 | 0 | 1603
0.05856 | 5 | 0.00115 | 16 | 0.3 | 43000 | 527000 | 569000 | 12 | 134.3083 | 28.3 | 49 | 0 | 1286
0.05856 | 5 | 0.00115 | 16 | 0.2 | 37000 | 352000 | 387000 | 12 | 96.5021 | 28.3 | 49 | 0 | 1100
0.05856 | 5 | 0.00115 | 16 | 0.15 | 31000 | 264000 | 294000 | 12 | 77.0426 | 28.3 | 49 | 0 | 924
0.05856 | 5 | 0.00115 | 15.5 | 1 | 177000 | 1758000 | 1930000 | 12 | 416.6499 | 28.3 | 49 | 0 | 5310
0.05856 | 5 | 0.00115 | 15.5 | 0.9 | 145000 | 1582000 | 1723000 | 12 | 373.605 | 28.3 | 49 | 0 | 4343
0.05856 | 5 | 0.00115 | 15.5 | 0.8 | 119000 | 1406000 | 1522000 | 12 | 331.8822 | 28.3 | 49 | 0 | 3573
0.05856 | 5 | 0.00115 | 15.5 | 0.7 | 97000 | 1231000 | 1325000 | 12 | 290.8774 | 28.3 | 49 | 0 | 2909
0.05856 | 5 | 0.00115 | 15.5 | 0.6 | 78000 | 1055000 | 1131000 | 12 | 250.5906 | 28.3 | 49 | 0 | 2353
0.05856 | 5 | 0.00115 | 15.5 | 0.5 | 63000 | 879000 | 941000 | 12 | 211.0283 | 28.3 | 49 | 0 | 1904
0.05856 | 5 | 0.00115 | 15.5 | 0.4 | 52000 | 703000 | 753000 | 12 | 172.0802 | 28.3 | 49 | 0 | 1547
0.05856 | 5 | 0.00115 | 15.5 | 0.3 | 44000 | 527000 | 570000 | 12 | 133.9348 | 28.3 | 49 | 0 | 1309
0.05856 | 5 | 0.00115 | 15.5 | 0.2 | 35000 | 352000 | 386000 | 12 | 95.7006 | 28.3 | 49 | 0 | 1058
0.05856 | 5 | 0.00115 | 15.5 | 0.15 | 30000 | 264000 | 292000 | 12 | 76.3026 | 28.3 | 49 | 0 | 890
0.05856 | 5 | 0.00115 | 15 | 1 | 175000 | 1758000 | 1927000 | 12 | 415.5833 | 28.3 | 49 | 0 | 5237
0.05856 | 5 | 0.00115 | 15 | 0.9 | 142000 | 1582000 | 1720000 | 12 | 372.4567 | 28.3 | 49 | 0 | 4257
0.05856 | 5 | 0.00115 | 15 | 0.8 | 116000 | 1406000 | 1519000 | 12 | 330.7428 | 28.3 | 49 | 0 | 3487
0.05856 | 5 | 0.00115 | 15 | 0.7 | 94000 | 1231000 | 1322000 | 12 | 289.7677 | 28.3 | 49 | 0 | 2827
0.05856 | 5 | 0.00115 | 15 | 0.6 | 76000 | 1055000 | 1129000 | 12 | 249.5532 | 28.3 | 49 | 0 | 2280
0.05856 | 5 | 0.00115 | 15 | 0.5 | 61000 | 879000 | 938000 | 12 | 210.0429 | 28.3 | 49 | 0 | 1838
0.05856 | 5 | 0.00115 | 15 | 0.4 | 50000 | 703000 | 751000 | 12 | 171.1669 | 28.3 | 49 | 0 | 1490
0.05856 | 5 | 0.00115 | 15 | 0.3 | 42000 | 527000 | 568000 | 12 | 133.0148 | 28.3 | 49 | 0 | 1250
0.05856 | 5 | 0.00115 | 15 | 0.2 | 34000 | 352000 | 384000 | 12 | 94.8348 | 28.3 | 49 | 0 | 1006
0.05856 | 5 | 0.00115 | 15 | 0.15 | 29000 | 264000 | 291000 | 12 | 75.5611 | 28.3 | 49 | 0 | 856
0.05856 | 5 | 0.00115 | 14.5 | 1 | 173000 | 1758000 | 1925000 | 12 | 414.5868 | 28.3 | 49 | 0 | 5176
0.05856 | 5 | 0.00115 | 14.5 | 0.9 | 139000 | 1582000 | 1717000 | 12 | 371.3054 | 28.3 | 49 | 0 | 4171
0.05856 | 5 | 0.00115 | 14.5 | 0.8 | 113000 | 1406000 | 1516000 | 12 | 329.6112 | 28.3 | 49 | 0 | 3403
0.05856 | 5 | 0.00115 | 14.5 | 0.7 | 92000 | 1231000 | 1319000 | 12 | 288.6882 | 28.3 | 49 | 0 | 2749
0.05856 | 5 | 0.00115 | 14.5 | 0.6 | 74000 | 1055000 | 1126000 | 12 | 248.5138 | 28.3 | 49 | 0 | 2207
0.05856 | 5 | 0.00115 | 14.5 | 0.5 | 59000 | 879000 | 936000 | 12 | 209.0711 | 28.3 | 49 | 0 | 1773
0.05856 | 5 | 0.00115 | 14.5 | 0.4 | 49000 | 703000 | 750000 | 12 | 170.4069 | 28.3 | 49 | 0 | 1456
0.05856 | 5 | 0.00115 | 14.5 | 0.3 | 40000 | 527000 | 566000 | 12 | 132.0926 | 28.3 | 49 | 0 | 1191
0.05856 | 5 | 0.00115 | 14.5 | 0.2 | 32000 | 352000 | 383000 | 12 | 94.0406 | 28.3 | 49 | 0 | 964
0.05856 | 5 | 0.00115 | 14.5 | 0.15 | 28000 | 264000 | 290000 | 12 | 74.8614 | 28.3 | 49 | 0 | 828
0.05856 | 5 | 0.00115 | 14 | 1 | 171000 | 1758000 | 1924000 | 12 | 413.6659 | 28.3 | 49 | 0 | 5125
0.05856 | 5 | 0.00115 | 14 | 0.9 | 136000 | 1582000 | 1714000 | 12 | 370.1763 | 28.3 | 49 | 0 | 4088
0.05856 | 5 | 0.00115 | 14 | 0.8 | 111000 | 1406000 | 1514000 | 12 | 328.4884 | 28.3 | 49 | 0 | 3320
0.05856 | 5 | 0.00115 | 14 | 0.7 | 89000 | 1231000 | 1317000 | 12 | 287.6231 | 28.3 | 49 | 0 | 2673
0.05856 | 5 | 0.00115 | 14 | 0.6 | 71000 | 1055000 | 1124000 | 12 | 247.4948 | 28.3 | 49 | 0 | 2137
0.05856 | 5 | 0.00115 | 14 | 0.5 | 57000 | 879000 | 934000 | 12 | 208.0984 | 28.3 | 49 | 0 | 1709
0.05856 | 5 | 0.00115 | 14 | 0.4 | 47000 | 703000 | 748000 | 12 | 169.467 | 28.3 | 49 | 0 | 1395
0.05856 | 5 | 0.00115 | 14 | 0.3 | 38000 | 527000 | 564000 | 12 | 131.2559 | 28.3 | 49 | 0 | 1144
0.05856 | 5 | 0.00115 | 14 | 0.2 | 31000 | 352000 | 382000 | 12 | 93.2901 | 28.3 | 49 | 0 | 929
0.05856 | 5 | 0.00115 | 14 | 0.15 | 28000 | 264000 | 291000 | 12 | 74.3693 | 28.3 | 49 | 0 | 831
0.05856 | 5 | 0.00115 | 13.5 | 1 | 180000 | 1758000 | 1933000 | 12 | 414.951 | 28.3 | 49 | 0 | 5404
0.05856 | 5 | 0.00115 | 13.5 | 0.9 | 134000 | 1582000 | 1712000 | 12 | 369.0907 | 28.3 | 49 | 0 | 4012
0.05856 | 5 | 0.00115 | 13.5 | 0.8 | 108000 | 1406000 | 1511000 | 12 | 327.3747 | 28.3 | 49 | 0 | 3238
0.05856 | 5 | 0.00115 | 13.5 | 0.7 | 87000 | 1231000 | 1315000 | 12 | 286.5602 | 28.3 | 49 | 0 | 2598
0.05856 | 5 | 0.00115 | 13.5 | 0.6 | 69000 | 1055000 | 1122000 | 12 | 246.477 | 28.3 | 49 | 0 | 2067
0.05856 | 5 | 0.00115 | 13.5 | 0.5 | 55000 | 879000 | 932000 | 12 | 207.1349 | 28.3 | 49 | 0 | 1646
0.05856 | 5 | 0.00115 | 13.5 | 0.4 | 45000 | 703000 | 747000 | 12 | 168.5767 | 28.3 | 49 | 0 | 1342
0.05856 | 5 | 0.00115 | 13.5 | 0.3 | 37000 | 527000 | 563000 | 12 | 130.4787 | 28.3 | 49 | 0 | 1106
0.05856 | 5 | 0.00115 | 13.5 | 0.2 | 30000 | 352000 | 381000 | 12 | 92.5815 | 28.3 | 49 | 0 | 901
0.05856 | 5 | 0.00115 | 13.5 | 0.15 | 27000 | 264000 | 290000 | 12 | 73.6877 | 28.3 | 49 | 0 | 806
0.05856 | 5 | 0.00115 | 13 | 1 | 180000 | 1758000 | 1933000 | 12 | 414.4325 | 28.3 | 49 | 0 | 5414
0.05856 | 5 | 0.00115 | 13 | 0.9 | 132000 | 1582000 | 1710000 | 12 | 368.067 | 28.3 | 49 | 0 | 3946
0.05856 | 5 | 0.00115 | 13 | 0.8 | 105000 | 1406000 | 1509000 | 12 | 326.2707 | 28.3 | 49 | 0 | 3158
0.05856 | 5 | 0.00115 | 13 | 0.7 | 84000 | 1231000 | 1312000 | 12 | 285.5244 | 28.3 | 49 | 0 | 2527
0.05856 | 5 | 0.00115 | 13 | 0.6 | 67000 | 1055000 | 1119000 | 12 | 245.463 | 28.3 | 49 | 0 | 1998
0.05856 | 5 | 0.00115 | 13 | 0.5 | 53000 | 879000 | 930000 | 12 | 206.1946 | 28.3 | 49 | 0 | 1587
0.05856 | 5 | 0.00115 | 13 | 0.4 | 43000 | 703000 | 745000 | 12 | 167.7874 | 28.3 | 49 | 0 | 1304
0.05856 | 5 | 0.00115 | 13 | 0.3 | 36000 | 527000 | 562000 | 12 | 129.7516 | 28.3 | 49 | 0 | 1076
0.05856 | 5 | 0.00115 | 13 | 0.2 | 29000 | 352000 | 380000 | 12 | 91.8989 | 28.3 | 49 | 0 | 876
0.05856 | 5 | 0.00115 | 13 | 0.15 | 26000 | 264000 | 289000 | 12 | 73.0268 | 28.3 | 49 | 0 | 784
0.05856 | 5 | 0.00115 | 12.5 | 1 | 181000 | 1758000 | 1934000 | 12 | 413.9467 | 28.3 | 49 | 0 | 5429
0.05856 | 5 | 0.00115 | 12.5 | 0.9 | 129000 | 1582000 | 1708000 | 12 | 367.0571 | 28.3 | 49 | 0 | 3881
0.05856 | 5 | 0.00115 | 12.5 | 0.8 | 103000 | 1406000 | 1506000 | 12 | 325.1919 | 28.3 | 49 | 0 | 3082
0.05856 | 5 | 0.00115 | 12.5 | 0.7 | 82000 | 1231000 | 1310000 | 12 | 284.4805 | 28.3 | 49 | 0 | 2455
0.05856 | 5 | 0.00115 | 12.5 | 0.6 | 64000 | 1055000 | 1117000 | 12 | 244.4627 | 28.3 | 49 | 0 | 1931
0.05856 | 5 | 0.00115 | 12.5 | 0.5 | 51000 | 879000 | 928000 | 12 | 205.2578 | 28.3 | 49 | 0 | 1528
0.05856 | 5 | 0.00115 | 12.5 | 0.4 | 42000 | 703000 | 744000 | 12 | 166.9967 | 28.3 | 49 | 0 | 1266
0.05856 | 5 | 0.00115 | 12.5 | 0.3 | 35000 | 527000 | 561000 | 12 | 129.0537 | 28.3 | 49 | 0 | 1051
0.05856 | 5 | 0.00115 | 12.5 | 0.2 | 28000 | 352000 | 379000 | 12 | 91.2342 | 28.3 | 49 | 0 | 854
0.05856 | 5 | 0.00115 | 12.5 | 0.15 | 26000 | 264000 | 288000 | 12 | 72.3866 | 28.3 | 49 | 0 | 765
0.05856 | 5 | 0.00115 | 12 | 1 | 180000 | 1758000 | 1933000 | 12 | 413.2614 | 28.3 | 49 | 0 | 5414
0.05856 | 5 | 0.00115 | 12 | 0.9 | 127000 | 1582000 | 1706000 | 12 | 366.0808 | 28.3 | 49 | 0 | 3822
0.05856 | 5 | 0.00115 | 12 | 0.8 | 100000 | 1406000 | 1504000 | 12 | 324.1221 | 28.3 | 49 | 0 | 3007
0.05856 | 5 | 0.00115 | 12 | 0.7 | 79000 | 1231000 | 1308000 | 12 | 283.4525 | 28.3 | 49 | 0 | 2385
0.05856 | 5 | 0.00115 | 12 | 0.6 | 62000 | 1055000 | 1115000 | 12 | 243.4616 | 28.3 | 49 | 0 | 1864
0.05856 | 5 | 0.00115 | 12 | 0.5 | 50000 | 879000 | 927000 | 12 | 204.4325 | 28.3 | 49 | 0 | 1486
0.05856 | 5 | 0.00115 | 12 | 0.4 | 41000 | 703000 | 743000 | 12 | 166.2347 | 28.3 | 49 | 0 | 1232
0.05856 | 5 | 0.00115 | 12 | 0.3 | 34000 | 527000 | 560000 | 12 | 128.3191 | 28.3 | 49 | 0 | 1019
0.05856 | 5 | 0.00115 | 12 | 0.2 | 28000 | 352000 | 379000 | 12 | 90.5854 | 28.3 | 49 | 0 | 834
0.05856 | 5 | 0.00115 | 12 | 0.15 | 25000 | 264000 | 288000 | 12 | 71.7522 | 28.3 | 49 | 0 | 747
0.05856 | 5 | 0.00115 | 11.5 | 1 | 180000 | 1758000 | 1933000 | 12 | 412.5568 | 28.3 | 49 | 0 | 5397
0.05856 | 5 | 0.00115 | 11.5 | 0.9 | 126000 | 1582000 | 1704000 | 12 | 365.1356 | 28.3 | 49 | 0 | 3767
0.05856 | 5 | 0.00115 | 11.5 | 0.8 | 98000 | 1406000 | 1501000 | 12 | 323.0888 | 28.3 | 49 | 0 | 2938
0.05856 | 5 | 0.00115 | 11.5 | 0.7 | 77000 | 1231000 | 1305000 | 12 | 282.4205 | 28.3 | 49 | 0 | 2315
0.05856 | 5 | 0.00115 | 11.5 | 0.6 | 60000 | 1055000 | 1113000 | 12 | 242.4695 | 28.3 | 49 | 0 | 1798
0.05856 | 5 | 0.00115 | 11.5 | 0.5 | 48000 | 879000 | 926000 | 12 | 203.6432 | 28.3 | 49 | 0 | 1449
0.05856 | 5 | 0.00115 | 11.5 | 0.4 | 40000 | 703000 | 742000 | 12 | 165.5581 | 28.3 | 49 | 0 | 1210
0.05856 | 5 | 0.00115 | 11.5 | 0.3 | 33000 | 527000 | 560000 | 12 | 127.6508 | 28.3 | 49 | 0 | 998
0.05856 | 5 | 0.00115 | 11.5 | 0.2 | 27000 | 352000 | 378000 | 12 | 89.9297 | 28.3 | 49 | 0 | 814
0.05856 | 5 | 0.00115 | 11.5 | 0.15 | 24000 | 264000 | 287000 | 12 | 71.1278 | 28.3 | 49 | 0 | 730
0.05856 | 5 | 0.00115 | 11 | 1 | 178000 | 1758000 | 1930000 | 12 | 411.5052 | 28.3 | 49 | 0 | 5328
0.05856 | 5 | 0.00115 | 11 | 0.9 | 135000 | 1582000 | 1713000 | 12 | 366.3839 | 28.3 | 49 | 0 | 4040
0.05856 | 5 | 0.00115 | 11 | 0.8 | 96000 | 1406000 | 1499000 | 12 | 322.0756 | 28.3 | 49 | 0 | 2872
0.05856 | 5 | 0.00115 | 11 | 0.7 | 75000 | 1231000 | 1303000 | 12 | 281.4056 | 28.3 | 49 | 0 | 2247
0.05856 | 5 | 0.00115 | 11 | 0.6 | 58000 | 1055000 | 1111000 | 12 | 241.4813 | 28.3 | 49 | 0 | 1733
0.05856 | 5 | 0.00115 | 11 | 0.5 | 47000 | 879000 | 925000 | 12 | 202.906 | 28.3 | 49 | 0 | 1420
0.05856 | 5 | 0.00115 | 11 | 0.4 | 39000 | 703000 | 741000 | 12 | 164.8278 | 28.3 | 49 | 0 | 1181
0.05856 | 5 | 0.00115 | 11 | 0.3 | 33000 | 527000 | 559000 | 12 | 126.9961 | 28.3 | 49 | 0 | 979
0.05856 | 5 | 0.00115 | 11 | 0.2 | 27000 | 352000 | 377000 | 12 | 89.3086 | 28.3 | 49 | 0 | 798
0.05856 | 5 | 0.00115 | 11 | 0.15 | 24000 | 264000 | 287000 | 12 | 70.5168 | 28.3 | 49 | 0 | 716
0.05856 | 5 | 0.00115 | 10.5 | 1 | 0 | 1758000 | 0 | 12 | 0 | 28.3 | 49 | 0 | 0
0.05856 | 5 | 0.00115 | 10.5 | 0.9 | 136000 | 1582000 | 1714000 | 12 | 366.0819 | 28.3 | 49 | 0 | 4081
0.05856 | 5 | 0.00115 | 10.5 | 0.8 | 94000 | 1406000 | 1497000 | 12 | 321.1186 | 28.3 | 49 | 0 | 2815
0.05856 | 5 | 0.00115 | 10.5 | 0.7 | 73000 | 1231000 | 1301000 | 12 | 280.4071 | 28.3 | 49 | 0 | 2182
0.05856 | 5 | 0.00115 | 10.5 | 0.6 | 57000 | 1055000 | 1110000 | 12 | 240.8212 | 28.3 | 49 | 0 | 1717
0.05856 | 5 | 0.00115 | 10.5 | 0.5 | 46000 | 879000 | 924000 | 12 | 202.1661 | 28.3 | 49 | 0 | 1391
0.05856 | 5 | 0.00115 | 10.5 | 0.4 | 39000 | 703000 | 741000 | 12 | 164.1831 | 28.3 | 49 | 0 | 1165
0.05856 | 5 | 0.00115 | 10.5 | 0.3 | 32000 | 527000 | 558000 | 12 | 126.3497 | 28.3 | 49 | 0 | 961
0.05856 | 5 | 0.00115 | 10.5 | 0.2 | 26000 | 352000 | 377000 | 12 | 88.6911 | 28.3 | 49 | 0 | 784
0.05856 | 5 | 0.00115 | 10.5 | 0.15 | 23000 | 264000 | 286000 | 12 | 69.9177 | 28.3 | 49 | 0 | 703
0.05585 | 5 | 0.077 | 30 | 1 | 313000 | 1758000 | 2061000 | 12 | 36.4332 | 26.1 | 24 | 0 | 9378
0.05585 | 5 | 0.077 | 30 | 0.9 | 273000 | 1582000 | 1847000 | 12 | 35.7636 | 26.1 | 24 | 0 | 8180
0.05585 | 5 | 0.077 | 30 | 0.8 | 236000 | 1406000 | 1635000 | 12 | 35.1039 | 26.1 | 24 | 0 | 7079
0.05585 | 5 | 0.077 | 30 | 0.7 | 206000 | 1231000 | 1430000 | 12 | 34.4635 | 26.1 | 24 | 0 | 6170
0.05585 | 5 | 0.077 | 30 | 0.6 | 182000 | 1055000 | 1231000 | 12 | 33.8428 | 26.1 | 24 | 0 | 5457
0.05585 | 5 | 0.077 | 30 | 0.5 | 154000 | 879000 | 1029000 | 12 | 33.2106 | 26.1 | 24 | 0 | 4630
0.05585 | 5 | 0.077 | 30 | 0.4 | 131000 | 703000 | 830000 | 12 | 32.591 | 26.1 | 24 | 0 | 3927
0.05585 | 5 | 0.077 | 30 | 0.3 | 108000 | 527000 | 632000 | 12 | 31.973 | 26.1 | 24 | 0 | 3240
0.05585 | 5 | 0.077 | 30 | 0.2 | 85000 | 352000 | 434000 | 12 | 31.3553 | 26.1 | 24 | 0 | 2556
0.05585 | 5 | 0.077 | 30 | 0.15 | 73000 | 264000 | 334000 | 12 | 31.0439 | 26.1 | 24 | 0 | 2188
0.05585 | 5 | 0.077 | 27 | 1 | 280000 | 1758000 | 2030000 | 12 | 33.3291 | 26.1 | 24 | 0 | 8411
0.05585 | 5 | 0.077 | 27 | 0.9 | 243000 | 1582000 | 1818000 | 12 | 32.669 | 26.1 | 24 | 0 | 7300
0.05585 | 5 | 0.077 | 27 | 0.8 | 209000 | 1406000 | 1609000 | 12 | 32.0158 | 26.1 | 24 | 0 | 6258
0.05585 | 5 | 0.077 | 27 | 0.7 | 180000 | 1231000 | 1405000 | 12 | 31.3811 | 26.1 | 24 | 0 | 5399
0.05585 | 5 | 0.077 | 27 | 0.6 | 154000 | 1055000 | 1204000 | 12 | 30.7544 | 26.1 | 24 | 0 | 4620
0.05585 | 5 | 0.077 | 27 | 0.5 | 134000 | 879000 | 1009000 | 12 | 30.1473 | 26.1 | 24 | 0 | 4034
0.05585 | 5 | 0.077 | 27 | 0.4 | 112000 | 703000 | 812000 | 12 | 29.5317 | 26.1 | 24 | 0 | 3365
0.05585 | 5 | 0.077 | 27 | 0.3 | 92000 | 527000 | 617000 | 12 | 28.9238 | 26.1 | 24 | 0 | 2772
0.05585 | 5 | 0.077 | 27 | 0.2 | 73000 | 352000 | 422000 | 12 | 28.3166 | 26.1 | 24 | 0 | 2186
0.05585 | 5 | 0.077 | 27 | 0.15 | 63000 | 264000 | 324000 | 12 | 28.0115 | 26.1 | 24 | 0 | 1878
0.05585 | 5 | 0.077 | 24 | 1 | 251000 | 1758000 | 2001000 | 12 | 30.233 | 26.1 | 24 | 0 | 7522
0.05585 | 5 | 0.077 | 24 | 0.9 | 215000 | 1582000 | 1791000 | 12 | 29.5772 | 26.1 | 24 | 0 | 6447
0.05585 | 5 | 0.077 | 24 | 0.8 | 185000 | 1406000 | 1586000 | 12 | 28.9384 | 26.1 | 24 | 0 | 5541
0.05585 | 5 | 0.077 | 24 | 0.7 | 157000 | 1231000 | 1383000 | 12 | 28.3066 | 26.1 | 24 | 0 | 4704
0.05585 | 5 | 0.077 | 24 | 0.6 | 133000 | 1055000 | 1184000 | 12 | 27.6869 | 26.1 | 24 | 0 | 3988
0.05585 | 5 | 0.077 | 24 | 0.5 | 113000 | 879000 | 989000 | 12 | 27.0793 | 26.1 | 24 | 0 | 3392
0.05585 | 5 | 0.077 | 24 | 0.4 | 98000 | 703000 | 798000 | 12 | 26.4855 | 26.1 | 24 | 0 | 2932
0.05585 | 5 | 0.077 | 24 | 0.3 | 79000 | 527000 | 604000 | 12 | 25.8806 | 26.1 | 24 | 0 | 2363
0.05585 | 5 | 0.077 | 24 | 0.2 | 62000 | 352000 | 412000 | 12 | 25.2831 | 26.1 | 24 | 0 | 1867
0.05585 | 5 | 0.077 | 24 | 0.15 | 54000 | 264000 | 316000 | 12 | 24.9833 | 26.1 | 24 | 0 | 1609
0.05585 | 5 | 0.077 | 21 | 1 | 222000 | 1758000 | 1973000 | 12 | 27.1397 | 26.1 | 24 | 0 | 6661
0.05585 | 5 | 0.077 | 21 | 0.9 | 190000 | 1582000 | 1767000 | 12 | 26.4965 | 26.1 | 24 | 0 | 5704
0.05585 | 5 | 0.077 | 21 | 0.8 | 161000 | 1406000 | 1563000 | 12 | 25.8618 | 26.1 | 24 | 0 | 4832
0.05585 | 5 | 0.077 | 21 | 0.7 | 135000 | 1231000 | 1362000 | 12 | 25.2375 | 26.1 | 24 | 0 | 4064
0.05585 | 5 | 0.077 | 21 | 0.6 | 113000 | 1055000 | 1165000 | 12 | 24.6242 | 26.1 | 24 | 0 | 3404
0.05585 | 5 | 0.077 | 21 | 0.5 | 95000 | 879000 | 971000 | 12 | 24.0212 | 26.1 | 24 | 0 | 2847
0.05585 | 5 | 0.077 | 21 | 0.4 | 82000 | 703000 | 783000 | 12 | 23.435 | 26.1 | 24 | 0 | 2457
0.05585 | 5 | 0.077 | 21 | 0.3 | 66000 | 527000 | 591000 | 12 | 22.8397 | 26.1 | 24 | 0 | 1976
0.05585 | 5 | 0.077 | 21 | 0.2 | 52000 | 352000 | 402000 | 12 | 22.2509 | 26.1 | 24 | 0 | 1561
0.05585 | 5 | 0.077 | 21 | 0.15 | 45000 | 264000 | 307000 | 12 | 21.9563 | 26.1 | 24 | 0 | 1350
0.05585 | 5 | 0.077 | 18 | 1 | 198000 | 1758000 | 1950000 | 12 | 24.06 | 26.1 | 24 | 0 | 5936
0.05585 | 5 | 0.077 | 18 | 0.9 | 166000 | 1582000 | 1744000 | 12 | 23.419 | 26.1 | 24 | 0 | 4994
0.05585 | 5 | 0.077 | 18 | 0.8 | 140000 | 1406000 | 1542000 | 12 | 22.7914 | 26.1 | 24 | 0 | 4186
0.05585 | 5 | 0.077 | 18 | 0.7 | 116000 | 1231000 | 1344000 | 12 | 22.1754 | 26.1 | 24 | 0 | 3493
0.05585 | 5 | 0.077 | 18 | 0.6 | 96000 | 1055000 | 1148000 | 12 | 21.5669 | 26.1 | 24 | 0 | 2874
0.05585 | 5 | 0.077 | 18 | 0.5 | 79000 | 879000 | 956000 | 12 | 20.9703 | 26.1 | 24 | 0 | 2374
0.05585 | 5 | 0.077 | 18 | 0.4 | 65000 | 703000 | 766000 | 12 | 20.3806 | 26.1 | 24 | 0 | 1943
0.05585 | 5 | 0.077 | 18 | 0.3 | 55000 | 527000 | 581000 | 12 | 19.8064 | 26.1 | 24 | 0 | 1665
0.05585 | 5 | 0.077 | 18 | 0.2 | 43000 | 352000 | 393000 | 12 | 19.2216 | 26.1 | 24 | 0 | 1283
0.05585 | 5 | 0.077 | 18 | 0.15 | 37000 | 264000 | 300000 | 12 | 18.9313 | 26.1 | 24 | 0 | 1113
0.05585 | 5 | 0.077 | 17.5 | 1 | 194000 | 1758000 | 1946000 | 12 | 23.5469 | 26.1 | 24 | 0 | 5817
0.05585 | 5 | 0.077 | 17.5 | 0.9 | 163000 | 1582000 | 1740000 | 12 | 22.9067 | 26.1 | 24 | 0 | 4882
0.05585 | 5 | 0.077 | 17.5 | 0.8 | 136000 | 1406000 | 1539000 | 12 | 22.2807 | 26.1 | 24 | 0 | 4088
0.05585 | 5 | 0.077 | 17.5 | 0.7 | 113000 | 1231000 | 1341000 | 12 | 21.6653 | 26.1 | 24 | 0 | 3399
0.05585 | 5 | 0.077 | 17.5 | 0.6 | 93000 | 1055000 | 1145000 | 12 | 21.0578 | 26.1 | 24 | 0 | 2790
0.05585 | 5 | 0.077 | 17.5 | 0.5 | 77000 | 879000 | 953000 | 12 | 20.4622 | 26.1 | 24 | 0 | 2299
0.05585 | 5 | 0.077 | 17.5 | 0.4 | 63000 | 703000 | 764000 | 12 | 19.8737 | 26.1 | 24 | 0 | 1879
0.05585 | 5 | 0.077 | 17.5 | 0.3 | 54000 | 527000 | 579000 | 12 | 19.3002 | 26.1 | 24 | 0 | 1607
0.05585 | 5 | 0.077 | 17.5 | 0.2 | 41000 | 352000 | 392000 | 12 | 18.717 | 26.1 | 24 | 0 | 1239
0.05585 | 5 | 0.077 | 17.5 | 0.15 | 36000 | 264000 | 298000 | 12 | 18.4274 | 26.1 | 24 | 0 | 1075
0.05585 | 5 | 0.077 | 17 | 1 | 190000 | 1758000 | 1942000 | 12 | 23.0325 | 26.1 | 24 | 0 | 5685
0.05585 | 5 | 0.077 | 17 | 0.9 | 159000 | 1582000 | 1736000 | 12 | 22.3944 | 26.1 | 24 | 0 | 4770
0.05585 | 5 | 0.077 | 17 | 0.8 | 133000 | 1406000 | 1535000 | 12 | 21.7697 | 26.1 | 24 | 0 | 3988
0.05585 | 5 | 0.077 | 17 | 0.7 | 110000 | 1231000 | 1338000 | 12 | 21.1553 | 26.1 | 24 | 0 | 3308
0.05585 | 5 | 0.077 | 17 | 0.6 | 90000 | 1055000 | 1142000 | 12 | 20.5488 | 26.1 | 24 | 0 | 2707
0.05585 | 5 | 0.077 | 17 | 0.5 | 74000 | 879000 | 951000 | 12 | 19.9542 | 26.1 | 24 | 0 | 2225
0.05585 | 5 | 0.077 | 17 | 0.4 | 61000 | 703000 | 762000 | 12 | 19.3669 | 26.1 | 24 | 0 | 1815
0.05585 | 5 | 0.077 | 17 | 0.3 | 52000 | 527000 | 578000 | 12 | 18.7941 | 26.1 | 24 | 0 | 1550
0.05585 | 5 | 0.077 | 17 | 0.2 | 40000 | 352000 | 390000 | 12 | 18.2123 | 26.1 | 24 | 0 | 1195
0.05585 | 5 | 0.077 | 17 | 0.15 | 35000 | 264000 | 297000 | 12 | 17.9235 | 26.1 | 24 | 0 | 1039
0.05585 | 5 | 0.077 | 16.5 | 1 | 185000 | 1758000 | 1938000 | 12 | 22.5181 | 26.1 | 24 | 0 | 5553
0.05585 | 5 | 0.077 | 16.5 | 0.9 | 155000 | 1582000 | 1733000 | 12 | 21.8826 | 26.1 | 24 | 0 | 4663
0.05585 | 5 | 0.077 | 16.5 | 0.8 | 130000 | 1406000 | 1532000 | 12 | 21.2592 | 26.1 | 24 | 0 | 3892
0.05585 | 5 | 0.077 | 16.5 | 0.7 | 107000 | 1231000 | 1335000 | 12 | 20.6455 | 26.1 | 24 | 0 | 3219
0.05585 | 5 | 0.077 | 16.5 | 0.6 | 88000 | 1055000 | 1140000 | 12 | 20.0399 | 26.1 | 24 | 0 | 2626
0.05585 | 5 | 0.077 | 16.5 | 0.5 | 72000 | 879000 | 949000 | 12 | 19.4465 | 26.1 | 24 | 0 | 2154
0.05585 | 5 | 0.077 | 16.5 | 0.4 | 59000 | 703000 | 760000 | 12 | 18.8604 | 26.1 | 24 | 0 | 1755
0.05585 | 5 | 0.077 | 16.5 | 0.3 | 50000 | 527000 | 576000 | 12 | 18.2882 | 26.1 | 24 | 0 | 1494
0.05585 | 5 | 0.077 | 16.5 | 0.2 | 38000 | 352000 | 389000 | 12 | 17.7078 | 26.1 | 24 | 0 | 1152
0.05585 | 5 | 0.077 | 16.5 | 0.15 | 33000 | 264000 | 296000 | 12 | 17.4197 | 26.1 | 24 | 0 | 1003
0.05585 | 5 | 0.077 | 16 | 1 | 181000 | 1758000 | 1934000 | 12 | 22.0044 | 26.1 | 24 | 0 | 5429
0.05585 | 5 | 0.077 | 16 | 0.9 | 152000 | 1582000 | 1729000 | 12 | 21.3707 | 26.1 | 24 | 0 | 4555
0.05585 | 5 | 0.077 | 16 | 0.8 | 126000 | 1406000 | 1529000 | 12 | 20.7484 | 26.1 | 24 | 0 | 3794
0.05585 | 5 | 0.077 | 16 | 0.7 | 104000 | 1231000 | 1332000 | 12 | 20.1356 | 26.1 | 24 | 0 | 3129
0.05585 | 5 | 0.077 | 16 | 0.6 | 85000 | 1055000 | 1137000 | 12 | 19.5312 | 26.1 | 24 | 0 | 2546
0.05585 | 5 | 0.077 | 16 | 0.5 | 69000 | 879000 | 946000 | 12 | 18.9388 | 26.1 | 24 | 0 | 2083
0.05585 | 5 | 0.077 | 16 | 0.4 | 56000 | 703000 | 758000 | 12 | 18.3538 | 26.1 | 24 | 0 | 1694
0.05585 | 5 | 0.077 | 16 | 0.3 | 48000 | 527000 | 574000 | 12 | 17.7827 | 26.1 | 24 | 0 | 1444
0.05585 | 5 | 0.077 | 16 | 0.2 | 37000 | 352000 | 388000 | 12 | 17.2034 | 26.1 | 24 | 0 | 1111
0.05585 | 5 | 0.077 | 16 | 0.15 | 32000 | 264000 | 295000 | 12 | 16.9161 | 26.1 | 24 | 0 | 968
0.05585 | 5 | 0.077 | 15.5 | 1 | 177000 | 1758000 | 1930000 | 12 | 21.4923 | 26.1 | 24 | 0 | 5320
0.05585 | 5 | 0.077 | 15.5 | 0.9 | 148000 | 1582000 | 1726000 | 12 | 20.8585 | 26.1 | 24 | 0 | 4444
0.05585 | 5 | 0.077 | 15.5 | 0.8 | 123000 | 1406000 | 1526000 | 12 | 20.2381 | 26.1 | 24 | 0 | 3701
0.05585 | 5 | 0.077 | 15.5 | 0.7 | 101000 | 1231000 | 1329000 | 12 | 19.626 | 26.1 | 24 | 0 | 3041
0.05585 | 5 | 0.077 | 15.5 | 0.6 | 82000 | 1055000 | 1135000 | 12 | 19.0225 | 26.1 | 24 | 0 | 2466
0.05585 | 5 | 0.077 | 15.5 | 0.5 | 67000 | 879000 | 944000 | 12 | 18.4313 | 26.1 | 24 | 0 | 2015
0.05585 | 5 | 0.077 | 15.5 | 0.4 | 55000 | 703000 | 756000 | 12 | 17.8476 | 26.1 | 24 | 0 | 1637
0.05585 | 5 | 0.077 | 15.5 | 0.3 | 44000 | 527000 | 570000 | 12 | 17.2686 | 26.1 | 24 | 0 | 1307
0.05585 | 5 | 0.077 | 15.5 | 0.2 | 36000 | 352000 | 386000 | 12 | 16.6993 | 26.1 | 24 | 0 | 1072
0.05585 | 5 | 0.077 | 15.5 | 0.15 | 31000 | 264000 | 294000 | 12 | 16.4125 | 26.1 | 24 | 0 | 934
0.05585 | 5 | 0.077 | 15 | 1 | 174000 | 1758000 | 1927000 | 12 | 20.9822 | 26.1 | 24 | 0 | 5232
0.05585 | 5 | 0.077 | 15 | 0.9 | 145000 | 1582000 | 1723000 | 12 | 20.3472 | 26.1 | 24 | 0 | 4343
0.05585 | 5 | 0.077 | 15 | 0.8 | 120000 | 1406000 | 1523000 | 12 | 19.7279 | 26.1 | 24 | 0 | 3609
0.05585 | 5 | 0.077 | 15 | 0.7 | 99000 | 1231000 | 1326000 | 12 | 19.1166 | 26.1 | 24 | 0 | 2956
0.05585 | 5 | 0.077 | 15 | 0.6 | 80000 | 1055000 | 1132000 | 12 | 18.5141 | 26.1 | 24 | 0 | 2390
0.05585 | 5 | 0.077 | 15 | 0.5 | 65000 | 879000 | 942000 | 12 | 17.9239 | 26.1 | 24 | 0 | 1946
0.05585 | 5 | 0.077 | 15 | 0.4 | 53000 | 703000 | 754000 | 12 | 17.3412 | 26.1 | 24 | 0 | 1578
0.05585 | 5 | 0.077 | 15 | 0.3 | 45000 | 527000 | 571000 | 12 | 16.7712 | 26.1 | 24 | 0 | 1336
0.05585 | 5 | 0.077 | 15 | 0.2 | 36000 | 352000 | 386000 | 12 | 16.1985 | 26.1 | 24 | 0 | 1067
0.05585 | 5 | 0.077 | 15 | 0.15 | 30000 | 264000 | 293000 | 12 | 15.9086 | 26.1 | 24 | 0 | 897
0.05585 | 5 | 0.077 | 14.5 | 1 | 172000 | 1758000 | 1925000 | 12 | 20.4743 | 26.1 | 24 | 0 | 5166
0.05585 | 5 | 0.077 | 14.5 | 0.9 | 142000 | 1582000 | 1719000 | 12 | 19.8364 | 26.1 | 24 | 0 | 4246
0.05585 | 5 | 0.077 | 14.5 | 0.8 | 117000 | 1406000 | 1520000 | 12 | 19.2179 | 26.1 | 24 | 0 | 3519
0.05585 | 5 | 0.077 | 14.5 | 0.7 | 96000 | 1231000 | 1323000 | 12 | 18.6072 | 26.1 | 24 | 0 | 2871
0.05585 | 5 | 0.077 | 14.5 | 0.6 | 77000 | 1055000 | 1130000 | 12 | 18.0059 | 26.1 | 24 | 0 | 2315
0.05585 | 5 | 0.077 | 14.5 | 0.5 | 63000 | 879000 | 940000 | 12 | 17.4166 | 26.1 | 24 | 0 | 1880
0.05585 | 5 | 0.077 | 14.5 | 0.4 | 51000 | 703000 | 752000 | 12 | 16.835 | 26.1 | 24 | 0 | 1521
0.05585 | 5 | 0.077 | 14.5 | 0.3 | 42000 | 527000 | 568000 | 12 | 16.2643 | 26.1 | 24 | 0 | 1271
0.05585 | 5 | 0.077 | 14.5 | 0.2 | 34000 | 352000 | 385000 | 12 | 15.6936 | 26.1 | 24 | 0 | 1020
0.05585 | 5 | 0.077 | 14.5 | 0.15 | 29000 | 264000 | 292000 | 12 | 15.4052 | 26.1 | 24 | 0 | 865
0.05585 | 5 | 0.077 | 14 | 1 | 171000 | 1758000 | 1924000 | 12 | 19.9685 | 26.1 | 24 | 0 | 5120
0.05585 | 5 | 0.077 | 14 | 0.9 | 139000 | 1582000 | 1717000 | 12 | 19.3263 | 26.1 | 24 | 0 | 4156
0.05585 | 5 | 0.077 | 14 | 0.8 | 114000 | 1406000 | 1517000 | 12 | 18.7077 | 26.1 | 24 | 0 | 3427
0.05585 | 5 | 0.077 | 14 | 0.7 | 93000 | 1231000 | 1321000 | 12 | 18.0981 | 26.1 | 24 | 0 | 2788
0.05585 | 5 | 0.077 | 14 | 0.6 | 75000 | 1055000 | 1127000 | 12 | 17.4977 | 26.1 | 24 | 0 | 2241
0.05585 | 5 | 0.077 | 14 | 0.5 | 60000 | 879000 | 938000 | 12 | 16.9094 | 26.1 | 24 | 0 | 1814
0.05585 | 5 | 0.077 | 14 | 0.4 | 50000 | 703000 | 752000 | 12 | 16.3318 | 26.1 | 24 | 0 | 1494
0.05585 | 5 | 0.077 | 14 | 0.3 | 41000 | 527000 | 567000 | 12 | 15.7584 | 26.1 | 24 | 0 | 1215
0.05585 | 5 | 0.077 | 14 | 0.2 | 33000 | 352000 | 383000 | 12 | 15.1893 | 26.1 | 24 | 0 | 980
0.05585 | 5 | 0.077 | 14 | 0.15 | 28000 | 264000 | 291000 | 12 | 14.9024 | 26.1 | 24 | 0 | 839
0.05585 | 5 | 0.077 | 13.5 | 1 | 170000 | 1758000 | 1923000 | 12 | 19.4648 | 26.1 | 24 | 0 | 5096
0.05585 | 5 | 0.077 | 13.5 | 0.9 | 136000 | 1582000 | 1714000 | 12 | 18.8166 | 26.1 | 24 | 0 | 4071
0.05585 | 5 | 0.077 | 13.5 | 0.8 | 111000 | 1406000 | 1514000 | 12 | 18.198 | 26.1 | 24 | 0 | 3341
0.05585 | 5 | 0.077 | 13.5 | 0.7 | 90000 | 1231000 | 1318000 | 12 | 17.5893 | 26.1 | 24 | 0 | 2709
0.05585 | 5 | 0.077 | 13.5 | 0.6 | 73000 | 1055000 | 1125000 | 12 | 16.9907 | 26.1 | 24 | 0 | 2178
0.05585 | 5 | 0.077 | 13.5 | 0.5 | 58000 | 879000 | 936000 | 12 | 16.4022 | 26.1 | 24 | 0 | 1749
0.05585 | 5 | 0.077 | 13.5 | 0.4 | 48000 | 703000 | 750000 | 12 | 15.8252 | 26.1 | 24 | 0 | 1433
0.05585 | 5 | 0.077 | 13.5 | 0.3 | 39000 | 527000 | 565000 | 12 | 15.2534 | 26.1 | 24 | 0 | 1169
0.05585 | 5 | 0.077 | 13.5 | 0.2 | 32000 | 352000 | 382000 | 12 | 14.6858 | 26.1 | 24 | 0 | 948
0.05585 | 5 | 0.077 | 13.5 | 0.15 | 27000 | 264000 | 290000 | 12 | 14.3996 | 26.1 | 24 | 0 | 813
0.05585 | 5 | 0.077 | 13 | 1 | 169000 | 1758000 | 1922000 | 12 | 18.9611 | 26.1 | 24 | 0 | 5071
0.05585 | 5 | 0.077 | 13 | 0.9 | 133000 | 1582000 | 1711000 | 12 | 18.3073 | 26.1 | 24 | 0 | 3989
0.05585 | 5 | 0.077 | 13 | 0.8 | 108000 | 1406000 | 1512000 | 12 | 17.6882 | 26.1 | 24 | 0 | 3253
0.05585 | 5 | 0.077 | 13 | 0.7 | 88000 | 1231000 | 1316000 | 12 | 17.0806 | 26.1 | 24 | 0 | 2631
0.05585 | 5 | 0.077 | 13 | 0.6 | 70000 | 1055000 | 1123000 | 12 | 16.4826 | 26.1 | 24 | 0 | 2105
0.05585 | 5 | 0.077 | 13 | 0.5 | 56000 | 879000 | 933000 | 12 | 15.8952 | 26.1 | 24 | 0 | 1685
0.05585 | 5 | 0.077 | 13 | 0.4 | 46000 | 703000 | 748000 | 12 | 15.3193 | 26.1 | 24 | 0 | 1379
0.05585 | 5 | 0.077 | 13 | 0.3 | 38000 | 527000 | 564000 | 12 | 14.7489 | 26.1 | 24 | 0 | 1129
0.05585 | 5 | 0.077 | 13 | 0.2 | 31000 | 352000 | 381000 | 12 | 14.1828 | 26.1 | 24 | 0 | 920
0.05585 | 5 | 0.077 | 13 | 0.15 | 27000 | 264000 | 290000 | 12 | 13.9001 | 26.1 | 24 | 0 | 820
0.05585 | 5 | 0.077 | 12.5 | 1 | 168000 | 1758000 | 1921000 | 12 | 18.4578 | 26.1 | 24 | 0 | 5052
0.05585 | 5 | 0.077 | 12.5 | 0.9 | 130000 | 1582000 | 1709000 | 12 | 17.7979 | 26.1 | 24 | 0 | 3907
0.05585 | 5 | 0.077 | 12.5 | 0.8 | 106000 | 1406000 | 1509000 | 12 | 17.1787 | 26.1 | 24 | 0 | 3168
0.05585 | 5 | 0.077 | 12.5 | 0.7 | 85000 | 1231000 | 1313000 | 12 | 16.5721 | 26.1 | 24 | 0 | 2555
0.05585 | 5 | 0.077 | 12.5 | 0.6 | 68000 | 1055000 | 1121000 | 12 | 15.9748 | 26.1 | 24 | 0 | 2035
0.05585 | 5 | 0.077 | 12.5 | 0.5 | 54000 | 879000 | 932000 | 12 | 15.3886 | 26.1 | 24 | 0 | 1625
0.05585 | 5 | 0.077 | 12.5 | 0.4 | 44000 | 703000 | 746000 | 12 | 14.8142 | 26.1 | 24 | 0 | 1333
0.05585 | 5 | 0.077 | 12.5 | 0.3 | 37000 | 527000 | 563000 | 12 | 14.2453 | 26.1 | 24 | 0 | 1096
0.05585 | 5 | 0.077 | 12.5 | 0.2 | 30000 | 352000 | 380000 | 12 | 13.6795 | 26.1 | 24 | 0 | 890
0.05585 | 5 | 0.077 | 12.5 | 0.15 | 27000 | 264000 | 290000 | 12 | 13.3978 | 26.1 | 24 | 0 | 799
0.05585 | 5 | 0.077 | 12 | 1 | 168000 | 1758000 | 1921000 | 12 | 17.9541 | 26.1 | 24 | 0 | 5028
0.05585 | 5 | 0.077 | 12 | 0.9 | 128000 | 1582000 | 1706000 | 12 | 17.2895 | 26.1 | 24 | 0 | 3834
0.05585 | 5 | 0.077 | 12 | 0.8 | 103000 | 1406000 | 1506000 | 12 | 16.6695 | 26.1 | 24 | 0 | 3086
0.05585 | 5 | 0.077 | 12 | 0.7 | 83000 | 1231000 | 1311000 | 12 | 16.0638 | 26.1 | 24 | 0 | 2481
0.05585 | 5 | 0.077 | 12 | 0.6 | 66000 | 1055000 | 1118000 | 12 | 15.4671 | 26.1 | 24 | 0 | 1965
0.05585 | 5 | 0.077 | 12 | 0.5 | 52000 | 879000 | 930000 | 12 | 14.8817 | 26.1 | 24 | 0 | 1562
0.05585 | 5 | 0.077 | 12 | 0.4 | 43000 | 703000 | 745000 | 12 | 14.3096 | 26.1 | 24 | 0 | 1293
0.05585 | 5 | 0.077 | 12 | 0.3 | 36000 | 527000 | 562000 | 12 | 13.7423 | 26.1 | 24 | 0 | 1070
0.05585 | 5 | 0.077 | 12 | 0.2 | 29000 | 352000 | 380000 | 12 | 13.1771 | 26.1 | 24 | 0 | 868
0.05585 | 5 | 0.077 | 12 | 0.15 | 26000 | 264000 | 289000 | 12 | 12.8957 | 26.1 | 24 | 0 | 780
0.05585 | 5 | 0.077 | 11.5 | 1 | 166000 | 1758000 | 1919000 | 12 | 17.4485 | 26.1 | 24 | 0 | 4985
0.05585 | 5 | 0.077 | 11.5 | 0.9 | 125000 | 1582000 | 1704000 | 12 | 16.781 | 26.1 | 24 | 0 | 3761
0.05585 | 5 | 0.077 | 11.5 | 0.8 | 100000 | 1406000 | 1504000 | 12 | 16.1605 | 26.1 | 24 | 0 | 3007
0.05585 | 5 | 0.077 | 11.5 | 0.7 | 80000 | 1231000 | 1308000 | 12 | 15.5554 | 26.1 | 24 | 0 | 2407
0.05585 | 5 | 0.077 | 11.5 | 0.6 | 63000 | 1055000 | 1116000 | 12 | 14.9595 | 26.1 | 24 | 0 | 1897
0.05585 | 5 | 0.077 | 11.5 | 0.5 | 51000 | 879000 | 928000 | 12 | 14.3764 | 26.1 | 24 | 0 | 1516
0.05585 | 5 | 0.077 | 11.5 | 0.4 | 42000 | 703000 | 744000 | 12 | 13.8064 | 26.1 | 24 | 0 | 1266
0.05585 | 5 | 0.077 | 11.5 | 0.3 | 35000 | 527000 | 561000 | 12 | 13.2395 | 26.1 | 24 | 0 | 1046
0.05585 | 5 | 0.077 | 11.5 | 0.2 | 29000 | 352000 | 379000 | 12 | 12.6755 | 26.1 | 24 | 0 | 855
0.05585 | 5 | 0.077 | 11.5 | 0.15 | 25000 | 264000 | 288000 | 12 | 12.3938 | 26.1 | 24 | 0 | 763
0.05585 | 5 | 0.077 | 11 | 1 | 164000 | 1758000 | 1917000 | 12 | 16.9397 | 26.1 | 24 | 0 | 4911
0.05585 | 5 | 0.077 | 11 | 0.9 | 123000 | 1582000 | 1701000 | 12 | 16.2725 | 26.1 | 24 | 0 | 3688
0.05585 | 5 | 0.077 | 11 | 0.8 | 98000 | 1406000 | 1501000 | 12 | 15.6519 | 26.1 | 24 | 0 | 2932
0.05585 | 5 | 0.077 | 11 | 0.7 | 78000 | 1231000 | 1306000 | 12 | 15.0474 | 26.1 | 24 | 0 | 2335
0.05585 | 5 | 0.077 | 11 | 0.6 | 61000 | 1055000 | 1114000 | 12 | 14.452 | 26.1 | 24 | 0 | 1830
0.05585 | 5 | 0.077 | 11 | 0.5 | 49000 | 879000 | 927000 | 12 | 13.8718 | 26.1 | 24 | 0 | 1476
0.05585 | 5 | 0.077 | 11 | 0.4 | 41000 | 703000 | 743000 | 12 | 13.3026 | 26.1 | 24 | 0 | 1233
0.05585 | 5 | 0.077 | 11 | 0.3 | 34000 | 527000 | 561000 | 12 | 12.7369 | 26.1 | 24 | 0 | 1024
0.05585 | 5 | 0.077 | 11 | 0.2 | 28000 | 352000 | 378000 | 12 | 12.1729 | 26.1 | 24 | 0 | 832
0.05585 | 5 | 0.077 | 11 | 0.15 | 25000 | 264000 | 288000 | 12 | 11.892 | 26.1 | 24 | 0 | 747
0.05585 | 5 | 0.077 | 10.5 | 1 | 161000 | 1758000 | 1914000 | 12 | 16.4298 | 26.1 | 24 | 0 | 4825
0.05585 | 5 | 0.077 | 10.5 | 0.9 | 121000 | 1582000 | 1699000 | 12 | 15.765 | 26.1 | 24 | 0 | 3626
0.05585 | 5 | 0.077 | 10.5 | 0.8 | 95000 | 1406000 | 1499000 | 12 | 15.1435 | 26.1 | 24 | 0 | 2859
0.05585 | 5 | 0.077 | 10.5 | 0.7 | 75000 | 1231000 | 1304000 | 12 | 14.5394 | 26.1 | 24 | 0 | 2265
0.05585 | 5 | 0.077 | 10.5 | 0.6 | 59000 | 1055000 | 1112000 | 12 | 13.9445 | 26.1 | 24 | 0 | 1763
0.05585 | 5 | 0.077 | 10.5 | 0.5 | 48000 | 879000 | 926000 | 12 | 13.3676 | 26.1 | 24 | 0 | 1441
0.05585 | 5 | 0.077 | 10.5 | 0.4 | 40000 | 703000 | 742000 | 12 | 12.8001 | 26.1 | 24 | 0 | 1213
0.05585 | 5 | 0.077 | 10.5 | 0.3 | 33000 | 527000 | 560000 | 12 | 12.2341 | 26.1 | 24 | 0 | 999
0.05585 | 5 | 0.077 | 10.5 | 0.2 | 27000 | 352000 | 378000 | 12 | 11.6711 | 26.1 | 24 | 0 | 816
0.05585 | 5 | 0.077 | 10.5 | 0.15 | 24000 | 264000 | 287000 | 12 | 11.3904 | 26.1 | 24 | 0 | 733
0.1398 | 9 | 0.077 | 30 | 1 | 273000 | 1758000 | 2023000 | 12 | 36.3139 | 131 | 23.9 | 0 | 8196
0.1398 | 9 | 0.077 | 30 | 0.9 | 235000 | 1582000 | 1810000 | 12 | 35.6506 | 131 | 23.9 | 0 | 7060
0.1398 | 9 | 0.077 | 30 | 0.8 | 202000 | 1406000 | 1602000 | 12 | 35.0009 | 131 | 23.9 | 0 | 6059
0.1398 | 9 | 0.077 | 30 | 0.7 | 173000 | 1231000 | 1399000 | 12 | 34.3651 | 131 | 23.9 | 0 | 5195
0.1398 | 9 | 0.077 | 30 | 0.6 | 148000 | 1055000 | 1198000 | 12 | 33.7404 | 131 | 23.9 | 0 | 4443
0.1398 | 9 | 0.077 | 30 | 0.5 | 129000 | 879000 | 1004000 | 12 | 33.1328 | 131 | 23.9 | 0 | 3859
0.1398 | 9 | 0.077 | 30 | 0.4 | 107000 | 703000 | 807000 | 12 | 32.5177 | 131 | 23.9 | 0 | 3201
0.1398 | 9 | 0.077 | 30 | 0.3 | 87000 | 527000 | 612000 | 12 | 31.9106 | 131 | 23.9 | 0 | 2622
0.1398 | 9 | 0.077 | 30 | 0.2 | 68000 | 352000 | 418000 | 12 | 31.3045 | 131 | 23.9 | 0 | 2053
0.1398 | 9 | 0.077 | 30 | 0.15 | 59000 | 264000 | 320000 | 12 | 31.0002 | 131 | 23.9 | 0 | 1756
0.1398 | 9 | 0.077 | 27 | 1 | 243000 | 1758000 | 1993000 | 12 | 33.2147 | 131 | 23.9 | 0 | 7276
0.1398 | 9 | 0.077 | 27 | 0.9 | 208000 | 1582000 | 1784000 | 12 | 32.5626 | 131 | 23.9 | 0 | 6245
0.1398 | 9 | 0.077 | 27 | 0.8 | 178000 | 1406000 | 1579000 | 12 | 31.9231 | 131 | 23.9 | 0 | 5338
0.1398 | 9 | 0.077 | 27 | 0.7 | 150000 | 1231000 | 1376000 | 12 | 31.2917 | 131 | 23.9 | 0 | 4512
0.1398 | 9 | 0.077 | 27 | 0.6 | 127000 | 1055000 | 1178000 | 12 | 30.6726 | 131 | 23.9 | 0 | 3808
0.1398 | 9 | 0.077 | 27 | 0.5 | 107000 | 879000 | 983000 | 12 | 30.0639 | 131 | 23.9 | 0 | 3207
0.1398 | 9 | 0.077 | 27 | 0.4 | 93000 | 703000 | 793000 | 12 | 29.4733 | 131 | 23.9 | 0 | 2786
0.1398 | 9 | 0.077 | 27 | 0.3 | 74000 | 527000 | 599000 | 12 | 28.8679 | 131 | 23.9 | 0 | 2217
0.1398 | 9 | 0.077 | 27 | 0.2 | 58000 | 352000 | 408000 | 12 | 28.2713 | 131 | 23.9 | 0 | 1737
0.1398 | 9 | 0.077 | 27 | 0.15 | 50000 | 264000 | 312000 | 12 | 27.9724 | 131 | 23.9 | 0 | 1490
0.1398 | 9 | 0.077 | 24 | 1 | 215000 | 1758000 | 1966000 | 12 | 30.1247 | 131 | 23.9 | 0 | 6447
0.1398 | 9 | 0.077 | 24 | 0.9 | 183000 | 1582000 | 1760000 | 12 | 29.4805 | 131 | 23.9 | 0 | 5487
0.1398 | 9 | 0.077 | 24 | 0.8 | 154000 | 1406000 | 1556000 | 12 | 28.8465 | 131 | 23.9 | 0 | 4629
0.1398 | 9 | 0.077 | 24 | 0.7 | 129000 | 1231000 | 1356000 | 12 | 28.2234 | 131 | 23.9 | 0 | 3878
0.1398 | 9 | 0.077 | 24 | 0.6 | 108000 | 1055000 | 1159000 | 12 | 27.6107 | 131 | 23.9 | 0 | 3232
0.1398 | 9 | 0.077 | 24 | 0.5 | 89000 | 879000 | 966000 | 12 | 27.0081 | 131 | 23.9 | 0 | 2685
0.1398 | 9 | 0.077 | 24 | 0.4 | 77000 | 703000 | 778000 | 12 | 26.4225 | 131 | 23.9 | 0 | 2307
0.1398 | 9 | 0.077 | 24 | 0.3 | 61000 | 527000 | 587000 | 12 | 25.8281 | 131 | 23.9 | 0 | 1842
0.1398 | 9 | 0.077 | 24 | 0.2 | 48000 | 352000 | 398000 | 12 | 25.2403 | 131 | 23.9 | 0 | 1442
0.1398 | 9 | 0.077 | 24 | 0.15 | 41000 | 264000 | 304000 | 12 | 24.9464 | 131 | 23.9 | 0 | 1242
0.1398 | 9 | 0.077 | 21 | 1 | 190000 | 1758000 | 1942000 | 12 | 27.0418 | 131 | 23.9 | 0 | 5688
0.1398 | 9 | 0.077 | 21 | 0.9 | 159000 | 1582000 | 1737000 | 12 | 26.403 | 131 | 23.9 | 0 | 4775
0.1398 | 9 | 0.077 | 21 | 0.8 | 133000 | 1406000 | 1535000 | 12 | 25.7773 | 131 | 23.9 | 0 | 3992
0.1398 | 9 | 0.077 | 21 | 0.7 | 110000 | 1231000 | 1338000 | 12 | 25.1618 | 131 | 23.9 | 0 | 3311
0.1398 | 9 | 0.077 | 21 | 0.6 | 90000 | 1055000 | 1142000 | 12 | 24.5543 | 131 | 23.9 | 0 | 2709
0.1398 | 9 | 0.077 | 21 | 0.5 | 74000 | 879000 | 951000 | 12 | 23.9585 | 131 | 23.9 | 0 | 2223
0.1398 | 9 | 0.077 | 21 | 0.4 | 60000 | 703000 | 762000 | 12 | 23.3697 | 131 | 23.9 | 0 | 1808
0.1398 | 9 | 0.077 | 21 | 0.3 | 51000 | 527000 | 577000 | 12 | 22.796 | 131 | 23.9 | 0 | 1542
0.1398 | 9 | 0.077 | 21 | 0.2 | 39000 | 352000 | 390000 | 12 | 22.2122 | 131 | 23.9 | 0 | 1176
0.1398 | 9 | 0.077 | 21 | 0.15 | 34000 | 264000 | 297000 | 12 | 21.9226 | 131 | 23.9 | 0 | 1016
0.1398 | 9 | 0.077 | 18 | 1 | 168000 | 1758000 | 1921000 | 12 | 23.9697 | 131 | 23.9 | 0 | 5037
0.1398 | 9 | 0.077 | 18 | 0.9 | 139000 | 1582000 | 1717000 | 12 | 23.3352 | 131 | 23.9 | 0 | 4160
0.1398 | 9 | 0.077 | 18 | 0.8 | 114000 | 1406000 | 1517000 | 12 | 22.7141 | 131 | 23.9 | 0 | 3416
0.1398 | 9 | 0.077 | 18 | 0.7 | 92000 | 1231000 | 1320000 | 12 | 22.1026 | 131 | 23.9 | 0 | 2767
0.1398 | 9 | 0.077 | 18 | 0.6 | 75000 | 1055000 | 1127000 | 12 | 21.5028 | 131 | 23.9 | 0 | 2236
0.1398 | 9 | 0.077 | 18 | 0.5 | 60000 | 879000 | 938000 | 12 | 20.9136 | 131 | 23.9 | 0 | 1810
0.1398 | 9 | 0.077 | 18 | 0.4 | 50000 | 703000 | 752000 | 12 | 20.3359 | 131 | 23.9 | 0 | 1497
0.1398 | 9 | 0.077 | 18 | 0.3 | 40000 | 527000 | 566000 | 12 | 19.7602 | 131 | 23.9 | 0 | 1206
0.1398 | 9 | 0.077 | 18 | 0.2 | 32000 | 352000 | 383000 | 12 | 19.1897 | 131 | 23.9 | 0 | 965
0.1398 | 9 | 0.077 | 18 | 0.15 | 27000 | 264000 | 290000 | 12 | 18.9017 | 131 | 23.9 | 0 | 817
0.1398 | 9 | 0.077 | 17.5 | 1 | 165000 | 1758000 | 1918000 | 12 | 23.4591 | 131 | 23.9 | 0 | 4943
0.1398 | 9 | 0.077 | 17.5 | 0.9 | 136000 | 1582000 | 1714000 | 12 | 22.8249 | 131 | 23.9 | 0 | 4067
0.1398 | 9 | 0.077 | 17.5 | 0.8 | 111000 | 1406000 | 1514000 | 12 | 22.204 | 131 | 23.9 | 0 | 3325
0.1398 | 9 | 0.077 | 17.5 | 0.7 | 90000 | 1231000 | 1317000 | 12 | 21.5937 | 131 | 23.9 | 0 | 2687
0.1398 | 9 | 0.077 | 17.5 | 0.6 | 72000 | 1055000 | 1125000 | 12 | 20.9948 | 131 | 23.9 | 0 | 2163
0.1398 | 9 | 0.077 | 17.5 | 0.5 | 58000 | 879000 | 935000 | 12 | 20.4065 | 131 | 23.9 | 0 | 1744
0.1398 | 9 | 0.077 | 17.5 | 0.4 | 48000 | 703000 | 749000 | 12 | 19.8286 | 131 | 23.9 | 0 | 1429
0.1398 | 9 | 0.077 | 17.5 | 0.3 | 39000 | 527000 | 565000 | 12 | 19.2552 | 131 | 23.9 | 0 | 1159
0.1398 | 9 | 0.077 | 17.5 | 0.2 | 31000 | 352000 | 382000 | 12 | 18.6862 | 131 | 23.9 | 0 | 933
0.1398 | 9 | 0.077 | 17.5 | 0.15 | 27000 | 264000 | 289000 | 12 | 18.3993 | 131 | 23.9 | 0 | 796
0.1398 | 9 | 0.077 | 17 | 1 | 162000 | 1758000 | 1915000 | 12 | 22.9483 | 131 | 23.9 | 0 | 4847
0.1398 | 9 | 0.077 | 17 | 0.9 | 133000 | 1582000 | 1711000 | 12 | 22.3146 | 131 | 23.9 | 0 | 3975
0.1398 | 9 | 0.077 | 17 | 0.8 | 108000 | 1406000 | 1511000 | 12 | 21.6941 | 131 | 23.9 | 0 | 3236
0.1398 | 9 | 0.077 | 17 | 0.7 | 87000 | 1231000 | 1315000 | 12 | 21.0849 | 131 | 23.9 | 0 | 2607
0.1398 | 9 | 0.077 | 17 | 0.6 | 70000 | 1055000 | 1122000 | 12 | 20.4867 | 131 | 23.9 | 0 | 2089
0.1398 | 9 | 0.077 | 17 | 0.5 | 56000 | 879000 | 933000 | 12 | 19.8994 | 131 | 23.9 | 0 | 1680
0.1398 | 9 | 0.077 | 17 | 0.4 | 46000 | 703000 | 748000 | 12 | 19.3224 | 131 | 23.9 | 0 | 1373
0.1398 | 9 | 0.077 | 17 | 0.3 | 37000 | 527000 | 564000 | 12 | 18.7511 | 131 | 23.9 | 0 | 1121
0.1398 | 9 | 0.077 | 17 | 0.2 | 30000 | 352000 | 381000 | 12 | 18.1832 | 131 | 23.9 | 0 | 905
0.1398 | 9 | 0.077 | 17 | 0.15 | 27000 | 264000 | 290000 | 12 | 17.9003 | 131 | 23.9 | 0 | 807
0.1398 | 9 | 0.077 | 16.5 | 1 | 159000 | 1758000 | 1912000 | 12 | 22.4384 | 131 | 23.9 | 0 | 4760
0.1398 | 9 | 0.077 | 16.5 | 0.9 | 130000 | 1582000 | 1708000 | 12 | 21.8047 | 131 | 23.9 | 0 | 3887
0.1398 | 9 | 0.077 | 16.5 | 0.8 | 105000 | 1406000 | 1508000 | 12 | 21.1847 | 131 | 23.9 | 0 | 3151
0.1398 | 9 | 0.077 | 16.5 | 0.7 | 84000 | 1231000 | 1312000 | 12 | 20.5762 | 131 | 23.9 | 0 | 2529
0.1398 | 9 | 0.077 | 16.5 | 0.6 | 67000 | 1055000 | 1120000 | 12 | 19.9789 | 131 | 23.9 | 0 | 2018
0.1398 | 9 | 0.077 | 16.5 | 0.5 | 54000 | 879000 | 931000 | 12 | 19.3928 | 131 | 23.9 | 0 | 1620
0.1398 | 9 | 0.077 | 16.5 | 0.4 | 44000 | 703000 | 746000 | 12 | 18.8177 | 131 | 23.9 | 0 | 1330
0.1398 | 9 | 0.077 | 16.5 | 0.3 | 36000 | 527000 | 563000 | 12 | 18.2476 | 131 | 23.9 | 0 | 1090
0.1398 | 9 | 0.077 | 16.5 | 0.2 | 29000 | 352000 | 380000 | 12 | 17.6806 | 131 | 23.9 | 0 | 881
0.1398 | 9 | 0.077 | 16.5 | 0.15 | 26000 | 264000 | 289000 | 12 | 17.3981 | 131 | 23.9 | 0 | 787
0.1398 | 9 | 0.077 | 16 | 1 | 156000 | 1758000 | 1909000 | 12 | 21.9287 | 131 | 23.9 | 0 | 4676
0.1398 | 9 | 0.077 | 16 | 0.9 | 127000 | 1582000 | 1705000 | 12 | 21.2949 | 131 | 23.9 | 0 | 3800
0.1398 | 9 | 0.077 | 16 | 0.8 | 102000 | 1406000 | 1506000 | 12 | 20.6753 | 131 | 23.9 | 0 | 3066
0.1398 | 9 | 0.077 | 16 | 0.7 | 82000 | 1231000 | 1310000 | 12 | 20.0676 | 131 | 23.9 | 0 | 2451
0.1398 | 9 | 0.077 | 16 | 0.6 | 65000 | 1055000 | 1118000 | 12 | 19.4711 | 131 | 23.9 | 0 | 1947
0.1398 | 9 | 0.077 | 16 | 0.5 | 52000 | 879000 | 929000 | 12 | 18.8864 | 131 | 23.9 | 0 | 1561
0.1398 | 9 | 0.077 | 16 | 0.4 | 43000 | 703000 | 745000 | 12 | 18.3133 | 131 | 23.9 | 0 | 1290
0.1398 | 9 | 0.077 | 16 | 0.3 | 35000 | 527000 | 562000 | 12 | 17.7438 | 131 | 23.9 | 0 | 1056
0.1398 | 9 | 0.077 | 16 | 0.2 | 29000 | 352000 | 379000 | 12 | 17.1782 | 131 | 23.9 | 0 | 860
0.1398 | 9 | 0.077 | 16 | 0.15 | 26000 | 264000 | 289000 | 12 | 16.8961 | 131 | 23.9 | 0 | 769
0.1398 | 9 | 0.077 | 15.5 | 1 | 154000 | 1758000 | 1907000 | 12 | 21.4206 | 131 | 23.9 | 0 | 4606
0.1398 | 9 | 0.077 | 15.5 | 0.9 | 124000 | 1582000 | 1702000 | 12 | 20.7852 | 131 | 23.9 | 0 | 3714
0.1398 | 9 | 0.077 | 15.5 | 0.8 | 100000 | 1406000 | 1503000 | 12 | 20.1663 | 131 | 23.9 | 0 | 2986
0.1398 | 9 | 0.077 | 15.5 | 0.7 | 79000 | 1231000 | 1307000 | 12 | 19.5592 | 131 | 23.9 | 0 | 2376
0.1398 | 9 | 0.077 | 15.5 | 0.6 | 63000 | 1055000 | 1116000 | 12 | 18.9643 | 131 | 23.9 | 0 | 1887
0.1398 | 9 | 0.077 | 15.5 | 0.5 | 50000 | 879000 | 928000 | 12 | 18.3811 | 131 | 23.9 | 0 | 1515
0.1398 | 9 | 0.077 | 15.5 | 0.4 | 42000 | 703000 | 744000 | 12 | 17.8091 | 131 | 23.9 | 0 | 1253
0.1398 | 9 | 0.077 | 15.5 | 0.3 | 34000 | 527000 | 561000 | 12 | 17.2411 | 131 | 23.9 | 0 | 1032
0.1398 | 9 | 0.077 | 15.5 | 0.2 | 28000 | 352000 | 379000 | 12 | 16.676 | 131 | 23.9 | 0 | 840
0.1398 | 9 | 0.077 | 15.5 | 0.15 | 25000 | 264000 | 288000 | 12 | 16.3939 | 131 | 23.9 | 0 | 748
0.1398 | 9 | 0.077 | 15 | 1 | 151000 | 1758000 | 1905000 | 12 | 20.9122 | 131 | 23.9 | 0 | 4535
0.1398 | 9 | 0.077 | 15 | 0.9 | 121000 | 1582000 | 1700000 | 12 | 20.2756 | 131 | 23.9 | 0 | 3629
0.1398 | 9 | 0.077 | 15 | 0.8 | 97000 | 1406000 | 1500000 | 12 | 19.6575 | 131 | 23.9 | 0 | 2908
0.1398 | 9 | 0.077 | 15 | 0.7 | 77000 | 1231000 | 1305000 | 12 | 19.051 | 131 | 23.9 | 0 | 2302
0.1398 | 9 | 0.077 | 15 | 0.6 | 61000 | 1055000 | 1114000 | 12 | 18.4568 | 131 | 23.9 | 0 | 1819
0.1398 | 9 | 0.077 | 15 | 0.5 | 49000 | 879000 | 927000 | 12 | 17.8765 | 131 | 23.9 | 0 | 1474
0.1398 | 9 | 0.077 | 15 | 0.4 | 41000 | 703000 | 743000 | 12 | 17.3062 | 131 | 23.9 | 0 | 1229
0.1398 | 9 | 0.077 | 15 | 0.3 | 34000 | 527000 | 560000 | 12 | 16.7385 | 131 | 23.9 | 0 | 1010
0.1398 | 9 | 0.077 | 15 | 0.2 | 27000 | 352000 | 378000 | 12 | 16.1737 | 131 | 23.9 | 0 | 820
0.1398 | 9 | 0.077 | 15 | 0.15 | 24000 | 264000 | 287000 | 12 | 15.8921 | 131 | 23.9 | 0 | 733
0.1398 | 9 | 0.077 | 14.5 | 1 | 149000 | 1758000 | 1902000 | 12 | 20.4041 | 131 | 23.9 | 0 | 4466
0.1398 | 9 | 0.077 | 14.5 | 0.9 | 118000 | 1582000 | 1697000 | 12 | 19.7663 | 131 | 23.9 | 0 | 3548
0.1398 | 9 | 0.077 | 14.5 | 0.8 | 94000 | 1406000 | 1498000 | 12 | 19.1489 | 131 | 23.9 | 0 | 2832
0.1398 | 9 | 0.077 | 14.5 | 0.7 | 74000 | 1231000 | 1303000 | 12 | 18.5427 | 131 | 23.9 | 0 | 2228
0.1398 | 9 | 0.077 | 14.5 | 0.6 | 59000 | 1055000 | 1112000 | 12 | 17.9512 | 131 | 23.9 | 0 | 1770
0.1398 | 9 | 0.077 | 14.5 | 0.5 | 48000 | 879000 | 926000 | 12 | 17.3723 | 131 | 23.9 | 0 | 1439
0.1398 | 9 | 0.077 | 14.5 | 0.4 | 40000 | 703000 | 742000 | 12 | 16.8026 | 131 | 23.9 | 0 | 1198
0.1398 | 9 | 0.077 | 14.5 | 0.3 | 33000 | 527000 | 559000 | 12 | 16.2361 | 131 | 23.9 | 0 | 990
0.1398 | 9 | 0.077 | 14.5 | 0.2 | 27000 | 352000 | 378000 | 12 | 15.6719 | 131 | 23.9 | 0 | 804
0.1398 | 9 | 0.077 | 14.5 | 0.15 | 24000 | 264000 | 287000 | 12 | 15.3906 | 131 | 23.9 | 0 | 719
0.1398 | 9 | 0.077 | 14 | 1 | 147000 | 1758000 | 1900000 | 12 | 19.8961 | 131 | 23.9 | 0 | 4399
0.1398 | 9 | 0.077 | 14 | 0.9 | 116000 | 1582000 | 1694000 | 12 | 19.2575 | 131 | 23.9 | 0 | 3470
0.1398 | 9 | 0.077 | 14 | 0.8 | 92000 | 1406000 | 1496000 | 12 | 18.6405 | 131 | 23.9 | 0 | 2758
0.1398 | 9 | 0.077 | 14 | 0.7 | 72000 | 1231000 | 1300000 | 12 | 18.0347 | 131 | 23.9 | 0 | 2156
0.1398 | 9 | 0.077 | 14 | 0.6 | 57000 | 1055000 | 1110000 | 12 | 17.4436 | 131 | 23.9 | 0 | 1701
0.1398 | 9 | 0.077 | 14 | 0.5 | 47000 | 879000 | 924000 | 12 | 16.8684 | 131 | 23.9 | 0 | 1406
0.1398 | 9 | 0.077 | 14 | 0.4 | 39000 | 703000 | 741000 | 12 | 16.3003 | 131 | 23.9 | 0 | 1180
0.1398 | 9 | 0.077 | 14 | 0.3 | 32000 | 527000 | 559000 | 12 | 15.7339 | 131 | 23.9 | 0 | 971
0.1398 | 9 | 0.077 | 14 | 0.2 | 26000 | 352000 | 377000 | 12 | 15.1701 | 131 | 23.9 | 0 | 789
0.1398 | 9 | 0.077 | 14 | 0.15 | 24000 | 264000 | 287000 | 12 | 14.8891 | 131 | 23.9 | 0 | 706
0.1398 | 9 | 0.077 | 13.5 | 1 | 144000 | 1758000 | 1898000 | 12 | 19.388 | 131 | 23.9 | 0 | 4330
0.1398 | 9 | 0.077 | 13.5 | 0.9 | 113000 | 1582000 | 1692000 | 12 | 18.7489 | 131 | 23.9 | 0 | 3395
0.1398 | 9 | 0.077 | 13.5 | 0.8 | 89000 | 1406000 | 1493000 | 12 | 18.1322 | 131 | 23.9 | 0 | 2684
0.1398 | 9 | 0.077 | 13.5 | 0.7 | 70000 | 1231000 | 1298000 | 12 | 17.5268 | 131 | 23.9 | 0 | 2086
0.1398 | 9 | 0.077 | 13.5 | 0.6 | 55000 | 1055000 | 1108000 | 12 | 16.9387 | 131 | 23.9 | 0 | 1659
0.1398 | 9 | 0.077 | 13.5 | 0.5 | 46000 | 879000 | 923000 | 12 | 16.3648 | 131 | 23.9 | 0 | 1376
0.1398 | 9 | 0.077 | 13.5 | 0.4 | 39000 | 703000 | 741000 | 12 | 15.7981 | 131 | 23.9 | 0 | 1163
0.1398 | 9 | 0.077 | 13.5 | 0.3 | 32000 | 527000 | 558000 | 12 | 15.2318 | 131 | 23.9 | 0 | 954
0.1398 | 9 | 0.077 | 13.5 | 0.2 | 26000 | 352000 | 377000 | 12 | 14.6685 | 131 | 23.9 | 0 | 776
0.1398 | 9 | 0.077 | 13.5 | 0.15 | 23000 | 264000 | 286000 | 12 | 14.3877 | 131 | 23.9 | 0 | 694
0.1398 | 9 | 0.077 | 13 | 1 | 152000 | 1758000 | 1905000 | 12 | 18.9085 | 131 | 23.9 | 0 | 4547
0.1398 | 9 | 0.077 | 13 | 0.9 | 111000 | 1582000 | 1690000 | 12 | 18.2413 | 131 | 23.9 | 0 | 3331
0.1398 | 9 | 0.077 | 13 | 0.8 | 87000 | 1406000 | 1491000 | 12 | 17.6242 | 131 | 23.9 | 0 | 2614
0.1398 | 9 | 0.077 | 13 | 0.7 | 67000 | 1231000 | 1296000 | 12 | 17.0189 | 131 | 23.9 | 0 | 2015
0.1398 | 9 | 0.077 | 13 | 0.6 | 54000 | 1055000 | 1107000 | 12 | 16.4345 | 131 | 23.9 | 0 | 1625
0.1398 | 9 | 0.077 | 13 | 0.5 | 45000 | 879000 | 923000 | 12 | 15.8627 | 131 | 23.9 | 0 | 1361
0.1398 | 9 | 0.077 | 13 | 0.4 | 38000 | 703000 | 740000 | 12 | 15.2949 | 131 | 23.9 | 0 | 1136
0.1398 | 9 | 0.077 | 13 | 0.3 | 31000 | 527000 | 558000 | 12 | 14.7299 | 131 | 23.9 | 0 | 939
0.1398 | 9 | 0.077 | 13 | 0.2 | 25000 | 352000 | 376000 | 12 | 14.167 | 131 | 23.9 | 0 | 763
0.1398 | 9 | 0.077 | 13 | 0.15 | 23000 | 264000 | 286000 | 12 | 13.8864 | 131 | 23.9 | 0 | 683
0.1398 | 9 | 0.077 | 12.5 | 1 | 0 | 1758000 | 0 | 12 | 0 | 131 | 23.9 | 0 | 0
0.1398 | 9 | 0.077 | 12.5 | 0.9 | 0 | 1582000 | 0 | 12 | 0 | 131 | 23.9 | 0 | 0
0.1398 | 9 | 0.077 | 12.5 | 0.8 | 85000 | 1406000 | 1489000 | 12 | 17.1164 | 131 | 23.9 | 0 | 2546
0.1398 | 9 | 0.077 | 12.5 | 0.7 | 65000 | 1231000 | 1294000 | 12 | 16.5111 | 131 | 23.9 | 0 | 1946
0.1398 | 9 | 0.077 | 12.5 | 0.6 | 53000 | 1055000 | 1106000 | 12 | 15.9306 | 131 | 23.9 | 0 | 1594
0.1398 | 9 | 0.077 | 12.5 | 0.5 | 44000 | 879000 | 922000 | 12 | 15.3594 | 131 | 23.9 | 0 | 1334
0.1398 | 9 | 0.077 | 12.5 | 0.4 | 37000 | 703000 | 739000 | 12 | 14.7926 | 131 | 23.9 | 0 | 1118
0.1398 | 9 | 0.077 | 12.5 | 0.3 | 31000 | 527000 | 557000 | 12 | 14.2281 | 131 | 23.9 | 0 | 924
0.1398 | 9 | 0.077 | 12.5 | 0.2 | 25000 | 352000 | 376000 | 12 | 13.6655 | 131 | 23.9 | 0 | 751
0.1398 | 9 | 0.077 | 12.5 | 0.15 | 22000 | 264000 | 285000 | 12 | 13.3851 | 131 | 23.9 | 0 | 673
0.1398 | 9 | 0.077 | 12 | 1 | 0 | 1758000 | 0 | 12 | 0 | 131 | 23.9 | 0 | 0
0.1398 | 9 | 0.077 | 12 | 0.9 | 0 | 1582000 | 0 | 12 | 0 | 131 | 23.9 | 0 | 0
0.1398 | 9 | 0.077 | 12 | 0.8 | 0 | 1406000 | 0 | 12 | 0 | 131 | 23.9 | 0 | 0
0.1398 | 9 | 0.077 | 12 | 0.7 | 0 | 1231000 | 0 | 12 | 0 | 131 | 23.9 | 0 | 0
0.1398 | 9 | 0.077 | 12 | 0.6 | 0 | 1055000 | 0 | 12 | 0 | 131 | 23.9 | 0 | 0
0.1398 | 9 | 0.077 | 12 | 0.5 | 0 | 879000 | 0 | 12 | 0 | 131 | 23.9 | 0 | 0
0.1398 | 9 | 0.077 | 12 | 0.4 | 0 | 703000 | 0 | 12 | 0 | 131 | 23.9 | 0 | 0
0.1398 | 9 | 0.077 | 12 | 0.3 | 0 | 527000 | 0 | 12 | 0 | 131 | 23.9 | 0 | 0
0.1398 | 9 | 0.077 | 12 | 0.2 | 25000 | 352000 | 376000 | 12 | 13.1642 | 131 | 23.9 | 0 | 740
0.1398 | 9 | 0.077 | 12 | 0.15 | 22000 | 264000 | 285000 | 12 | 12.8839 | 131 | 23.9 | 0 | 663
0.1398 | 9 | 0.115 | 30 | 1 | 257000 | 1758000 | 2007000 | 12 | 34.1942 | 131 | 49 | 0 | 7703
0.1398 | 9 | 0.115 | 30 | 0.9 | 222000 | 1582000 | 1797000 | 12 | 33.7556 | 131 | 49 | 0 | 6648
0.1398 | 9 | 0.115 | 30 | 0.8 | 191000 | 1406000 | 1592000 | 12 | 33.3266 | 131 | 49 | 0 | 5737
0.1398 | 9 | 0.115 | 30 | 0.7 | 164000 | 1231000 | 1390000 | 12 | 32.9046 | 131 | 49 | 0 | 4928
0.1398 | 9 | 0.115 | 30 | 0.6 | 141000 | 1055000 | 1191000 | 12 | 32.4895 | 131 | 49 | 0 | 4221
0.1398 | 9 | 0.115 | 30 | 0.5 | 123000 | 879000 | 998000 | 12 | 32.0865 | 131 | 49 | 0 | 3694
0.1398 | 9 | 0.115 | 30 | 0.4 | 103000 | 703000 | 803000 | 12 | 31.678 | 131 | 49 | 0 | 3086
0.1398 | 9 | 0.115 | 30 | 0.3 | 85000 | 527000 | 610000 | 12 | 31.2744 | 131 | 49 | 0 | 2550
0.1398 | 9 | 0.115 | 30 | 0.2 | 67000 | 352000 | 417000 | 12 | 30.8709 | 131 | 49 | 0 | 2015
0.1398 | 9 | 0.115 | 30 | 0.15 | 58000 | 264000 | 320000 | 12 | 30.668 | 131 | 49 | 0 | 1731
0.1398 | 9 | 0.115 | 27 | 1 | 227000 | 1758000 | 1979000 | 12 | 31.1304 | 131 | 49 | 0 | 6820
0.1398 | 9 | 0.115 | 27 | 0.9 | 196000 | 1582000 | 1772000 | 12 | 30.7001 | 131 | 49 | 0 | 5883
0.1398 | 9 | 0.115 | 27 | 0.8 | 167000 | 1406000 | 1569000 | 12 | 30.2751 | 131 | 49 | 0 | 5023
0.1398 | 9 | 0.115 | 27 | 0.7 | 142000 | 1231000 | 1368000 | 12 | 29.8567 | 131 | 49 | 0 | 4263
0.1398 | 9 | 0.115 | 27 | 0.6 | 120000 | 1055000 | 1172000 | 12 | 29.4456 | 131 | 49 | 0 | 3609
0.1398 | 9 | 0.115 | 27 | 0.5 | 102000 | 879000 | 978000 | 12 | 29.0408 | 131 | 49 | 0 | 3049
0.1398 | 9 | 0.115 | 27 | 0.4 | 89000 | 703000 | 789000 | 12 | 28.6477 | 131 | 49 | 0 | 2662
0.1398 | 9 | 0.115 | 27 | 0.3 | 72000 | 527000 | 597000 | 12 | 28.246 | 131 | 49 | 0 | 2148
0.1398 | 9 | 0.115 | 27 | 0.2 | 57000 | 352000 | 407000 | 12 | 27.8489 | 131 | 49 | 0 | 1702
0.1398 | 9 | 0.115 | 27 | 0.15 | 49000 | 264000 | 311000 | 12 | 27.6495 | 131 | 49 | 0 | 1467
0.1398 | 9 | 0.115 | 24 | 1 | 202000 | 1758000 | 1954000 | 12 | 28.0745 | 131 | 49 | 0 | 6056
0.1398 | 9 | 0.115 | 24 | 0.9 | 171000 | 1582000 | 1748000 | 12 | 27.6461 | 131 | 49 | 0 | 5140
0.1398 | 9 | 0.115 | 24 | 0.8 | 145000 | 1406000 | 1547000 | 12 | 27.2262 | 131 | 49 | 0 | 4348
0.1398 | 9 | 0.115 | 24 | 0.7 | 122000 | 1231000 | 1349000 | 12 | 26.8126 | 131 | 49 | 0 | 3652
0.1398 | 9 | 0.115 | 24 | 0.6 | 102000 | 1055000 | 1154000 | 12 | 26.4057 | 131 | 49 | 0 | 3054
0.1398 | 9 | 0.115 | 24 | 0.5 | 85000 | 879000 | 961000 | 12 | 26.0051 | 131 | 49 | 0 | 2550
0.1398 | 9 | 0.115 | 24 | 0.4 | 70000 | 703000 | 771000 | 12 | 25.6087 | 131 | 49 | 0 | 2110
0.1398 | 9 | 0.115 | 24 | 0.3 | 61000 | 527000 | 587000 | 12 | 25.2236 | 131 | 49 | 0 | 1835
0.1398 | 9 | 0.115 | 24 | 0.2 | 47000 | 352000 | 397000 | 12 | 24.8284 | 131 | 49 | 0 | 1411
0.1398 | 9 | 0.115 | 24 | 0.15 | 41000 | 264000 | 303000 | 12 | 24.6323 | 131 | 49 | 0 | 1221
0.1398 | 9 | 0.115 | 21 | 1 | 178000 | 1758000 | 1931000 | 12 | 25.0217 | 131 | 49 | 0 | 5336
0.1398 | 9 | 0.115 | 21 | 0.9 | 149000 | 1582000 | 1727000 | 12 | 24.5971 | 131 | 49 | 0 | 4469
0.1398 | 9 | 0.115 | 21 | 0.8 | 125000 | 1406000 | 1527000 | 12 | 24.1815 | 131 | 49 | 0 | 3737
0.1398 | 9 | 0.115 | 21 | 0.7 | 103000 | 1231000 | 1331000 | 12 | 23.7724 | 131 | 49 | 0 | 3100
0.1398 | 9 | 0.115 | 21 | 0.6 | 85000 | 1055000 | 1137000 | 12 | 23.3687 | 131 | 49 | 0 | 2544
0.1398 | 9 | 0.115 | 21 | 0.5 | 70000 | 879000 | 947000 | 12 | 22.9728 | 131 | 49 | 0 | 2103
0.1398 | 9 | 0.115 | 21 | 0.4 | 57000 | 703000 | 759000 | 12 | 22.5811 | 131 | 49 | 0 | 1725
0.1398 | 9 | 0.115 | 21 | 0.3 | 49000 | 527000 | 575000 | 12 | 22.1986 | 131 | 49 | 0 | 1483
0.1398 | 9 | 0.115 | 21 | 0.2 | 38000 | 352000 | 389000 | 12 | 21.8096 | 131 | 49 | 0 | 1146
0.1398 | 9 | 0.115 | 21 | 0.15 | 33000 | 264000 | 296000 | 12 | 21.6165 | 131 | 49 | 0 | 997
0.1398 | 9 | 0.115 | 18 | 1 | 160000 | 1758000 | 1913000 | 12 | 21.9805 | 131 | 49 | 0 | 4790
0.1398 | 9 | 0.115 | 18 | 0.9 | 130000 | 1582000 | 1708000 | 12 | 21.5548 | 131 | 49 | 0 | 3900
0.1398 | 9 | 0.115 | 18 | 0.8 | 106000 | 1406000 | 1509000 | 12 | 21.1408 | 131 | 49 | 0 | 3184
0.1398 | 9 | 0.115 | 18 | 0.7 | 86000 | 1231000 | 1314000 | 12 | 20.7343 | 131 | 49 | 0 | 2580
0.1398 | 9 | 0.115 | 18 | 0.6 | 70000 | 1055000 | 1122000 | 12 | 20.3353 | 131 | 49 | 0 | 2086
0.1398 | 9 | 0.115 | 18 | 0.5 | 57000 | 879000 | 934000 | 12 | 19.9433 | 131 | 49 | 0 | 1697
0.1398 | 9 | 0.115 | 18 | 0.4 | 47000 | 703000 | 749000 | 12 | 19.5578 | 131 | 49 | 0 | 1405
0.1398 | 9 | 0.115 | 18 | 0.3 | 39000 | 527000 | 565000 | 12 | 19.1754 | 131 | 49 | 0 | 1158
0.1398 | 9 | 0.115 | 18 | 0.2 | 31000 | 352000 | 382000 | 12 | 18.7951 | 131 | 49 | 0 | 943
0.1398 | 9 | 0.115 | 18 | 0.15 | 27000 | 264000 | 290000 | 12 | 18.6029 | 131 | 49 | 0 | 806
0.1398 | 9 | 0.115 | 17.5 | 1 | 157000 | 1758000 | 1911000 | 12 | 21.4751 | 131 | 49 | 0 | 4722
0.1398 | 9 | 0.115 | 17.5 | 0.9 | 127000 | 1582000 | 1705000 | 12 | 21.0482 | 131 | 49 | 0 | 3813
0.1398 | 9 | 0.115 | 17.5 | 0.8 | 103000 | 1406000 | 1507000 | 12 | 20.6344 | 131 | 49 | 0 | 3098
0.1398 | 9 | 0.115 | 17.5 | 0.7 | 83000 | 1231000 | 1311000 | 12 | 20.2285 | 131 | 49 | 0 | 2501
0.1398 | 9 | 0.115 | 17.5 | 0.6 | 67000 | 1055000 | 1120000 | 12 | 19.83 | 131 | 49 | 0 | 2014
0.1398 | 9 | 0.115 | 17.5 | 0.5 | 55000 | 879000 | 932000 | 12 | 19.4388 | 131 | 49 | 0 | 1636
0.1398 | 9 | 0.115 | 17.5 | 0.4 | 45000 | 703000 | 747000 | 12 | 19.0543 | 131 | 49 | 0 | 1357
0.1398 | 9 | 0.115 | 17.5 | 0.3 | 37000 | 527000 | 564000 | 12 | 18.6724 | 131 | 49 | 0 | 1117
0.1398 | 9 | 0.115 | 17.5 | 0.2 | 30000 | 352000 | 381000 | 12 | 18.2927 | 131 | 49 | 0 | 910
0.1398 | 9 | 0.115 | 17.5 | 0.15 | 26000 | 264000 | 289000 | 12 | 18.1015 | 131 | 49 | 0 | 786
0.1398 | 9 | 0.115 | 17 | 1 | 155000 | 1758000 | 1909000 | 12 | 20.9698 | 131 | 49 | 0 | 4655
0.1398 | 9 | 0.115 | 17 | 0.9 | 124000 | 1582000 | 1703000 | 12 | 20.5417 | 131 | 49 | 0 | 3726
0.1398 | 9 | 0.115 | 17 | 0.8 | 101000 | 1406000 | 1504000 | 12 | 20.1283 | 131 | 49 | 0 | 3016
0.1398 | 9 | 0.115 | 17 | 0.7 | 81000 | 1231000 | 1309000 | 12 | 19.7228 | 131 | 49 | 0 | 2424
0.1398 | 9 | 0.115 | 17 | 0.6 | 65000 | 1055000 | 1118000 | 12 | 19.3247 | 131 | 49 | 0 | 1943
0.1398 | 9 | 0.115 | 17 | 0.5 | 53000 | 879000 | 930000 | 12 | 18.9344 | 131 | 49 | 0 | 1576
0.1398 | 9 | 0.115 | 17 | 0.4 | 44000 | 703000 | 746000 | 12 | 18.551 | 131 | 49 | 0 | 1313
0.1398 | 9 | 0.115 | 17 | 0.3 | 36000 | 527000 | 562000 | 12 | 18.17 | 131 | 49 | 0 | 1085
0.1398 | 9 | 0.115 | 17 | 0.2 | 29000 | 352000 | 380000 | 12 | 17.7909 | 131 | 49 | 0 | 885
0.1398 | 9 | 0.115 | 17 | 0.15 | 27000 | 264000 | 289000 | 12 | 17.6021 | 131 | 49 | 0 | 796
0.1398 | 9 | 0.115 | 16.5 | 1 | 153000 | 1758000 | 1906000 | 12 | 20.4644 | 131 | 49 | 0 | 4586
0.1398 | 9 | 0.115 | 16.5 | 0.9 | 121000 | 1582000 | 1700000 | 12 | 20.0354 | 131 | 49 | 0 | 3643
0.1398 | 9 | 0.115 | 16.5 | 0.8 | 98000 | 1406000 | 1501000 | 12 | 19.6223 | 131 | 49 | 0 | 2936
0.1398 | 9 | 0.115 | 16.5 | 0.7 | 78000 | 1231000 | 1307000 | 12 | 19.2172 | 131 | 49 | 0 | 2348
0.1398 | 9 | 0.115 | 16.5 | 0.6 | 63000 | 1055000 | 1116000 | 12 | 18.8202 | 131 | 49 | 0 | 1882
0.1398 | 9 | 0.115 | 16.5 | 0.5 | 51000 | 879000 | 928000 | 12 | 18.4308 | 131 | 49 | 0 | 1528
0.1398 | 9 | 0.115 | 16.5 | 0.4 | 42000 | 703000 | 744000 | 12 | 18.0481 | 131 | 49 | 0 | 1274
0.1398 | 9 | 0.115 | 16.5 | 0.3 | 35000 | 527000 | 562000 | 12 | 17.6679 | 131 | 49 | 0 | 1058
0.1398 | 9 | 0.115 | 16.5 | 0.2 | 29000 | 352000 | 379000 | 12 | 17.2892 | 131 | 49 | 0 | 862
0.1398 | 9 | 0.115 | 16.5 | 0.15 | 26000 | 264000 | 289000 | 12 | 17.1003 | 131 | 49 | 0 | 772
0.1398 | 9 | 0.115 | 16 | 1 | 151000 | 1758000 | 1904000 | 12 | 19.9589 | 131 | 49 | 0 | 4515
0.1398 | 9 | 0.115 | 16 | 0.9 | 119000 | 1582000 | 1697000 | 12 | 19.5294 | 131 | 49 | 0 | 3564
0.1398 | 9 | 0.115 | 16 | 0.8 | 95000 | 1406000 | 1499000 | 12 | 19.1165 | 131 | 49 | 0 | 2859
0.1398 | 9 | 0.115 | 16 | 0.7 | 76000 | 1231000 | 1304000 | 12 | 18.7117 | 131 | 49 | 0 | 2275
0.1398 | 9 | 0.115 | 16 | 0.6 | 60000 | 1055000 | 1113000 | 12 | 18.315 | 131 | 49 | 0 | 1812
0.1398 | 9 | 0.115 | 16 | 0.5 | 50000 | 879000 | 927000 | 12 | 17.9276 | 131 | 49 | 0 | 1486
0.1398 | 9 | 0.115 | 16 | 0.4 | 42000 | 703000 | 744000 | 12 | 17.546 | 131 | 49 | 0 | 1248
0.1398 | 9 | 0.115 | 16 | 0.3 | 34000 | 527000 | 561000 | 12 | 17.1661 | 131 | 49 | 0 | 1033
0.1398 | 9 | 0.115 | 16 | 0.2 | 28000 | 352000 | 379000 | 12 | 16.7877 | 131 | 49 | 0 | 842
0.1398 | 9 | 0.115 | 16 | 0.15 | 25000 | 264000 | 288000 | 12 | 16.599 | 131 | 49 | 0 | 753
0.1398 | 9 | 0.115 | 15.5 | 1 | 148000 | 1758000 | 1902000 | 12 | 19.4533 | 131 | 49 | 0 | 4443
0.1398 | 9 | 0.115 | 15.5 | 0.9 | 116000 | 1582000 | 1695000 | 12 | 19.0236 | 131 | 49 | 0 | 3488
0.1398 | 9 | 0.115 | 15.5 | 0.8 | 93000 | 1406000 | 1496000 | 12 | 18.6108 | 131 | 49 | 0 | 2783
0.1398 | 9 | 0.115 | 15.5 | 0.7 | 73000 | 1231000 | 1302000 | 12 | 18.2062 | 131 | 49 | 0 | 2201
0.1398 | 9 | 0.115 | 15.5 | 0.6 | 59000 | 1055000 | 1112000 | 12 | 17.8113 | 131 | 49 | 0 | 1764
0.1398 | 9 | 0.115 | 15.5 | 0.5 | 48000 | 879000 | 926000 | 12 | 17.4247 | 131 | 49 | 0 | 1449
0.1398 | 9 | 0.115 | 15.5 | 0.4 | 40000 | 703000 | 742000 | 12 | 17.0435 | 131 | 49 | 0 | 1215
0.1398 | 9 | 0.115 | 15.5 | 0.3 | 34000 | 527000 | 560000 | 12 | 16.6644 | 131 | 49 | 0 | 1012
0.1398 | 9 | 0.115 | 15.5 | 0.2 | 27000 | 352000 | 378000 | 12 | 16.2864 | 131 | 49 | 0 | 825
0.1398 | 9 | 0.115 | 15.5 | 0.15 | 25000 | 264000 | 288000 | 12 | 16.0979 | 131 | 49 | 0 | 739
0.1398 | 9 | 0.115 | 15 | 1 | 154000 | 1758000 | 1907000 | 12 | 18.9642 | 131 | 49 | 0 | 4618
0.1398 | 9 | 0.115 | 15 | 0.9 | 114000 | 1582000 | 1693000 | 12 | 18.5181 | 131 | 49 | 0 | 3417
0.1398 | 9 | 0.115 | 15 | 0.8 | 90000 | 1406000 | 1494000 | 12 | 18.1053 | 131 | 49 | 0 | 2712
0.1398 | 9 | 0.115 | 15 | 0.7 | 71000 | 1231000 | 1299000 | 12 | 17.7008 | 131 | 49 | 0 | 2129
0.1398 | 9 | 0.115 | 15 | 0.6 | 57000 | 1055000 | 1110000 | 12 | 17.3067 | 131 | 49 | 0 | 1701
0.1398 | 9 | 0.115 | 15 | 0.5 | 47000 | 879000 | 925000 | 12 | 16.9221 | 131 | 49 | 0 | 1415
0.1398 | 9 | 0.115 | 15 | 0.4 | 40000 | 703000 | 742000 | 12 | 16.5418 | 131 | 49 | 0 | 1195
0.1398 | 9 | 0.115 | 15 | 0.3 | 33000 | 527000 | 559000 | 12 | 16.1626 | 131 | 49 | 0 | 989
0.1398 | 9 | 0.115 | 15 | 0.2 | 27000 | 352000 | 378000 | 12 | 15.7851 | 131 | 49 | 0 | 808
0.1398 | 9 | 0.115 | 15 | 0.15 | 24000 | 264000 | 287000 | 12 | 15.5968 | 131 | 49 | 0 | 725
0.1398 | 9 | 0.115 | 14.5 | 1 | 156000 | 1758000 | 1909000 | 12 | 18.4667 | 131 | 49 | 0 | 4667
0.1398 | 9 | 0.115 | 14.5 | 0.9 | 112000 | 1582000 | 1691000 | 12 | 18.0132 | 131 | 49 | 0 | 3354
0.1398 | 9 | 0.115 | 14.5 | 0.8 | 88000 | 1406000 | 1492000 | 12 | 17.5999 | 131 | 49 | 0 | 2640
0.1398 | 9 | 0.115 | 14.5 | 0.7 | 69000 | 1231000 | 1297000 | 12 | 17.1955 | 131 | 49 | 0 | 2058
0.1398 | 9 | 0.115 | 14.5 | 0.6 | 55000 | 1055000 | 1109000 | 12 | 16.8037 | 131 | 49 | 0 | 1664
0.1398 | 9 | 0.115 | 14.5 | 0.5 | 46000 | 879000 | 924000 | 12 | 16.4196 | 131 | 49 | 0 | 1384
0.1398 | 9 | 0.115 | 14.5 | 0.4 | 39000 | 703000 | 741000 | 12 | 16.0395 | 131 | 49 | 0 | 1165
0.1398 | 9 | 0.115 | 14.5 | 0.3 | 32000 | 527000 | 559000 | 12 | 15.6612 | 131 | 49 | 0 | 971
0.1398 | 9 | 0.115 | 14.5 | 0.2 | 26000 | 352000 | 377000 | 12 | 15.2839 | 131 | 49 | 0 | 793
0.1398 | 9 | 0.115 | 14.5 | 0.15 | 24000 | 264000 | 287000 | 12 | 15.0958 | 131 | 49 | 0 | 711
0.1398 | 9 | 0.115 | 14 | 1 | 0 | 1758000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 14 | 0.9 | 0 | 1582000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 14 | 0.8 | 86000 | 1406000 | 1490000 | 12 | 17.0947 | 131 | 49 | 0 | 2573
0.1398 | 9 | 0.115 | 14 | 0.7 | 66000 | 1231000 | 1295000 | 12 | 16.6902 | 131 | 49 | 0 | 1988
0.1398 | 9 | 0.115 | 14 | 0.6 | 54000 | 1055000 | 1107000 | 12 | 16.3009 | 131 | 49 | 0 | 1629
0.1398 | 9 | 0.115 | 14 | 0.5 | 46000 | 879000 | 923000 | 12 | 15.9181 | 131 | 49 | 0 | 1368
0.1398 | 9 | 0.115 | 14 | 0.4 | 38000 | 703000 | 740000 | 12 | 15.538 | 131 | 49 | 0 | 1148
0.1398 | 9 | 0.115 | 14 | 0.3 | 32000 | 527000 | 558000 | 12 | 15.1598 | 131 | 49 | 0 | 954
0.1398 | 9 | 0.115 | 14 | 0.2 | 26000 | 352000 | 377000 | 12 | 14.7828 | 131 | 49 | 0 | 779
0.1398 | 9 | 0.115 | 14 | 0.15 | 23000 | 264000 | 286000 | 12 | 14.5948 | 131 | 49 | 0 | 699
0.1398 | 9 | 0.115 | 13.5 | 1 | 0 | 1758000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 13.5 | 0.9 | 0 | 1582000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 13.5 | 0.8 | 0 | 1406000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 13.5 | 0.7 | 0 | 1231000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 13.5 | 0.6 | 53000 | 1055000 | 1106000 | 12 | 15.7983 | 131 | 49 | 0 | 1598
0.1398 | 9 | 0.115 | 13.5 | 0.5 | 45000 | 879000 | 922000 | 12 | 15.4159 | 131 | 49 | 0 | 1341
0.1398 | 9 | 0.115 | 13.5 | 0.4 | 38000 | 703000 | 740000 | 12 | 15.0365 | 131 | 49 | 0 | 1129
0.1398 | 9 | 0.115 | 13.5 | 0.3 | 31000 | 527000 | 558000 | 12 | 14.6585 | 131 | 49 | 0 | 938
0.1398 | 9 | 0.115 | 13.5 | 0.2 | 26000 | 352000 | 376000 | 12 | 14.2818 | 131 | 49 | 0 | 766
0.1398 | 9 | 0.115 | 13.5 | 0.15 | 23000 | 264000 | 286000 | 12 | 14.0939 | 131 | 49 | 0 | 688
0.1398 | 9 | 0.115 | 13 | 1 | 0 | 1758000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 13 | 0.9 | 0 | 1582000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 13 | 0.8 | 0 | 1406000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 13 | 0.7 | 0 | 1231000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 13 | 0.6 | 0 | 1055000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 13 | 0.5 | 0 | 879000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 13 | 0.4 | 37000 | 703000 | 739000 | 12 | 14.535 | 131 | 49 | 0 | 1111
0.1398 | 9 | 0.115 | 13 | 0.3 | 31000 | 527000 | 557000 | 12 | 14.1572 | 131 | 49 | 0 | 923
0.1398 | 9 | 0.115 | 13 | 0.2 | 25000 | 352000 | 376000 | 12 | 13.7808 | 131 | 49 | 0 | 754
0.1398 | 9 | 0.115 | 13 | 0.15 | 23000 | 264000 | 286000 | 12 | 13.5931 | 131 | 49 | 0 | 677
0.1398 | 9 | 0.115 | 12.5 | 1 | 0 | 1758000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 12.5 | 0.9 | 0 | 1582000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 12.5 | 0.8 | 0 | 1406000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 12.5 | 0.7 | 0 | 1231000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 12.5 | 0.6 | 0 | 1055000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 12.5 | 0.5 | 0 | 879000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 12.5 | 0.4 | 0 | 703000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 12.5 | 0.3 | 0 | 527000 | 0 | 12 | 0 | 131 | 49 | 0 | 0
0.1398 | 9 | 0.115 | 12.5 | 0.2 | 25000 | 352000 | 376000 | 12 | 13.2798 | 131 | 49 | 0 | 742
0.1398 | 9 | 0.115 | 12.5 | 0.15 | 22000 | 264000 | 285000 | 12 | 13.0923 | 131 | 49 | 0 | 667

## PerformanceMapStandby
chillerEnvironmentalDryBulbTemperature | inputPower
C | W
7 | 2000
25 | 1500
45 | 1500