## Instructions
This spreadsheet serves as a template for ASHRAE Standard 205 compliant representations corresponding to RS0002 "Unitary Cooling Air-Conditioning Equipment".
General Instructions:
Only the names and values are read out of this sheet using the SI-unit system defined in the standard. Any other columns are for user-information only.
Do not change Data Group, Data Element, or sheet names. These are used to translate the spreadsheet into simulation data.
If data group is not required, it's required elements are only required if the data group is present
RSID, RSVersion, and RSTitle should not be changed (they are set by the schema associated with this template).
Performance maps and array data groups each have separate sheets to enable an extensible number of entries in consecutive rows.
Performance map grid variables are colored in blue and must be entered in the order defined by the standard (with the rightmost column varying with the highest frequency)
The structure of the data here does not necessarily reflect the actual hierarchical data structure as defined in the standard. It has been modified for user readability, but contains all necessary data elements for simulation purposes.
This instruction sheet is informative only. It may be removed once data entry is complete.

## RS0002
Data Group | Data Element | Value | Units | Required?
ASHRAE205 |  |  |  | Yes
| RSID | RS0002 |  | Yes
| RSVersion | 0.1.0 |  | Yes
| RSTitle | Unitary Cooling Air-Conditioning Equipment |  | Yes
| ID | UID123456789 |  | Yes
| dataTimeStamp | 2019-02-07 10:10 |  | Yes
| dataVersion | A205DV-1
| description | Variable Speed Air Conditioner
| dataSource | ACSelect
notes
Description/ProductInformation
| outdoorUnitManufacturer | ColdAirInc |  | Yes
| outdoorUnitModelNumber | AC.2019.01 |  | Yes
| indoorUnitManufacturer | ColdAirInc
| indoorUnitModelNumber | AC.2019.02
| refrigerantType | R410A
| compressorType | Variable Speed Scroll
Description/RatingAHRI210240
| certifiedReferenceNumber | 456789 |  | Yes
| testStandardYear | 2017 |  | Yes
| manufacturerDataSourceVersion | 1.1.0 |  | Yes
| SEER | 22.5 | Btu/W-h | Yes
| EER | 14.5 | Btu/W-h | Yes
| capacity | 35600 | Btu/h | Yes
| ratingFanPowerPerFlow |  | W/(m3/s)
Description/RatingAHRI340360
| certifiedReferenceNumber |  |  | Yes
| testStandardYear |  |  | Yes
| manufacturerDataSourceVersion |  |  | Yes
| IEER |  | Btu/W-h | Yes
| EER |  | Btu/W-h | Yes
| capacity |  | Btu/h | Yes
| ratingFanPowerPerFlow |  | W/(m3/s)
Performance |  |  |  | Yes
| compressorControlMethod | Dynamic |  | Yes
fanRS
| fanPosition | BlowThrough |  | Yes
| nominalVolumetricAirFlowRate | 0.59 | m3/s | Yes
| cyclingDegradationCoefficient | 0.25 |  | Yes

## PerformanceMapCooling
outdoorCoilEnteringDryBulbTemperature | indoorCoilEnteringWetBulbTemperature | indoorCoilEnteringDryBulbTemperature | indoorCoilVolumetricFlowRatio | compressorSpeedRatio | ambientAbsoluteAirPressure | grossTotalCoolingCapacity | grossSensibleCoolingCapacity | grossCoolingPower
°C | °C | °C | L/s |  | Pa | W | W | W
29.4 | 15 | 24 | 413 | 1 | 101.325 | 9.3 | 8.277 | 1.79
29.4 | 15 | 27 | 413 | 1 | 101.325 | 9.3 | 9.3 | 1.79
29.4 | 15 | 29 | 413 | 1 | 101.325 | 9.3 | 9.3 | 1.79
29.4 | 15 | 24 | 590 | 1 | 101.325 | 10.5 | 10.5 | 1.75
29.4 | 15 | 27 | 590 | 1 | 101.325 | 10.5 | 10.5 | 1.75
29.4 | 15 | 29 | 590 | 1 | 101.325 | 10.5 | 10.5 | 1.75
29.4 | 15 | 24 | 637 | 1 | 101.325 | 10.8 | 10.8 | 1.73
29.4 | 15 | 27 | 637 | 1 | 101.325 | 10.8 | 10.8 | 1.73
29.4 | 15 | 29 | 637 | 1 | 101.325 | 10.8 | 10.8 | 1.73
35 | 15 | 24 | 413 | 1 | 101.325 | 9 | 8.19 | 2.08
35 | 15 | 27 | 413 | 1 | 101.325 | 9 | 9 | 2.08
35 | 15 | 29 | 413 | 1 | 101.325 | 9 | 9 | 2.08
35 | 15 | 24 | 590 | 1 | 101.325 | 10.1 | 10.1 | 2.04
35 | 15 | 27 | 590 | 1 | 101.325 | 10.1 | 10.1 | 2.04
35 | 15 | 29 | 590 | 1 | 101.325 | 10.1 | 10.1 | 2.04
35 | 15 | 24 | 637 | 1 | 101.325 | 10.4 | 10.4 | 2.02
35 | 15 | 27 | 637 | 1 | 101.325 | 10.4 | 10.4 | 2.02
35 | 15 | 29 | 637 | 1 | 101.325 | 10.4 | 10.4 | 2.02
40.6 | 15 | 24 | 413 | 1 | 101.325 | 8.6 | 7.998 | 2.38
40.6 | 15 | 27 | 413 | 1 | 101.325 | 8.6 | 8.6 | 2.38
40.6 | 15 | 29 | 413 | 1 | 101.325 | 8.6 | 8.6 | 2.38
40.6 | 15 | 24 | 590 | 1 | 101.325 | 8.6 | 8.6 | 2.34
40.6 | 15 | 27 | 590 | 1 | 101.325 | 8.6 | 8.6 | 2.34
40.6 | 15 | 29 | 590 | 1 | 101.325 | 8.6 | 8.6 | 2.34
40.6 | 15 | 24 | 637 | 1 | 101.325 | 8.6 | 8.6 | 2.33
40.6 | 15 | 27 | 637 | 1 | 101.325 | 8.6 | 8.6 | 2.33
40.6 | 15 | 29 | 637 | 1 | 101.325 | 8.6 | 8.6 | 2.33
46.1 | 15 | 24 | 413 | 1 | 101.325 | 8.2 | 7.872 | 2.72
46.1 | 15 | 27 | 413 | 1 | 101.325 | 8.2 | 8.2 | 2.72
46.1 | 15 | 29 | 413 | 1 | 101.325 | 8.2 | 8.2 | 2.72
46.1 | 15 | 24 | 590 | 1 | 101.325 | 9.2 | 9.2 | 2.67
46.1 | 15 | 27 | 590 | 1 | 101.325 | 9.2 | 9.2 | 2.67
46.1 | 15 | 29 | 590 | 1 | 101.325 | 9.2 | 9.2 | 2.67
46.1 | 15 | 24 | 637 | 1 | 101.325 | 9.4 | 9.4 | 2.66
46.1 | 15 | 27 | 637 | 1 | 101.325 | 9.4 | 9.4 | 2.66
46.1 | 15 | 29 | 637 | 1 | 101.325 | 9.4 | 9.4 | 2.66
29.4 | 17.2 | 24 | 413 | 1 | 101.325 | 9.8 | 7.154 | 1.77
29.4 | 17.2 | 27 | 413 | 1 | 101.325 | 9.8 | 8.428 | 1.77
29.4 | 17.2 | 29 | 413 | 1 | 101.325 | 9.8 | 9.604 | 1.77
29.4 | 17.2 | 24 | 590 | 1 | 101.325 | 10.7 | 8.667 | 1.74
29.4 | 17.2 | 27 | 590 | 1 | 101.325 | 10.7 | 10.379 | 1.74
29.4 | 17.2 | 29 | 590 | 1 | 101.325 | 10.7 | 10.7 | 1.74
29.4 | 17.2 | 24 | 637 | 1 | 101.325 | 10.8 | 9.072 | 1.73
29.4 | 17.2 | 27 | 637 | 1 | 101.325 | 10.8 | 10.692 | 1.73
29.4 | 17.2 | 29 | 637 | 1 | 101.325 | 10.8 | 10.8 | 1.73
35 | 17.2 | 24 | 413 | 1 | 101.325 | 9.4 | 6.956 | 2.06
35 | 17.2 | 27 | 413 | 1 | 101.325 | 9.4 | 8.272 | 2.06
35 | 17.2 | 29 | 413 | 1 | 101.325 | 9.4 | 9.4 | 2.06
35 | 17.2 | 24 | 590 | 1 | 101.325 | 10.1 | 8.383 | 2.03
35 | 17.2 | 27 | 590 | 1 | 101.325 | 10.1 | 9.999 | 2.03
35 | 17.2 | 29 | 590 | 1 | 101.325 | 10.1 | 10.1 | 2.03
35 | 17.2 | 24 | 637 | 1 | 101.325 | 10.4 | 8.944 | 2.02
35 | 17.2 | 27 | 637 | 1 | 101.325 | 10.4 | 10.4 | 2.02
35 | 17.2 | 29 | 637 | 1 | 101.325 | 10.4 | 10.4 | 2.02
40.6 | 17.2 | 24 | 413 | 1 | 101.325 | 8.9 | 6.764 | 2.37
40.6 | 17.2 | 27 | 413 | 1 | 101.325 | 8.9 | 8.01 | 2.37
40.6 | 17.2 | 29 | 413 | 1 | 101.325 | 8.9 | 8.9 | 2.37
40.6 | 17.2 | 24 | 590 | 1 | 101.325 | 8.9 | 7.565 | 2.34
40.6 | 17.2 | 27 | 590 | 1 | 101.325 | 8.9 | 8.9 | 2.34
40.6 | 17.2 | 29 | 590 | 1 | 101.325 | 8.9 | 8.9 | 2.34
40.6 | 17.2 | 24 | 637 | 1 | 101.325 | 8.9 | 7.832 | 2.33
40.6 | 17.2 | 27 | 637 | 1 | 101.325 | 8.9 | 8.9 | 2.33
40.6 | 17.2 | 29 | 637 | 1 | 101.325 | 8.9 | 8.9 | 2.33
46.1 | 17.2 | 24 | 413 | 1 | 101.325 | 8.4 | 6.468 | 2.71
46.1 | 17.2 | 27 | 413 | 1 | 101.325 | 8.4 | 7.728 | 2.71
46.1 | 17.2 | 29 | 413 | 1 | 101.325 | 8.4 | 8.4 | 2.71
46.1 | 17.2 | 24 | 590 | 1 | 101.325 | 9.2 | 8.004 | 2.67
46.1 | 17.2 | 27 | 590 | 1 | 101.325 | 9.2 | 9.2 | 2.67
46.1 | 17.2 | 29 | 590 | 1 | 101.325 | 9.2 | 9.2 | 2.67
46.1 | 17.2 | 24 | 637 | 1 | 101.325 | 9.4 | 8.554 | 2.66
46.1 | 17.2 | 27 | 637 | 1 | 101.325 | 9.4 | 9.4 | 2.66
46.1 | 17.2 | 29 | 637 | 1 | 101.325 | 9.4 | 9.4 | 2.66
29.4 | 19.4 | 24 | 413 | 1 | 101.325 | 10.4 | 6.032 | 1.75
29.4 | 19.4 | 27 | 413 | 1 | 101.325 | 10.4 | 7.28 | 1.75
29.4 | 19.4 | 29 | 413 | 1 | 101.325 | 10.4 | 8.528 | 1.75
29.4 | 19.4 | 24 | 590 | 1 | 101.325 | 11.3 | 7.119 | 1.71
29.4 | 19.4 | 27 | 590 | 1 | 101.325 | 11.3 | 8.927 | 1.71
29.4 | 19.4 | 29 | 590 | 1 | 101.325 | 11.3 | 10.509 | 1.71
29.4 | 19.4 | 24 | 637 | 1 | 101.325 | 11.4 | 7.41 | 1.7
29.4 | 19.4 | 27 | 637 | 1 | 101.325 | 11.4 | 9.234 | 1.7
29.4 | 19.4 | 29 | 637 | 1 | 101.325 | 11.4 | 10.944 | 1.7
35 | 19.4 | 24 | 413 | 1 | 101.325 | 10 | 5.9 | 2.03
35 | 19.4 | 27 | 413 | 1 | 101.325 | 10 | 7.2 | 2.03
35 | 19.4 | 29 | 413 | 1 | 101.325 | 10 | 8.4 | 2.03
35 | 19.4 | 24 | 590 | 1 | 101.325 | 10.7 | 6.955 | 2.01
35 | 19.4 | 27 | 590 | 1 | 101.325 | 10.7 | 8.667 | 2.01
35 | 19.4 | 29 | 590 | 1 | 101.325 | 10.7 | 10.272 | 2.01
35 | 19.4 | 24 | 637 | 1 | 101.325 | 10.9 | 7.194 | 1.99
35 | 19.4 | 27 | 637 | 1 | 101.325 | 10.9 | 9.047 | 1.99
35 | 19.4 | 29 | 637 | 1 | 101.325 | 10.9 | 10.791 | 1.99
40.6 | 19.4 | 24 | 413 | 1 | 101.325 | 9.5 | 5.7 | 2.35
40.6 | 19.4 | 27 | 413 | 1 | 101.325 | 9.5 | 6.935 | 2.35
40.6 | 19.4 | 29 | 413 | 1 | 101.325 | 9.5 | 8.17 | 2.35
40.6 | 19.4 | 24 | 590 | 1 | 101.325 | 9.5 | 6.27 | 2.31
40.6 | 19.4 | 27 | 590 | 1 | 101.325 | 9.5 | 7.885 | 2.31
40.6 | 19.4 | 29 | 590 | 1 | 101.325 | 9.5 | 9.31 | 2.31
40.6 | 19.4 | 24 | 637 | 1 | 101.325 | 9.5 | 6.46 | 2.31
40.6 | 19.4 | 27 | 637 | 1 | 101.325 | 9.5 | 8.17 | 2.31
40.6 | 19.4 | 29 | 637 | 1 | 101.325 | 9.5 | 9.5 | 2.31
46.1 | 19.4 | 24 | 413 | 1 | 101.325 | 9 | 5.49 | 2.68
46.1 | 19.4 | 27 | 413 | 1 | 101.325 | 9 | 6.75 | 2.68
46.1 | 19.4 | 29 | 413 | 1 | 101.325 | 9 | 8.01 | 2.68
46.1 | 19.4 | 24 | 590 | 1 | 101.325 | 9.7 | 6.499 | 2.65
46.1 | 19.4 | 27 | 590 | 1 | 101.325 | 9.7 | 8.245 | 2.65
46.1 | 19.4 | 29 | 590 | 1 | 101.325 | 9.7 | 9.7 | 2.65
46.1 | 19.4 | 24 | 637 | 1 | 101.325 | 9.8 | 6.762 | 2.64
46.1 | 19.4 | 27 | 637 | 1 | 101.325 | 9.8 | 8.624 | 2.64
46.1 | 19.4 | 29 | 637 | 1 | 101.325 | 9.8 | 9.8 | 2.64
29.4 | 21.7 | 24 | 413 | 1 | 101.325 | 11 | 4.95 | 1.72
29.4 | 21.7 | 27 | 413 | 1 | 101.325 | 11 | 6.27 | 1.72
29.4 | 21.7 | 29 | 413 | 1 | 101.325 | 11 | 7.48 | 1.72
29.4 | 21.7 | 24 | 590 | 1 | 101.325 | 11.9 | 5.712 | 1.68
29.4 | 21.7 | 27 | 590 | 1 | 101.325 | 11.9 | 7.378 | 1.68
29.4 | 21.7 | 29 | 590 | 1 | 101.325 | 11.9 | 9.044 | 1.68
29.4 | 21.7 | 24 | 637 | 1 | 101.325 | 12 | 5.88 | 1.67
29.4 | 21.7 | 27 | 637 | 1 | 101.325 | 12 | 7.68 | 1.67
29.4 | 21.7 | 29 | 637 | 1 | 101.325 | 12 | 9.48 | 1.67
35 | 21.7 | 24 | 413 | 1 | 101.325 | 10.5 | 4.83 | 2.01
35 | 21.7 | 27 | 413 | 1 | 101.325 | 10.5 | 5.985 | 2.01
35 | 21.7 | 29 | 413 | 1 | 101.325 | 10.5 | 7.245 | 2.01
35 | 21.7 | 24 | 590 | 1 | 101.325 | 11.3 | 5.424 | 1.97
35 | 21.7 | 27 | 590 | 1 | 101.325 | 11.3 | 7.119 | 1.97
35 | 21.7 | 29 | 590 | 1 | 101.325 | 11.3 | 8.814 | 1.97
35 | 21.7 | 24 | 637 | 1 | 101.325 | 11.6 | 5.684 | 1.97
35 | 21.7 | 27 | 637 | 1 | 101.325 | 11.6 | 7.54 | 1.97
35 | 21.7 | 29 | 637 | 1 | 101.325 | 11.6 | 9.396 | 1.97
40.6 | 21.7 | 24 | 413 | 1 | 101.325 | 10 | 4.6 | 2.32
40.6 | 21.7 | 27 | 413 | 1 | 101.325 | 10 | 5.8 | 2.32
40.6 | 21.7 | 29 | 413 | 1 | 101.325 | 10 | 7 | 2.32
40.6 | 21.7 | 24 | 590 | 1 | 101.325 | 10 | 4.9 | 2.29
40.6 | 21.7 | 27 | 590 | 1 | 101.325 | 10 | 6.4 | 2.29
40.6 | 21.7 | 29 | 590 | 1 | 101.325 | 10 | 8 | 2.29
40.6 | 21.7 | 24 | 637 | 1 | 101.325 | 10 | 5 | 2.27
40.6 | 21.7 | 27 | 637 | 1 | 101.325 | 10 | 6.7 | 2.27
40.6 | 21.7 | 29 | 637 | 1 | 101.325 | 10 | 8.3 | 2.27
46.1 | 21.7 | 24 | 413 | 1 | 101.325 | 9.5 | 4.37 | 2.66
46.1 | 21.7 | 27 | 413 | 1 | 101.325 | 9.5 | 5.605 | 2.66
46.1 | 21.7 | 29 | 413 | 1 | 101.325 | 9.5 | 6.84 | 2.66
46.1 | 21.7 | 24 | 590 | 1 | 101.325 | 10.2 | 4.998 | 2.62
46.1 | 21.7 | 27 | 590 | 1 | 101.325 | 10.2 | 6.732 | 2.62
46.1 | 21.7 | 29 | 590 | 1 | 101.325 | 10.2 | 8.364 | 2.62
46.1 | 21.7 | 24 | 637 | 1 | 101.325 | 10.4 | 5.304 | 2.61
46.1 | 21.7 | 27 | 637 | 1 | 101.325 | 10.4 | 7.072 | 2.61
46.1 | 21.7 | 29 | 637 | 1 | 101.325 | 10.4 | 8.944 | 2.61
23.9 | 15 | 24 | 264 | 0.55 | 101.325 | 5.8 | 5.336 | 0.73
23.9 | 15 | 27 | 264 | 0.55 | 101.325 | 5.8 | 5.8 | 0.73
23.9 | 15 | 29 | 264 | 0.55 | 101.325 | 5.8 | 5.8 | 0.73
23.9 | 15 | 24 | 378 | 0.55 | 101.325 | 6.5 | 6.5 | 0.68
23.9 | 15 | 27 | 378 | 0.55 | 101.325 | 6.5 | 6.5 | 0.68
23.9 | 15 | 29 | 378 | 0.55 | 101.325 | 6.5 | 6.5 | 0.68
23.9 | 15 | 24 | 389 | 0.55 | 101.325 | 6.6 | 6.6 | 0.68
23.9 | 15 | 27 | 389 | 0.55 | 101.325 | 6.6 | 6.6 | 0.68
23.9 | 15 | 29 | 389 | 0.55 | 101.325 | 6.6 | 6.6 | 0.68
29.4 | 15 | 24 | 264 | 0.55 | 101.325 | 5.6 | 5.264 | 0.89
29.4 | 15 | 27 | 264 | 0.55 | 101.325 | 5.6 | 5.6 | 0.89
29.4 | 15 | 29 | 264 | 0.55 | 101.325 | 5.6 | 5.6 | 0.89
29.4 | 15 | 24 | 378 | 0.55 | 101.325 | 6.3 | 6.3 | 0.86
29.4 | 15 | 27 | 378 | 0.55 | 101.325 | 6.3 | 6.3 | 0.86
29.4 | 15 | 29 | 378 | 0.55 | 101.325 | 6.3 | 6.3 | 0.86
29.4 | 15 | 24 | 389 | 0.55 | 101.325 | 6.3 | 6.3 | 0.85
29.4 | 15 | 27 | 389 | 0.55 | 101.325 | 6.3 | 6.3 | 0.85
29.4 | 15 | 29 | 389 | 0.55 | 101.325 | 6.3 | 6.3 | 0.85
35 | 15 | 24 | 264 | 0.55 | 101.325 | 5.4 | 5.184 | 1.07
35 | 15 | 27 | 264 | 0.55 | 101.325 | 5.4 | 5.4 | 1.07
35 | 15 | 29 | 264 | 0.55 | 101.325 | 5.4 | 5.4 | 1.07
35 | 15 | 24 | 378 | 0.55 | 101.325 | 5.4 | 5.4 | 1.04
35 | 15 | 27 | 378 | 0.55 | 101.325 | 5.4 | 5.4 | 1.04
35 | 15 | 29 | 378 | 0.55 | 101.325 | 5.4 | 5.4 | 1.04
35 | 15 | 24 | 389 | 0.55 | 101.325 | 5.4 | 5.4 | 1.04
35 | 15 | 27 | 389 | 0.55 | 101.325 | 5.4 | 5.4 | 1.04
35 | 15 | 29 | 389 | 0.55 | 101.325 | 5.4 | 5.4 | 1.04
40.6 | 15 | 24 | 264 | 0.55 | 101.325 | 5.1 | 5.049 | 1.27
40.6 | 15 | 27 | 264 | 0.55 | 101.325 | 5.1 | 5.1 | 1.27
40.6 | 15 | 29 | 264 | 0.55 | 101.325 | 5.1 | 5.1 | 1.27
40.6 | 15 | 24 | 378 | 0.55 | 101.325 | 5.7 | 5.7 | 1.24
40.6 | 15 | 27 | 378 | 0.55 | 101.325 | 5.7 | 5.7 | 1.24
40.6 | 15 | 29 | 378 | 0.55 | 101.325 | 5.7 | 5.7 | 1.24
40.6 | 15 | 24 | 389 | 0.55 | 101.325 | 5.8 | 5.8 | 1.24
40.6 | 15 | 27 | 389 | 0.55 | 101.325 | 5.8 | 5.8 | 1.24
40.6 | 15 | 29 | 389 | 0.55 | 101.325 | 5.8 | 5.8 | 1.24
23.9 | 17.2 | 24 | 264 | 0.55 | 101.325 | 6 | 4.5 | 0.72
23.9 | 17.2 | 27 | 264 | 0.55 | 101.325 | 6 | 5.28 | 0.72
23.9 | 17.2 | 29 | 264 | 0.55 | 101.325 | 6 | 6 | 0.72
23.9 | 17.2 | 24 | 378 | 0.55 | 101.325 | 6.5 | 5.46 | 0.68
23.9 | 17.2 | 27 | 378 | 0.55 | 101.325 | 6.5 | 6.5 | 0.68
23.9 | 17.2 | 29 | 378 | 0.55 | 101.325 | 6.5 | 6.5 | 0.68
23.9 | 17.2 | 24 | 389 | 0.55 | 101.325 | 6.6 | 5.61 | 0.68
23.9 | 17.2 | 27 | 389 | 0.55 | 101.325 | 6.6 | 6.6 | 0.68
23.9 | 17.2 | 29 | 389 | 0.55 | 101.325 | 6.6 | 6.6 | 0.68
29.4 | 17.2 | 24 | 264 | 0.55 | 101.325 | 5.8 | 4.408 | 0.88
29.4 | 17.2 | 27 | 264 | 0.55 | 101.325 | 5.8 | 5.22 | 0.88
29.4 | 17.2 | 29 | 264 | 0.55 | 101.325 | 5.8 | 5.8 | 0.88
29.4 | 17.2 | 24 | 378 | 0.55 | 101.325 | 6.3 | 5.418 | 0.85
29.4 | 17.2 | 27 | 378 | 0.55 | 101.325 | 6.3 | 6.3 | 0.85
29.4 | 17.2 | 29 | 378 | 0.55 | 101.325 | 6.3 | 6.3 | 0.85
29.4 | 17.2 | 24 | 389 | 0.55 | 101.325 | 6.3 | 5.481 | 0.85
29.4 | 17.2 | 27 | 389 | 0.55 | 101.325 | 6.3 | 6.3 | 0.85
29.4 | 17.2 | 29 | 389 | 0.55 | 101.325 | 6.3 | 6.3 | 0.85
35 | 17.2 | 24 | 264 | 0.55 | 101.325 | 5.5 | 4.29 | 1.06
35 | 17.2 | 27 | 264 | 0.55 | 101.325 | 5.5 | 5.115 | 1.06
35 | 17.2 | 29 | 264 | 0.55 | 101.325 | 5.5 | 5.5 | 1.06
35 | 17.2 | 24 | 378 | 0.55 | 101.325 | 5.5 | 4.84 | 1.04
35 | 17.2 | 27 | 378 | 0.55 | 101.325 | 5.5 | 5.5 | 1.04
35 | 17.2 | 29 | 378 | 0.55 | 101.325 | 5.5 | 5.5 | 1.04
35 | 17.2 | 24 | 389 | 0.55 | 101.325 | 5.5 | 4.895 | 1.04
35 | 17.2 | 27 | 389 | 0.55 | 101.325 | 5.5 | 5.5 | 1.04
35 | 17.2 | 29 | 389 | 0.55 | 101.325 | 5.5 | 5.5 | 1.04
40.6 | 17.2 | 24 | 264 | 0.55 | 101.325 | 5.2 | 4.16 | 1.26
40.6 | 17.2 | 27 | 264 | 0.55 | 101.325 | 5.2 | 4.94 | 1.26
40.6 | 17.2 | 29 | 264 | 0.55 | 101.325 | 5.2 | 5.2 | 1.26
40.6 | 17.2 | 24 | 378 | 0.55 | 101.325 | 5.7 | 5.187 | 1.24
40.6 | 17.2 | 27 | 378 | 0.55 | 101.325 | 5.7 | 5.7 | 1.24
40.6 | 17.2 | 29 | 378 | 0.55 | 101.325 | 5.7 | 5.7 | 1.24
40.6 | 17.2 | 24 | 389 | 0.55 | 101.325 | 5.8 | 5.336 | 1.24
40.6 | 17.2 | 27 | 389 | 0.55 | 101.325 | 5.8 | 5.8 | 1.24
40.6 | 17.2 | 29 | 389 | 0.55 | 101.325 | 5.8 | 5.8 | 1.24
23.9 | 19.4 | 24 | 264 | 0.55 | 101.325 | 6.4 | 3.776 | 0.69
23.9 | 19.4 | 27 | 264 | 0.55 | 101.325 | 6.4 | 4.608 | 0.69
23.9 | 19.4 | 29 | 264 | 0.55 | 101.325 | 6.4 | 5.44 | 0.69
23.9 | 19.4 | 24 | 378 | 0.55 | 101.325 | 6.9 | 4.416 | 0.66
23.9 | 19.4 | 27 | 378 | 0.55 | 101.325 | 6.9 | 5.589 | 0.66
23.9 | 19.4 | 29 | 378 | 0.55 | 101.325 | 6.9 | 6.693 | 0.66
23.9 | 19.4 | 24 | 389 | 0.55 | 101.325 | 6.9 | 4.485 | 0.65
23.9 | 19.4 | 27 | 389 | 0.55 | 101.325 | 6.9 | 5.658 | 0.65
23.9 | 19.4 | 29 | 389 | 0.55 | 101.325 | 6.9 | 6.762 | 0.65
29.4 | 19.4 | 24 | 264 | 0.55 | 101.325 | 6.1 | 3.66 | 0.86
29.4 | 19.4 | 27 | 264 | 0.55 | 101.325 | 6.1 | 4.453 | 0.86
29.4 | 19.4 | 29 | 264 | 0.55 | 101.325 | 6.1 | 5.307 | 0.86
29.4 | 19.4 | 24 | 378 | 0.55 | 101.325 | 6.6 | 4.356 | 0.84
29.4 | 19.4 | 27 | 378 | 0.55 | 101.325 | 6.6 | 5.478 | 0.84
29.4 | 19.4 | 29 | 378 | 0.55 | 101.325 | 6.6 | 6.534 | 0.84
29.4 | 19.4 | 24 | 389 | 0.55 | 101.325 | 6.6 | 4.422 | 0.83
29.4 | 19.4 | 27 | 389 | 0.55 | 101.325 | 6.6 | 5.544 | 0.83
29.4 | 19.4 | 29 | 389 | 0.55 | 101.325 | 6.6 | 6.6 | 0.83
35 | 19.4 | 24 | 264 | 0.55 | 101.325 | 5.8 | 3.538 | 1.05
35 | 19.4 | 27 | 264 | 0.55 | 101.325 | 5.8 | 4.35 | 1.05
35 | 19.4 | 29 | 264 | 0.55 | 101.325 | 5.8 | 5.162 | 1.05
35 | 19.4 | 24 | 378 | 0.55 | 101.325 | 5.8 | 3.886 | 1.03
35 | 19.4 | 27 | 378 | 0.55 | 101.325 | 5.8 | 4.988 | 1.03
35 | 19.4 | 29 | 378 | 0.55 | 101.325 | 5.8 | 5.8 | 1.03
35 | 19.4 | 24 | 389 | 0.55 | 101.325 | 5.8 | 3.944 | 1.03
35 | 19.4 | 27 | 389 | 0.55 | 101.325 | 5.8 | 5.046 | 1.03
35 | 19.4 | 29 | 389 | 0.55 | 101.325 | 5.8 | 5.8 | 1.03
40.6 | 19.4 | 24 | 264 | 0.55 | 101.325 | 5.5 | 3.41 | 1.25
40.6 | 19.4 | 27 | 264 | 0.55 | 101.325 | 5.5 | 4.235 | 1.25
40.6 | 19.4 | 29 | 264 | 0.55 | 101.325 | 5.5 | 5.06 | 1.25
40.6 | 19.4 | 24 | 378 | 0.55 | 101.325 | 5.9 | 4.071 | 1.24
40.6 | 19.4 | 27 | 378 | 0.55 | 101.325 | 5.9 | 5.192 | 1.24
40.6 | 19.4 | 29 | 378 | 0.55 | 101.325 | 5.9 | 5.9 | 1.24
40.6 | 19.4 | 24 | 389 | 0.55 | 101.325 | 5.9 | 4.071 | 1.24
40.6 | 19.4 | 27 | 389 | 0.55 | 101.325 | 5.9 | 5.31 | 1.24
40.6 | 19.4 | 29 | 389 | 0.55 | 101.325 | 5.9 | 5.9 | 1.24
23.9 | 21.7 | 24 | 264 | 0.55 | 101.325 | 6.7 | 3.015 | 0.67
23.9 | 21.7 | 27 | 264 | 0.55 | 101.325 | 6.7 | 3.886 | 0.67
23.9 | 21.7 | 29 | 264 | 0.55 | 101.325 | 6.7 | 4.69 | 0.67
23.9 | 21.7 | 24 | 378 | 0.55 | 101.325 | 7.3 | 3.431 | 0.63
23.9 | 21.7 | 27 | 378 | 0.55 | 101.325 | 7.3 | 4.599 | 0.63
23.9 | 21.7 | 29 | 378 | 0.55 | 101.325 | 7.3 | 5.767 | 0.63
23.9 | 21.7 | 24 | 389 | 0.55 | 101.325 | 7.3 | 3.504 | 0.63
23.9 | 21.7 | 27 | 389 | 0.55 | 101.325 | 7.3 | 4.599 | 0.63
23.9 | 21.7 | 29 | 389 | 0.55 | 101.325 | 7.3 | 5.84 | 0.63
29.4 | 21.7 | 24 | 264 | 0.55 | 101.325 | 6.4 | 2.944 | 0.84
29.4 | 21.7 | 27 | 264 | 0.55 | 101.325 | 6.4 | 3.712 | 0.84
29.4 | 21.7 | 29 | 264 | 0.55 | 101.325 | 6.4 | 4.544 | 0.84
29.4 | 21.7 | 24 | 378 | 0.55 | 101.325 | 7 | 3.36 | 0.81
29.4 | 21.7 | 27 | 378 | 0.55 | 101.325 | 7 | 4.55 | 0.81
29.4 | 21.7 | 29 | 378 | 0.55 | 101.325 | 7 | 5.67 | 0.81
29.4 | 21.7 | 24 | 389 | 0.55 | 101.325 | 7 | 3.43 | 0.81
29.4 | 21.7 | 27 | 389 | 0.55 | 101.325 | 7 | 4.62 | 0.81
29.4 | 21.7 | 29 | 389 | 0.55 | 101.325 | 7 | 5.74 | 0.81
35 | 21.7 | 24 | 264 | 0.55 | 101.325 | 6.2 | 2.852 | 1.03
35 | 21.7 | 27 | 264 | 0.55 | 101.325 | 6.2 | 3.658 | 1.03
35 | 21.7 | 29 | 264 | 0.55 | 101.325 | 6.2 | 4.464 | 1.03
35 | 21.7 | 24 | 378 | 0.55 | 101.325 | 6.2 | 3.038 | 1.01
35 | 21.7 | 27 | 378 | 0.55 | 101.325 | 6.2 | 4.092 | 1.01
35 | 21.7 | 29 | 378 | 0.55 | 101.325 | 6.2 | 5.146 | 1.01
35 | 21.7 | 24 | 389 | 0.55 | 101.325 | 6.2 | 3.038 | 1.01
35 | 21.7 | 27 | 389 | 0.55 | 101.325 | 6.2 | 4.154 | 1.01
35 | 21.7 | 29 | 389 | 0.55 | 101.325 | 6.2 | 5.208 | 1.01
40.6 | 21.7 | 24 | 264 | 0.55 | 101.325 | 5.9 | 2.714 | 1.24
40.6 | 21.7 | 27 | 264 | 0.55 | 101.325 | 5.9 | 3.599 | 1.24
40.6 | 21.7 | 29 | 264 | 0.55 | 101.325 | 5.9 | 4.425 | 1.24
40.6 | 21.7 | 24 | 378 | 0.55 | 101.325 | 6.3 | 3.087 | 1.22
40.6 | 21.7 | 27 | 378 | 0.55 | 101.325 | 6.3 | 4.284 | 1.22
40.6 | 21.7 | 29 | 378 | 0.55 | 101.325 | 6.3 | 5.418 | 1.22
40.6 | 21.7 | 24 | 389 | 0.55 | 101.325 | 6.3 | 3.15 | 1.22
40.6 | 21.7 | 27 | 389 | 0.55 | 101.325 | 6.3 | 4.347 | 1.22
40.6 | 21.7 | 29 | 389 | 0.55 | 101.325 | 6.3 | 5.481 | 1.22
23.9 | 15 | 24 | 179 | 0.33 | 101.325 | 3.5 | 3.5 | 0.4
23.9 | 15 | 27 | 179 | 0.33 | 101.325 | 3.5 | 3.5 | 0.4
23.9 | 15 | 29 | 179 | 0.33 | 101.325 | 3.5 | 3.5 | 0.4
23.9 | 15 | 24 | 248 | 0.33 | 101.325 | 3.9 | 3.9 | 0.37
23.9 | 15 | 27 | 248 | 0.33 | 101.325 | 3.9 | 3.9 | 0.37
23.9 | 15 | 29 | 248 | 0.33 | 101.325 | 3.9 | 3.9 | 0.37
23.9 | 15 | 24 | 267 | 0.33 | 101.325 | 4 | 4 | 0.36
23.9 | 15 | 27 | 267 | 0.33 | 101.325 | 4 | 4 | 0.36
23.9 | 15 | 29 | 267 | 0.33 | 101.325 | 4 | 4 | 0.36
29.4 | 15 | 24 | 179 | 0.33 | 101.325 | 3.2 | 3.2 | 0.52
29.4 | 15 | 27 | 179 | 0.33 | 101.325 | 3.2 | 3.2 | 0.52
29.4 | 15 | 29 | 179 | 0.33 | 101.325 | 3.2 | 3.2 | 0.52
29.4 | 15 | 24 | 248 | 0.33 | 101.325 | 3.6 | 3.6 | 0.48
29.4 | 15 | 27 | 248 | 0.33 | 101.325 | 3.6 | 3.6 | 0.48
29.4 | 15 | 29 | 248 | 0.33 | 101.325 | 3.6 | 3.6 | 0.48
29.4 | 15 | 24 | 267 | 0.33 | 101.325 | 3.7 | 3.7 | 0.47
29.4 | 15 | 27 | 267 | 0.33 | 101.325 | 3.7 | 3.7 | 0.47
29.4 | 15 | 29 | 267 | 0.33 | 101.325 | 3.7 | 3.7 | 0.47
35 | 15 | 24 | 179 | 0.33 | 101.325 | 3 | 3 | 0.64
35 | 15 | 27 | 179 | 0.33 | 101.325 | 3 | 3 | 0.64
35 | 15 | 29 | 179 | 0.33 | 101.325 | 3 | 3 | 0.64
35 | 15 | 24 | 248 | 0.33 | 101.325 | 3 | 3 | 0.62
35 | 15 | 27 | 248 | 0.33 | 101.325 | 3 | 3 | 0.62
35 | 15 | 29 | 248 | 0.33 | 101.325 | 3 | 3 | 0.62
35 | 15 | 24 | 267 | 0.33 | 101.325 | 3 | 3 | 0.61
35 | 15 | 27 | 267 | 0.33 | 101.325 | 3 | 3 | 0.61
35 | 15 | 29 | 267 | 0.33 | 101.325 | 3 | 3 | 0.61
40.6 | 15 | 24 | 179 | 0.33 | 101.325 | 2.8 | 2.8 | 0.79
40.6 | 15 | 27 | 179 | 0.33 | 101.325 | 2.8 | 2.8 | 0.79
40.6 | 15 | 29 | 179 | 0.33 | 101.325 | 2.8 | 2.8 | 0.79
40.6 | 15 | 24 | 248 | 0.33 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 15 | 27 | 248 | 0.33 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 15 | 29 | 248 | 0.33 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 15 | 24 | 267 | 0.33 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 15 | 27 | 267 | 0.33 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 15 | 29 | 267 | 0.33 | 101.325 | 3.1 | 3.1 | 0.76
23.9 | 17.2 | 24 | 179 | 0.33 | 101.325 | 3.5 | 2.835 | 0.4
23.9 | 17.2 | 27 | 179 | 0.33 | 101.325 | 3.5 | 3.395 | 0.4
23.9 | 17.2 | 29 | 179 | 0.33 | 101.325 | 3.5 | 3.5 | 0.4
23.9 | 17.2 | 24 | 248 | 0.33 | 101.325 | 3.9 | 3.549 | 0.37
23.9 | 17.2 | 27 | 248 | 0.33 | 101.325 | 3.9 | 3.9 | 0.37
23.9 | 17.2 | 29 | 248 | 0.33 | 101.325 | 3.9 | 3.9 | 0.37
23.9 | 17.2 | 24 | 267 | 0.33 | 101.325 | 4 | 3.76 | 0.36
23.9 | 17.2 | 27 | 267 | 0.33 | 101.325 | 4 | 4 | 0.36
23.9 | 17.2 | 29 | 267 | 0.33 | 101.325 | 4 | 4 | 0.36
29.4 | 17.2 | 24 | 179 | 0.33 | 101.325 | 3.2 | 2.72 | 0.52
29.4 | 17.2 | 27 | 179 | 0.33 | 101.325 | 3.2 | 3.2 | 0.52
29.4 | 17.2 | 29 | 179 | 0.33 | 101.325 | 3.2 | 3.2 | 0.52
29.4 | 17.2 | 24 | 248 | 0.33 | 101.325 | 3.6 | 3.456 | 0.48
29.4 | 17.2 | 27 | 248 | 0.33 | 101.325 | 3.6 | 3.6 | 0.48
29.4 | 17.2 | 29 | 248 | 0.33 | 101.325 | 3.6 | 3.6 | 0.48
29.4 | 17.2 | 24 | 267 | 0.33 | 101.325 | 3.6 | 3.564 | 0.48
29.4 | 17.2 | 27 | 267 | 0.33 | 101.325 | 3.6 | 3.6 | 0.48
29.4 | 17.2 | 29 | 267 | 0.33 | 101.325 | 3.6 | 3.6 | 0.48
35 | 17.2 | 24 | 179 | 0.33 | 101.325 | 3 | 2.67 | 0.65
35 | 17.2 | 27 | 179 | 0.33 | 101.325 | 3 | 3 | 0.65
35 | 17.2 | 29 | 179 | 0.33 | 101.325 | 3 | 3 | 0.65
35 | 17.2 | 24 | 248 | 0.33 | 101.325 | 3 | 3 | 0.61
35 | 17.2 | 27 | 248 | 0.33 | 101.325 | 3 | 3 | 0.61
35 | 17.2 | 29 | 248 | 0.33 | 101.325 | 3 | 3 | 0.61
35 | 17.2 | 24 | 267 | 0.33 | 101.325 | 3 | 3 | 0.61
35 | 17.2 | 27 | 267 | 0.33 | 101.325 | 3 | 3 | 0.61
35 | 17.2 | 29 | 267 | 0.33 | 101.325 | 3 | 3 | 0.61
40.6 | 17.2 | 24 | 179 | 0.33 | 101.325 | 2.8 | 2.604 | 0.79
40.6 | 17.2 | 27 | 179 | 0.33 | 101.325 | 2.8 | 2.8 | 0.79
40.6 | 17.2 | 29 | 179 | 0.33 | 101.325 | 2.8 | 2.8 | 0.79
40.6 | 17.2 | 24 | 248 | 0.33 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 17.2 | 27 | 248 | 0.33 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 17.2 | 29 | 248 | 0.33 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 17.2 | 24 | 267 | 0.33 | 101.325 | 3.1 | 3.1 | 0.75
40.6 | 17.2 | 27 | 267 | 0.33 | 101.325 | 3.1 | 3.1 | 0.75
40.6 | 17.2 | 29 | 267 | 0.33 | 101.325 | 3.1 | 3.1 | 0.75
23.9 | 19.4 | 24 | 179 | 0.33 | 101.325 | 3.8 | 2.356 | 0.38
23.9 | 19.4 | 27 | 179 | 0.33 | 101.325 | 3.8 | 2.964 | 0.38
23.9 | 19.4 | 29 | 179 | 0.33 | 101.325 | 3.8 | 3.534 | 0.38
23.9 | 19.4 | 24 | 248 | 0.33 | 101.325 | 4 | 2.76 | 0.35
23.9 | 19.4 | 27 | 248 | 0.33 | 101.325 | 4 | 3.52 | 0.35
23.9 | 19.4 | 29 | 248 | 0.33 | 101.325 | 4 | 4 | 0.35
23.9 | 19.4 | 24 | 267 | 0.33 | 101.325 | 4.1 | 2.87 | 0.35
23.9 | 19.4 | 27 | 267 | 0.33 | 101.325 | 4.1 | 3.731 | 0.35
23.9 | 19.4 | 29 | 267 | 0.33 | 101.325 | 4.1 | 4.1 | 0.35
29.4 | 19.4 | 24 | 179 | 0.33 | 101.325 | 3.4 | 2.21 | 0.5
29.4 | 19.4 | 27 | 179 | 0.33 | 101.325 | 3.4 | 2.788 | 0.5
29.4 | 19.4 | 29 | 179 | 0.33 | 101.325 | 3.4 | 3.332 | 0.5
29.4 | 19.4 | 24 | 248 | 0.33 | 101.325 | 3.6 | 2.592 | 0.47
29.4 | 19.4 | 27 | 248 | 0.33 | 101.325 | 3.6 | 3.348 | 0.47
29.4 | 19.4 | 29 | 248 | 0.33 | 101.325 | 3.6 | 3.6 | 0.47
29.4 | 19.4 | 24 | 267 | 0.33 | 101.325 | 3.7 | 2.738 | 0.47
29.4 | 19.4 | 27 | 267 | 0.33 | 101.325 | 3.7 | 3.552 | 0.47
29.4 | 19.4 | 29 | 267 | 0.33 | 101.325 | 3.7 | 3.7 | 0.47
35 | 19.4 | 24 | 179 | 0.33 | 101.325 | 3.1 | 2.077 | 0.63
35 | 19.4 | 27 | 179 | 0.33 | 101.325 | 3.1 | 2.666 | 0.63
35 | 19.4 | 29 | 179 | 0.33 | 101.325 | 3.1 | 3.1 | 0.63
35 | 19.4 | 24 | 248 | 0.33 | 101.325 | 3.1 | 2.325 | 0.61
35 | 19.4 | 27 | 248 | 0.33 | 101.325 | 3.1 | 3.038 | 0.61
35 | 19.4 | 29 | 248 | 0.33 | 101.325 | 3.1 | 3.1 | 0.61
35 | 19.4 | 24 | 267 | 0.33 | 101.325 | 3.1 | 2.418 | 0.61
35 | 19.4 | 27 | 267 | 0.33 | 101.325 | 3.1 | 3.1 | 0.61
35 | 19.4 | 29 | 267 | 0.33 | 101.325 | 3.1 | 3.1 | 0.61
40.6 | 19.4 | 24 | 179 | 0.33 | 101.325 | 2.9 | 2.03 | 0.78
40.6 | 19.4 | 27 | 179 | 0.33 | 101.325 | 2.9 | 2.61 | 0.78
40.6 | 19.4 | 29 | 179 | 0.33 | 101.325 | 2.9 | 2.9 | 0.78
40.6 | 19.4 | 24 | 248 | 0.33 | 101.325 | 3.1 | 2.449 | 0.76
40.6 | 19.4 | 27 | 248 | 0.33 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 19.4 | 29 | 248 | 0.33 | 101.325 | 3.1 | 3.1 | 0.76
40.6 | 19.4 | 24 | 267 | 0.33 | 101.325 | 3.1 | 2.511 | 0.75
40.6 | 19.4 | 27 | 267 | 0.33 | 101.325 | 3.1 | 3.1 | 0.75
40.6 | 19.4 | 29 | 267 | 0.33 | 101.325 | 3.1 | 3.1 | 0.75
23.9 | 21.7 | 24 | 179 | 0.33 | 101.325 | 4 | 1.84 | 0.35
23.9 | 21.7 | 27 | 179 | 0.33 | 101.325 | 4 | 2.44 | 0.35
23.9 | 21.7 | 29 | 179 | 0.33 | 101.325 | 4 | 3 | 0.35
23.9 | 21.7 | 24 | 248 | 0.33 | 101.325 | 4.3 | 2.107 | 0.33
23.9 | 21.7 | 27 | 248 | 0.33 | 101.325 | 4.3 | 2.881 | 0.33
23.9 | 21.7 | 29 | 248 | 0.33 | 101.325 | 4.3 | 3.698 | 0.33
23.9 | 21.7 | 24 | 267 | 0.33 | 101.325 | 4.3 | 2.15 | 0.32
23.9 | 21.7 | 27 | 267 | 0.33 | 101.325 | 4.3 | 2.967 | 0.32
23.9 | 21.7 | 29 | 267 | 0.33 | 101.325 | 4.3 | 3.784 | 0.32
29.4 | 21.7 | 24 | 179 | 0.33 | 101.325 | 3.7 | 1.739 | 0.47
29.4 | 21.7 | 27 | 179 | 0.33 | 101.325 | 3.7 | 2.331 | 0.47
29.4 | 21.7 | 29 | 179 | 0.33 | 101.325 | 3.7 | 2.923 | 0.47
29.4 | 21.7 | 24 | 248 | 0.33 | 101.325 | 3.9 | 1.989 | 0.45
29.4 | 21.7 | 27 | 248 | 0.33 | 101.325 | 3.9 | 2.769 | 0.45
29.4 | 21.7 | 29 | 248 | 0.33 | 101.325 | 3.9 | 3.51 | 0.45
29.4 | 21.7 | 24 | 267 | 0.33 | 101.325 | 3.9 | 1.989 | 0.45
29.4 | 21.7 | 27 | 267 | 0.33 | 101.325 | 3.9 | 2.847 | 0.45
29.4 | 21.7 | 29 | 267 | 0.33 | 101.325 | 3.9 | 3.627 | 0.45
35 | 21.7 | 24 | 179 | 0.33 | 101.325 | 3.3 | 1.584 | 0.61
35 | 21.7 | 27 | 179 | 0.33 | 101.325 | 3.3 | 2.178 | 0.61
35 | 21.7 | 29 | 179 | 0.33 | 101.325 | 3.3 | 2.706 | 0.61
35 | 21.7 | 24 | 248 | 0.33 | 101.325 | 3.3 | 1.716 | 0.59
35 | 21.7 | 27 | 248 | 0.33 | 101.325 | 3.3 | 2.442 | 0.59
35 | 21.7 | 29 | 248 | 0.33 | 101.325 | 3.3 | 3.135 | 0.59
35 | 21.7 | 24 | 267 | 0.33 | 101.325 | 3.3 | 1.749 | 0.59
35 | 21.7 | 27 | 267 | 0.33 | 101.325 | 3.3 | 2.541 | 0.59
35 | 21.7 | 29 | 267 | 0.33 | 101.325 | 3.3 | 3.267 | 0.59
40.6 | 21.7 | 24 | 179 | 0.33 | 101.325 | 3.1 | 1.519 | 0.76
40.6 | 21.7 | 27 | 179 | 0.33 | 101.325 | 3.1 | 2.108 | 0.76
40.6 | 21.7 | 29 | 179 | 0.33 | 101.325 | 3.1 | 2.697 | 0.76
40.6 | 21.7 | 24 | 248 | 0.33 | 101.325 | 3.3 | 1.782 | 0.74
40.6 | 21.7 | 27 | 248 | 0.33 | 101.325 | 3.3 | 2.574 | 0.74
40.6 | 21.7 | 29 | 248 | 0.33 | 101.325 | 3.3 | 3.3 | 0.74
40.6 | 21.7 | 24 | 267 | 0.33 | 101.325 | 3.3 | 1.815 | 0.74
40.6 | 21.7 | 27 | 267 | 0.33 | 101.325 | 3.3 | 2.64 | 0.74
40.6 | 21.7 | 29 | 267 | 0.33 | 101.325 | 3.3 | 3.3 | 0.74

## PerformanceMapStandby
outdoorCoilEnvironmentalDryBulbTemperature | grossPower
°C | W
37.78 | 0
10.5 | 0
10 | 40
-17.78 | 40