## Instructions
This spreadsheet serves as a template for ASHRAE Standard 205 compliant representations corresponding to RS0003 "Fan Assembly".
General Instructions:
Only the names and values are read out of this sheet using the SI-unit system defined in the standard. Any other columns are for user-information only.
Do not change Data Group, Data Element, or sheet names. These are used to translate the spreadsheet into simulation data.
If data group is not required, it's required elements are only required if the data group is present
RSID, RSVersion, and RSTitle should not be changed (they are set by the schema associated with this template).
Performance maps and array data groups each have separate sheets to enable an extensible number of entries in consecutive rows.
Performance map grid variables are colored in blue and must be entered in the order defined by the standard (with the rightmost column varying with the highest frequency)
The structure of the data here does not necessarily reflect the actual hierarchical data structure as defined in the standard. It has been modified for user readability, but contains all necessary data elements for simulation purposes.
This instruction sheet is informative only. It may be removed once data entry is complete.
RS Specific Instructions:
AssemblyComponents will be listed in the sheet "Description/AssemblyComponents"
Exactly one of "PerformanceMapContinuous" or "PerformanceMapDiscrete" shall contain data. Files with data in both sheets will be invalid.

## RS0003
Data Group | Data Element | Value | Units | Required?
ASHRAE205 |  |  |  | Yes
| RSID | RS0003 |  | Yes
| RSVersion | 0.1.0 |  | Yes
| RSTitle | Fan Assembly |  | Yes
| ID | Furn-Discrete |  | Yes
| dataTimeStamp | 2019-02-08 |  | Yes
dataVersion
description
dataSource
| notes | Speeds 1-4 are Heating, 1st stage, settings (low,mlo,norm,hi). Speeds 5-8 are Heating, 2nd stage, settings (low,mlo,norm,hi), Speeds 9-11 are Cooling, settings (low,norm,hi)
Description/ProductInformation
| manufacturer | XYZFurnace Co |  | Yes
| modelNumber | F060 |  | Yes
| hasMotor | TRUE |  | Yes
| Enclosed | TRUE |  | Yes
| impellerType | CentrifugalForwardCurved
| directDriveImpeller | TRUE
Performance
| nominalVolumetricAirFlowRate | #DIV/0! | m3/s | Yes
| wetSurfacePressureDrop | 24.8 | Pa | Yes
| motorHeatFraction | 1 |  | Yes
| powerStandby | 8 | W | Yes

## DescriptionAssemblyComponent
componentType | componentDescription | componentID
Furnace | Furnance HX | null
Filter | filter section | null

## PerformanceMapDiscrete
speedNumber | staticPressureDifference | volumetricAirFlowRate | inputPower
| Pa | m3/s | W
1 | 25 | 0.283 | 85
1 | 75 | 0.283 | 110
1 | 120 | 0.283 | 155
1 | 170 | 0.283 | 190
2 | 25 | 0.33 | 90
2 | 75 | 0.33 | 130
2 | 120 | 0.33 | 175
2 | 170 | 0.33 | 210
3 | 25 | 0.366 | 105
3 | 75 | 0.366 | 155
3 | 120 | 0.366 | 195
3 | 170 | 0.366 | 240
4 | 25 | 0.411 | 135
4 | 75 | 0.411 | 185
4 | 120 | 0.411 | 235
4 | 170 | 0.411 | 290
5 | 25 | 0.406 | 140
5 | 75 | 0.434 | 200
5 | 120 | 0.434 | 245
5 | 170 | 0.434 | 300
5 | 220 | 0.316 | 245
6 | 25 | 0.472 | 190
6 | 75 | 0.472 | 255
6 | 120 | 0.472 | 305
6 | 170 | 0.472 | 340
6 | 220 | 0.33 | 255
7 | 25 | 0.531 | 250
7 | 75 | 0.531 | 315
7 | 120 | 0.531 | 370
7 | 170 | 0.484 | 355
7 | 220 | 0.366 | 285
8 | 25 | 0.59 | 340
8 | 75 | 0.59 | 405
8 | 120 | 0.59 | 445
8 | 170 | 0.519 | 390
8 | 220 | 0.472 | 355
9 | 25 | 0.496 | 195
9 | 75 | 0.496 | 260
9 | 120 | 0.496 | 305
9 | 170 | 0.496 | 350
9 | 220 | 0.434 | 315
10 | 25 | 0.566 | 275
10 | 75 | 0.566 | 330
10 | 120 | 0.566 | 385
10 | 170 | 0.519 | 385
10 | 220 | 0.444 | 330
11 | 25 | 0.625 | 360
11 | 75 | 0.625 | 425
11 | 120 | 0.614 | 460
11 | 170 | 0.555 | 425
11 | 220 | 0.472 | 365