## RS0001
RS0001: Liquid-Cooler Chillers
Data Group | Data Element | Value | Units | Required
ASHRAE205 |  |  |  | ✓
| standard_version | PPR2 |  | ✓
| schema_version | 0.1.0 |  | ✓
| RS_ID | RS0001 |  | ✓
| description | Water Cooled Centrifugal Chiller |  | ✓
| ID | bcf8b859-67a3-42f4-8f8d-4e57af1ccf22 |  | ✓
| data_timestamp | 2019-09-10T00:00Z |  | ✓
| data_version | 1 |  | ✓
| data_source | CWI-ChilSelect
| disclaimer | Example file - not for simulation
| notes | This is a JSON version of the sample RS0001 file
ASHRAE205.RS_instance |  |  |  | ✓
ASHRAE205.RS_instance.RS0001
ASHRAE205.RS_instance.RS0001.description
ASHRAE205.RS_instance.RS0001.description.product_information
| manufacturer | ColdWaterInc |  | ✓
| manufacturer_software_version | Cw.2019.01
| model_number | CC-500-VS |  | ✓
| nominal_voltage | 460 | V
| nominal_frequency | 60 | Hz
| tolerance_standard | AHRI_551_591_2015
| compressor_type | CENTRIFUGAL
| speed_control_type | VARIABLE_SPEED
| liquid_data_source | AHRI 551/591-2015
| refrigerant_type | R134A
| hotgas_bypass_installed | FALSE
ASHRAE205.RS_instance.RS0001.description.rating_AHRI
| certification_reference_number | 987654 |  | ✓
| standard_rating_version | AHRI_551_591_2015 |  | ✓
| net_refrigerating_capacity | 1758000 | W | ✓
| input_power | 284900 | W | ✓
| COP | 6.171 | - | ✓
| part_load_value | 10.36 | - | ✓
| evaporator_liquid_volumetric_flow_rate | 0.00839 | m3/s | ✓
| evaporator_liquid_leaving_temperature | 280.15 | K | ✓
| evaporator_liquid_entering_temperature | 293.15 | K | ✓
| evaporator_liquid_differential_pressure | 53100 | Pa | ✓
| condenser_liquid_volumetric_flow_rate | 0.00974 | m3/s | ✓
| condenser_liquid_entering_temperature | 303.15 | K | ✓
| condenser_liquid_leaving_temperature | 308.15 | K | ✓
| condenser_liquid_dfferential_pressure | 36400 | Pa | ✓
| rating_reproducible_from_performance_data | FALSE |  | ✓
ASHRAE205.RS_instance.RS0001.performance |  |  |  | ✓
ASHRAE205.RS_instance.RS0001.performance.evaporator_liquid_type |  |  |  | ✓
ASHRAE205.RS_instance.RS0001.performance.evaporator_liquid_type.liquid_components |  | $liquid_components
| concentration_type | BY_VOLUME
ASHRAE205.RS_instance.RS0001.performance.condenser_liquid_type |  |  |  | ✓
ASHRAE205.RS_instance.RS0001.performance.condenser_liquid_type.liquid_components |  | $liquid_components0
| concentration_type | BY_VOLUME
| evaporator_fouling_factor | 1.8e-05 | m2-K/W | ✓
| condenser_fouling_factor | 4.4e-05 | m2-K/W | ✓
| unit_power_limit | 315000 | W
ASHRAE205.RS_instance.RS0001.performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
ASHRAE205.RS_instance.RS0001.performance.performance_map_standby |  | $performance_map_standby |  | ✓

## liquid_components
ASHRAE205.RS_instance.RS0001.performance.evaporator_liquid_type.liquid_components.liquid_constituent
liquid_constituent | concentration
WATER | 1

## liquid_components0
ASHRAE205.RS_instance.RS0001.performance.condenser_liquid_type.liquid_components.liquid_constituent
liquid_constituent | concentration
WATER | 1

## performance_map_cooling
ASHRAE205.RS_instance.RS0001.performance.performance_map_cooling.grid_variables
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | net_evaporator_capacity_fraction | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | motor_controller_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.05585 | 278.15 | 0.00115 | 283.65 | 0.15
0.05585 | 278.15 | 0.00115 | 283.65 | 0.2
0.05585 | 278.15 | 0.00115 | 283.65 | 0.3
0.05585 | 278.15 | 0.00115 | 283.65 | 0.4
0.05585 | 278.15 | 0.00115 | 283.65 | 0.5
0.05585 | 278.15 | 0.00115 | 283.65 | 0.6
0.05585 | 278.15 | 0.00115 | 283.65 | 0.7
0.05585 | 278.15 | 0.00115 | 283.65 | 0.8
0.05585 | 278.15 | 0.00115 | 283.65 | 0.9
0.05585 | 278.15 | 0.00115 | 283.65 | 1
0.05585 | 278.15 | 0.00115 | 284.15 | 0.15
0.05585 | 278.15 | 0.00115 | 284.15 | 0.2
0.05585 | 278.15 | 0.00115 | 284.15 | 0.3
0.05585 | 278.15 | 0.00115 | 284.15 | 0.4
0.05585 | 278.15 | 0.00115 | 284.15 | 0.5
0.05585 | 278.15 | 0.00115 | 284.15 | 0.6
0.05585 | 278.15 | 0.00115 | 284.15 | 0.7
0.05585 | 278.15 | 0.00115 | 284.15 | 0.8
0.05585 | 278.15 | 0.00115 | 284.15 | 0.9
0.05585 | 278.15 | 0.00115 | 284.15 | 1
0.05585 | 278.15 | 0.00115 | 284.65 | 0.15
0.05585 | 278.15 | 0.00115 | 284.65 | 0.2
0.05585 | 278.15 | 0.00115 | 284.65 | 0.3
0.05585 | 278.15 | 0.00115 | 284.65 | 0.4
0.05585 | 278.15 | 0.00115 | 284.65 | 0.5
0.05585 | 278.15 | 0.00115 | 284.65 | 0.6
0.05585 | 278.15 | 0.00115 | 284.65 | 0.7
0.05585 | 278.15 | 0.00115 | 284.65 | 0.8
0.05585 | 278.15 | 0.00115 | 284.65 | 0.9
0.05585 | 278.15 | 0.00115 | 284.65 | 1
0.05585 | 278.15 | 0.00115 | 285.15 | 0.15
0.05585 | 278.15 | 0.00115 | 285.15 | 0.2
0.05585 | 278.15 | 0.00115 | 285.15 | 0.3
0.05585 | 278.15 | 0.00115 | 285.15 | 0.4
0.05585 | 278.15 | 0.00115 | 285.15 | 0.5
0.05585 | 278.15 | 0.00115 | 285.15 | 0.6
0.05585 | 278.15 | 0.00115 | 285.15 | 0.7
0.05585 | 278.15 | 0.00115 | 285.15 | 0.8
0.05585 | 278.15 | 0.00115 | 285.15 | 0.9
0.05585 | 278.15 | 0.00115 | 285.15 | 1
0.05585 | 278.15 | 0.00115 | 285.65 | 0.15
0.05585 | 278.15 | 0.00115 | 285.65 | 0.2
0.05585 | 278.15 | 0.00115 | 285.65 | 0.3
0.05585 | 278.15 | 0.00115 | 285.65 | 0.4
0.05585 | 278.15 | 0.00115 | 285.65 | 0.5
0.05585 | 278.15 | 0.00115 | 285.65 | 0.6
0.05585 | 278.15 | 0.00115 | 285.65 | 0.7
0.05585 | 278.15 | 0.00115 | 285.65 | 0.8
0.05585 | 278.15 | 0.00115 | 285.65 | 0.9
0.05585 | 278.15 | 0.00115 | 285.65 | 1
0.05585 | 278.15 | 0.00115 | 286.15 | 0.15
0.05585 | 278.15 | 0.00115 | 286.15 | 0.2
0.05585 | 278.15 | 0.00115 | 286.15 | 0.3
0.05585 | 278.15 | 0.00115 | 286.15 | 0.4
0.05585 | 278.15 | 0.00115 | 286.15 | 0.5
0.05585 | 278.15 | 0.00115 | 286.15 | 0.6
0.05585 | 278.15 | 0.00115 | 286.15 | 0.7
0.05585 | 278.15 | 0.00115 | 286.15 | 0.8
0.05585 | 278.15 | 0.00115 | 286.15 | 0.9
0.05585 | 278.15 | 0.00115 | 286.15 | 1
0.05585 | 278.15 | 0.00115 | 286.65 | 0.15
0.05585 | 278.15 | 0.00115 | 286.65 | 0.2
0.05585 | 278.15 | 0.00115 | 286.65 | 0.3
0.05585 | 278.15 | 0.00115 | 286.65 | 0.4
0.05585 | 278.15 | 0.00115 | 286.65 | 0.5
0.05585 | 278.15 | 0.00115 | 286.65 | 0.6
0.05585 | 278.15 | 0.00115 | 286.65 | 0.7
0.05585 | 278.15 | 0.00115 | 286.65 | 0.8
0.05585 | 278.15 | 0.00115 | 286.65 | 0.9
0.05585 | 278.15 | 0.00115 | 286.65 | 1
0.05585 | 278.15 | 0.00115 | 287.15 | 0.15
0.05585 | 278.15 | 0.00115 | 287.15 | 0.2
0.05585 | 278.15 | 0.00115 | 287.15 | 0.3
0.05585 | 278.15 | 0.00115 | 287.15 | 0.4
0.05585 | 278.15 | 0.00115 | 287.15 | 0.5
0.05585 | 278.15 | 0.00115 | 287.15 | 0.6
0.05585 | 278.15 | 0.00115 | 287.15 | 0.7
0.05585 | 278.15 | 0.00115 | 287.15 | 0.8
0.05585 | 278.15 | 0.00115 | 287.15 | 0.9
0.05585 | 278.15 | 0.00115 | 287.15 | 1
0.05585 | 278.15 | 0.00115 | 287.65 | 0.15
0.05585 | 278.15 | 0.00115 | 287.65 | 0.2
0.05585 | 278.15 | 0.00115 | 287.65 | 0.3
0.05585 | 278.15 | 0.00115 | 287.65 | 0.4
0.05585 | 278.15 | 0.00115 | 287.65 | 0.5
0.05585 | 278.15 | 0.00115 | 287.65 | 0.6
0.05585 | 278.15 | 0.00115 | 287.65 | 0.7
0.05585 | 278.15 | 0.00115 | 287.65 | 0.8
0.05585 | 278.15 | 0.00115 | 287.65 | 0.9
0.05585 | 278.15 | 0.00115 | 287.65 | 1
0.05585 | 278.15 | 0.00115 | 288.15 | 0.15
0.05585 | 278.15 | 0.00115 | 288.15 | 0.2
0.05585 | 278.15 | 0.00115 | 288.15 | 0.3
0.05585 | 278.15 | 0.00115 | 288.15 | 0.4
0.05585 | 278.15 | 0.00115 | 288.15 | 0.5
0.05585 | 278.15 | 0.00115 | 288.15 | 0.6
0.05585 | 278.15 | 0.00115 | 288.15 | 0.7
0.05585 | 278.15 | 0.00115 | 288.15 | 0.8
0.05585 | 278.15 | 0.00115 | 288.15 | 0.9
0.05585 | 278.15 | 0.00115 | 288.15 | 1
0.05585 | 278.15 | 0.00115 | 288.65 | 0.15
0.05585 | 278.15 | 0.00115 | 288.65 | 0.2
0.05585 | 278.15 | 0.00115 | 288.65 | 0.3
0.05585 | 278.15 | 0.00115 | 288.65 | 0.4
0.05585 | 278.15 | 0.00115 | 288.65 | 0.5
0.05585 | 278.15 | 0.00115 | 288.65 | 0.6
0.05585 | 278.15 | 0.00115 | 288.65 | 0.7
0.05585 | 278.15 | 0.00115 | 288.65 | 0.8
0.05585 | 278.15 | 0.00115 | 288.65 | 0.9
0.05585 | 278.15 | 0.00115 | 288.65 | 1
0.05585 | 278.15 | 0.00115 | 289.15 | 0.15
0.05585 | 278.15 | 0.00115 | 289.15 | 0.2
0.05585 | 278.15 | 0.00115 | 289.15 | 0.3
0.05585 | 278.15 | 0.00115 | 289.15 | 0.4
0.05585 | 278.15 | 0.00115 | 289.15 | 0.5
0.05585 | 278.15 | 0.00115 | 289.15 | 0.6
0.05585 | 278.15 | 0.00115 | 289.15 | 0.7
0.05585 | 278.15 | 0.00115 | 289.15 | 0.8
0.05585 | 278.15 | 0.00115 | 289.15 | 0.9
0.05585 | 278.15 | 0.00115 | 289.15 | 1
0.05585 | 278.15 | 0.00115 | 289.65 | 0.15
0.05585 | 278.15 | 0.00115 | 289.65 | 0.2
0.05585 | 278.15 | 0.00115 | 289.65 | 0.3
0.05585 | 278.15 | 0.00115 | 289.65 | 0.4
0.05585 | 278.15 | 0.00115 | 289.65 | 0.5
0.05585 | 278.15 | 0.00115 | 289.65 | 0.6
0.05585 | 278.15 | 0.00115 | 289.65 | 0.7
0.05585 | 278.15 | 0.00115 | 289.65 | 0.8
0.05585 | 278.15 | 0.00115 | 289.65 | 0.9
0.05585 | 278.15 | 0.00115 | 289.65 | 1
0.05585 | 278.15 | 0.00115 | 290.15 | 0.15
0.05585 | 278.15 | 0.00115 | 290.15 | 0.2
0.05585 | 278.15 | 0.00115 | 290.15 | 0.3
0.05585 | 278.15 | 0.00115 | 290.15 | 0.4
0.05585 | 278.15 | 0.00115 | 290.15 | 0.5
0.05585 | 278.15 | 0.00115 | 290.15 | 0.6
0.05585 | 278.15 | 0.00115 | 290.15 | 0.7
0.05585 | 278.15 | 0.00115 | 290.15 | 0.8
0.05585 | 278.15 | 0.00115 | 290.15 | 0.9
0.05585 | 278.15 | 0.00115 | 290.15 | 1
0.05585 | 278.15 | 0.00115 | 290.65 | 0.15
0.05585 | 278.15 | 0.00115 | 290.65 | 0.2
0.05585 | 278.15 | 0.00115 | 290.65 | 0.3
0.05585 | 278.15 | 0.00115 | 290.65 | 0.4
0.05585 | 278.15 | 0.00115 | 290.65 | 0.5
0.05585 | 278.15 | 0.00115 | 290.65 | 0.6
0.05585 | 278.15 | 0.00115 | 290.65 | 0.7
0.05585 | 278.15 | 0.00115 | 290.65 | 0.8
0.05585 | 278.15 | 0.00115 | 290.65 | 0.9
0.05585 | 278.15 | 0.00115 | 290.65 | 1
0.05585 | 278.15 | 0.00115 | 291.15 | 0.15
0.05585 | 278.15 | 0.00115 | 291.15 | 0.2
0.05585 | 278.15 | 0.00115 | 291.15 | 0.3
0.05585 | 278.15 | 0.00115 | 291.15 | 0.4
0.05585 | 278.15 | 0.00115 | 291.15 | 0.5
0.05585 | 278.15 | 0.00115 | 291.15 | 0.6
0.05585 | 278.15 | 0.00115 | 291.15 | 0.7
0.05585 | 278.15 | 0.00115 | 291.15 | 0.8
0.05585 | 278.15 | 0.00115 | 291.15 | 0.9
0.05585 | 278.15 | 0.00115 | 291.15 | 1
0.05585 | 278.15 | 0.00115 | 294.15 | 0.15
0.05585 | 278.15 | 0.00115 | 294.15 | 0.2
0.05585 | 278.15 | 0.00115 | 294.15 | 0.3
0.05585 | 278.15 | 0.00115 | 294.15 | 0.4
0.05585 | 278.15 | 0.00115 | 294.15 | 0.5
0.05585 | 278.15 | 0.00115 | 294.15 | 0.6
0.05585 | 278.15 | 0.00115 | 294.15 | 0.7
0.05585 | 278.15 | 0.00115 | 294.15 | 0.8
0.05585 | 278.15 | 0.00115 | 294.15 | 0.9
0.05585 | 278.15 | 0.00115 | 294.15 | 1
0.05585 | 278.15 | 0.00115 | 297.15 | 0.15
0.05585 | 278.15 | 0.00115 | 297.15 | 0.2
0.05585 | 278.15 | 0.00115 | 297.15 | 0.3
0.05585 | 278.15 | 0.00115 | 297.15 | 0.4
0.05585 | 278.15 | 0.00115 | 297.15 | 0.5
0.05585 | 278.15 | 0.00115 | 297.15 | 0.6
0.05585 | 278.15 | 0.00115 | 297.15 | 0.7
0.05585 | 278.15 | 0.00115 | 297.15 | 0.8
0.05585 | 278.15 | 0.00115 | 297.15 | 0.9
0.05585 | 278.15 | 0.00115 | 297.15 | 1
0.05585 | 278.15 | 0.00115 | 300.15 | 0.15
0.05585 | 278.15 | 0.00115 | 300.15 | 0.2
0.05585 | 278.15 | 0.00115 | 300.15 | 0.3
0.05585 | 278.15 | 0.00115 | 300.15 | 0.4
0.05585 | 278.15 | 0.00115 | 300.15 | 0.5
0.05585 | 278.15 | 0.00115 | 300.15 | 0.6
0.05585 | 278.15 | 0.00115 | 300.15 | 0.7
0.05585 | 278.15 | 0.00115 | 300.15 | 0.8
0.05585 | 278.15 | 0.00115 | 300.15 | 0.9
0.05585 | 278.15 | 0.00115 | 300.15 | 1
0.05585 | 278.15 | 0.00115 | 303.15 | 0.15
0.05585 | 278.15 | 0.00115 | 303.15 | 0.2
0.05585 | 278.15 | 0.00115 | 303.15 | 0.3
0.05585 | 278.15 | 0.00115 | 303.15 | 0.4
0.05585 | 278.15 | 0.00115 | 303.15 | 0.5
0.05585 | 278.15 | 0.00115 | 303.15 | 0.6
0.05585 | 278.15 | 0.00115 | 303.15 | 0.7
0.05585 | 278.15 | 0.00115 | 303.15 | 0.8
0.05585 | 278.15 | 0.00115 | 303.15 | 0.9
0.05585 | 278.15 | 0.00115 | 303.15 | 1
0.05585 | 278.15 | 0.077 | 283.65 | 0.15
0.05585 | 278.15 | 0.077 | 283.65 | 0.2
0.05585 | 278.15 | 0.077 | 283.65 | 0.3
0.05585 | 278.15 | 0.077 | 283.65 | 0.4
0.05585 | 278.15 | 0.077 | 283.65 | 0.5
0.05585 | 278.15 | 0.077 | 283.65 | 0.6
0.05585 | 278.15 | 0.077 | 283.65 | 0.7
0.05585 | 278.15 | 0.077 | 283.65 | 0.8
0.05585 | 278.15 | 0.077 | 283.65 | 0.9
0.05585 | 278.15 | 0.077 | 283.65 | 1
0.05585 | 278.15 | 0.077 | 284.15 | 0.15
0.05585 | 278.15 | 0.077 | 284.15 | 0.2
0.05585 | 278.15 | 0.077 | 284.15 | 0.3
0.05585 | 278.15 | 0.077 | 284.15 | 0.4
0.05585 | 278.15 | 0.077 | 284.15 | 0.5
0.05585 | 278.15 | 0.077 | 284.15 | 0.6
0.05585 | 278.15 | 0.077 | 284.15 | 0.7
0.05585 | 278.15 | 0.077 | 284.15 | 0.8
0.05585 | 278.15 | 0.077 | 284.15 | 0.9
0.05585 | 278.15 | 0.077 | 284.15 | 1
0.05585 | 278.15 | 0.077 | 284.65 | 0.15
0.05585 | 278.15 | 0.077 | 284.65 | 0.2
0.05585 | 278.15 | 0.077 | 284.65 | 0.3
0.05585 | 278.15 | 0.077 | 284.65 | 0.4
0.05585 | 278.15 | 0.077 | 284.65 | 0.5
0.05585 | 278.15 | 0.077 | 284.65 | 0.6
0.05585 | 278.15 | 0.077 | 284.65 | 0.7
0.05585 | 278.15 | 0.077 | 284.65 | 0.8
0.05585 | 278.15 | 0.077 | 284.65 | 0.9
0.05585 | 278.15 | 0.077 | 284.65 | 1
0.05585 | 278.15 | 0.077 | 285.15 | 0.15
0.05585 | 278.15 | 0.077 | 285.15 | 0.2
0.05585 | 278.15 | 0.077 | 285.15 | 0.3
0.05585 | 278.15 | 0.077 | 285.15 | 0.4
0.05585 | 278.15 | 0.077 | 285.15 | 0.5
0.05585 | 278.15 | 0.077 | 285.15 | 0.6
0.05585 | 278.15 | 0.077 | 285.15 | 0.7
0.05585 | 278.15 | 0.077 | 285.15 | 0.8
0.05585 | 278.15 | 0.077 | 285.15 | 0.9
0.05585 | 278.15 | 0.077 | 285.15 | 1
0.05585 | 278.15 | 0.077 | 285.65 | 0.15
0.05585 | 278.15 | 0.077 | 285.65 | 0.2
0.05585 | 278.15 | 0.077 | 285.65 | 0.3
0.05585 | 278.15 | 0.077 | 285.65 | 0.4
0.05585 | 278.15 | 0.077 | 285.65 | 0.5
0.05585 | 278.15 | 0.077 | 285.65 | 0.6
0.05585 | 278.15 | 0.077 | 285.65 | 0.7
0.05585 | 278.15 | 0.077 | 285.65 | 0.8
0.05585 | 278.15 | 0.077 | 285.65 | 0.9
0.05585 | 278.15 | 0.077 | 285.65 | 1
0.05585 | 278.15 | 0.077 | 286.15 | 0.15
0.05585 | 278.15 | 0.077 | 286.15 | 0.2
0.05585 | 278.15 | 0.077 | 286.15 | 0.3
0.05585 | 278.15 | 0.077 | 286.15 | 0.4
0.05585 | 278.15 | 0.077 | 286.15 | 0.5
0.05585 | 278.15 | 0.077 | 286.15 | 0.6
0.05585 | 278.15 | 0.077 | 286.15 | 0.7
0.05585 | 278.15 | 0.077 | 286.15 | 0.8
0.05585 | 278.15 | 0.077 | 286.15 | 0.9
0.05585 | 278.15 | 0.077 | 286.15 | 1
0.05585 | 278.15 | 0.077 | 286.65 | 0.15
0.05585 | 278.15 | 0.077 | 286.65 | 0.2
0.05585 | 278.15 | 0.077 | 286.65 | 0.3
0.05585 | 278.15 | 0.077 | 286.65 | 0.4
0.05585 | 278.15 | 0.077 | 286.65 | 0.5
0.05585 | 278.15 | 0.077 | 286.65 | 0.6
0.05585 | 278.15 | 0.077 | 286.65 | 0.7
0.05585 | 278.15 | 0.077 | 286.65 | 0.8
0.05585 | 278.15 | 0.077 | 286.65 | 0.9
0.05585 | 278.15 | 0.077 | 286.65 | 1
0.05585 | 278.15 | 0.077 | 287.15 | 0.15
0.05585 | 278.15 | 0.077 | 287.15 | 0.2
0.05585 | 278.15 | 0.077 | 287.15 | 0.3
0.05585 | 278.15 | 0.077 | 287.15 | 0.4
0.05585 | 278.15 | 0.077 | 287.15 | 0.5
0.05585 | 278.15 | 0.077 | 287.15 | 0.6
0.05585 | 278.15 | 0.077 | 287.15 | 0.7
0.05585 | 278.15 | 0.077 | 287.15 | 0.8
0.05585 | 278.15 | 0.077 | 287.15 | 0.9
0.05585 | 278.15 | 0.077 | 287.15 | 1
0.05585 | 278.15 | 0.077 | 287.65 | 0.15
0.05585 | 278.15 | 0.077 | 287.65 | 0.2
0.05585 | 278.15 | 0.077 | 287.65 | 0.3
0.05585 | 278.15 | 0.077 | 287.65 | 0.4
0.05585 | 278.15 | 0.077 | 287.65 | 0.5
0.05585 | 278.15 | 0.077 | 287.65 | 0.6
0.05585 | 278.15 | 0.077 | 287.65 | 0.7
0.05585 | 278.15 | 0.077 | 287.65 | 0.8
0.05585 | 278.15 | 0.077 | 287.65 | 0.9
0.05585 | 278.15 | 0.077 | 287.65 | 1
0.05585 | 278.15 | 0.077 | 288.15 | 0.15
0.05585 | 278.15 | 0.077 | 288.15 | 0.2
0.05585 | 278.15 | 0.077 | 288.15 | 0.3
0.05585 | 278.15 | 0.077 | 288.15 | 0.4
0.05585 | 278.15 | 0.077 | 288.15 | 0.5
0.05585 | 278.15 | 0.077 | 288.15 | 0.6
0.05585 | 278.15 | 0.077 | 288.15 | 0.7
0.05585 | 278.15 | 0.077 | 288.15 | 0.8
0.05585 | 278.15 | 0.077 | 288.15 | 0.9
0.05585 | 278.15 | 0.077 | 288.15 | 1
0.05585 | 278.15 | 0.077 | 288.65 | 0.15
0.05585 | 278.15 | 0.077 | 288.65 | 0.2
0.05585 | 278.15 | 0.077 | 288.65 | 0.3
0.05585 | 278.15 | 0.077 | 288.65 | 0.4
0.05585 | 278.15 | 0.077 | 288.65 | 0.5
0.05585 | 278.15 | 0.077 | 288.65 | 0.6
0.05585 | 278.15 | 0.077 | 288.65 | 0.7
0.05585 | 278.15 | 0.077 | 288.65 | 0.8
0.05585 | 278.15 | 0.077 | 288.65 | 0.9
0.05585 | 278.15 | 0.077 | 288.65 | 1
0.05585 | 278.15 | 0.077 | 289.15 | 0.15
0.05585 | 278.15 | 0.077 | 289.15 | 0.2
0.05585 | 278.15 | 0.077 | 289.15 | 0.3
0.05585 | 278.15 | 0.077 | 289.15 | 0.4
0.05585 | 278.15 | 0.077 | 289.15 | 0.5
0.05585 | 278.15 | 0.077 | 289.15 | 0.6
0.05585 | 278.15 | 0.077 | 289.15 | 0.7
0.05585 | 278.15 | 0.077 | 289.15 | 0.8
0.05585 | 278.15 | 0.077 | 289.15 | 0.9
0.05585 | 278.15 | 0.077 | 289.15 | 1
0.05585 | 278.15 | 0.077 | 289.65 | 0.15
0.05585 | 278.15 | 0.077 | 289.65 | 0.2
0.05585 | 278.15 | 0.077 | 289.65 | 0.3
0.05585 | 278.15 | 0.077 | 289.65 | 0.4
0.05585 | 278.15 | 0.077 | 289.65 | 0.5
0.05585 | 278.15 | 0.077 | 289.65 | 0.6
0.05585 | 278.15 | 0.077 | 289.65 | 0.7
0.05585 | 278.15 | 0.077 | 289.65 | 0.8
0.05585 | 278.15 | 0.077 | 289.65 | 0.9
0.05585 | 278.15 | 0.077 | 289.65 | 1
0.05585 | 278.15 | 0.077 | 290.15 | 0.15
0.05585 | 278.15 | 0.077 | 290.15 | 0.2
0.05585 | 278.15 | 0.077 | 290.15 | 0.3
0.05585 | 278.15 | 0.077 | 290.15 | 0.4
0.05585 | 278.15 | 0.077 | 290.15 | 0.5
0.05585 | 278.15 | 0.077 | 290.15 | 0.6
0.05585 | 278.15 | 0.077 | 290.15 | 0.7
0.05585 | 278.15 | 0.077 | 290.15 | 0.8
0.05585 | 278.15 | 0.077 | 290.15 | 0.9
0.05585 | 278.15 | 0.077 | 290.15 | 1
0.05585 | 278.15 | 0.077 | 290.65 | 0.15
0.05585 | 278.15 | 0.077 | 290.65 | 0.2
0.05585 | 278.15 | 0.077 | 290.65 | 0.3
0.05585 | 278.15 | 0.077 | 290.65 | 0.4
0.05585 | 278.15 | 0.077 | 290.65 | 0.5
0.05585 | 278.15 | 0.077 | 290.65 | 0.6
0.05585 | 278.15 | 0.077 | 290.65 | 0.7
0.05585 | 278.15 | 0.077 | 290.65 | 0.8
0.05585 | 278.15 | 0.077 | 290.65 | 0.9
0.05585 | 278.15 | 0.077 | 290.65 | 1
0.05585 | 278.15 | 0.077 | 291.15 | 0.15
0.05585 | 278.15 | 0.077 | 291.15 | 0.2
0.05585 | 278.15 | 0.077 | 291.15 | 0.3
0.05585 | 278.15 | 0.077 | 291.15 | 0.4
0.05585 | 278.15 | 0.077 | 291.15 | 0.5
0.05585 | 278.15 | 0.077 | 291.15 | 0.6
0.05585 | 278.15 | 0.077 | 291.15 | 0.7
0.05585 | 278.15 | 0.077 | 291.15 | 0.8
0.05585 | 278.15 | 0.077 | 291.15 | 0.9
0.05585 | 278.15 | 0.077 | 291.15 | 1
0.05585 | 278.15 | 0.077 | 294.15 | 0.15
0.05585 | 278.15 | 0.077 | 294.15 | 0.2
0.05585 | 278.15 | 0.077 | 294.15 | 0.3
0.05585 | 278.15 | 0.077 | 294.15 | 0.4
0.05585 | 278.15 | 0.077 | 294.15 | 0.5
0.05585 | 278.15 | 0.077 | 294.15 | 0.6
0.05585 | 278.15 | 0.077 | 294.15 | 0.7
0.05585 | 278.15 | 0.077 | 294.15 | 0.8
0.05585 | 278.15 | 0.077 | 294.15 | 0.9
0.05585 | 278.15 | 0.077 | 294.15 | 1
0.05585 | 278.15 | 0.077 | 297.15 | 0.15
0.05585 | 278.15 | 0.077 | 297.15 | 0.2
0.05585 | 278.15 | 0.077 | 297.15 | 0.3
0.05585 | 278.15 | 0.077 | 297.15 | 0.4
0.05585 | 278.15 | 0.077 | 297.15 | 0.5
0.05585 | 278.15 | 0.077 | 297.15 | 0.6
0.05585 | 278.15 | 0.077 | 297.15 | 0.7
0.05585 | 278.15 | 0.077 | 297.15 | 0.8
0.05585 | 278.15 | 0.077 | 297.15 | 0.9
0.05585 | 278.15 | 0.077 | 297.15 | 1
0.05585 | 278.15 | 0.077 | 300.15 | 0.15
0.05585 | 278.15 | 0.077 | 300.15 | 0.2
0.05585 | 278.15 | 0.077 | 300.15 | 0.3
0.05585 | 278.15 | 0.077 | 300.15 | 0.4
0.05585 | 278.15 | 0.077 | 300.15 | 0.5
0.05585 | 278.15 | 0.077 | 300.15 | 0.6
0.05585 | 278.15 | 0.077 | 300.15 | 0.7
0.05585 | 278.15 | 0.077 | 300.15 | 0.8
0.05585 | 278.15 | 0.077 | 300.15 | 0.9
0.05585 | 278.15 | 0.077 | 300.15 | 1
0.05585 | 278.15 | 0.077 | 303.15 | 0.15
0.05585 | 278.15 | 0.077 | 303.15 | 0.2
0.05585 | 278.15 | 0.077 | 303.15 | 0.3
0.05585 | 278.15 | 0.077 | 303.15 | 0.4
0.05585 | 278.15 | 0.077 | 303.15 | 0.5
0.05585 | 278.15 | 0.077 | 303.15 | 0.6
0.05585 | 278.15 | 0.077 | 303.15 | 0.7
0.05585 | 278.15 | 0.077 | 303.15 | 0.8
0.05585 | 278.15 | 0.077 | 303.15 | 0.9
0.05585 | 278.15 | 0.077 | 303.15 | 1
0.05585 | 278.15 | 0.09437 | 283.65 | 0.15
0.05585 | 278.15 | 0.09437 | 283.65 | 0.2
0.05585 | 278.15 | 0.09437 | 283.65 | 0.3
0.05585 | 278.15 | 0.09437 | 283.65 | 0.4
0.05585 | 278.15 | 0.09437 | 283.65 | 0.5
0.05585 | 278.15 | 0.09437 | 283.65 | 0.6
0.05585 | 278.15 | 0.09437 | 283.65 | 0.7
0.05585 | 278.15 | 0.09437 | 283.65 | 0.8
0.05585 | 278.15 | 0.09437 | 283.65 | 0.9
0.05585 | 278.15 | 0.09437 | 283.65 | 1
0.05585 | 278.15 | 0.09437 | 284.15 | 0.15
0.05585 | 278.15 | 0.09437 | 284.15 | 0.2
0.05585 | 278.15 | 0.09437 | 284.15 | 0.3
0.05585 | 278.15 | 0.09437 | 284.15 | 0.4
0.05585 | 278.15 | 0.09437 | 284.15 | 0.5
0.05585 | 278.15 | 0.09437 | 284.15 | 0.6
0.05585 | 278.15 | 0.09437 | 284.15 | 0.7
0.05585 | 278.15 | 0.09437 | 284.15 | 0.8
0.05585 | 278.15 | 0.09437 | 284.15 | 0.9
0.05585 | 278.15 | 0.09437 | 284.15 | 1
0.05585 | 278.15 | 0.09437 | 284.65 | 0.15
0.05585 | 278.15 | 0.09437 | 284.65 | 0.2
0.05585 | 278.15 | 0.09437 | 284.65 | 0.3
0.05585 | 278.15 | 0.09437 | 284.65 | 0.4
0.05585 | 278.15 | 0.09437 | 284.65 | 0.5
0.05585 | 278.15 | 0.09437 | 284.65 | 0.6
0.05585 | 278.15 | 0.09437 | 284.65 | 0.7
0.05585 | 278.15 | 0.09437 | 284.65 | 0.8
0.05585 | 278.15 | 0.09437 | 284.65 | 0.9
0.05585 | 278.15 | 0.09437 | 284.65 | 1
0.05585 | 278.15 | 0.09437 | 285.15 | 0.15
0.05585 | 278.15 | 0.09437 | 285.15 | 0.2
0.05585 | 278.15 | 0.09437 | 285.15 | 0.3
0.05585 | 278.15 | 0.09437 | 285.15 | 0.4
0.05585 | 278.15 | 0.09437 | 285.15 | 0.5
0.05585 | 278.15 | 0.09437 | 285.15 | 0.6
0.05585 | 278.15 | 0.09437 | 285.15 | 0.7
0.05585 | 278.15 | 0.09437 | 285.15 | 0.8
0.05585 | 278.15 | 0.09437 | 285.15 | 0.9
0.05585 | 278.15 | 0.09437 | 285.15 | 1
0.05585 | 278.15 | 0.09437 | 285.65 | 0.15
0.05585 | 278.15 | 0.09437 | 285.65 | 0.2
0.05585 | 278.15 | 0.09437 | 285.65 | 0.3
0.05585 | 278.15 | 0.09437 | 285.65 | 0.4
0.05585 | 278.15 | 0.09437 | 285.65 | 0.5
0.05585 | 278.15 | 0.09437 | 285.65 | 0.6
0.05585 | 278.15 | 0.09437 | 285.65 | 0.7
0.05585 | 278.15 | 0.09437 | 285.65 | 0.8
0.05585 | 278.15 | 0.09437 | 285.65 | 0.9
0.05585 | 278.15 | 0.09437 | 285.65 | 1
0.05585 | 278.15 | 0.09437 | 286.15 | 0.15
0.05585 | 278.15 | 0.09437 | 286.15 | 0.2
0.05585 | 278.15 | 0.09437 | 286.15 | 0.3
0.05585 | 278.15 | 0.09437 | 286.15 | 0.4
0.05585 | 278.15 | 0.09437 | 286.15 | 0.5
0.05585 | 278.15 | 0.09437 | 286.15 | 0.6
0.05585 | 278.15 | 0.09437 | 286.15 | 0.7
0.05585 | 278.15 | 0.09437 | 286.15 | 0.8
0.05585 | 278.15 | 0.09437 | 286.15 | 0.9
0.05585 | 278.15 | 0.09437 | 286.15 | 1
0.05585 | 278.15 | 0.09437 | 286.65 | 0.15
0.05585 | 278.15 | 0.09437 | 286.65 | 0.2
0.05585 | 278.15 | 0.09437 | 286.65 | 0.3
0.05585 | 278.15 | 0.09437 | 286.65 | 0.4
0.05585 | 278.15 | 0.09437 | 286.65 | 0.5
0.05585 | 278.15 | 0.09437 | 286.65 | 0.6
0.05585 | 278.15 | 0.09437 | 286.65 | 0.7
0.05585 | 278.15 | 0.09437 | 286.65 | 0.8
0.05585 | 278.15 | 0.09437 | 286.65 | 0.9
0.05585 | 278.15 | 0.09437 | 286.65 | 1
0.05585 | 278.15 | 0.09437 | 287.15 | 0.15
0.05585 | 278.15 | 0.09437 | 287.15 | 0.2
0.05585 | 278.15 | 0.09437 | 287.15 | 0.3
0.05585 | 278.15 | 0.09437 | 287.15 | 0.4
0.05585 | 278.15 | 0.09437 | 287.15 | 0.5
0.05585 | 278.15 | 0.09437 | 287.15 | 0.6
0.05585 | 278.15 | 0.09437 | 287.15 | 0.7
0.05585 | 278.15 | 0.09437 | 287.15 | 0.8
0.05585 | 278.15 | 0.09437 | 287.15 | 0.9
0.05585 | 278.15 | 0.09437 | 287.15 | 1
0.05585 | 278.15 | 0.09437 | 287.65 | 0.15
0.05585 | 278.15 | 0.09437 | 287.65 | 0.2
0.05585 | 278.15 | 0.09437 | 287.65 | 0.3
0.05585 | 278.15 | 0.09437 | 287.65 | 0.4
0.05585 | 278.15 | 0.09437 | 287.65 | 0.5
0.05585 | 278.15 | 0.09437 | 287.65 | 0.6
0.05585 | 278.15 | 0.09437 | 287.65 | 0.7
0.05585 | 278.15 | 0.09437 | 287.65 | 0.8
0.05585 | 278.15 | 0.09437 | 287.65 | 0.9
0.05585 | 278.15 | 0.09437 | 287.65 | 1
0.05585 | 278.15 | 0.09437 | 288.15 | 0.15
0.05585 | 278.15 | 0.09437 | 288.15 | 0.2
0.05585 | 278.15 | 0.09437 | 288.15 | 0.3
0.05585 | 278.15 | 0.09437 | 288.15 | 0.4
0.05585 | 278.15 | 0.09437 | 288.15 | 0.5
0.05585 | 278.15 | 0.09437 | 288.15 | 0.6
0.05585 | 278.15 | 0.09437 | 288.15 | 0.7
0.05585 | 278.15 | 0.09437 | 288.15 | 0.8
0.05585 | 278.15 | 0.09437 | 288.15 | 0.9
0.05585 | 278.15 | 0.09437 | 288.15 | 1
0.05585 | 278.15 | 0.09437 | 288.65 | 0.15
0.05585 | 278.15 | 0.09437 | 288.65 | 0.2
0.05585 | 278.15 | 0.09437 | 288.65 | 0.3
0.05585 | 278.15 | 0.09437 | 288.65 | 0.4
0.05585 | 278.15 | 0.09437 | 288.65 | 0.5
0.05585 | 278.15 | 0.09437 | 288.65 | 0.6
0.05585 | 278.15 | 0.09437 | 288.65 | 0.7
0.05585 | 278.15 | 0.09437 | 288.65 | 0.8
0.05585 | 278.15 | 0.09437 | 288.65 | 0.9
0.05585 | 278.15 | 0.09437 | 288.65 | 1
0.05585 | 278.15 | 0.09437 | 289.15 | 0.15
0.05585 | 278.15 | 0.09437 | 289.15 | 0.2
0.05585 | 278.15 | 0.09437 | 289.15 | 0.3
0.05585 | 278.15 | 0.09437 | 289.15 | 0.4
0.05585 | 278.15 | 0.09437 | 289.15 | 0.5
0.05585 | 278.15 | 0.09437 | 289.15 | 0.6
0.05585 | 278.15 | 0.09437 | 289.15 | 0.7
0.05585 | 278.15 | 0.09437 | 289.15 | 0.8
0.05585 | 278.15 | 0.09437 | 289.15 | 0.9
0.05585 | 278.15 | 0.09437 | 289.15 | 1
0.05585 | 278.15 | 0.09437 | 289.65 | 0.15
0.05585 | 278.15 | 0.09437 | 289.65 | 0.2
0.05585 | 278.15 | 0.09437 | 289.65 | 0.3
0.05585 | 278.15 | 0.09437 | 289.65 | 0.4
0.05585 | 278.15 | 0.09437 | 289.65 | 0.5
0.05585 | 278.15 | 0.09437 | 289.65 | 0.6
0.05585 | 278.15 | 0.09437 | 289.65 | 0.7
0.05585 | 278.15 | 0.09437 | 289.65 | 0.8
0.05585 | 278.15 | 0.09437 | 289.65 | 0.9
0.05585 | 278.15 | 0.09437 | 289.65 | 1
0.05585 | 278.15 | 0.09437 | 290.15 | 0.15
0.05585 | 278.15 | 0.09437 | 290.15 | 0.2
0.05585 | 278.15 | 0.09437 | 290.15 | 0.3
0.05585 | 278.15 | 0.09437 | 290.15 | 0.4
0.05585 | 278.15 | 0.09437 | 290.15 | 0.5
0.05585 | 278.15 | 0.09437 | 290.15 | 0.6
0.05585 | 278.15 | 0.09437 | 290.15 | 0.7
0.05585 | 278.15 | 0.09437 | 290.15 | 0.8
0.05585 | 278.15 | 0.09437 | 290.15 | 0.9
0.05585 | 278.15 | 0.09437 | 290.15 | 1
0.05585 | 278.15 | 0.09437 | 290.65 | 0.15
0.05585 | 278.15 | 0.09437 | 290.65 | 0.2
0.05585 | 278.15 | 0.09437 | 290.65 | 0.3
0.05585 | 278.15 | 0.09437 | 290.65 | 0.4
0.05585 | 278.15 | 0.09437 | 290.65 | 0.5
0.05585 | 278.15 | 0.09437 | 290.65 | 0.6
0.05585 | 278.15 | 0.09437 | 290.65 | 0.7
0.05585 | 278.15 | 0.09437 | 290.65 | 0.8
0.05585 | 278.15 | 0.09437 | 290.65 | 0.9
0.05585 | 278.15 | 0.09437 | 290.65 | 1
0.05585 | 278.15 | 0.09437 | 291.15 | 0.15
0.05585 | 278.15 | 0.09437 | 291.15 | 0.2
0.05585 | 278.15 | 0.09437 | 291.15 | 0.3
0.05585 | 278.15 | 0.09437 | 291.15 | 0.4
0.05585 | 278.15 | 0.09437 | 291.15 | 0.5
0.05585 | 278.15 | 0.09437 | 291.15 | 0.6
0.05585 | 278.15 | 0.09437 | 291.15 | 0.7
0.05585 | 278.15 | 0.09437 | 291.15 | 0.8
0.05585 | 278.15 | 0.09437 | 291.15 | 0.9
0.05585 | 278.15 | 0.09437 | 291.15 | 1
0.05585 | 278.15 | 0.09437 | 294.15 | 0.15
0.05585 | 278.15 | 0.09437 | 294.15 | 0.2
0.05585 | 278.15 | 0.09437 | 294.15 | 0.3
0.05585 | 278.15 | 0.09437 | 294.15 | 0.4
0.05585 | 278.15 | 0.09437 | 294.15 | 0.5
0.05585 | 278.15 | 0.09437 | 294.15 | 0.6
0.05585 | 278.15 | 0.09437 | 294.15 | 0.7
0.05585 | 278.15 | 0.09437 | 294.15 | 0.8
0.05585 | 278.15 | 0.09437 | 294.15 | 0.9
0.05585 | 278.15 | 0.09437 | 294.15 | 1
0.05585 | 278.15 | 0.09437 | 297.15 | 0.15
0.05585 | 278.15 | 0.09437 | 297.15 | 0.2
0.05585 | 278.15 | 0.09437 | 297.15 | 0.3
0.05585 | 278.15 | 0.09437 | 297.15 | 0.4
0.05585 | 278.15 | 0.09437 | 297.15 | 0.5
0.05585 | 278.15 | 0.09437 | 297.15 | 0.6
0.05585 | 278.15 | 0.09437 | 297.15 | 0.7
0.05585 | 278.15 | 0.09437 | 297.15 | 0.8
0.05585 | 278.15 | 0.09437 | 297.15 | 0.9
0.05585 | 278.15 | 0.09437 | 297.15 | 1
0.05585 | 278.15 | 0.09437 | 300.15 | 0.15
0.05585 | 278.15 | 0.09437 | 300.15 | 0.2
0.05585 | 278.15 | 0.09437 | 300.15 | 0.3
0.05585 | 278.15 | 0.09437 | 300.15 | 0.4
0.05585 | 278.15 | 0.09437 | 300.15 | 0.5
0.05585 | 278.15 | 0.09437 | 300.15 | 0.6
0.05585 | 278.15 | 0.09437 | 300.15 | 0.7
0.05585 | 278.15 | 0.09437 | 300.15 | 0.8
0.05585 | 278.15 | 0.09437 | 300.15 | 0.9
0.05585 | 278.15 | 0.09437 | 300.15 | 1
0.05585 | 278.15 | 0.09437 | 303.15 | 0.15
0.05585 | 278.15 | 0.09437 | 303.15 | 0.2
0.05585 | 278.15 | 0.09437 | 303.15 | 0.3
0.05585 | 278.15 | 0.09437 | 303.15 | 0.4
0.05585 | 278.15 | 0.09437 | 303.15 | 0.5
0.05585 | 278.15 | 0.09437 | 303.15 | 0.6
0.05585 | 278.15 | 0.09437 | 303.15 | 0.7
0.05585 | 278.15 | 0.09437 | 303.15 | 0.8
0.05585 | 278.15 | 0.09437 | 303.15 | 0.9
0.05585 | 278.15 | 0.09437 | 303.15 | 1
0.05585 | 278.15 | 0.09644 | 283.65 | 0.15
0.05585 | 278.15 | 0.09644 | 283.65 | 0.2
0.05585 | 278.15 | 0.09644 | 283.65 | 0.3
0.05585 | 278.15 | 0.09644 | 283.65 | 0.4
0.05585 | 278.15 | 0.09644 | 283.65 | 0.5
0.05585 | 278.15 | 0.09644 | 283.65 | 0.6
0.05585 | 278.15 | 0.09644 | 283.65 | 0.7
0.05585 | 278.15 | 0.09644 | 283.65 | 0.8
0.05585 | 278.15 | 0.09644 | 283.65 | 0.9
0.05585 | 278.15 | 0.09644 | 283.65 | 1
0.05585 | 278.15 | 0.09644 | 284.15 | 0.15
0.05585 | 278.15 | 0.09644 | 284.15 | 0.2
0.05585 | 278.15 | 0.09644 | 284.15 | 0.3
0.05585 | 278.15 | 0.09644 | 284.15 | 0.4
0.05585 | 278.15 | 0.09644 | 284.15 | 0.5
0.05585 | 278.15 | 0.09644 | 284.15 | 0.6
0.05585 | 278.15 | 0.09644 | 284.15 | 0.7
0.05585 | 278.15 | 0.09644 | 284.15 | 0.8
0.05585 | 278.15 | 0.09644 | 284.15 | 0.9
0.05585 | 278.15 | 0.09644 | 284.15 | 1
0.05585 | 278.15 | 0.09644 | 284.65 | 0.15
0.05585 | 278.15 | 0.09644 | 284.65 | 0.2
0.05585 | 278.15 | 0.09644 | 284.65 | 0.3
0.05585 | 278.15 | 0.09644 | 284.65 | 0.4
0.05585 | 278.15 | 0.09644 | 284.65 | 0.5
0.05585 | 278.15 | 0.09644 | 284.65 | 0.6
0.05585 | 278.15 | 0.09644 | 284.65 | 0.7
0.05585 | 278.15 | 0.09644 | 284.65 | 0.8
0.05585 | 278.15 | 0.09644 | 284.65 | 0.9
0.05585 | 278.15 | 0.09644 | 284.65 | 1
0.05585 | 278.15 | 0.09644 | 285.15 | 0.15
0.05585 | 278.15 | 0.09644 | 285.15 | 0.2
0.05585 | 278.15 | 0.09644 | 285.15 | 0.3
0.05585 | 278.15 | 0.09644 | 285.15 | 0.4
0.05585 | 278.15 | 0.09644 | 285.15 | 0.5
0.05585 | 278.15 | 0.09644 | 285.15 | 0.6
0.05585 | 278.15 | 0.09644 | 285.15 | 0.7
0.05585 | 278.15 | 0.09644 | 285.15 | 0.8
0.05585 | 278.15 | 0.09644 | 285.15 | 0.9
0.05585 | 278.15 | 0.09644 | 285.15 | 1
0.05585 | 278.15 | 0.09644 | 285.65 | 0.15
0.05585 | 278.15 | 0.09644 | 285.65 | 0.2
0.05585 | 278.15 | 0.09644 | 285.65 | 0.3
0.05585 | 278.15 | 0.09644 | 285.65 | 0.4
0.05585 | 278.15 | 0.09644 | 285.65 | 0.5
0.05585 | 278.15 | 0.09644 | 285.65 | 0.6
0.05585 | 278.15 | 0.09644 | 285.65 | 0.7
0.05585 | 278.15 | 0.09644 | 285.65 | 0.8
0.05585 | 278.15 | 0.09644 | 285.65 | 0.9
0.05585 | 278.15 | 0.09644 | 285.65 | 1
0.05585 | 278.15 | 0.09644 | 286.15 | 0.15
0.05585 | 278.15 | 0.09644 | 286.15 | 0.2
0.05585 | 278.15 | 0.09644 | 286.15 | 0.3
0.05585 | 278.15 | 0.09644 | 286.15 | 0.4
0.05585 | 278.15 | 0.09644 | 286.15 | 0.5
0.05585 | 278.15 | 0.09644 | 286.15 | 0.6
0.05585 | 278.15 | 0.09644 | 286.15 | 0.7
0.05585 | 278.15 | 0.09644 | 286.15 | 0.8
0.05585 | 278.15 | 0.09644 | 286.15 | 0.9
0.05585 | 278.15 | 0.09644 | 286.15 | 1
0.05585 | 278.15 | 0.09644 | 286.65 | 0.15
0.05585 | 278.15 | 0.09644 | 286.65 | 0.2
0.05585 | 278.15 | 0.09644 | 286.65 | 0.3
0.05585 | 278.15 | 0.09644 | 286.65 | 0.4
0.05585 | 278.15 | 0.09644 | 286.65 | 0.5
0.05585 | 278.15 | 0.09644 | 286.65 | 0.6
0.05585 | 278.15 | 0.09644 | 286.65 | 0.7
0.05585 | 278.15 | 0.09644 | 286.65 | 0.8
0.05585 | 278.15 | 0.09644 | 286.65 | 0.9
0.05585 | 278.15 | 0.09644 | 286.65 | 1
0.05585 | 278.15 | 0.09644 | 287.15 | 0.15
0.05585 | 278.15 | 0.09644 | 287.15 | 0.2
0.05585 | 278.15 | 0.09644 | 287.15 | 0.3
0.05585 | 278.15 | 0.09644 | 287.15 | 0.4
0.05585 | 278.15 | 0.09644 | 287.15 | 0.5
0.05585 | 278.15 | 0.09644 | 287.15 | 0.6
0.05585 | 278.15 | 0.09644 | 287.15 | 0.7
0.05585 | 278.15 | 0.09644 | 287.15 | 0.8
0.05585 | 278.15 | 0.09644 | 287.15 | 0.9
0.05585 | 278.15 | 0.09644 | 287.15 | 1
0.05585 | 278.15 | 0.09644 | 287.65 | 0.15
0.05585 | 278.15 | 0.09644 | 287.65 | 0.2
0.05585 | 278.15 | 0.09644 | 287.65 | 0.3
0.05585 | 278.15 | 0.09644 | 287.65 | 0.4
0.05585 | 278.15 | 0.09644 | 287.65 | 0.5
0.05585 | 278.15 | 0.09644 | 287.65 | 0.6
0.05585 | 278.15 | 0.09644 | 287.65 | 0.7
0.05585 | 278.15 | 0.09644 | 287.65 | 0.8
0.05585 | 278.15 | 0.09644 | 287.65 | 0.9
0.05585 | 278.15 | 0.09644 | 287.65 | 1
0.05585 | 278.15 | 0.09644 | 288.15 | 0.15
0.05585 | 278.15 | 0.09644 | 288.15 | 0.2
0.05585 | 278.15 | 0.09644 | 288.15 | 0.3
0.05585 | 278.15 | 0.09644 | 288.15 | 0.4
0.05585 | 278.15 | 0.09644 | 288.15 | 0.5
0.05585 | 278.15 | 0.09644 | 288.15 | 0.6
0.05585 | 278.15 | 0.09644 | 288.15 | 0.7
0.05585 | 278.15 | 0.09644 | 288.15 | 0.8
0.05585 | 278.15 | 0.09644 | 288.15 | 0.9
0.05585 | 278.15 | 0.09644 | 288.15 | 1
0.05585 | 278.15 | 0.09644 | 288.65 | 0.15
0.05585 | 278.15 | 0.09644 | 288.65 | 0.2
0.05585 | 278.15 | 0.09644 | 288.65 | 0.3
0.05585 | 278.15 | 0.09644 | 288.65 | 0.4
0.05585 | 278.15 | 0.09644 | 288.65 | 0.5
0.05585 | 278.15 | 0.09644 | 288.65 | 0.6
0.05585 | 278.15 | 0.09644 | 288.65 | 0.7
0.05585 | 278.15 | 0.09644 | 288.65 | 0.8
0.05585 | 278.15 | 0.09644 | 288.65 | 0.9
0.05585 | 278.15 | 0.09644 | 288.65 | 1
0.05585 | 278.15 | 0.09644 | 289.15 | 0.15
0.05585 | 278.15 | 0.09644 | 289.15 | 0.2
0.05585 | 278.15 | 0.09644 | 289.15 | 0.3
0.05585 | 278.15 | 0.09644 | 289.15 | 0.4
0.05585 | 278.15 | 0.09644 | 289.15 | 0.5
0.05585 | 278.15 | 0.09644 | 289.15 | 0.6
0.05585 | 278.15 | 0.09644 | 289.15 | 0.7
0.05585 | 278.15 | 0.09644 | 289.15 | 0.8
0.05585 | 278.15 | 0.09644 | 289.15 | 0.9
0.05585 | 278.15 | 0.09644 | 289.15 | 1
0.05585 | 278.15 | 0.09644 | 289.65 | 0.15
0.05585 | 278.15 | 0.09644 | 289.65 | 0.2
0.05585 | 278.15 | 0.09644 | 289.65 | 0.3
0.05585 | 278.15 | 0.09644 | 289.65 | 0.4
0.05585 | 278.15 | 0.09644 | 289.65 | 0.5
0.05585 | 278.15 | 0.09644 | 289.65 | 0.6
0.05585 | 278.15 | 0.09644 | 289.65 | 0.7
0.05585 | 278.15 | 0.09644 | 289.65 | 0.8
0.05585 | 278.15 | 0.09644 | 289.65 | 0.9
0.05585 | 278.15 | 0.09644 | 289.65 | 1
0.05585 | 278.15 | 0.09644 | 290.15 | 0.15
0.05585 | 278.15 | 0.09644 | 290.15 | 0.2
0.05585 | 278.15 | 0.09644 | 290.15 | 0.3
0.05585 | 278.15 | 0.09644 | 290.15 | 0.4
0.05585 | 278.15 | 0.09644 | 290.15 | 0.5
0.05585 | 278.15 | 0.09644 | 290.15 | 0.6
0.05585 | 278.15 | 0.09644 | 290.15 | 0.7
0.05585 | 278.15 | 0.09644 | 290.15 | 0.8
0.05585 | 278.15 | 0.09644 | 290.15 | 0.9
0.05585 | 278.15 | 0.09644 | 290.15 | 1
0.05585 | 278.15 | 0.09644 | 290.65 | 0.15
0.05585 | 278.15 | 0.09644 | 290.65 | 0.2
0.05585 | 278.15 | 0.09644 | 290.65 | 0.3
0.05585 | 278.15 | 0.09644 | 290.65 | 0.4
0.05585 | 278.15 | 0.09644 | 290.65 | 0.5
0.05585 | 278.15 | 0.09644 | 290.65 | 0.6
0.05585 | 278.15 | 0.09644 | 290.65 | 0.7
0.05585 | 278.15 | 0.09644 | 290.65 | 0.8
0.05585 | 278.15 | 0.09644 | 290.65 | 0.9
0.05585 | 278.15 | 0.09644 | 290.65 | 1
0.05585 | 278.15 | 0.09644 | 291.15 | 0.15
0.05585 | 278.15 | 0.09644 | 291.15 | 0.2
0.05585 | 278.15 | 0.09644 | 291.15 | 0.3
0.05585 | 278.15 | 0.09644 | 291.15 | 0.4
0.05585 | 278.15 | 0.09644 | 291.15 | 0.5
0.05585 | 278.15 | 0.09644 | 291.15 | 0.6
0.05585 | 278.15 | 0.09644 | 291.15 | 0.7
0.05585 | 278.15 | 0.09644 | 291.15 | 0.8
0.05585 | 278.15 | 0.09644 | 291.15 | 0.9
0.05585 | 278.15 | 0.09644 | 291.15 | 1
0.05585 | 278.15 | 0.09644 | 294.15 | 0.15
0.05585 | 278.15 | 0.09644 | 294.15 | 0.2
0.05585 | 278.15 | 0.09644 | 294.15 | 0.3
0.05585 | 278.15 | 0.09644 | 294.15 | 0.4
0.05585 | 278.15 | 0.09644 | 294.15 | 0.5
0.05585 | 278.15 | 0.09644 | 294.15 | 0.6
0.05585 | 278.15 | 0.09644 | 294.15 | 0.7
0.05585 | 278.15 | 0.09644 | 294.15 | 0.8
0.05585 | 278.15 | 0.09644 | 294.15 | 0.9
0.05585 | 278.15 | 0.09644 | 294.15 | 1
0.05585 | 278.15 | 0.09644 | 297.15 | 0.15
0.05585 | 278.15 | 0.09644 | 297.15 | 0.2
0.05585 | 278.15 | 0.09644 | 297.15 | 0.3
0.05585 | 278.15 | 0.09644 | 297.15 | 0.4
0.05585 | 278.15 | 0.09644 | 297.15 | 0.5
0.05585 | 278.15 | 0.09644 | 297.15 | 0.6
0.05585 | 278.15 | 0.09644 | 297.15 | 0.7
0.05585 | 278.15 | 0.09644 | 297.15 | 0.8
0.05585 | 278.15 | 0.09644 | 297.15 | 0.9
0.05585 | 278.15 | 0.09644 | 297.15 | 1
0.05585 | 278.15 | 0.09644 | 300.15 | 0.15
0.05585 | 278.15 | 0.09644 | 300.15 | 0.2
0.05585 | 278.15 | 0.09644 | 300.15 | 0.3
0.05585 | 278.15 | 0.09644 | 300.15 | 0.4
0.05585 | 278.15 | 0.09644 | 300.15 | 0.5
0.05585 | 278.15 | 0.09644 | 300.15 | 0.6
0.05585 | 278.15 | 0.09644 | 300.15 | 0.7
0.05585 | 278.15 | 0.09644 | 300.15 | 0.8
0.05585 | 278.15 | 0.09644 | 300.15 | 0.9
0.05585 | 278.15 | 0.09644 | 300.15 | 1
0.05585 | 278.15 | 0.09644 | 303.15 | 0.15
0.05585 | 278.15 | 0.09644 | 303.15 | 0.2
0.05585 | 278.15 | 0.09644 | 303.15 | 0.3
0.05585 | 278.15 | 0.09644 | 303.15 | 0.4
0.05585 | 278.15 | 0.09644 | 303.15 | 0.5
0.05585 | 278.15 | 0.09644 | 303.15 | 0.6
0.05585 | 278.15 | 0.09644 | 303.15 | 0.7
0.05585 | 278.15 | 0.09644 | 303.15 | 0.8
0.05585 | 278.15 | 0.09644 | 303.15 | 0.9
0.05585 | 278.15 | 0.09644 | 303.15 | 1
0.05585 | 278.15 | 0.09737 | 283.65 | 0.15
0.05585 | 278.15 | 0.09737 | 283.65 | 0.2
0.05585 | 278.15 | 0.09737 | 283.65 | 0.3
0.05585 | 278.15 | 0.09737 | 283.65 | 0.4
0.05585 | 278.15 | 0.09737 | 283.65 | 0.5
0.05585 | 278.15 | 0.09737 | 283.65 | 0.6
0.05585 | 278.15 | 0.09737 | 283.65 | 0.7
0.05585 | 278.15 | 0.09737 | 283.65 | 0.8
0.05585 | 278.15 | 0.09737 | 283.65 | 0.9
0.05585 | 278.15 | 0.09737 | 283.65 | 1
0.05585 | 278.15 | 0.09737 | 284.15 | 0.15
0.05585 | 278.15 | 0.09737 | 284.15 | 0.2
0.05585 | 278.15 | 0.09737 | 284.15 | 0.3
0.05585 | 278.15 | 0.09737 | 284.15 | 0.4
0.05585 | 278.15 | 0.09737 | 284.15 | 0.5
0.05585 | 278.15 | 0.09737 | 284.15 | 0.6
0.05585 | 278.15 | 0.09737 | 284.15 | 0.7
0.05585 | 278.15 | 0.09737 | 284.15 | 0.8
0.05585 | 278.15 | 0.09737 | 284.15 | 0.9
0.05585 | 278.15 | 0.09737 | 284.15 | 1
0.05585 | 278.15 | 0.09737 | 284.65 | 0.15
0.05585 | 278.15 | 0.09737 | 284.65 | 0.2
0.05585 | 278.15 | 0.09737 | 284.65 | 0.3
0.05585 | 278.15 | 0.09737 | 284.65 | 0.4
0.05585 | 278.15 | 0.09737 | 284.65 | 0.5
0.05585 | 278.15 | 0.09737 | 284.65 | 0.6
0.05585 | 278.15 | 0.09737 | 284.65 | 0.7
0.05585 | 278.15 | 0.09737 | 284.65 | 0.8
0.05585 | 278.15 | 0.09737 | 284.65 | 0.9
0.05585 | 278.15 | 0.09737 | 284.65 | 1
0.05585 | 278.15 | 0.09737 | 285.15 | 0.15
0.05585 | 278.15 | 0.09737 | 285.15 | 0.2
0.05585 | 278.15 | 0.09737 | 285.15 | 0.3
0.05585 | 278.15 | 0.09737 | 285.15 | 0.4
0.05585 | 278.15 | 0.09737 | 285.15 | 0.5
0.05585 | 278.15 | 0.09737 | 285.15 | 0.6
0.05585 | 278.15 | 0.09737 | 285.15 | 0.7
0.05585 | 278.15 | 0.09737 | 285.15 | 0.8
0.05585 | 278.15 | 0.09737 | 285.15 | 0.9
0.05585 | 278.15 | 0.09737 | 285.15 | 1
0.05585 | 278.15 | 0.09737 | 285.65 | 0.15
0.05585 | 278.15 | 0.09737 | 285.65 | 0.2
0.05585 | 278.15 | 0.09737 | 285.65 | 0.3
0.05585 | 278.15 | 0.09737 | 285.65 | 0.4
0.05585 | 278.15 | 0.09737 | 285.65 | 0.5
0.05585 | 278.15 | 0.09737 | 285.65 | 0.6
0.05585 | 278.15 | 0.09737 | 285.65 | 0.7
0.05585 | 278.15 | 0.09737 | 285.65 | 0.8
0.05585 | 278.15 | 0.09737 | 285.65 | 0.9
0.05585 | 278.15 | 0.09737 | 285.65 | 1
0.05585 | 278.15 | 0.09737 | 286.15 | 0.15
0.05585 | 278.15 | 0.09737 | 286.15 | 0.2
0.05585 | 278.15 | 0.09737 | 286.15 | 0.3
0.05585 | 278.15 | 0.09737 | 286.15 | 0.4
0.05585 | 278.15 | 0.09737 | 286.15 | 0.5
0.05585 | 278.15 | 0.09737 | 286.15 | 0.6
0.05585 | 278.15 | 0.09737 | 286.15 | 0.7
0.05585 | 278.15 | 0.09737 | 286.15 | 0.8
0.05585 | 278.15 | 0.09737 | 286.15 | 0.9
0.05585 | 278.15 | 0.09737 | 286.15 | 1
0.05585 | 278.15 | 0.09737 | 286.65 | 0.15
0.05585 | 278.15 | 0.09737 | 286.65 | 0.2
0.05585 | 278.15 | 0.09737 | 286.65 | 0.3
0.05585 | 278.15 | 0.09737 | 286.65 | 0.4
0.05585 | 278.15 | 0.09737 | 286.65 | 0.5
0.05585 | 278.15 | 0.09737 | 286.65 | 0.6
0.05585 | 278.15 | 0.09737 | 286.65 | 0.7
0.05585 | 278.15 | 0.09737 | 286.65 | 0.8
0.05585 | 278.15 | 0.09737 | 286.65 | 0.9
0.05585 | 278.15 | 0.09737 | 286.65 | 1
0.05585 | 278.15 | 0.09737 | 287.15 | 0.15
0.05585 | 278.15 | 0.09737 | 287.15 | 0.2
0.05585 | 278.15 | 0.09737 | 287.15 | 0.3
0.05585 | 278.15 | 0.09737 | 287.15 | 0.4
0.05585 | 278.15 | 0.09737 | 287.15 | 0.5
0.05585 | 278.15 | 0.09737 | 287.15 | 0.6
0.05585 | 278.15 | 0.09737 | 287.15 | 0.7
0.05585 | 278.15 | 0.09737 | 287.15 | 0.8
0.05585 | 278.15 | 0.09737 | 287.15 | 0.9
0.05585 | 278.15 | 0.09737 | 287.15 | 1
0.05585 | 278.15 | 0.09737 | 287.65 | 0.15
0.05585 | 278.15 | 0.09737 | 287.65 | 0.2
0.05585 | 278.15 | 0.09737 | 287.65 | 0.3
0.05585 | 278.15 | 0.09737 | 287.65 | 0.4
0.05585 | 278.15 | 0.09737 | 287.65 | 0.5
0.05585 | 278.15 | 0.09737 | 287.65 | 0.6
0.05585 | 278.15 | 0.09737 | 287.65 | 0.7
0.05585 | 278.15 | 0.09737 | 287.65 | 0.8
0.05585 | 278.15 | 0.09737 | 287.65 | 0.9
0.05585 | 278.15 | 0.09737 | 287.65 | 1
0.05585 | 278.15 | 0.09737 | 288.15 | 0.15
0.05585 | 278.15 | 0.09737 | 288.15 | 0.2
0.05585 | 278.15 | 0.09737 | 288.15 | 0.3
0.05585 | 278.15 | 0.09737 | 288.15 | 0.4
0.05585 | 278.15 | 0.09737 | 288.15 | 0.5
0.05585 | 278.15 | 0.09737 | 288.15 | 0.6
0.05585 | 278.15 | 0.09737 | 288.15 | 0.7
0.05585 | 278.15 | 0.09737 | 288.15 | 0.8
0.05585 | 278.15 | 0.09737 | 288.15 | 0.9
0.05585 | 278.15 | 0.09737 | 288.15 | 1
0.05585 | 278.15 | 0.09737 | 288.65 | 0.15
0.05585 | 278.15 | 0.09737 | 288.65 | 0.2
0.05585 | 278.15 | 0.09737 | 288.65 | 0.3
0.05585 | 278.15 | 0.09737 | 288.65 | 0.4
0.05585 | 278.15 | 0.09737 | 288.65 | 0.5
0.05585 | 278.15 | 0.09737 | 288.65 | 0.6
0.05585 | 278.15 | 0.09737 | 288.65 | 0.7
0.05585 | 278.15 | 0.09737 | 288.65 | 0.8
0.05585 | 278.15 | 0.09737 | 288.65 | 0.9
0.05585 | 278.15 | 0.09737 | 288.65 | 1
0.05585 | 278.15 | 0.09737 | 289.15 | 0.15
0.05585 | 278.15 | 0.09737 | 289.15 | 0.2
0.05585 | 278.15 | 0.09737 | 289.15 | 0.3
0.05585 | 278.15 | 0.09737 | 289.15 | 0.4
0.05585 | 278.15 | 0.09737 | 289.15 | 0.5
0.05585 | 278.15 | 0.09737 | 289.15 | 0.6
0.05585 | 278.15 | 0.09737 | 289.15 | 0.7
0.05585 | 278.15 | 0.09737 | 289.15 | 0.8
0.05585 | 278.15 | 0.09737 | 289.15 | 0.9
0.05585 | 278.15 | 0.09737 | 289.15 | 1
0.05585 | 278.15 | 0.09737 | 289.65 | 0.15
0.05585 | 278.15 | 0.09737 | 289.65 | 0.2
0.05585 | 278.15 | 0.09737 | 289.65 | 0.3
0.05585 | 278.15 | 0.09737 | 289.65 | 0.4
0.05585 | 278.15 | 0.09737 | 289.65 | 0.5
0.05585 | 278.15 | 0.09737 | 289.65 | 0.6
0.05585 | 278.15 | 0.09737 | 289.65 | 0.7
0.05585 | 278.15 | 0.09737 | 289.65 | 0.8
0.05585 | 278.15 | 0.09737 | 289.65 | 0.9
0.05585 | 278.15 | 0.09737 | 289.65 | 1
0.05585 | 278.15 | 0.09737 | 290.15 | 0.15
0.05585 | 278.15 | 0.09737 | 290.15 | 0.2
0.05585 | 278.15 | 0.09737 | 290.15 | 0.3
0.05585 | 278.15 | 0.09737 | 290.15 | 0.4
0.05585 | 278.15 | 0.09737 | 290.15 | 0.5
0.05585 | 278.15 | 0.09737 | 290.15 | 0.6
0.05585 | 278.15 | 0.09737 | 290.15 | 0.7
0.05585 | 278.15 | 0.09737 | 290.15 | 0.8
0.05585 | 278.15 | 0.09737 | 290.15 | 0.9
0.05585 | 278.15 | 0.09737 | 290.15 | 1
0.05585 | 278.15 | 0.09737 | 290.65 | 0.15
0.05585 | 278.15 | 0.09737 | 290.65 | 0.2
0.05585 | 278.15 | 0.09737 | 290.65 | 0.3
0.05585 | 278.15 | 0.09737 | 290.65 | 0.4
0.05585 | 278.15 | 0.09737 | 290.65 | 0.5
0.05585 | 278.15 | 0.09737 | 290.65 | 0.6
0.05585 | 278.15 | 0.09737 | 290.65 | 0.7
0.05585 | 278.15 | 0.09737 | 290.65 | 0.8
0.05585 | 278.15 | 0.09737 | 290.65 | 0.9
0.05585 | 278.15 | 0.09737 | 290.65 | 1
0.05585 | 278.15 | 0.09737 | 291.15 | 0.15
0.05585 | 278.15 | 0.09737 | 291.15 | 0.2
0.05585 | 278.15 | 0.09737 | 291.15 | 0.3
0.05585 | 278.15 | 0.09737 | 291.15 | 0.4
0.05585 | 278.15 | 0.09737 | 291.15 | 0.5
0.05585 | 278.15 | 0.09737 | 291.15 | 0.6
0.05585 | 278.15 | 0.09737 | 291.15 | 0.7
0.05585 | 278.15 | 0.09737 | 291.15 | 0.8
0.05585 | 278.15 | 0.09737 | 291.15 | 0.9
0.05585 | 278.15 | 0.09737 | 291.15 | 1
0.05585 | 278.15 | 0.09737 | 294.15 | 0.15
0.05585 | 278.15 | 0.09737 | 294.15 | 0.2
0.05585 | 278.15 | 0.09737 | 294.15 | 0.3
0.05585 | 278.15 | 0.09737 | 294.15 | 0.4
0.05585 | 278.15 | 0.09737 | 294.15 | 0.5
0.05585 | 278.15 | 0.09737 | 294.15 | 0.6
0.05585 | 278.15 | 0.09737 | 294.15 | 0.7
0.05585 | 278.15 | 0.09737 | 294.15 | 0.8
0.05585 | 278.15 | 0.09737 | 294.15 | 0.9
0.05585 | 278.15 | 0.09737 | 294.15 | 1
0.05585 | 278.15 | 0.09737 | 297.15 | 0.15
0.05585 | 278.15 | 0.09737 | 297.15 | 0.2
0.05585 | 278.15 | 0.09737 | 297.15 | 0.3
0.05585 | 278.15 | 0.09737 | 297.15 | 0.4
0.05585 | 278.15 | 0.09737 | 297.15 | 0.5
0.05585 | 278.15 | 0.09737 | 297.15 | 0.6
0.05585 | 278.15 | 0.09737 | 297.15 | 0.7
0.05585 | 278.15 | 0.09737 | 297.15 | 0.8
0.05585 | 278.15 | 0.09737 | 297.15 | 0.9
0.05585 | 278.15 | 0.09737 | 297.15 | 1
0.05585 | 278.15 | 0.09737 | 300.15 | 0.15
0.05585 | 278.15 | 0.09737 | 300.15 | 0.2
0.05585 | 278.15 | 0.09737 | 300.15 | 0.3
0.05585 | 278.15 | 0.09737 | 300.15 | 0.4
0.05585 | 278.15 | 0.09737 | 300.15 | 0.5
0.05585 | 278.15 | 0.09737 | 300.15 | 0.6
0.05585 | 278.15 | 0.09737 | 300.15 | 0.7
0.05585 | 278.15 | 0.09737 | 300.15 | 0.8
0.05585 | 278.15 | 0.09737 | 300.15 | 0.9
0.05585 | 278.15 | 0.09737 | 300.15 | 1
0.05585 | 278.15 | 0.09737 | 303.15 | 0.15
0.05585 | 278.15 | 0.09737 | 303.15 | 0.2
0.05585 | 278.15 | 0.09737 | 303.15 | 0.3
0.05585 | 278.15 | 0.09737 | 303.15 | 0.4
0.05585 | 278.15 | 0.09737 | 303.15 | 0.5
0.05585 | 278.15 | 0.09737 | 303.15 | 0.6
0.05585 | 278.15 | 0.09737 | 303.15 | 0.7
0.05585 | 278.15 | 0.09737 | 303.15 | 0.8
0.05585 | 278.15 | 0.09737 | 303.15 | 0.9
0.05585 | 278.15 | 0.09737 | 303.15 | 1
0.05585 | 278.15 | 0.115 | 283.65 | 0.15
0.05585 | 278.15 | 0.115 | 283.65 | 0.2
0.05585 | 278.15 | 0.115 | 283.65 | 0.3
0.05585 | 278.15 | 0.115 | 283.65 | 0.4
0.05585 | 278.15 | 0.115 | 283.65 | 0.5
0.05585 | 278.15 | 0.115 | 283.65 | 0.6
0.05585 | 278.15 | 0.115 | 283.65 | 0.7
0.05585 | 278.15 | 0.115 | 283.65 | 0.8
0.05585 | 278.15 | 0.115 | 283.65 | 0.9
0.05585 | 278.15 | 0.115 | 283.65 | 1
0.05585 | 278.15 | 0.115 | 284.15 | 0.15
0.05585 | 278.15 | 0.115 | 284.15 | 0.2
0.05585 | 278.15 | 0.115 | 284.15 | 0.3
0.05585 | 278.15 | 0.115 | 284.15 | 0.4
0.05585 | 278.15 | 0.115 | 284.15 | 0.5
0.05585 | 278.15 | 0.115 | 284.15 | 0.6
0.05585 | 278.15 | 0.115 | 284.15 | 0.7
0.05585 | 278.15 | 0.115 | 284.15 | 0.8
0.05585 | 278.15 | 0.115 | 284.15 | 0.9
0.05585 | 278.15 | 0.115 | 284.15 | 1
0.05585 | 278.15 | 0.115 | 284.65 | 0.15
0.05585 | 278.15 | 0.115 | 284.65 | 0.2
0.05585 | 278.15 | 0.115 | 284.65 | 0.3
0.05585 | 278.15 | 0.115 | 284.65 | 0.4
0.05585 | 278.15 | 0.115 | 284.65 | 0.5
0.05585 | 278.15 | 0.115 | 284.65 | 0.6
0.05585 | 278.15 | 0.115 | 284.65 | 0.7
0.05585 | 278.15 | 0.115 | 284.65 | 0.8
0.05585 | 278.15 | 0.115 | 284.65 | 0.9
0.05585 | 278.15 | 0.115 | 284.65 | 1
0.05585 | 278.15 | 0.115 | 285.15 | 0.15
0.05585 | 278.15 | 0.115 | 285.15 | 0.2
0.05585 | 278.15 | 0.115 | 285.15 | 0.3
0.05585 | 278.15 | 0.115 | 285.15 | 0.4
0.05585 | 278.15 | 0.115 | 285.15 | 0.5
0.05585 | 278.15 | 0.115 | 285.15 | 0.6
0.05585 | 278.15 | 0.115 | 285.15 | 0.7
0.05585 | 278.15 | 0.115 | 285.15 | 0.8
0.05585 | 278.15 | 0.115 | 285.15 | 0.9
0.05585 | 278.15 | 0.115 | 285.15 | 1
0.05585 | 278.15 | 0.115 | 285.65 | 0.15
0.05585 | 278.15 | 0.115 | 285.65 | 0.2
0.05585 | 278.15 | 0.115 | 285.65 | 0.3
0.05585 | 278.15 | 0.115 | 285.65 | 0.4
0.05585 | 278.15 | 0.115 | 285.65 | 0.5
0.05585 | 278.15 | 0.115 | 285.65 | 0.6
0.05585 | 278.15 | 0.115 | 285.65 | 0.7
0.05585 | 278.15 | 0.115 | 285.65 | 0.8
0.05585 | 278.15 | 0.115 | 285.65 | 0.9
0.05585 | 278.15 | 0.115 | 285.65 | 1
0.05585 | 278.15 | 0.115 | 286.15 | 0.15
0.05585 | 278.15 | 0.115 | 286.15 | 0.2
0.05585 | 278.15 | 0.115 | 286.15 | 0.3
0.05585 | 278.15 | 0.115 | 286.15 | 0.4
0.05585 | 278.15 | 0.115 | 286.15 | 0.5
0.05585 | 278.15 | 0.115 | 286.15 | 0.6
0.05585 | 278.15 | 0.115 | 286.15 | 0.7
0.05585 | 278.15 | 0.115 | 286.15 | 0.8
0.05585 | 278.15 | 0.115 | 286.15 | 0.9
0.05585 | 278.15 | 0.115 | 286.15 | 1
0.05585 | 278.15 | 0.115 | 286.65 | 0.15
0.05585 | 278.15 | 0.115 | 286.65 | 0.2
0.05585 | 278.15 | 0.115 | 286.65 | 0.3
0.05585 | 278.15 | 0.115 | 286.65 | 0.4
0.05585 | 278.15 | 0.115 | 286.65 | 0.5
0.05585 | 278.15 | 0.115 | 286.65 | 0.6
0.05585 | 278.15 | 0.115 | 286.65 | 0.7
0.05585 | 278.15 | 0.115 | 286.65 | 0.8
0.05585 | 278.15 | 0.115 | 286.65 | 0.9
0.05585 | 278.15 | 0.115 | 286.65 | 1
0.05585 | 278.15 | 0.115 | 287.15 | 0.15
0.05585 | 278.15 | 0.115 | 287.15 | 0.2
0.05585 | 278.15 | 0.115 | 287.15 | 0.3
0.05585 | 278.15 | 0.115 | 287.15 | 0.4
0.05585 | 278.15 | 0.115 | 287.15 | 0.5
0.05585 | 278.15 | 0.115 | 287.15 | 0.6
0.05585 | 278.15 | 0.115 | 287.15 | 0.7
0.05585 | 278.15 | 0.115 | 287.15 | 0.8
0.05585 | 278.15 | 0.115 | 287.15 | 0.9
0.05585 | 278.15 | 0.115 | 287.15 | 1
0.05585 | 278.15 | 0.115 | 287.65 | 0.15
0.05585 | 278.15 | 0.115 | 287.65 | 0.2
0.05585 | 278.15 | 0.115 | 287.65 | 0.3
0.05585 | 278.15 | 0.115 | 287.65 | 0.4
0.05585 | 278.15 | 0.115 | 287.65 | 0.5
0.05585 | 278.15 | 0.115 | 287.65 | 0.6
0.05585 | 278.15 | 0.115 | 287.65 | 0.7
0.05585 | 278.15 | 0.115 | 287.65 | 0.8
0.05585 | 278.15 | 0.115 | 287.65 | 0.9
0.05585 | 278.15 | 0.115 | 287.65 | 1
0.05585 | 278.15 | 0.115 | 288.15 | 0.15
0.05585 | 278.15 | 0.115 | 288.15 | 0.2
0.05585 | 278.15 | 0.115 | 288.15 | 0.3
0.05585 | 278.15 | 0.115 | 288.15 | 0.4
0.05585 | 278.15 | 0.115 | 288.15 | 0.5
0.05585 | 278.15 | 0.115 | 288.15 | 0.6
0.05585 | 278.15 | 0.115 | 288.15 | 0.7
0.05585 | 278.15 | 0.115 | 288.15 | 0.8
0.05585 | 278.15 | 0.115 | 288.15 | 0.9
0.05585 | 278.15 | 0.115 | 288.15 | 1
0.05585 | 278.15 | 0.115 | 288.65 | 0.15
0.05585 | 278.15 | 0.115 | 288.65 | 0.2
0.05585 | 278.15 | 0.115 | 288.65 | 0.3
0.05585 | 278.15 | 0.115 | 288.65 | 0.4
0.05585 | 278.15 | 0.115 | 288.65 | 0.5
0.05585 | 278.15 | 0.115 | 288.65 | 0.6
0.05585 | 278.15 | 0.115 | 288.65 | 0.7
0.05585 | 278.15 | 0.115 | 288.65 | 0.8
0.05585 | 278.15 | 0.115 | 288.65 | 0.9
0.05585 | 278.15 | 0.115 | 288.65 | 1
0.05585 | 278.15 | 0.115 | 289.15 | 0.15
0.05585 | 278.15 | 0.115 | 289.15 | 0.2
0.05585 | 278.15 | 0.115 | 289.15 | 0.3
0.05585 | 278.15 | 0.115 | 289.15 | 0.4
0.05585 | 278.15 | 0.115 | 289.15 | 0.5
0.05585 | 278.15 | 0.115 | 289.15 | 0.6
0.05585 | 278.15 | 0.115 | 289.15 | 0.7
0.05585 | 278.15 | 0.115 | 289.15 | 0.8
0.05585 | 278.15 | 0.115 | 289.15 | 0.9
0.05585 | 278.15 | 0.115 | 289.15 | 1
0.05585 | 278.15 | 0.115 | 289.65 | 0.15
0.05585 | 278.15 | 0.115 | 289.65 | 0.2
0.05585 | 278.15 | 0.115 | 289.65 | 0.3
0.05585 | 278.15 | 0.115 | 289.65 | 0.4
0.05585 | 278.15 | 0.115 | 289.65 | 0.5
0.05585 | 278.15 | 0.115 | 289.65 | 0.6
0.05585 | 278.15 | 0.115 | 289.65 | 0.7
0.05585 | 278.15 | 0.115 | 289.65 | 0.8
0.05585 | 278.15 | 0.115 | 289.65 | 0.9
0.05585 | 278.15 | 0.115 | 289.65 | 1
0.05585 | 278.15 | 0.115 | 290.15 | 0.15
0.05585 | 278.15 | 0.115 | 290.15 | 0.2
0.05585 | 278.15 | 0.115 | 290.15 | 0.3
0.05585 | 278.15 | 0.115 | 290.15 | 0.4
0.05585 | 278.15 | 0.115 | 290.15 | 0.5
0.05585 | 278.15 | 0.115 | 290.15 | 0.6
0.05585 | 278.15 | 0.115 | 290.15 | 0.7
0.05585 | 278.15 | 0.115 | 290.15 | 0.8
0.05585 | 278.15 | 0.115 | 290.15 | 0.9
0.05585 | 278.15 | 0.115 | 290.15 | 1
0.05585 | 278.15 | 0.115 | 290.65 | 0.15
0.05585 | 278.15 | 0.115 | 290.65 | 0.2
0.05585 | 278.15 | 0.115 | 290.65 | 0.3
0.05585 | 278.15 | 0.115 | 290.65 | 0.4
0.05585 | 278.15 | 0.115 | 290.65 | 0.5
0.05585 | 278.15 | 0.115 | 290.65 | 0.6
0.05585 | 278.15 | 0.115 | 290.65 | 0.7
0.05585 | 278.15 | 0.115 | 290.65 | 0.8
0.05585 | 278.15 | 0.115 | 290.65 | 0.9
0.05585 | 278.15 | 0.115 | 290.65 | 1
0.05585 | 278.15 | 0.115 | 291.15 | 0.15
0.05585 | 278.15 | 0.115 | 291.15 | 0.2
0.05585 | 278.15 | 0.115 | 291.15 | 0.3
0.05585 | 278.15 | 0.115 | 291.15 | 0.4
0.05585 | 278.15 | 0.115 | 291.15 | 0.5
0.05585 | 278.15 | 0.115 | 291.15 | 0.6
0.05585 | 278.15 | 0.115 | 291.15 | 0.7
0.05585 | 278.15 | 0.115 | 291.15 | 0.8
0.05585 | 278.15 | 0.115 | 291.15 | 0.9
0.05585 | 278.15 | 0.115 | 291.15 | 1
0.05585 | 278.15 | 0.115 | 294.15 | 0.15
0.05585 | 278.15 | 0.115 | 294.15 | 0.2
0.05585 | 278.15 | 0.115 | 294.15 | 0.3
0.05585 | 278.15 | 0.115 | 294.15 | 0.4
0.05585 | 278.15 | 0.115 | 294.15 | 0.5
0.05585 | 278.15 | 0.115 | 294.15 | 0.6
0.05585 | 278.15 | 0.115 | 294.15 | 0.7
0.05585 | 278.15 | 0.115 | 294.15 | 0.8
0.05585 | 278.15 | 0.115 | 294.15 | 0.9
0.05585 | 278.15 | 0.115 | 294.15 | 1
0.05585 | 278.15 | 0.115 | 297.15 | 0.15
0.05585 | 278.15 | 0.115 | 297.15 | 0.2
0.05585 | 278.15 | 0.115 | 297.15 | 0.3
0.05585 | 278.15 | 0.115 | 297.15 | 0.4
0.05585 | 278.15 | 0.115 | 297.15 | 0.5
0.05585 | 278.15 | 0.115 | 297.15 | 0.6
0.05585 | 278.15 | 0.115 | 297.15 | 0.7
0.05585 | 278.15 | 0.115 | 297.15 | 0.8
0.05585 | 278.15 | 0.115 | 297.15 | 0.9
0.05585 | 278.15 | 0.115 | 297.15 | 1
0.05585 | 278.15 | 0.115 | 300.15 | 0.15
0.05585 | 278.15 | 0.115 | 300.15 | 0.2
0.05585 | 278.15 | 0.115 | 300.15 | 0.3
0.05585 | 278.15 | 0.115 | 300.15 | 0.4
0.05585 | 278.15 | 0.115 | 300.15 | 0.5
0.05585 | 278.15 | 0.115 | 300.15 | 0.6
0.05585 | 278.15 | 0.115 | 300.15 | 0.7
0.05585 | 278.15 | 0.115 | 300.15 | 0.8
0.05585 | 278.15 | 0.115 | 300.15 | 0.9
0.05585 | 278.15 | 0.115 | 300.15 | 1
0.05585 | 278.15 | 0.115 | 303.15 | 0.15
0.05585 | 278.15 | 0.115 | 303.15 | 0.2
0.05585 | 278.15 | 0.115 | 303.15 | 0.3
0.05585 | 278.15 | 0.115 | 303.15 | 0.4
0.05585 | 278.15 | 0.115 | 303.15 | 0.5
0.05585 | 278.15 | 0.115 | 303.15 | 0.6
0.05585 | 278.15 | 0.115 | 303.15 | 0.7
0.05585 | 278.15 | 0.115 | 303.15 | 0.8
0.05585 | 278.15 | 0.115 | 303.15 | 0.9
0.05585 | 278.15 | 0.115 | 303.15 | 1
0.05585 | 280.15 | 0.00115 | 283.65 | 0.15
0.05585 | 280.15 | 0.00115 | 283.65 | 0.2
0.05585 | 280.15 | 0.00115 | 283.65 | 0.3
0.05585 | 280.15 | 0.00115 | 283.65 | 0.4
0.05585 | 280.15 | 0.00115 | 283.65 | 0.5
0.05585 | 280.15 | 0.00115 | 283.65 | 0.6
0.05585 | 280.15 | 0.00115 | 283.65 | 0.7
0.05585 | 280.15 | 0.00115 | 283.65 | 0.8
0.05585 | 280.15 | 0.00115 | 283.65 | 0.9
0.05585 | 280.15 | 0.00115 | 283.65 | 1
0.05585 | 280.15 | 0.00115 | 284.15 | 0.15
0.05585 | 280.15 | 0.00115 | 284.15 | 0.2
0.05585 | 280.15 | 0.00115 | 284.15 | 0.3
0.05585 | 280.15 | 0.00115 | 284.15 | 0.4
0.05585 | 280.15 | 0.00115 | 284.15 | 0.5
0.05585 | 280.15 | 0.00115 | 284.15 | 0.6
0.05585 | 280.15 | 0.00115 | 284.15 | 0.7
0.05585 | 280.15 | 0.00115 | 284.15 | 0.8
0.05585 | 280.15 | 0.00115 | 284.15 | 0.9
0.05585 | 280.15 | 0.00115 | 284.15 | 1
0.05585 | 280.15 | 0.00115 | 284.65 | 0.15
0.05585 | 280.15 | 0.00115 | 284.65 | 0.2
0.05585 | 280.15 | 0.00115 | 284.65 | 0.3
0.05585 | 280.15 | 0.00115 | 284.65 | 0.4
0.05585 | 280.15 | 0.00115 | 284.65 | 0.5
0.05585 | 280.15 | 0.00115 | 284.65 | 0.6
0.05585 | 280.15 | 0.00115 | 284.65 | 0.7
0.05585 | 280.15 | 0.00115 | 284.65 | 0.8
0.05585 | 280.15 | 0.00115 | 284.65 | 0.9
0.05585 | 280.15 | 0.00115 | 284.65 | 1
0.05585 | 280.15 | 0.00115 | 285.15 | 0.15
0.05585 | 280.15 | 0.00115 | 285.15 | 0.2
0.05585 | 280.15 | 0.00115 | 285.15 | 0.3
0.05585 | 280.15 | 0.00115 | 285.15 | 0.4
0.05585 | 280.15 | 0.00115 | 285.15 | 0.5
0.05585 | 280.15 | 0.00115 | 285.15 | 0.6
0.05585 | 280.15 | 0.00115 | 285.15 | 0.7
0.05585 | 280.15 | 0.00115 | 285.15 | 0.8
0.05585 | 280.15 | 0.00115 | 285.15 | 0.9
0.05585 | 280.15 | 0.00115 | 285.15 | 1
0.05585 | 280.15 | 0.00115 | 285.65 | 0.15
0.05585 | 280.15 | 0.00115 | 285.65 | 0.2
0.05585 | 280.15 | 0.00115 | 285.65 | 0.3
0.05585 | 280.15 | 0.00115 | 285.65 | 0.4
0.05585 | 280.15 | 0.00115 | 285.65 | 0.5
0.05585 | 280.15 | 0.00115 | 285.65 | 0.6
0.05585 | 280.15 | 0.00115 | 285.65 | 0.7
0.05585 | 280.15 | 0.00115 | 285.65 | 0.8
0.05585 | 280.15 | 0.00115 | 285.65 | 0.9
0.05585 | 280.15 | 0.00115 | 285.65 | 1
0.05585 | 280.15 | 0.00115 | 286.15 | 0.15
0.05585 | 280.15 | 0.00115 | 286.15 | 0.2
0.05585 | 280.15 | 0.00115 | 286.15 | 0.3
0.05585 | 280.15 | 0.00115 | 286.15 | 0.4
0.05585 | 280.15 | 0.00115 | 286.15 | 0.5
0.05585 | 280.15 | 0.00115 | 286.15 | 0.6
0.05585 | 280.15 | 0.00115 | 286.15 | 0.7
0.05585 | 280.15 | 0.00115 | 286.15 | 0.8
0.05585 | 280.15 | 0.00115 | 286.15 | 0.9
0.05585 | 280.15 | 0.00115 | 286.15 | 1
0.05585 | 280.15 | 0.00115 | 286.65 | 0.15
0.05585 | 280.15 | 0.00115 | 286.65 | 0.2
0.05585 | 280.15 | 0.00115 | 286.65 | 0.3
0.05585 | 280.15 | 0.00115 | 286.65 | 0.4
0.05585 | 280.15 | 0.00115 | 286.65 | 0.5
0.05585 | 280.15 | 0.00115 | 286.65 | 0.6
0.05585 | 280.15 | 0.00115 | 286.65 | 0.7
0.05585 | 280.15 | 0.00115 | 286.65 | 0.8
0.05585 | 280.15 | 0.00115 | 286.65 | 0.9
0.05585 | 280.15 | 0.00115 | 286.65 | 1
0.05585 | 280.15 | 0.00115 | 287.15 | 0.15
0.05585 | 280.15 | 0.00115 | 287.15 | 0.2
0.05585 | 280.15 | 0.00115 | 287.15 | 0.3
0.05585 | 280.15 | 0.00115 | 287.15 | 0.4
0.05585 | 280.15 | 0.00115 | 287.15 | 0.5
0.05585 | 280.15 | 0.00115 | 287.15 | 0.6
0.05585 | 280.15 | 0.00115 | 287.15 | 0.7
0.05585 | 280.15 | 0.00115 | 287.15 | 0.8
0.05585 | 280.15 | 0.00115 | 287.15 | 0.9
0.05585 | 280.15 | 0.00115 | 287.15 | 1
0.05585 | 280.15 | 0.00115 | 287.65 | 0.15
0.05585 | 280.15 | 0.00115 | 287.65 | 0.2
0.05585 | 280.15 | 0.00115 | 287.65 | 0.3
0.05585 | 280.15 | 0.00115 | 287.65 | 0.4
0.05585 | 280.15 | 0.00115 | 287.65 | 0.5
0.05585 | 280.15 | 0.00115 | 287.65 | 0.6
0.05585 | 280.15 | 0.00115 | 287.65 | 0.7
0.05585 | 280.15 | 0.00115 | 287.65 | 0.8
0.05585 | 280.15 | 0.00115 | 287.65 | 0.9
0.05585 | 280.15 | 0.00115 | 287.65 | 1
0.05585 | 280.15 | 0.00115 | 288.15 | 0.15
0.05585 | 280.15 | 0.00115 | 288.15 | 0.2
0.05585 | 280.15 | 0.00115 | 288.15 | 0.3
0.05585 | 280.15 | 0.00115 | 288.15 | 0.4
0.05585 | 280.15 | 0.00115 | 288.15 | 0.5
0.05585 | 280.15 | 0.00115 | 288.15 | 0.6
0.05585 | 280.15 | 0.00115 | 288.15 | 0.7
0.05585 | 280.15 | 0.00115 | 288.15 | 0.8
0.05585 | 280.15 | 0.00115 | 288.15 | 0.9
0.05585 | 280.15 | 0.00115 | 288.15 | 1
0.05585 | 280.15 | 0.00115 | 288.65 | 0.15
0.05585 | 280.15 | 0.00115 | 288.65 | 0.2
0.05585 | 280.15 | 0.00115 | 288.65 | 0.3
0.05585 | 280.15 | 0.00115 | 288.65 | 0.4
0.05585 | 280.15 | 0.00115 | 288.65 | 0.5
0.05585 | 280.15 | 0.00115 | 288.65 | 0.6
0.05585 | 280.15 | 0.00115 | 288.65 | 0.7
0.05585 | 280.15 | 0.00115 | 288.65 | 0.8
0.05585 | 280.15 | 0.00115 | 288.65 | 0.9
0.05585 | 280.15 | 0.00115 | 288.65 | 1
0.05585 | 280.15 | 0.00115 | 289.15 | 0.15
0.05585 | 280.15 | 0.00115 | 289.15 | 0.2
0.05585 | 280.15 | 0.00115 | 289.15 | 0.3
0.05585 | 280.15 | 0.00115 | 289.15 | 0.4
0.05585 | 280.15 | 0.00115 | 289.15 | 0.5
0.05585 | 280.15 | 0.00115 | 289.15 | 0.6
0.05585 | 280.15 | 0.00115 | 289.15 | 0.7
0.05585 | 280.15 | 0.00115 | 289.15 | 0.8
0.05585 | 280.15 | 0.00115 | 289.15 | 0.9
0.05585 | 280.15 | 0.00115 | 289.15 | 1
0.05585 | 280.15 | 0.00115 | 289.65 | 0.15
0.05585 | 280.15 | 0.00115 | 289.65 | 0.2
0.05585 | 280.15 | 0.00115 | 289.65 | 0.3
0.05585 | 280.15 | 0.00115 | 289.65 | 0.4
0.05585 | 280.15 | 0.00115 | 289.65 | 0.5
0.05585 | 280.15 | 0.00115 | 289.65 | 0.6
0.05585 | 280.15 | 0.00115 | 289.65 | 0.7
0.05585 | 280.15 | 0.00115 | 289.65 | 0.8
0.05585 | 280.15 | 0.00115 | 289.65 | 0.9
0.05585 | 280.15 | 0.00115 | 289.65 | 1
0.05585 | 280.15 | 0.00115 | 290.15 | 0.15
0.05585 | 280.15 | 0.00115 | 290.15 | 0.2
0.05585 | 280.15 | 0.00115 | 290.15 | 0.3
0.05585 | 280.15 | 0.00115 | 290.15 | 0.4
0.05585 | 280.15 | 0.00115 | 290.15 | 0.5
0.05585 | 280.15 | 0.00115 | 290.15 | 0.6
0.05585 | 280.15 | 0.00115 | 290.15 | 0.7
0.05585 | 280.15 | 0.00115 | 290.15 | 0.8
0.05585 | 280.15 | 0.00115 | 290.15 | 0.9
0.05585 | 280.15 | 0.00115 | 290.15 | 1
0.05585 | 280.15 | 0.00115 | 290.65 | 0.15
0.05585 | 280.15 | 0.00115 | 290.65 | 0.2
0.05585 | 280.15 | 0.00115 | 290.65 | 0.3
0.05585 | 280.15 | 0.00115 | 290.65 | 0.4
0.05585 | 280.15 | 0.00115 | 290.65 | 0.5
0.05585 | 280.15 | 0.00115 | 290.65 | 0.6
0.05585 | 280.15 | 0.00115 | 290.65 | 0.7
0.05585 | 280.15 | 0.00115 | 290.65 | 0.8
0.05585 | 280.15 | 0.00115 | 290.65 | 0.9
0.05585 | 280.15 | 0.00115 | 290.65 | 1
0.05585 | 280.15 | 0.00115 | 291.15 | 0.15
0.05585 | 280.15 | 0.00115 | 291.15 | 0.2
0.05585 | 280.15 | 0.00115 | 291.15 | 0.3
0.05585 | 280.15 | 0.00115 | 291.15 | 0.4
0.05585 | 280.15 | 0.00115 | 291.15 | 0.5
0.05585 | 280.15 | 0.00115 | 291.15 | 0.6
0.05585 | 280.15 | 0.00115 | 291.15 | 0.7
0.05585 | 280.15 | 0.00115 | 291.15 | 0.8
0.05585 | 280.15 | 0.00115 | 291.15 | 0.9
0.05585 | 280.15 | 0.00115 | 291.15 | 1
0.05585 | 280.15 | 0.00115 | 294.15 | 0.15
0.05585 | 280.15 | 0.00115 | 294.15 | 0.2
0.05585 | 280.15 | 0.00115 | 294.15 | 0.3
0.05585 | 280.15 | 0.00115 | 294.15 | 0.4
0.05585 | 280.15 | 0.00115 | 294.15 | 0.5
0.05585 | 280.15 | 0.00115 | 294.15 | 0.6
0.05585 | 280.15 | 0.00115 | 294.15 | 0.7
0.05585 | 280.15 | 0.00115 | 294.15 | 0.8
0.05585 | 280.15 | 0.00115 | 294.15 | 0.9
0.05585 | 280.15 | 0.00115 | 294.15 | 1
0.05585 | 280.15 | 0.00115 | 297.15 | 0.15
0.05585 | 280.15 | 0.00115 | 297.15 | 0.2
0.05585 | 280.15 | 0.00115 | 297.15 | 0.3
0.05585 | 280.15 | 0.00115 | 297.15 | 0.4
0.05585 | 280.15 | 0.00115 | 297.15 | 0.5
0.05585 | 280.15 | 0.00115 | 297.15 | 0.6
0.05585 | 280.15 | 0.00115 | 297.15 | 0.7
0.05585 | 280.15 | 0.00115 | 297.15 | 0.8
0.05585 | 280.15 | 0.00115 | 297.15 | 0.9
0.05585 | 280.15 | 0.00115 | 297.15 | 1
0.05585 | 280.15 | 0.00115 | 300.15 | 0.15
0.05585 | 280.15 | 0.00115 | 300.15 | 0.2
0.05585 | 280.15 | 0.00115 | 300.15 | 0.3
0.05585 | 280.15 | 0.00115 | 300.15 | 0.4
0.05585 | 280.15 | 0.00115 | 300.15 | 0.5
0.05585 | 280.15 | 0.00115 | 300.15 | 0.6
0.05585 | 280.15 | 0.00115 | 300.15 | 0.7
0.05585 | 280.15 | 0.00115 | 300.15 | 0.8
0.05585 | 280.15 | 0.00115 | 300.15 | 0.9
0.05585 | 280.15 | 0.00115 | 300.15 | 1
0.05585 | 280.15 | 0.00115 | 303.15 | 0.15
0.05585 | 280.15 | 0.00115 | 303.15 | 0.2
0.05585 | 280.15 | 0.00115 | 303.15 | 0.3
0.05585 | 280.15 | 0.00115 | 303.15 | 0.4
0.05585 | 280.15 | 0.00115 | 303.15 | 0.5
0.05585 | 280.15 | 0.00115 | 303.15 | 0.6
0.05585 | 280.15 | 0.00115 | 303.15 | 0.7
0.05585 | 280.15 | 0.00115 | 303.15 | 0.8
0.05585 | 280.15 | 0.00115 | 303.15 | 0.9
0.05585 | 280.15 | 0.00115 | 303.15 | 1
0.05585 | 280.15 | 0.077 | 283.65 | 0.15
0.05585 | 280.15 | 0.077 | 283.65 | 0.2
0.05585 | 280.15 | 0.077 | 283.65 | 0.3
0.05585 | 280.15 | 0.077 | 283.65 | 0.4
0.05585 | 280.15 | 0.077 | 283.65 | 0.5
0.05585 | 280.15 | 0.077 | 283.65 | 0.6
0.05585 | 280.15 | 0.077 | 283.65 | 0.7
0.05585 | 280.15 | 0.077 | 283.65 | 0.8
0.05585 | 280.15 | 0.077 | 283.65 | 0.9
0.05585 | 280.15 | 0.077 | 283.65 | 1
0.05585 | 280.15 | 0.077 | 284.15 | 0.15
0.05585 | 280.15 | 0.077 | 284.15 | 0.2
0.05585 | 280.15 | 0.077 | 284.15 | 0.3
0.05585 | 280.15 | 0.077 | 284.15 | 0.4
0.05585 | 280.15 | 0.077 | 284.15 | 0.5
0.05585 | 280.15 | 0.077 | 284.15 | 0.6
0.05585 | 280.15 | 0.077 | 284.15 | 0.7
0.05585 | 280.15 | 0.077 | 284.15 | 0.8
0.05585 | 280.15 | 0.077 | 284.15 | 0.9
0.05585 | 280.15 | 0.077 | 284.15 | 1
0.05585 | 280.15 | 0.077 | 284.65 | 0.15
0.05585 | 280.15 | 0.077 | 284.65 | 0.2
0.05585 | 280.15 | 0.077 | 284.65 | 0.3
0.05585 | 280.15 | 0.077 | 284.65 | 0.4
0.05585 | 280.15 | 0.077 | 284.65 | 0.5
0.05585 | 280.15 | 0.077 | 284.65 | 0.6
0.05585 | 280.15 | 0.077 | 284.65 | 0.7
0.05585 | 280.15 | 0.077 | 284.65 | 0.8
0.05585 | 280.15 | 0.077 | 284.65 | 0.9
0.05585 | 280.15 | 0.077 | 284.65 | 1
0.05585 | 280.15 | 0.077 | 285.15 | 0.15
0.05585 | 280.15 | 0.077 | 285.15 | 0.2
0.05585 | 280.15 | 0.077 | 285.15 | 0.3
0.05585 | 280.15 | 0.077 | 285.15 | 0.4
0.05585 | 280.15 | 0.077 | 285.15 | 0.5
0.05585 | 280.15 | 0.077 | 285.15 | 0.6
0.05585 | 280.15 | 0.077 | 285.15 | 0.7
0.05585 | 280.15 | 0.077 | 285.15 | 0.8
0.05585 | 280.15 | 0.077 | 285.15 | 0.9
0.05585 | 280.15 | 0.077 | 285.15 | 1
0.05585 | 280.15 | 0.077 | 285.65 | 0.15
0.05585 | 280.15 | 0.077 | 285.65 | 0.2
0.05585 | 280.15 | 0.077 | 285.65 | 0.3
0.05585 | 280.15 | 0.077 | 285.65 | 0.4
0.05585 | 280.15 | 0.077 | 285.65 | 0.5
0.05585 | 280.15 | 0.077 | 285.65 | 0.6
0.05585 | 280.15 | 0.077 | 285.65 | 0.7
0.05585 | 280.15 | 0.077 | 285.65 | 0.8
0.05585 | 280.15 | 0.077 | 285.65 | 0.9
0.05585 | 280.15 | 0.077 | 285.65 | 1
0.05585 | 280.15 | 0.077 | 286.15 | 0.15
0.05585 | 280.15 | 0.077 | 286.15 | 0.2
0.05585 | 280.15 | 0.077 | 286.15 | 0.3
0.05585 | 280.15 | 0.077 | 286.15 | 0.4
0.05585 | 280.15 | 0.077 | 286.15 | 0.5
0.05585 | 280.15 | 0.077 | 286.15 | 0.6
0.05585 | 280.15 | 0.077 | 286.15 | 0.7
0.05585 | 280.15 | 0.077 | 286.15 | 0.8
0.05585 | 280.15 | 0.077 | 286.15 | 0.9
0.05585 | 280.15 | 0.077 | 286.15 | 1
0.05585 | 280.15 | 0.077 | 286.65 | 0.15
0.05585 | 280.15 | 0.077 | 286.65 | 0.2
0.05585 | 280.15 | 0.077 | 286.65 | 0.3
0.05585 | 280.15 | 0.077 | 286.65 | 0.4
0.05585 | 280.15 | 0.077 | 286.65 | 0.5
0.05585 | 280.15 | 0.077 | 286.65 | 0.6
0.05585 | 280.15 | 0.077 | 286.65 | 0.7
0.05585 | 280.15 | 0.077 | 286.65 | 0.8
0.05585 | 280.15 | 0.077 | 286.65 | 0.9
0.05585 | 280.15 | 0.077 | 286.65 | 1
0.05585 | 280.15 | 0.077 | 287.15 | 0.15
0.05585 | 280.15 | 0.077 | 287.15 | 0.2
0.05585 | 280.15 | 0.077 | 287.15 | 0.3
0.05585 | 280.15 | 0.077 | 287.15 | 0.4
0.05585 | 280.15 | 0.077 | 287.15 | 0.5
0.05585 | 280.15 | 0.077 | 287.15 | 0.6
0.05585 | 280.15 | 0.077 | 287.15 | 0.7
0.05585 | 280.15 | 0.077 | 287.15 | 0.8
0.05585 | 280.15 | 0.077 | 287.15 | 0.9
0.05585 | 280.15 | 0.077 | 287.15 | 1
0.05585 | 280.15 | 0.077 | 287.65 | 0.15
0.05585 | 280.15 | 0.077 | 287.65 | 0.2
0.05585 | 280.15 | 0.077 | 287.65 | 0.3
0.05585 | 280.15 | 0.077 | 287.65 | 0.4
0.05585 | 280.15 | 0.077 | 287.65 | 0.5
0.05585 | 280.15 | 0.077 | 287.65 | 0.6
0.05585 | 280.15 | 0.077 | 287.65 | 0.7
0.05585 | 280.15 | 0.077 | 287.65 | 0.8
0.05585 | 280.15 | 0.077 | 287.65 | 0.9
0.05585 | 280.15 | 0.077 | 287.65 | 1
0.05585 | 280.15 | 0.077 | 288.15 | 0.15
0.05585 | 280.15 | 0.077 | 288.15 | 0.2
0.05585 | 280.15 | 0.077 | 288.15 | 0.3
0.05585 | 280.15 | 0.077 | 288.15 | 0.4
0.05585 | 280.15 | 0.077 | 288.15 | 0.5
0.05585 | 280.15 | 0.077 | 288.15 | 0.6
0.05585 | 280.15 | 0.077 | 288.15 | 0.7
0.05585 | 280.15 | 0.077 | 288.15 | 0.8
0.05585 | 280.15 | 0.077 | 288.15 | 0.9
0.05585 | 280.15 | 0.077 | 288.15 | 1
0.05585 | 280.15 | 0.077 | 288.65 | 0.15
0.05585 | 280.15 | 0.077 | 288.65 | 0.2
0.05585 | 280.15 | 0.077 | 288.65 | 0.3
0.05585 | 280.15 | 0.077 | 288.65 | 0.4
0.05585 | 280.15 | 0.077 | 288.65 | 0.5
0.05585 | 280.15 | 0.077 | 288.65 | 0.6
0.05585 | 280.15 | 0.077 | 288.65 | 0.7
0.05585 | 280.15 | 0.077 | 288.65 | 0.8
0.05585 | 280.15 | 0.077 | 288.65 | 0.9
0.05585 | 280.15 | 0.077 | 288.65 | 1
0.05585 | 280.15 | 0.077 | 289.15 | 0.15
0.05585 | 280.15 | 0.077 | 289.15 | 0.2
0.05585 | 280.15 | 0.077 | 289.15 | 0.3
0.05585 | 280.15 | 0.077 | 289.15 | 0.4
0.05585 | 280.15 | 0.077 | 289.15 | 0.5
0.05585 | 280.15 | 0.077 | 289.15 | 0.6
0.05585 | 280.15 | 0.077 | 289.15 | 0.7
0.05585 | 280.15 | 0.077 | 289.15 | 0.8
0.05585 | 280.15 | 0.077 | 289.15 | 0.9
0.05585 | 280.15 | 0.077 | 289.15 | 1
0.05585 | 280.15 | 0.077 | 289.65 | 0.15
0.05585 | 280.15 | 0.077 | 289.65 | 0.2
0.05585 | 280.15 | 0.077 | 289.65 | 0.3
0.05585 | 280.15 | 0.077 | 289.65 | 0.4
0.05585 | 280.15 | 0.077 | 289.65 | 0.5
0.05585 | 280.15 | 0.077 | 289.65 | 0.6
0.05585 | 280.15 | 0.077 | 289.65 | 0.7
0.05585 | 280.15 | 0.077 | 289.65 | 0.8
0.05585 | 280.15 | 0.077 | 289.65 | 0.9
0.05585 | 280.15 | 0.077 | 289.65 | 1
0.05585 | 280.15 | 0.077 | 290.15 | 0.15
0.05585 | 280.15 | 0.077 | 290.15 | 0.2
0.05585 | 280.15 | 0.077 | 290.15 | 0.3
0.05585 | 280.15 | 0.077 | 290.15 | 0.4
0.05585 | 280.15 | 0.077 | 290.15 | 0.5
0.05585 | 280.15 | 0.077 | 290.15 | 0.6
0.05585 | 280.15 | 0.077 | 290.15 | 0.7
0.05585 | 280.15 | 0.077 | 290.15 | 0.8
0.05585 | 280.15 | 0.077 | 290.15 | 0.9
0.05585 | 280.15 | 0.077 | 290.15 | 1
0.05585 | 280.15 | 0.077 | 290.65 | 0.15
0.05585 | 280.15 | 0.077 | 290.65 | 0.2
0.05585 | 280.15 | 0.077 | 290.65 | 0.3
0.05585 | 280.15 | 0.077 | 290.65 | 0.4
0.05585 | 280.15 | 0.077 | 290.65 | 0.5
0.05585 | 280.15 | 0.077 | 290.65 | 0.6
0.05585 | 280.15 | 0.077 | 290.65 | 0.7
0.05585 | 280.15 | 0.077 | 290.65 | 0.8
0.05585 | 280.15 | 0.077 | 290.65 | 0.9
0.05585 | 280.15 | 0.077 | 290.65 | 1
0.05585 | 280.15 | 0.077 | 291.15 | 0.15
0.05585 | 280.15 | 0.077 | 291.15 | 0.2
0.05585 | 280.15 | 0.077 | 291.15 | 0.3
0.05585 | 280.15 | 0.077 | 291.15 | 0.4
0.05585 | 280.15 | 0.077 | 291.15 | 0.5
0.05585 | 280.15 | 0.077 | 291.15 | 0.6
0.05585 | 280.15 | 0.077 | 291.15 | 0.7
0.05585 | 280.15 | 0.077 | 291.15 | 0.8
0.05585 | 280.15 | 0.077 | 291.15 | 0.9
0.05585 | 280.15 | 0.077 | 291.15 | 1
0.05585 | 280.15 | 0.077 | 294.15 | 0.15
0.05585 | 280.15 | 0.077 | 294.15 | 0.2
0.05585 | 280.15 | 0.077 | 294.15 | 0.3
0.05585 | 280.15 | 0.077 | 294.15 | 0.4
0.05585 | 280.15 | 0.077 | 294.15 | 0.5
0.05585 | 280.15 | 0.077 | 294.15 | 0.6
0.05585 | 280.15 | 0.077 | 294.15 | 0.7
0.05585 | 280.15 | 0.077 | 294.15 | 0.8
0.05585 | 280.15 | 0.077 | 294.15 | 0.9
0.05585 | 280.15 | 0.077 | 294.15 | 1
0.05585 | 280.15 | 0.077 | 297.15 | 0.15
0.05585 | 280.15 | 0.077 | 297.15 | 0.2
0.05585 | 280.15 | 0.077 | 297.15 | 0.3
0.05585 | 280.15 | 0.077 | 297.15 | 0.4
0.05585 | 280.15 | 0.077 | 297.15 | 0.5
0.05585 | 280.15 | 0.077 | 297.15 | 0.6
0.05585 | 280.15 | 0.077 | 297.15 | 0.7
0.05585 | 280.15 | 0.077 | 297.15 | 0.8
0.05585 | 280.15 | 0.077 | 297.15 | 0.9
0.05585 | 280.15 | 0.077 | 297.15 | 1
0.05585 | 280.15 | 0.077 | 300.15 | 0.15
0.05585 | 280.15 | 0.077 | 300.15 | 0.2
0.05585 | 280.15 | 0.077 | 300.15 | 0.3
0.05585 | 280.15 | 0.077 | 300.15 | 0.4
0.05585 | 280.15 | 0.077 | 300.15 | 0.5
0.05585 | 280.15 | 0.077 | 300.15 | 0.6
0.05585 | 280.15 | 0.077 | 300.15 | 0.7
0.05585 | 280.15 | 0.077 | 300.15 | 0.8
0.05585 | 280.15 | 0.077 | 300.15 | 0.9
0.05585 | 280.15 | 0.077 | 300.15 | 1
0.05585 | 280.15 | 0.077 | 303.15 | 0.15
0.05585 | 280.15 | 0.077 | 303.15 | 0.2
0.05585 | 280.15 | 0.077 | 303.15 | 0.3
0.05585 | 280.15 | 0.077 | 303.15 | 0.4
0.05585 | 280.15 | 0.077 | 303.15 | 0.5
0.05585 | 280.15 | 0.077 | 303.15 | 0.6
0.05585 | 280.15 | 0.077 | 303.15 | 0.7
0.05585 | 280.15 | 0.077 | 303.15 | 0.8
0.05585 | 280.15 | 0.077 | 303.15 | 0.9
0.05585 | 280.15 | 0.077 | 303.15 | 1
0.05585 | 280.15 | 0.09437 | 283.65 | 0.15
0.05585 | 280.15 | 0.09437 | 283.65 | 0.2
0.05585 | 280.15 | 0.09437 | 283.65 | 0.3
0.05585 | 280.15 | 0.09437 | 283.65 | 0.4
0.05585 | 280.15 | 0.09437 | 283.65 | 0.5
0.05585 | 280.15 | 0.09437 | 283.65 | 0.6
0.05585 | 280.15 | 0.09437 | 283.65 | 0.7
0.05585 | 280.15 | 0.09437 | 283.65 | 0.8
0.05585 | 280.15 | 0.09437 | 283.65 | 0.9
0.05585 | 280.15 | 0.09437 | 283.65 | 1
0.05585 | 280.15 | 0.09437 | 284.15 | 0.15
0.05585 | 280.15 | 0.09437 | 284.15 | 0.2
0.05585 | 280.15 | 0.09437 | 284.15 | 0.3
0.05585 | 280.15 | 0.09437 | 284.15 | 0.4
0.05585 | 280.15 | 0.09437 | 284.15 | 0.5
0.05585 | 280.15 | 0.09437 | 284.15 | 0.6
0.05585 | 280.15 | 0.09437 | 284.15 | 0.7
0.05585 | 280.15 | 0.09437 | 284.15 | 0.8
0.05585 | 280.15 | 0.09437 | 284.15 | 0.9
0.05585 | 280.15 | 0.09437 | 284.15 | 1
0.05585 | 280.15 | 0.09437 | 284.65 | 0.15
0.05585 | 280.15 | 0.09437 | 284.65 | 0.2
0.05585 | 280.15 | 0.09437 | 284.65 | 0.3
0.05585 | 280.15 | 0.09437 | 284.65 | 0.4
0.05585 | 280.15 | 0.09437 | 284.65 | 0.5
0.05585 | 280.15 | 0.09437 | 284.65 | 0.6
0.05585 | 280.15 | 0.09437 | 284.65 | 0.7
0.05585 | 280.15 | 0.09437 | 284.65 | 0.8
0.05585 | 280.15 | 0.09437 | 284.65 | 0.9
0.05585 | 280.15 | 0.09437 | 284.65 | 1
0.05585 | 280.15 | 0.09437 | 285.15 | 0.15
0.05585 | 280.15 | 0.09437 | 285.15 | 0.2
0.05585 | 280.15 | 0.09437 | 285.15 | 0.3
0.05585 | 280.15 | 0.09437 | 285.15 | 0.4
0.05585 | 280.15 | 0.09437 | 285.15 | 0.5
0.05585 | 280.15 | 0.09437 | 285.15 | 0.6
0.05585 | 280.15 | 0.09437 | 285.15 | 0.7
0.05585 | 280.15 | 0.09437 | 285.15 | 0.8
0.05585 | 280.15 | 0.09437 | 285.15 | 0.9
0.05585 | 280.15 | 0.09437 | 285.15 | 1
0.05585 | 280.15 | 0.09437 | 285.65 | 0.15
0.05585 | 280.15 | 0.09437 | 285.65 | 0.2
0.05585 | 280.15 | 0.09437 | 285.65 | 0.3
0.05585 | 280.15 | 0.09437 | 285.65 | 0.4
0.05585 | 280.15 | 0.09437 | 285.65 | 0.5
0.05585 | 280.15 | 0.09437 | 285.65 | 0.6
0.05585 | 280.15 | 0.09437 | 285.65 | 0.7
0.05585 | 280.15 | 0.09437 | 285.65 | 0.8
0.05585 | 280.15 | 0.09437 | 285.65 | 0.9
0.05585 | 280.15 | 0.09437 | 285.65 | 1
0.05585 | 280.15 | 0.09437 | 286.15 | 0.15
0.05585 | 280.15 | 0.09437 | 286.15 | 0.2
0.05585 | 280.15 | 0.09437 | 286.15 | 0.3
0.05585 | 280.15 | 0.09437 | 286.15 | 0.4
0.05585 | 280.15 | 0.09437 | 286.15 | 0.5
0.05585 | 280.15 | 0.09437 | 286.15 | 0.6
0.05585 | 280.15 | 0.09437 | 286.15 | 0.7
0.05585 | 280.15 | 0.09437 | 286.15 | 0.8
0.05585 | 280.15 | 0.09437 | 286.15 | 0.9
0.05585 | 280.15 | 0.09437 | 286.15 | 1
0.05585 | 280.15 | 0.09437 | 286.65 | 0.15
0.05585 | 280.15 | 0.09437 | 286.65 | 0.2
0.05585 | 280.15 | 0.09437 | 286.65 | 0.3
0.05585 | 280.15 | 0.09437 | 286.65 | 0.4
0.05585 | 280.15 | 0.09437 | 286.65 | 0.5
0.05585 | 280.15 | 0.09437 | 286.65 | 0.6
0.05585 | 280.15 | 0.09437 | 286.65 | 0.7
0.05585 | 280.15 | 0.09437 | 286.65 | 0.8
0.05585 | 280.15 | 0.09437 | 286.65 | 0.9
0.05585 | 280.15 | 0.09437 | 286.65 | 1
0.05585 | 280.15 | 0.09437 | 287.15 | 0.15
0.05585 | 280.15 | 0.09437 | 287.15 | 0.2
0.05585 | 280.15 | 0.09437 | 287.15 | 0.3
0.05585 | 280.15 | 0.09437 | 287.15 | 0.4
0.05585 | 280.15 | 0.09437 | 287.15 | 0.5
0.05585 | 280.15 | 0.09437 | 287.15 | 0.6
0.05585 | 280.15 | 0.09437 | 287.15 | 0.7
0.05585 | 280.15 | 0.09437 | 287.15 | 0.8
0.05585 | 280.15 | 0.09437 | 287.15 | 0.9
0.05585 | 280.15 | 0.09437 | 287.15 | 1
0.05585 | 280.15 | 0.09437 | 287.65 | 0.15
0.05585 | 280.15 | 0.09437 | 287.65 | 0.2
0.05585 | 280.15 | 0.09437 | 287.65 | 0.3
0.05585 | 280.15 | 0.09437 | 287.65 | 0.4
0.05585 | 280.15 | 0.09437 | 287.65 | 0.5
0.05585 | 280.15 | 0.09437 | 287.65 | 0.6
0.05585 | 280.15 | 0.09437 | 287.65 | 0.7
0.05585 | 280.15 | 0.09437 | 287.65 | 0.8
0.05585 | 280.15 | 0.09437 | 287.65 | 0.9
0.05585 | 280.15 | 0.09437 | 287.65 | 1
0.05585 | 280.15 | 0.09437 | 288.15 | 0.15
0.05585 | 280.15 | 0.09437 | 288.15 | 0.2
0.05585 | 280.15 | 0.09437 | 288.15 | 0.3
0.05585 | 280.15 | 0.09437 | 288.15 | 0.4
0.05585 | 280.15 | 0.09437 | 288.15 | 0.5
0.05585 | 280.15 | 0.09437 | 288.15 | 0.6
0.05585 | 280.15 | 0.09437 | 288.15 | 0.7
0.05585 | 280.15 | 0.09437 | 288.15 | 0.8
0.05585 | 280.15 | 0.09437 | 288.15 | 0.9
0.05585 | 280.15 | 0.09437 | 288.15 | 1
0.05585 | 280.15 | 0.09437 | 288.65 | 0.15
0.05585 | 280.15 | 0.09437 | 288.65 | 0.2
0.05585 | 280.15 | 0.09437 | 288.65 | 0.3
0.05585 | 280.15 | 0.09437 | 288.65 | 0.4
0.05585 | 280.15 | 0.09437 | 288.65 | 0.5
0.05585 | 280.15 | 0.09437 | 288.65 | 0.6
0.05585 | 280.15 | 0.09437 | 288.65 | 0.7
0.05585 | 280.15 | 0.09437 | 288.65 | 0.8
0.05585 | 280.15 | 0.09437 | 288.65 | 0.9
0.05585 | 280.15 | 0.09437 | 288.65 | 1
0.05585 | 280.15 | 0.09437 | 289.15 | 0.15
0.05585 | 280.15 | 0.09437 | 289.15 | 0.2
0.05585 | 280.15 | 0.09437 | 289.15 | 0.3
0.05585 | 280.15 | 0.09437 | 289.15 | 0.4
0.05585 | 280.15 | 0.09437 | 289.15 | 0.5
0.05585 | 280.15 | 0.09437 | 289.15 | 0.6
0.05585 | 280.15 | 0.09437 | 289.15 | 0.7
0.05585 | 280.15 | 0.09437 | 289.15 | 0.8
0.05585 | 280.15 | 0.09437 | 289.15 | 0.9
0.05585 | 280.15 | 0.09437 | 289.15 | 1
0.05585 | 280.15 | 0.09437 | 289.65 | 0.15
0.05585 | 280.15 | 0.09437 | 289.65 | 0.2
0.05585 | 280.15 | 0.09437 | 289.65 | 0.3
0.05585 | 280.15 | 0.09437 | 289.65 | 0.4
0.05585 | 280.15 | 0.09437 | 289.65 | 0.5
0.05585 | 280.15 | 0.09437 | 289.65 | 0.6
0.05585 | 280.15 | 0.09437 | 289.65 | 0.7
0.05585 | 280.15 | 0.09437 | 289.65 | 0.8
0.05585 | 280.15 | 0.09437 | 289.65 | 0.9
0.05585 | 280.15 | 0.09437 | 289.65 | 1
0.05585 | 280.15 | 0.09437 | 290.15 | 0.15
0.05585 | 280.15 | 0.09437 | 290.15 | 0.2
0.05585 | 280.15 | 0.09437 | 290.15 | 0.3
0.05585 | 280.15 | 0.09437 | 290.15 | 0.4
0.05585 | 280.15 | 0.09437 | 290.15 | 0.5
0.05585 | 280.15 | 0.09437 | 290.15 | 0.6
0.05585 | 280.15 | 0.09437 | 290.15 | 0.7
0.05585 | 280.15 | 0.09437 | 290.15 | 0.8
0.05585 | 280.15 | 0.09437 | 290.15 | 0.9
0.05585 | 280.15 | 0.09437 | 290.15 | 1
0.05585 | 280.15 | 0.09437 | 290.65 | 0.15
0.05585 | 280.15 | 0.09437 | 290.65 | 0.2
0.05585 | 280.15 | 0.09437 | 290.65 | 0.3
0.05585 | 280.15 | 0.09437 | 290.65 | 0.4
0.05585 | 280.15 | 0.09437 | 290.65 | 0.5
0.05585 | 280.15 | 0.09437 | 290.65 | 0.6
0.05585 | 280.15 | 0.09437 | 290.65 | 0.7
0.05585 | 280.15 | 0.09437 | 290.65 | 0.8
0.05585 | 280.15 | 0.09437 | 290.65 | 0.9
0.05585 | 280.15 | 0.09437 | 290.65 | 1
0.05585 | 280.15 | 0.09437 | 291.15 | 0.15
0.05585 | 280.15 | 0.09437 | 291.15 | 0.2
0.05585 | 280.15 | 0.09437 | 291.15 | 0.3
0.05585 | 280.15 | 0.09437 | 291.15 | 0.4
0.05585 | 280.15 | 0.09437 | 291.15 | 0.5
0.05585 | 280.15 | 0.09437 | 291.15 | 0.6
0.05585 | 280.15 | 0.09437 | 291.15 | 0.7
0.05585 | 280.15 | 0.09437 | 291.15 | 0.8
0.05585 | 280.15 | 0.09437 | 291.15 | 0.9
0.05585 | 280.15 | 0.09437 | 291.15 | 1
0.05585 | 280.15 | 0.09437 | 294.15 | 0.15
0.05585 | 280.15 | 0.09437 | 294.15 | 0.2
0.05585 | 280.15 | 0.09437 | 294.15 | 0.3
0.05585 | 280.15 | 0.09437 | 294.15 | 0.4
0.05585 | 280.15 | 0.09437 | 294.15 | 0.5
0.05585 | 280.15 | 0.09437 | 294.15 | 0.6
0.05585 | 280.15 | 0.09437 | 294.15 | 0.7
0.05585 | 280.15 | 0.09437 | 294.15 | 0.8
0.05585 | 280.15 | 0.09437 | 294.15 | 0.9
0.05585 | 280.15 | 0.09437 | 294.15 | 1
0.05585 | 280.15 | 0.09437 | 297.15 | 0.15
0.05585 | 280.15 | 0.09437 | 297.15 | 0.2
0.05585 | 280.15 | 0.09437 | 297.15 | 0.3
0.05585 | 280.15 | 0.09437 | 297.15 | 0.4
0.05585 | 280.15 | 0.09437 | 297.15 | 0.5
0.05585 | 280.15 | 0.09437 | 297.15 | 0.6
0.05585 | 280.15 | 0.09437 | 297.15 | 0.7
0.05585 | 280.15 | 0.09437 | 297.15 | 0.8
0.05585 | 280.15 | 0.09437 | 297.15 | 0.9
0.05585 | 280.15 | 0.09437 | 297.15 | 1
0.05585 | 280.15 | 0.09437 | 300.15 | 0.15
0.05585 | 280.15 | 0.09437 | 300.15 | 0.2
0.05585 | 280.15 | 0.09437 | 300.15 | 0.3
0.05585 | 280.15 | 0.09437 | 300.15 | 0.4
0.05585 | 280.15 | 0.09437 | 300.15 | 0.5
0.05585 | 280.15 | 0.09437 | 300.15 | 0.6
0.05585 | 280.15 | 0.09437 | 300.15 | 0.7
0.05585 | 280.15 | 0.09437 | 300.15 | 0.8
0.05585 | 280.15 | 0.09437 | 300.15 | 0.9
0.05585 | 280.15 | 0.09437 | 300.15 | 1
0.05585 | 280.15 | 0.09437 | 303.15 | 0.15
0.05585 | 280.15 | 0.09437 | 303.15 | 0.2
0.05585 | 280.15 | 0.09437 | 303.15 | 0.3
0.05585 | 280.15 | 0.09437 | 303.15 | 0.4
0.05585 | 280.15 | 0.09437 | 303.15 | 0.5
0.05585 | 280.15 | 0.09437 | 303.15 | 0.6
0.05585 | 280.15 | 0.09437 | 303.15 | 0.7
0.05585 | 280.15 | 0.09437 | 303.15 | 0.8
0.05585 | 280.15 | 0.09437 | 303.15 | 0.9
0.05585 | 280.15 | 0.09437 | 303.15 | 1
0.05585 | 280.15 | 0.09644 | 283.65 | 0.15
0.05585 | 280.15 | 0.09644 | 283.65 | 0.2
0.05585 | 280.15 | 0.09644 | 283.65 | 0.3
0.05585 | 280.15 | 0.09644 | 283.65 | 0.4
0.05585 | 280.15 | 0.09644 | 283.65 | 0.5
0.05585 | 280.15 | 0.09644 | 283.65 | 0.6
0.05585 | 280.15 | 0.09644 | 283.65 | 0.7
0.05585 | 280.15 | 0.09644 | 283.65 | 0.8
0.05585 | 280.15 | 0.09644 | 283.65 | 0.9
0.05585 | 280.15 | 0.09644 | 283.65 | 1
0.05585 | 280.15 | 0.09644 | 284.15 | 0.15
0.05585 | 280.15 | 0.09644 | 284.15 | 0.2
0.05585 | 280.15 | 0.09644 | 284.15 | 0.3
0.05585 | 280.15 | 0.09644 | 284.15 | 0.4
0.05585 | 280.15 | 0.09644 | 284.15 | 0.5
0.05585 | 280.15 | 0.09644 | 284.15 | 0.6
0.05585 | 280.15 | 0.09644 | 284.15 | 0.7
0.05585 | 280.15 | 0.09644 | 284.15 | 0.8
0.05585 | 280.15 | 0.09644 | 284.15 | 0.9
0.05585 | 280.15 | 0.09644 | 284.15 | 1
0.05585 | 280.15 | 0.09644 | 284.65 | 0.15
0.05585 | 280.15 | 0.09644 | 284.65 | 0.2
0.05585 | 280.15 | 0.09644 | 284.65 | 0.3
0.05585 | 280.15 | 0.09644 | 284.65 | 0.4
0.05585 | 280.15 | 0.09644 | 284.65 | 0.5
0.05585 | 280.15 | 0.09644 | 284.65 | 0.6
0.05585 | 280.15 | 0.09644 | 284.65 | 0.7
0.05585 | 280.15 | 0.09644 | 284.65 | 0.8
0.05585 | 280.15 | 0.09644 | 284.65 | 0.9
0.05585 | 280.15 | 0.09644 | 284.65 | 1
0.05585 | 280.15 | 0.09644 | 285.15 | 0.15
0.05585 | 280.15 | 0.09644 | 285.15 | 0.2
0.05585 | 280.15 | 0.09644 | 285.15 | 0.3
0.05585 | 280.15 | 0.09644 | 285.15 | 0.4
0.05585 | 280.15 | 0.09644 | 285.15 | 0.5
0.05585 | 280.15 | 0.09644 | 285.15 | 0.6
0.05585 | 280.15 | 0.09644 | 285.15 | 0.7
0.05585 | 280.15 | 0.09644 | 285.15 | 0.8
0.05585 | 280.15 | 0.09644 | 285.15 | 0.9
0.05585 | 280.15 | 0.09644 | 285.15 | 1
0.05585 | 280.15 | 0.09644 | 285.65 | 0.15
0.05585 | 280.15 | 0.09644 | 285.65 | 0.2
0.05585 | 280.15 | 0.09644 | 285.65 | 0.3
0.05585 | 280.15 | 0.09644 | 285.65 | 0.4
0.05585 | 280.15 | 0.09644 | 285.65 | 0.5
0.05585 | 280.15 | 0.09644 | 285.65 | 0.6
0.05585 | 280.15 | 0.09644 | 285.65 | 0.7
0.05585 | 280.15 | 0.09644 | 285.65 | 0.8
0.05585 | 280.15 | 0.09644 | 285.65 | 0.9
0.05585 | 280.15 | 0.09644 | 285.65 | 1
0.05585 | 280.15 | 0.09644 | 286.15 | 0.15
0.05585 | 280.15 | 0.09644 | 286.15 | 0.2
0.05585 | 280.15 | 0.09644 | 286.15 | 0.3
0.05585 | 280.15 | 0.09644 | 286.15 | 0.4
0.05585 | 280.15 | 0.09644 | 286.15 | 0.5
0.05585 | 280.15 | 0.09644 | 286.15 | 0.6
0.05585 | 280.15 | 0.09644 | 286.15 | 0.7
0.05585 | 280.15 | 0.09644 | 286.15 | 0.8
0.05585 | 280.15 | 0.09644 | 286.15 | 0.9
0.05585 | 280.15 | 0.09644 | 286.15 | 1
0.05585 | 280.15 | 0.09644 | 286.65 | 0.15
0.05585 | 280.15 | 0.09644 | 286.65 | 0.2
0.05585 | 280.15 | 0.09644 | 286.65 | 0.3
0.05585 | 280.15 | 0.09644 | 286.65 | 0.4
0.05585 | 280.15 | 0.09644 | 286.65 | 0.5
0.05585 | 280.15 | 0.09644 | 286.65 | 0.6
0.05585 | 280.15 | 0.09644 | 286.65 | 0.7
0.05585 | 280.15 | 0.09644 | 286.65 | 0.8
0.05585 | 280.15 | 0.09644 | 286.65 | 0.9
0.05585 | 280.15 | 0.09644 | 286.65 | 1
0.05585 | 280.15 | 0.09644 | 287.15 | 0.15
0.05585 | 280.15 | 0.09644 | 287.15 | 0.2
0.05585 | 280.15 | 0.09644 | 287.15 | 0.3
0.05585 | 280.15 | 0.09644 | 287.15 | 0.4
0.05585 | 280.15 | 0.09644 | 287.15 | 0.5
0.05585 | 280.15 | 0.09644 | 287.15 | 0.6
0.05585 | 280.15 | 0.09644 | 287.15 | 0.7
0.05585 | 280.15 | 0.09644 | 287.15 | 0.8
0.05585 | 280.15 | 0.09644 | 287.15 | 0.9
0.05585 | 280.15 | 0.09644 | 287.15 | 1
0.05585 | 280.15 | 0.09644 | 287.65 | 0.15
0.05585 | 280.15 | 0.09644 | 287.65 | 0.2
0.05585 | 280.15 | 0.09644 | 287.65 | 0.3
0.05585 | 280.15 | 0.09644 | 287.65 | 0.4
0.05585 | 280.15 | 0.09644 | 287.65 | 0.5
0.05585 | 280.15 | 0.09644 | 287.65 | 0.6
0.05585 | 280.15 | 0.09644 | 287.65 | 0.7
0.05585 | 280.15 | 0.09644 | 287.65 | 0.8
0.05585 | 280.15 | 0.09644 | 287.65 | 0.9
0.05585 | 280.15 | 0.09644 | 287.65 | 1
0.05585 | 280.15 | 0.09644 | 288.15 | 0.15
0.05585 | 280.15 | 0.09644 | 288.15 | 0.2
0.05585 | 280.15 | 0.09644 | 288.15 | 0.3
0.05585 | 280.15 | 0.09644 | 288.15 | 0.4
0.05585 | 280.15 | 0.09644 | 288.15 | 0.5
0.05585 | 280.15 | 0.09644 | 288.15 | 0.6
0.05585 | 280.15 | 0.09644 | 288.15 | 0.7
0.05585 | 280.15 | 0.09644 | 288.15 | 0.8
0.05585 | 280.15 | 0.09644 | 288.15 | 0.9
0.05585 | 280.15 | 0.09644 | 288.15 | 1
0.05585 | 280.15 | 0.09644 | 288.65 | 0.15
0.05585 | 280.15 | 0.09644 | 288.65 | 0.2
0.05585 | 280.15 | 0.09644 | 288.65 | 0.3
0.05585 | 280.15 | 0.09644 | 288.65 | 0.4
0.05585 | 280.15 | 0.09644 | 288.65 | 0.5
0.05585 | 280.15 | 0.09644 | 288.65 | 0.6
0.05585 | 280.15 | 0.09644 | 288.65 | 0.7
0.05585 | 280.15 | 0.09644 | 288.65 | 0.8
0.05585 | 280.15 | 0.09644 | 288.65 | 0.9
0.05585 | 280.15 | 0.09644 | 288.65 | 1
0.05585 | 280.15 | 0.09644 | 289.15 | 0.15
0.05585 | 280.15 | 0.09644 | 289.15 | 0.2
0.05585 | 280.15 | 0.09644 | 289.15 | 0.3
0.05585 | 280.15 | 0.09644 | 289.15 | 0.4
0.05585 | 280.15 | 0.09644 | 289.15 | 0.5
0.05585 | 280.15 | 0.09644 | 289.15 | 0.6
0.05585 | 280.15 | 0.09644 | 289.15 | 0.7
0.05585 | 280.15 | 0.09644 | 289.15 | 0.8
0.05585 | 280.15 | 0.09644 | 289.15 | 0.9
0.05585 | 280.15 | 0.09644 | 289.15 | 1
0.05585 | 280.15 | 0.09644 | 289.65 | 0.15
0.05585 | 280.15 | 0.09644 | 289.65 | 0.2
0.05585 | 280.15 | 0.09644 | 289.65 | 0.3
0.05585 | 280.15 | 0.09644 | 289.65 | 0.4
0.05585 | 280.15 | 0.09644 | 289.65 | 0.5
0.05585 | 280.15 | 0.09644 | 289.65 | 0.6
0.05585 | 280.15 | 0.09644 | 289.65 | 0.7
0.05585 | 280.15 | 0.09644 | 289.65 | 0.8
0.05585 | 280.15 | 0.09644 | 289.65 | 0.9
0.05585 | 280.15 | 0.09644 | 289.65 | 1
0.05585 | 280.15 | 0.09644 | 290.15 | 0.15
0.05585 | 280.15 | 0.09644 | 290.15 | 0.2
0.05585 | 280.15 | 0.09644 | 290.15 | 0.3
0.05585 | 280.15 | 0.09644 | 290.15 | 0.4
0.05585 | 280.15 | 0.09644 | 290.15 | 0.5
0.05585 | 280.15 | 0.09644 | 290.15 | 0.6
0.05585 | 280.15 | 0.09644 | 290.15 | 0.7
0.05585 | 280.15 | 0.09644 | 290.15 | 0.8
0.05585 | 280.15 | 0.09644 | 290.15 | 0.9
0.05585 | 280.15 | 0.09644 | 290.15 | 1
0.05585 | 280.15 | 0.09644 | 290.65 | 0.15
0.05585 | 280.15 | 0.09644 | 290.65 | 0.2
0.05585 | 280.15 | 0.09644 | 290.65 | 0.3
0.05585 | 280.15 | 0.09644 | 290.65 | 0.4
0.05585 | 280.15 | 0.09644 | 290.65 | 0.5
0.05585 | 280.15 | 0.09644 | 290.65 | 0.6
0.05585 | 280.15 | 0.09644 | 290.65 | 0.7
0.05585 | 280.15 | 0.09644 | 290.65 | 0.8
0.05585 | 280.15 | 0.09644 | 290.65 | 0.9
0.05585 | 280.15 | 0.09644 | 290.65 | 1
0.05585 | 280.15 | 0.09644 | 291.15 | 0.15
0.05585 | 280.15 | 0.09644 | 291.15 | 0.2
0.05585 | 280.15 | 0.09644 | 291.15 | 0.3
0.05585 | 280.15 | 0.09644 | 291.15 | 0.4
0.05585 | 280.15 | 0.09644 | 291.15 | 0.5
0.05585 | 280.15 | 0.09644 | 291.15 | 0.6
0.05585 | 280.15 | 0.09644 | 291.15 | 0.7
0.05585 | 280.15 | 0.09644 | 291.15 | 0.8
0.05585 | 280.15 | 0.09644 | 291.15 | 0.9
0.05585 | 280.15 | 0.09644 | 291.15 | 1
0.05585 | 280.15 | 0.09644 | 294.15 | 0.15
0.05585 | 280.15 | 0.09644 | 294.15 | 0.2
0.05585 | 280.15 | 0.09644 | 294.15 | 0.3
0.05585 | 280.15 | 0.09644 | 294.15 | 0.4
0.05585 | 280.15 | 0.09644 | 294.15 | 0.5
0.05585 | 280.15 | 0.09644 | 294.15 | 0.6
0.05585 | 280.15 | 0.09644 | 294.15 | 0.7
0.05585 | 280.15 | 0.09644 | 294.15 | 0.8
0.05585 | 280.15 | 0.09644 | 294.15 | 0.9
0.05585 | 280.15 | 0.09644 | 294.15 | 1
0.05585 | 280.15 | 0.09644 | 297.15 | 0.15
0.05585 | 280.15 | 0.09644 | 297.15 | 0.2
0.05585 | 280.15 | 0.09644 | 297.15 | 0.3
0.05585 | 280.15 | 0.09644 | 297.15 | 0.4
0.05585 | 280.15 | 0.09644 | 297.15 | 0.5
0.05585 | 280.15 | 0.09644 | 297.15 | 0.6
0.05585 | 280.15 | 0.09644 | 297.15 | 0.7
0.05585 | 280.15 | 0.09644 | 297.15 | 0.8
0.05585 | 280.15 | 0.09644 | 297.15 | 0.9
0.05585 | 280.15 | 0.09644 | 297.15 | 1
0.05585 | 280.15 | 0.09644 | 300.15 | 0.15
0.05585 | 280.15 | 0.09644 | 300.15 | 0.2
0.05585 | 280.15 | 0.09644 | 300.15 | 0.3
0.05585 | 280.15 | 0.09644 | 300.15 | 0.4
0.05585 | 280.15 | 0.09644 | 300.15 | 0.5
0.05585 | 280.15 | 0.09644 | 300.15 | 0.6
0.05585 | 280.15 | 0.09644 | 300.15 | 0.7
0.05585 | 280.15 | 0.09644 | 300.15 | 0.8
0.05585 | 280.15 | 0.09644 | 300.15 | 0.9
0.05585 | 280.15 | 0.09644 | 300.15 | 1
0.05585 | 280.15 | 0.09644 | 303.15 | 0.15
0.05585 | 280.15 | 0.09644 | 303.15 | 0.2
0.05585 | 280.15 | 0.09644 | 303.15 | 0.3
0.05585 | 280.15 | 0.09644 | 303.15 | 0.4
0.05585 | 280.15 | 0.09644 | 303.15 | 0.5
0.05585 | 280.15 | 0.09644 | 303.15 | 0.6
0.05585 | 280.15 | 0.09644 | 303.15 | 0.7
0.05585 | 280.15 | 0.09644 | 303.15 | 0.8
0.05585 | 280.15 | 0.09644 | 303.15 | 0.9
0.05585 | 280.15 | 0.09644 | 303.15 | 1
0.05585 | 280.15 | 0.09737 | 283.65 | 0.15
0.05585 | 280.15 | 0.09737 | 283.65 | 0.2
0.05585 | 280.15 | 0.09737 | 283.65 | 0.3
0.05585 | 280.15 | 0.09737 | 283.65 | 0.4
0.05585 | 280.15 | 0.09737 | 283.65 | 0.5
0.05585 | 280.15 | 0.09737 | 283.65 | 0.6
0.05585 | 280.15 | 0.09737 | 283.65 | 0.7
0.05585 | 280.15 | 0.09737 | 283.65 | 0.8
0.05585 | 280.15 | 0.09737 | 283.65 | 0.9
0.05585 | 280.15 | 0.09737 | 283.65 | 1
0.05585 | 280.15 | 0.09737 | 284.15 | 0.15
0.05585 | 280.15 | 0.09737 | 284.15 | 0.2
0.05585 | 280.15 | 0.09737 | 284.15 | 0.3
0.05585 | 280.15 | 0.09737 | 284.15 | 0.4
0.05585 | 280.15 | 0.09737 | 284.15 | 0.5
0.05585 | 280.15 | 0.09737 | 284.15 | 0.6
0.05585 | 280.15 | 0.09737 | 284.15 | 0.7
0.05585 | 280.15 | 0.09737 | 284.15 | 0.8
0.05585 | 280.15 | 0.09737 | 284.15 | 0.9
0.05585 | 280.15 | 0.09737 | 284.15 | 1
0.05585 | 280.15 | 0.09737 | 284.65 | 0.15
0.05585 | 280.15 | 0.09737 | 284.65 | 0.2
0.05585 | 280.15 | 0.09737 | 284.65 | 0.3
0.05585 | 280.15 | 0.09737 | 284.65 | 0.4
0.05585 | 280.15 | 0.09737 | 284.65 | 0.5
0.05585 | 280.15 | 0.09737 | 284.65 | 0.6
0.05585 | 280.15 | 0.09737 | 284.65 | 0.7
0.05585 | 280.15 | 0.09737 | 284.65 | 0.8
0.05585 | 280.15 | 0.09737 | 284.65 | 0.9
0.05585 | 280.15 | 0.09737 | 284.65 | 1
0.05585 | 280.15 | 0.09737 | 285.15 | 0.15
0.05585 | 280.15 | 0.09737 | 285.15 | 0.2
0.05585 | 280.15 | 0.09737 | 285.15 | 0.3
0.05585 | 280.15 | 0.09737 | 285.15 | 0.4
0.05585 | 280.15 | 0.09737 | 285.15 | 0.5
0.05585 | 280.15 | 0.09737 | 285.15 | 0.6
0.05585 | 280.15 | 0.09737 | 285.15 | 0.7
0.05585 | 280.15 | 0.09737 | 285.15 | 0.8
0.05585 | 280.15 | 0.09737 | 285.15 | 0.9
0.05585 | 280.15 | 0.09737 | 285.15 | 1
0.05585 | 280.15 | 0.09737 | 285.65 | 0.15
0.05585 | 280.15 | 0.09737 | 285.65 | 0.2
0.05585 | 280.15 | 0.09737 | 285.65 | 0.3
0.05585 | 280.15 | 0.09737 | 285.65 | 0.4
0.05585 | 280.15 | 0.09737 | 285.65 | 0.5
0.05585 | 280.15 | 0.09737 | 285.65 | 0.6
0.05585 | 280.15 | 0.09737 | 285.65 | 0.7
0.05585 | 280.15 | 0.09737 | 285.65 | 0.8
0.05585 | 280.15 | 0.09737 | 285.65 | 0.9
0.05585 | 280.15 | 0.09737 | 285.65 | 1
0.05585 | 280.15 | 0.09737 | 286.15 | 0.15
0.05585 | 280.15 | 0.09737 | 286.15 | 0.2
0.05585 | 280.15 | 0.09737 | 286.15 | 0.3
0.05585 | 280.15 | 0.09737 | 286.15 | 0.4
0.05585 | 280.15 | 0.09737 | 286.15 | 0.5
0.05585 | 280.15 | 0.09737 | 286.15 | 0.6
0.05585 | 280.15 | 0.09737 | 286.15 | 0.7
0.05585 | 280.15 | 0.09737 | 286.15 | 0.8
0.05585 | 280.15 | 0.09737 | 286.15 | 0.9
0.05585 | 280.15 | 0.09737 | 286.15 | 1
0.05585 | 280.15 | 0.09737 | 286.65 | 0.15
0.05585 | 280.15 | 0.09737 | 286.65 | 0.2
0.05585 | 280.15 | 0.09737 | 286.65 | 0.3
0.05585 | 280.15 | 0.09737 | 286.65 | 0.4
0.05585 | 280.15 | 0.09737 | 286.65 | 0.5
0.05585 | 280.15 | 0.09737 | 286.65 | 0.6
0.05585 | 280.15 | 0.09737 | 286.65 | 0.7
0.05585 | 280.15 | 0.09737 | 286.65 | 0.8
0.05585 | 280.15 | 0.09737 | 286.65 | 0.9
0.05585 | 280.15 | 0.09737 | 286.65 | 1
0.05585 | 280.15 | 0.09737 | 287.15 | 0.15
0.05585 | 280.15 | 0.09737 | 287.15 | 0.2
0.05585 | 280.15 | 0.09737 | 287.15 | 0.3
0.05585 | 280.15 | 0.09737 | 287.15 | 0.4
0.05585 | 280.15 | 0.09737 | 287.15 | 0.5
0.05585 | 280.15 | 0.09737 | 287.15 | 0.6
0.05585 | 280.15 | 0.09737 | 287.15 | 0.7
0.05585 | 280.15 | 0.09737 | 287.15 | 0.8
0.05585 | 280.15 | 0.09737 | 287.15 | 0.9
0.05585 | 280.15 | 0.09737 | 287.15 | 1
0.05585 | 280.15 | 0.09737 | 287.65 | 0.15
0.05585 | 280.15 | 0.09737 | 287.65 | 0.2
0.05585 | 280.15 | 0.09737 | 287.65 | 0.3
0.05585 | 280.15 | 0.09737 | 287.65 | 0.4
0.05585 | 280.15 | 0.09737 | 287.65 | 0.5
0.05585 | 280.15 | 0.09737 | 287.65 | 0.6
0.05585 | 280.15 | 0.09737 | 287.65 | 0.7
0.05585 | 280.15 | 0.09737 | 287.65 | 0.8
0.05585 | 280.15 | 0.09737 | 287.65 | 0.9
0.05585 | 280.15 | 0.09737 | 287.65 | 1
0.05585 | 280.15 | 0.09737 | 288.15 | 0.15
0.05585 | 280.15 | 0.09737 | 288.15 | 0.2
0.05585 | 280.15 | 0.09737 | 288.15 | 0.3
0.05585 | 280.15 | 0.09737 | 288.15 | 0.4
0.05585 | 280.15 | 0.09737 | 288.15 | 0.5
0.05585 | 280.15 | 0.09737 | 288.15 | 0.6
0.05585 | 280.15 | 0.09737 | 288.15 | 0.7
0.05585 | 280.15 | 0.09737 | 288.15 | 0.8
0.05585 | 280.15 | 0.09737 | 288.15 | 0.9
0.05585 | 280.15 | 0.09737 | 288.15 | 1
0.05585 | 280.15 | 0.09737 | 288.65 | 0.15
0.05585 | 280.15 | 0.09737 | 288.65 | 0.2
0.05585 | 280.15 | 0.09737 | 288.65 | 0.3
0.05585 | 280.15 | 0.09737 | 288.65 | 0.4
0.05585 | 280.15 | 0.09737 | 288.65 | 0.5
0.05585 | 280.15 | 0.09737 | 288.65 | 0.6
0.05585 | 280.15 | 0.09737 | 288.65 | 0.7
0.05585 | 280.15 | 0.09737 | 288.65 | 0.8
0.05585 | 280.15 | 0.09737 | 288.65 | 0.9
0.05585 | 280.15 | 0.09737 | 288.65 | 1
0.05585 | 280.15 | 0.09737 | 289.15 | 0.15
0.05585 | 280.15 | 0.09737 | 289.15 | 0.2
0.05585 | 280.15 | 0.09737 | 289.15 | 0.3
0.05585 | 280.15 | 0.09737 | 289.15 | 0.4
0.05585 | 280.15 | 0.09737 | 289.15 | 0.5
0.05585 | 280.15 | 0.09737 | 289.15 | 0.6
0.05585 | 280.15 | 0.09737 | 289.15 | 0.7
0.05585 | 280.15 | 0.09737 | 289.15 | 0.8
0.05585 | 280.15 | 0.09737 | 289.15 | 0.9
0.05585 | 280.15 | 0.09737 | 289.15 | 1
0.05585 | 280.15 | 0.09737 | 289.65 | 0.15
0.05585 | 280.15 | 0.09737 | 289.65 | 0.2
0.05585 | 280.15 | 0.09737 | 289.65 | 0.3
0.05585 | 280.15 | 0.09737 | 289.65 | 0.4
0.05585 | 280.15 | 0.09737 | 289.65 | 0.5
0.05585 | 280.15 | 0.09737 | 289.65 | 0.6
0.05585 | 280.15 | 0.09737 | 289.65 | 0.7
0.05585 | 280.15 | 0.09737 | 289.65 | 0.8
0.05585 | 280.15 | 0.09737 | 289.65 | 0.9
0.05585 | 280.15 | 0.09737 | 289.65 | 1
0.05585 | 280.15 | 0.09737 | 290.15 | 0.15
0.05585 | 280.15 | 0.09737 | 290.15 | 0.2
0.05585 | 280.15 | 0.09737 | 290.15 | 0.3
0.05585 | 280.15 | 0.09737 | 290.15 | 0.4
0.05585 | 280.15 | 0.09737 | 290.15 | 0.5
0.05585 | 280.15 | 0.09737 | 290.15 | 0.6
0.05585 | 280.15 | 0.09737 | 290.15 | 0.7
0.05585 | 280.15 | 0.09737 | 290.15 | 0.8
0.05585 | 280.15 | 0.09737 | 290.15 | 0.9
0.05585 | 280.15 | 0.09737 | 290.15 | 1
0.05585 | 280.15 | 0.09737 | 290.65 | 0.15
0.05585 | 280.15 | 0.09737 | 290.65 | 0.2
0.05585 | 280.15 | 0.09737 | 290.65 | 0.3
0.05585 | 280.15 | 0.09737 | 290.65 | 0.4
0.05585 | 280.15 | 0.09737 | 290.65 | 0.5
0.05585 | 280.15 | 0.09737 | 290.65 | 0.6
0.05585 | 280.15 | 0.09737 | 290.65 | 0.7
0.05585 | 280.15 | 0.09737 | 290.65 | 0.8
0.05585 | 280.15 | 0.09737 | 290.65 | 0.9
0.05585 | 280.15 | 0.09737 | 290.65 | 1
0.05585 | 280.15 | 0.09737 | 291.15 | 0.15
0.05585 | 280.15 | 0.09737 | 291.15 | 0.2
0.05585 | 280.15 | 0.09737 | 291.15 | 0.3
0.05585 | 280.15 | 0.09737 | 291.15 | 0.4
0.05585 | 280.15 | 0.09737 | 291.15 | 0.5
0.05585 | 280.15 | 0.09737 | 291.15 | 0.6
0.05585 | 280.15 | 0.09737 | 291.15 | 0.7
0.05585 | 280.15 | 0.09737 | 291.15 | 0.8
0.05585 | 280.15 | 0.09737 | 291.15 | 0.9
0.05585 | 280.15 | 0.09737 | 291.15 | 1
0.05585 | 280.15 | 0.09737 | 294.15 | 0.15
0.05585 | 280.15 | 0.09737 | 294.15 | 0.2
0.05585 | 280.15 | 0.09737 | 294.15 | 0.3
0.05585 | 280.15 | 0.09737 | 294.15 | 0.4
0.05585 | 280.15 | 0.09737 | 294.15 | 0.5
0.05585 | 280.15 | 0.09737 | 294.15 | 0.6
0.05585 | 280.15 | 0.09737 | 294.15 | 0.7
0.05585 | 280.15 | 0.09737 | 294.15 | 0.8
0.05585 | 280.15 | 0.09737 | 294.15 | 0.9
0.05585 | 280.15 | 0.09737 | 294.15 | 1
0.05585 | 280.15 | 0.09737 | 297.15 | 0.15
0.05585 | 280.15 | 0.09737 | 297.15 | 0.2
0.05585 | 280.15 | 0.09737 | 297.15 | 0.3
0.05585 | 280.15 | 0.09737 | 297.15 | 0.4
0.05585 | 280.15 | 0.09737 | 297.15 | 0.5
0.05585 | 280.15 | 0.09737 | 297.15 | 0.6
0.05585 | 280.15 | 0.09737 | 297.15 | 0.7
0.05585 | 280.15 | 0.09737 | 297.15 | 0.8
0.05585 | 280.15 | 0.09737 | 297.15 | 0.9
0.05585 | 280.15 | 0.09737 | 297.15 | 1
0.05585 | 280.15 | 0.09737 | 300.15 | 0.15
0.05585 | 280.15 | 0.09737 | 300.15 | 0.2
0.05585 | 280.15 | 0.09737 | 300.15 | 0.3
0.05585 | 280.15 | 0.09737 | 300.15 | 0.4
0.05585 | 280.15 | 0.09737 | 300.15 | 0.5
0.05585 | 280.15 | 0.09737 | 300.15 | 0.6
0.05585 | 280.15 | 0.09737 | 300.15 | 0.7
0.05585 | 280.15 | 0.09737 | 300.15 | 0.8
0.05585 | 280.15 | 0.09737 | 300.15 | 0.9
0.05585 | 280.15 | 0.09737 | 300.15 | 1
0.05585 | 280.15 | 0.09737 | 303.15 | 0.15
0.05585 | 280.15 | 0.09737 | 303.15 | 0.2
0.05585 | 280.15 | 0.09737 | 303.15 | 0.3
0.05585 | 280.15 | 0.09737 | 303.15 | 0.4
0.05585 | 280.15 | 0.09737 | 303.15 | 0.5
0.05585 | 280.15 | 0.09737 | 303.15 | 0.6
0.05585 | 280.15 | 0.09737 | 303.15 | 0.7
0.05585 | 280.15 | 0.09737 | 303.15 | 0.8
0.05585 | 280.15 | 0.09737 | 303.15 | 0.9
0.05585 | 280.15 | 0.09737 | 303.15 | 1
0.05585 | 280.15 | 0.115 | 283.65 | 0.15
0.05585 | 280.15 | 0.115 | 283.65 | 0.2
0.05585 | 280.15 | 0.115 | 283.65 | 0.3
0.05585 | 280.15 | 0.115 | 283.65 | 0.4
0.05585 | 280.15 | 0.115 | 283.65 | 0.5
0.05585 | 280.15 | 0.115 | 283.65 | 0.6
0.05585 | 280.15 | 0.115 | 283.65 | 0.7
0.05585 | 280.15 | 0.115 | 283.65 | 0.8
0.05585 | 280.15 | 0.115 | 283.65 | 0.9
0.05585 | 280.15 | 0.115 | 283.65 | 1
0.05585 | 280.15 | 0.115 | 284.15 | 0.15
0.05585 | 280.15 | 0.115 | 284.15 | 0.2
0.05585 | 280.15 | 0.115 | 284.15 | 0.3
0.05585 | 280.15 | 0.115 | 284.15 | 0.4
0.05585 | 280.15 | 0.115 | 284.15 | 0.5
0.05585 | 280.15 | 0.115 | 284.15 | 0.6
0.05585 | 280.15 | 0.115 | 284.15 | 0.7
0.05585 | 280.15 | 0.115 | 284.15 | 0.8
0.05585 | 280.15 | 0.115 | 284.15 | 0.9
0.05585 | 280.15 | 0.115 | 284.15 | 1
0.05585 | 280.15 | 0.115 | 284.65 | 0.15
0.05585 | 280.15 | 0.115 | 284.65 | 0.2
0.05585 | 280.15 | 0.115 | 284.65 | 0.3
0.05585 | 280.15 | 0.115 | 284.65 | 0.4
0.05585 | 280.15 | 0.115 | 284.65 | 0.5
0.05585 | 280.15 | 0.115 | 284.65 | 0.6
0.05585 | 280.15 | 0.115 | 284.65 | 0.7
0.05585 | 280.15 | 0.115 | 284.65 | 0.8
0.05585 | 280.15 | 0.115 | 284.65 | 0.9
0.05585 | 280.15 | 0.115 | 284.65 | 1
0.05585 | 280.15 | 0.115 | 285.15 | 0.15
0.05585 | 280.15 | 0.115 | 285.15 | 0.2
0.05585 | 280.15 | 0.115 | 285.15 | 0.3
0.05585 | 280.15 | 0.115 | 285.15 | 0.4
0.05585 | 280.15 | 0.115 | 285.15 | 0.5
0.05585 | 280.15 | 0.115 | 285.15 | 0.6
0.05585 | 280.15 | 0.115 | 285.15 | 0.7
0.05585 | 280.15 | 0.115 | 285.15 | 0.8
0.05585 | 280.15 | 0.115 | 285.15 | 0.9
0.05585 | 280.15 | 0.115 | 285.15 | 1
0.05585 | 280.15 | 0.115 | 285.65 | 0.15
0.05585 | 280.15 | 0.115 | 285.65 | 0.2
0.05585 | 280.15 | 0.115 | 285.65 | 0.3
0.05585 | 280.15 | 0.115 | 285.65 | 0.4
0.05585 | 280.15 | 0.115 | 285.65 | 0.5
0.05585 | 280.15 | 0.115 | 285.65 | 0.6
0.05585 | 280.15 | 0.115 | 285.65 | 0.7
0.05585 | 280.15 | 0.115 | 285.65 | 0.8
0.05585 | 280.15 | 0.115 | 285.65 | 0.9
0.05585 | 280.15 | 0.115 | 285.65 | 1
0.05585 | 280.15 | 0.115 | 286.15 | 0.15
0.05585 | 280.15 | 0.115 | 286.15 | 0.2
0.05585 | 280.15 | 0.115 | 286.15 | 0.3
0.05585 | 280.15 | 0.115 | 286.15 | 0.4
0.05585 | 280.15 | 0.115 | 286.15 | 0.5
0.05585 | 280.15 | 0.115 | 286.15 | 0.6
0.05585 | 280.15 | 0.115 | 286.15 | 0.7
0.05585 | 280.15 | 0.115 | 286.15 | 0.8
0.05585 | 280.15 | 0.115 | 286.15 | 0.9
0.05585 | 280.15 | 0.115 | 286.15 | 1
0.05585 | 280.15 | 0.115 | 286.65 | 0.15
0.05585 | 280.15 | 0.115 | 286.65 | 0.2
0.05585 | 280.15 | 0.115 | 286.65 | 0.3
0.05585 | 280.15 | 0.115 | 286.65 | 0.4
0.05585 | 280.15 | 0.115 | 286.65 | 0.5
0.05585 | 280.15 | 0.115 | 286.65 | 0.6
0.05585 | 280.15 | 0.115 | 286.65 | 0.7
0.05585 | 280.15 | 0.115 | 286.65 | 0.8
0.05585 | 280.15 | 0.115 | 286.65 | 0.9
0.05585 | 280.15 | 0.115 | 286.65 | 1
0.05585 | 280.15 | 0.115 | 287.15 | 0.15
0.05585 | 280.15 | 0.115 | 287.15 | 0.2
0.05585 | 280.15 | 0.115 | 287.15 | 0.3
0.05585 | 280.15 | 0.115 | 287.15 | 0.4
0.05585 | 280.15 | 0.115 | 287.15 | 0.5
0.05585 | 280.15 | 0.115 | 287.15 | 0.6
0.05585 | 280.15 | 0.115 | 287.15 | 0.7
0.05585 | 280.15 | 0.115 | 287.15 | 0.8
0.05585 | 280.15 | 0.115 | 287.15 | 0.9
0.05585 | 280.15 | 0.115 | 287.15 | 1
0.05585 | 280.15 | 0.115 | 287.65 | 0.15
0.05585 | 280.15 | 0.115 | 287.65 | 0.2
0.05585 | 280.15 | 0.115 | 287.65 | 0.3
0.05585 | 280.15 | 0.115 | 287.65 | 0.4
0.05585 | 280.15 | 0.115 | 287.65 | 0.5
0.05585 | 280.15 | 0.115 | 287.65 | 0.6
0.05585 | 280.15 | 0.115 | 287.65 | 0.7
0.05585 | 280.15 | 0.115 | 287.65 | 0.8
0.05585 | 280.15 | 0.115 | 287.65 | 0.9
0.05585 | 280.15 | 0.115 | 287.65 | 1
0.05585 | 280.15 | 0.115 | 288.15 | 0.15
0.05585 | 280.15 | 0.115 | 288.15 | 0.2
0.05585 | 280.15 | 0.115 | 288.15 | 0.3
0.05585 | 280.15 | 0.115 | 288.15 | 0.4
0.05585 | 280.15 | 0.115 | 288.15 | 0.5
0.05585 | 280.15 | 0.115 | 288.15 | 0.6
0.05585 | 280.15 | 0.115 | 288.15 | 0.7
0.05585 | 280.15 | 0.115 | 288.15 | 0.8
0.05585 | 280.15 | 0.115 | 288.15 | 0.9
0.05585 | 280.15 | 0.115 | 288.15 | 1
0.05585 | 280.15 | 0.115 | 288.65 | 0.15
0.05585 | 280.15 | 0.115 | 288.65 | 0.2
0.05585 | 280.15 | 0.115 | 288.65 | 0.3
0.05585 | 280.15 | 0.115 | 288.65 | 0.4
0.05585 | 280.15 | 0.115 | 288.65 | 0.5
0.05585 | 280.15 | 0.115 | 288.65 | 0.6
0.05585 | 280.15 | 0.115 | 288.65 | 0.7
0.05585 | 280.15 | 0.115 | 288.65 | 0.8
0.05585 | 280.15 | 0.115 | 288.65 | 0.9
0.05585 | 280.15 | 0.115 | 288.65 | 1
0.05585 | 280.15 | 0.115 | 289.15 | 0.15
0.05585 | 280.15 | 0.115 | 289.15 | 0.2
0.05585 | 280.15 | 0.115 | 289.15 | 0.3
0.05585 | 280.15 | 0.115 | 289.15 | 0.4
0.05585 | 280.15 | 0.115 | 289.15 | 0.5
0.05585 | 280.15 | 0.115 | 289.15 | 0.6
0.05585 | 280.15 | 0.115 | 289.15 | 0.7
0.05585 | 280.15 | 0.115 | 289.15 | 0.8
0.05585 | 280.15 | 0.115 | 289.15 | 0.9
0.05585 | 280.15 | 0.115 | 289.15 | 1
0.05585 | 280.15 | 0.115 | 289.65 | 0.15
0.05585 | 280.15 | 0.115 | 289.65 | 0.2
0.05585 | 280.15 | 0.115 | 289.65 | 0.3
0.05585 | 280.15 | 0.115 | 289.65 | 0.4
0.05585 | 280.15 | 0.115 | 289.65 | 0.5
0.05585 | 280.15 | 0.115 | 289.65 | 0.6
0.05585 | 280.15 | 0.115 | 289.65 | 0.7
0.05585 | 280.15 | 0.115 | 289.65 | 0.8
0.05585 | 280.15 | 0.115 | 289.65 | 0.9
0.05585 | 280.15 | 0.115 | 289.65 | 1
0.05585 | 280.15 | 0.115 | 290.15 | 0.15
0.05585 | 280.15 | 0.115 | 290.15 | 0.2
0.05585 | 280.15 | 0.115 | 290.15 | 0.3
0.05585 | 280.15 | 0.115 | 290.15 | 0.4
0.05585 | 280.15 | 0.115 | 290.15 | 0.5
0.05585 | 280.15 | 0.115 | 290.15 | 0.6
0.05585 | 280.15 | 0.115 | 290.15 | 0.7
0.05585 | 280.15 | 0.115 | 290.15 | 0.8
0.05585 | 280.15 | 0.115 | 290.15 | 0.9
0.05585 | 280.15 | 0.115 | 290.15 | 1
0.05585 | 280.15 | 0.115 | 290.65 | 0.15
0.05585 | 280.15 | 0.115 | 290.65 | 0.2
0.05585 | 280.15 | 0.115 | 290.65 | 0.3
0.05585 | 280.15 | 0.115 | 290.65 | 0.4
0.05585 | 280.15 | 0.115 | 290.65 | 0.5
0.05585 | 280.15 | 0.115 | 290.65 | 0.6
0.05585 | 280.15 | 0.115 | 290.65 | 0.7
0.05585 | 280.15 | 0.115 | 290.65 | 0.8
0.05585 | 280.15 | 0.115 | 290.65 | 0.9
0.05585 | 280.15 | 0.115 | 290.65 | 1
0.05585 | 280.15 | 0.115 | 291.15 | 0.15
0.05585 | 280.15 | 0.115 | 291.15 | 0.2
0.05585 | 280.15 | 0.115 | 291.15 | 0.3
0.05585 | 280.15 | 0.115 | 291.15 | 0.4
0.05585 | 280.15 | 0.115 | 291.15 | 0.5
0.05585 | 280.15 | 0.115 | 291.15 | 0.6
0.05585 | 280.15 | 0.115 | 291.15 | 0.7
0.05585 | 280.15 | 0.115 | 291.15 | 0.8
0.05585 | 280.15 | 0.115 | 291.15 | 0.9
0.05585 | 280.15 | 0.115 | 291.15 | 1
0.05585 | 280.15 | 0.115 | 294.15 | 0.15
0.05585 | 280.15 | 0.115 | 294.15 | 0.2
0.05585 | 280.15 | 0.115 | 294.15 | 0.3
0.05585 | 280.15 | 0.115 | 294.15 | 0.4
0.05585 | 280.15 | 0.115 | 294.15 | 0.5
0.05585 | 280.15 | 0.115 | 294.15 | 0.6
0.05585 | 280.15 | 0.115 | 294.15 | 0.7
0.05585 | 280.15 | 0.115 | 294.15 | 0.8
0.05585 | 280.15 | 0.115 | 294.15 | 0.9
0.05585 | 280.15 | 0.115 | 294.15 | 1
0.05585 | 280.15 | 0.115 | 297.15 | 0.15
0.05585 | 280.15 | 0.115 | 297.15 | 0.2
0.05585 | 280.15 | 0.115 | 297.15 | 0.3
0.05585 | 280.15 | 0.115 | 297.15 | 0.4
0.05585 | 280.15 | 0.115 | 297.15 | 0.5
0.05585 | 280.15 | 0.115 | 297.15 | 0.6
0.05585 | 280.15 | 0.115 | 297.15 | 0.7
0.05585 | 280.15 | 0.115 | 297.15 | 0.8
0.05585 | 280.15 | 0.115 | 297.15 | 0.9
0.05585 | 280.15 | 0.115 | 297.15 | 1
0.05585 | 280.15 | 0.115 | 300.15 | 0.15
0.05585 | 280.15 | 0.115 | 300.15 | 0.2
0.05585 | 280.15 | 0.115 | 300.15 | 0.3
0.05585 | 280.15 | 0.115 | 300.15 | 0.4
0.05585 | 280.15 | 0.115 | 300.15 | 0.5
0.05585 | 280.15 | 0.115 | 300.15 | 0.6
0.05585 | 280.15 | 0.115 | 300.15 | 0.7
0.05585 | 280.15 | 0.115 | 300.15 | 0.8
0.05585 | 280.15 | 0.115 | 300.15 | 0.9
0.05585 | 280.15 | 0.115 | 300.15 | 1
0.05585 | 280.15 | 0.115 | 303.15 | 0.15
0.05585 | 280.15 | 0.115 | 303.15 | 0.2
0.05585 | 280.15 | 0.115 | 303.15 | 0.3
0.05585 | 280.15 | 0.115 | 303.15 | 0.4
0.05585 | 280.15 | 0.115 | 303.15 | 0.5
0.05585 | 280.15 | 0.115 | 303.15 | 0.6
0.05585 | 280.15 | 0.115 | 303.15 | 0.7
0.05585 | 280.15 | 0.115 | 303.15 | 0.8
0.05585 | 280.15 | 0.115 | 303.15 | 0.9
0.05585 | 280.15 | 0.115 | 303.15 | 1
0.05585 | 282.15 | 0.00115 | 283.65 | 0.15
0.05585 | 282.15 | 0.00115 | 283.65 | 0.2
0.05585 | 282.15 | 0.00115 | 283.65 | 0.3
0.05585 | 282.15 | 0.00115 | 283.65 | 0.4
0.05585 | 282.15 | 0.00115 | 283.65 | 0.5
0.05585 | 282.15 | 0.00115 | 283.65 | 0.6
0.05585 | 282.15 | 0.00115 | 283.65 | 0.7
0.05585 | 282.15 | 0.00115 | 283.65 | 0.8
0.05585 | 282.15 | 0.00115 | 283.65 | 0.9
0.05585 | 282.15 | 0.00115 | 283.65 | 1
0.05585 | 282.15 | 0.00115 | 284.15 | 0.15
0.05585 | 282.15 | 0.00115 | 284.15 | 0.2
0.05585 | 282.15 | 0.00115 | 284.15 | 0.3
0.05585 | 282.15 | 0.00115 | 284.15 | 0.4
0.05585 | 282.15 | 0.00115 | 284.15 | 0.5
0.05585 | 282.15 | 0.00115 | 284.15 | 0.6
0.05585 | 282.15 | 0.00115 | 284.15 | 0.7
0.05585 | 282.15 | 0.00115 | 284.15 | 0.8
0.05585 | 282.15 | 0.00115 | 284.15 | 0.9
0.05585 | 282.15 | 0.00115 | 284.15 | 1
0.05585 | 282.15 | 0.00115 | 284.65 | 0.15
0.05585 | 282.15 | 0.00115 | 284.65 | 0.2
0.05585 | 282.15 | 0.00115 | 284.65 | 0.3
0.05585 | 282.15 | 0.00115 | 284.65 | 0.4
0.05585 | 282.15 | 0.00115 | 284.65 | 0.5
0.05585 | 282.15 | 0.00115 | 284.65 | 0.6
0.05585 | 282.15 | 0.00115 | 284.65 | 0.7
0.05585 | 282.15 | 0.00115 | 284.65 | 0.8
0.05585 | 282.15 | 0.00115 | 284.65 | 0.9
0.05585 | 282.15 | 0.00115 | 284.65 | 1
0.05585 | 282.15 | 0.00115 | 285.15 | 0.15
0.05585 | 282.15 | 0.00115 | 285.15 | 0.2
0.05585 | 282.15 | 0.00115 | 285.15 | 0.3
0.05585 | 282.15 | 0.00115 | 285.15 | 0.4
0.05585 | 282.15 | 0.00115 | 285.15 | 0.5
0.05585 | 282.15 | 0.00115 | 285.15 | 0.6
0.05585 | 282.15 | 0.00115 | 285.15 | 0.7
0.05585 | 282.15 | 0.00115 | 285.15 | 0.8
0.05585 | 282.15 | 0.00115 | 285.15 | 0.9
0.05585 | 282.15 | 0.00115 | 285.15 | 1
0.05585 | 282.15 | 0.00115 | 285.65 | 0.15
0.05585 | 282.15 | 0.00115 | 285.65 | 0.2
0.05585 | 282.15 | 0.00115 | 285.65 | 0.3
0.05585 | 282.15 | 0.00115 | 285.65 | 0.4
0.05585 | 282.15 | 0.00115 | 285.65 | 0.5
0.05585 | 282.15 | 0.00115 | 285.65 | 0.6
0.05585 | 282.15 | 0.00115 | 285.65 | 0.7
0.05585 | 282.15 | 0.00115 | 285.65 | 0.8
0.05585 | 282.15 | 0.00115 | 285.65 | 0.9
0.05585 | 282.15 | 0.00115 | 285.65 | 1
0.05585 | 282.15 | 0.00115 | 286.15 | 0.15
0.05585 | 282.15 | 0.00115 | 286.15 | 0.2
0.05585 | 282.15 | 0.00115 | 286.15 | 0.3
0.05585 | 282.15 | 0.00115 | 286.15 | 0.4
0.05585 | 282.15 | 0.00115 | 286.15 | 0.5
0.05585 | 282.15 | 0.00115 | 286.15 | 0.6
0.05585 | 282.15 | 0.00115 | 286.15 | 0.7
0.05585 | 282.15 | 0.00115 | 286.15 | 0.8
0.05585 | 282.15 | 0.00115 | 286.15 | 0.9
0.05585 | 282.15 | 0.00115 | 286.15 | 1
0.05585 | 282.15 | 0.00115 | 286.65 | 0.15
0.05585 | 282.15 | 0.00115 | 286.65 | 0.2
0.05585 | 282.15 | 0.00115 | 286.65 | 0.3
0.05585 | 282.15 | 0.00115 | 286.65 | 0.4
0.05585 | 282.15 | 0.00115 | 286.65 | 0.5
0.05585 | 282.15 | 0.00115 | 286.65 | 0.6
0.05585 | 282.15 | 0.00115 | 286.65 | 0.7
0.05585 | 282.15 | 0.00115 | 286.65 | 0.8
0.05585 | 282.15 | 0.00115 | 286.65 | 0.9
0.05585 | 282.15 | 0.00115 | 286.65 | 1
0.05585 | 282.15 | 0.00115 | 287.15 | 0.15
0.05585 | 282.15 | 0.00115 | 287.15 | 0.2
0.05585 | 282.15 | 0.00115 | 287.15 | 0.3
0.05585 | 282.15 | 0.00115 | 287.15 | 0.4
0.05585 | 282.15 | 0.00115 | 287.15 | 0.5
0.05585 | 282.15 | 0.00115 | 287.15 | 0.6
0.05585 | 282.15 | 0.00115 | 287.15 | 0.7
0.05585 | 282.15 | 0.00115 | 287.15 | 0.8
0.05585 | 282.15 | 0.00115 | 287.15 | 0.9
0.05585 | 282.15 | 0.00115 | 287.15 | 1
0.05585 | 282.15 | 0.00115 | 287.65 | 0.15
0.05585 | 282.15 | 0.00115 | 287.65 | 0.2
0.05585 | 282.15 | 0.00115 | 287.65 | 0.3
0.05585 | 282.15 | 0.00115 | 287.65 | 0.4
0.05585 | 282.15 | 0.00115 | 287.65 | 0.5
0.05585 | 282.15 | 0.00115 | 287.65 | 0.6
0.05585 | 282.15 | 0.00115 | 287.65 | 0.7
0.05585 | 282.15 | 0.00115 | 287.65 | 0.8
0.05585 | 282.15 | 0.00115 | 287.65 | 0.9
0.05585 | 282.15 | 0.00115 | 287.65 | 1
0.05585 | 282.15 | 0.00115 | 288.15 | 0.15
0.05585 | 282.15 | 0.00115 | 288.15 | 0.2
0.05585 | 282.15 | 0.00115 | 288.15 | 0.3
0.05585 | 282.15 | 0.00115 | 288.15 | 0.4
0.05585 | 282.15 | 0.00115 | 288.15 | 0.5
0.05585 | 282.15 | 0.00115 | 288.15 | 0.6
0.05585 | 282.15 | 0.00115 | 288.15 | 0.7
0.05585 | 282.15 | 0.00115 | 288.15 | 0.8
0.05585 | 282.15 | 0.00115 | 288.15 | 0.9
0.05585 | 282.15 | 0.00115 | 288.15 | 1
0.05585 | 282.15 | 0.00115 | 288.65 | 0.15
0.05585 | 282.15 | 0.00115 | 288.65 | 0.2
0.05585 | 282.15 | 0.00115 | 288.65 | 0.3
0.05585 | 282.15 | 0.00115 | 288.65 | 0.4
0.05585 | 282.15 | 0.00115 | 288.65 | 0.5
0.05585 | 282.15 | 0.00115 | 288.65 | 0.6
0.05585 | 282.15 | 0.00115 | 288.65 | 0.7
0.05585 | 282.15 | 0.00115 | 288.65 | 0.8
0.05585 | 282.15 | 0.00115 | 288.65 | 0.9
0.05585 | 282.15 | 0.00115 | 288.65 | 1
0.05585 | 282.15 | 0.00115 | 289.15 | 0.15
0.05585 | 282.15 | 0.00115 | 289.15 | 0.2
0.05585 | 282.15 | 0.00115 | 289.15 | 0.3
0.05585 | 282.15 | 0.00115 | 289.15 | 0.4
0.05585 | 282.15 | 0.00115 | 289.15 | 0.5
0.05585 | 282.15 | 0.00115 | 289.15 | 0.6
0.05585 | 282.15 | 0.00115 | 289.15 | 0.7
0.05585 | 282.15 | 0.00115 | 289.15 | 0.8
0.05585 | 282.15 | 0.00115 | 289.15 | 0.9
0.05585 | 282.15 | 0.00115 | 289.15 | 1
0.05585 | 282.15 | 0.00115 | 289.65 | 0.15
0.05585 | 282.15 | 0.00115 | 289.65 | 0.2
0.05585 | 282.15 | 0.00115 | 289.65 | 0.3
0.05585 | 282.15 | 0.00115 | 289.65 | 0.4
0.05585 | 282.15 | 0.00115 | 289.65 | 0.5
0.05585 | 282.15 | 0.00115 | 289.65 | 0.6
0.05585 | 282.15 | 0.00115 | 289.65 | 0.7
0.05585 | 282.15 | 0.00115 | 289.65 | 0.8
0.05585 | 282.15 | 0.00115 | 289.65 | 0.9
0.05585 | 282.15 | 0.00115 | 289.65 | 1
0.05585 | 282.15 | 0.00115 | 290.15 | 0.15
0.05585 | 282.15 | 0.00115 | 290.15 | 0.2
0.05585 | 282.15 | 0.00115 | 290.15 | 0.3
0.05585 | 282.15 | 0.00115 | 290.15 | 0.4
0.05585 | 282.15 | 0.00115 | 290.15 | 0.5
0.05585 | 282.15 | 0.00115 | 290.15 | 0.6
0.05585 | 282.15 | 0.00115 | 290.15 | 0.7
0.05585 | 282.15 | 0.00115 | 290.15 | 0.8
0.05585 | 282.15 | 0.00115 | 290.15 | 0.9
0.05585 | 282.15 | 0.00115 | 290.15 | 1
0.05585 | 282.15 | 0.00115 | 290.65 | 0.15
0.05585 | 282.15 | 0.00115 | 290.65 | 0.2
0.05585 | 282.15 | 0.00115 | 290.65 | 0.3
0.05585 | 282.15 | 0.00115 | 290.65 | 0.4
0.05585 | 282.15 | 0.00115 | 290.65 | 0.5
0.05585 | 282.15 | 0.00115 | 290.65 | 0.6
0.05585 | 282.15 | 0.00115 | 290.65 | 0.7
0.05585 | 282.15 | 0.00115 | 290.65 | 0.8
0.05585 | 282.15 | 0.00115 | 290.65 | 0.9
0.05585 | 282.15 | 0.00115 | 290.65 | 1
0.05585 | 282.15 | 0.00115 | 291.15 | 0.15
0.05585 | 282.15 | 0.00115 | 291.15 | 0.2
0.05585 | 282.15 | 0.00115 | 291.15 | 0.3
0.05585 | 282.15 | 0.00115 | 291.15 | 0.4
0.05585 | 282.15 | 0.00115 | 291.15 | 0.5
0.05585 | 282.15 | 0.00115 | 291.15 | 0.6
0.05585 | 282.15 | 0.00115 | 291.15 | 0.7
0.05585 | 282.15 | 0.00115 | 291.15 | 0.8
0.05585 | 282.15 | 0.00115 | 291.15 | 0.9
0.05585 | 282.15 | 0.00115 | 291.15 | 1
0.05585 | 282.15 | 0.00115 | 294.15 | 0.15
0.05585 | 282.15 | 0.00115 | 294.15 | 0.2
0.05585 | 282.15 | 0.00115 | 294.15 | 0.3
0.05585 | 282.15 | 0.00115 | 294.15 | 0.4
0.05585 | 282.15 | 0.00115 | 294.15 | 0.5
0.05585 | 282.15 | 0.00115 | 294.15 | 0.6
0.05585 | 282.15 | 0.00115 | 294.15 | 0.7
0.05585 | 282.15 | 0.00115 | 294.15 | 0.8
0.05585 | 282.15 | 0.00115 | 294.15 | 0.9
0.05585 | 282.15 | 0.00115 | 294.15 | 1
0.05585 | 282.15 | 0.00115 | 297.15 | 0.15
0.05585 | 282.15 | 0.00115 | 297.15 | 0.2
0.05585 | 282.15 | 0.00115 | 297.15 | 0.3
0.05585 | 282.15 | 0.00115 | 297.15 | 0.4
0.05585 | 282.15 | 0.00115 | 297.15 | 0.5
0.05585 | 282.15 | 0.00115 | 297.15 | 0.6
0.05585 | 282.15 | 0.00115 | 297.15 | 0.7
0.05585 | 282.15 | 0.00115 | 297.15 | 0.8
0.05585 | 282.15 | 0.00115 | 297.15 | 0.9
0.05585 | 282.15 | 0.00115 | 297.15 | 1
0.05585 | 282.15 | 0.00115 | 300.15 | 0.15
0.05585 | 282.15 | 0.00115 | 300.15 | 0.2
0.05585 | 282.15 | 0.00115 | 300.15 | 0.3
0.05585 | 282.15 | 0.00115 | 300.15 | 0.4
0.05585 | 282.15 | 0.00115 | 300.15 | 0.5
0.05585 | 282.15 | 0.00115 | 300.15 | 0.6
0.05585 | 282.15 | 0.00115 | 300.15 | 0.7
0.05585 | 282.15 | 0.00115 | 300.15 | 0.8
0.05585 | 282.15 | 0.00115 | 300.15 | 0.9
0.05585 | 282.15 | 0.00115 | 300.15 | 1
0.05585 | 282.15 | 0.00115 | 303.15 | 0.15
0.05585 | 282.15 | 0.00115 | 303.15 | 0.2
0.05585 | 282.15 | 0.00115 | 303.15 | 0.3
0.05585 | 282.15 | 0.00115 | 303.15 | 0.4
0.05585 | 282.15 | 0.00115 | 303.15 | 0.5
0.05585 | 282.15 | 0.00115 | 303.15 | 0.6
0.05585 | 282.15 | 0.00115 | 303.15 | 0.7
0.05585 | 282.15 | 0.00115 | 303.15 | 0.8
0.05585 | 282.15 | 0.00115 | 303.15 | 0.9
0.05585 | 282.15 | 0.00115 | 303.15 | 1
0.05585 | 282.15 | 0.077 | 283.65 | 0.15
0.05585 | 282.15 | 0.077 | 283.65 | 0.2
0.05585 | 282.15 | 0.077 | 283.65 | 0.3
0.05585 | 282.15 | 0.077 | 283.65 | 0.4
0.05585 | 282.15 | 0.077 | 283.65 | 0.5
0.05585 | 282.15 | 0.077 | 283.65 | 0.6
0.05585 | 282.15 | 0.077 | 283.65 | 0.7
0.05585 | 282.15 | 0.077 | 283.65 | 0.8
0.05585 | 282.15 | 0.077 | 283.65 | 0.9
0.05585 | 282.15 | 0.077 | 283.65 | 1
0.05585 | 282.15 | 0.077 | 284.15 | 0.15
0.05585 | 282.15 | 0.077 | 284.15 | 0.2
0.05585 | 282.15 | 0.077 | 284.15 | 0.3
0.05585 | 282.15 | 0.077 | 284.15 | 0.4
0.05585 | 282.15 | 0.077 | 284.15 | 0.5
0.05585 | 282.15 | 0.077 | 284.15 | 0.6
0.05585 | 282.15 | 0.077 | 284.15 | 0.7
0.05585 | 282.15 | 0.077 | 284.15 | 0.8
0.05585 | 282.15 | 0.077 | 284.15 | 0.9
0.05585 | 282.15 | 0.077 | 284.15 | 1
0.05585 | 282.15 | 0.077 | 284.65 | 0.15
0.05585 | 282.15 | 0.077 | 284.65 | 0.2
0.05585 | 282.15 | 0.077 | 284.65 | 0.3
0.05585 | 282.15 | 0.077 | 284.65 | 0.4
0.05585 | 282.15 | 0.077 | 284.65 | 0.5
0.05585 | 282.15 | 0.077 | 284.65 | 0.6
0.05585 | 282.15 | 0.077 | 284.65 | 0.7
0.05585 | 282.15 | 0.077 | 284.65 | 0.8
0.05585 | 282.15 | 0.077 | 284.65 | 0.9
0.05585 | 282.15 | 0.077 | 284.65 | 1
0.05585 | 282.15 | 0.077 | 285.15 | 0.15
0.05585 | 282.15 | 0.077 | 285.15 | 0.2
0.05585 | 282.15 | 0.077 | 285.15 | 0.3
0.05585 | 282.15 | 0.077 | 285.15 | 0.4
0.05585 | 282.15 | 0.077 | 285.15 | 0.5
0.05585 | 282.15 | 0.077 | 285.15 | 0.6
0.05585 | 282.15 | 0.077 | 285.15 | 0.7
0.05585 | 282.15 | 0.077 | 285.15 | 0.8
0.05585 | 282.15 | 0.077 | 285.15 | 0.9
0.05585 | 282.15 | 0.077 | 285.15 | 1
0.05585 | 282.15 | 0.077 | 285.65 | 0.15
0.05585 | 282.15 | 0.077 | 285.65 | 0.2
0.05585 | 282.15 | 0.077 | 285.65 | 0.3
0.05585 | 282.15 | 0.077 | 285.65 | 0.4
0.05585 | 282.15 | 0.077 | 285.65 | 0.5
0.05585 | 282.15 | 0.077 | 285.65 | 0.6
0.05585 | 282.15 | 0.077 | 285.65 | 0.7
0.05585 | 282.15 | 0.077 | 285.65 | 0.8
0.05585 | 282.15 | 0.077 | 285.65 | 0.9
0.05585 | 282.15 | 0.077 | 285.65 | 1
0.05585 | 282.15 | 0.077 | 286.15 | 0.15
0.05585 | 282.15 | 0.077 | 286.15 | 0.2
0.05585 | 282.15 | 0.077 | 286.15 | 0.3
0.05585 | 282.15 | 0.077 | 286.15 | 0.4
0.05585 | 282.15 | 0.077 | 286.15 | 0.5
0.05585 | 282.15 | 0.077 | 286.15 | 0.6
0.05585 | 282.15 | 0.077 | 286.15 | 0.7
0.05585 | 282.15 | 0.077 | 286.15 | 0.8
0.05585 | 282.15 | 0.077 | 286.15 | 0.9
0.05585 | 282.15 | 0.077 | 286.15 | 1
0.05585 | 282.15 | 0.077 | 286.65 | 0.15
0.05585 | 282.15 | 0.077 | 286.65 | 0.2
0.05585 | 282.15 | 0.077 | 286.65 | 0.3
0.05585 | 282.15 | 0.077 | 286.65 | 0.4
0.05585 | 282.15 | 0.077 | 286.65 | 0.5
0.05585 | 282.15 | 0.077 | 286.65 | 0.6
0.05585 | 282.15 | 0.077 | 286.65 | 0.7
0.05585 | 282.15 | 0.077 | 286.65 | 0.8
0.05585 | 282.15 | 0.077 | 286.65 | 0.9
0.05585 | 282.15 | 0.077 | 286.65 | 1
0.05585 | 282.15 | 0.077 | 287.15 | 0.15
0.05585 | 282.15 | 0.077 | 287.15 | 0.2
0.05585 | 282.15 | 0.077 | 287.15 | 0.3
0.05585 | 282.15 | 0.077 | 287.15 | 0.4
0.05585 | 282.15 | 0.077 | 287.15 | 0.5
0.05585 | 282.15 | 0.077 | 287.15 | 0.6
0.05585 | 282.15 | 0.077 | 287.15 | 0.7
0.05585 | 282.15 | 0.077 | 287.15 | 0.8
0.05585 | 282.15 | 0.077 | 287.15 | 0.9
0.05585 | 282.15 | 0.077 | 287.15 | 1
0.05585 | 282.15 | 0.077 | 287.65 | 0.15
0.05585 | 282.15 | 0.077 | 287.65 | 0.2
0.05585 | 282.15 | 0.077 | 287.65 | 0.3
0.05585 | 282.15 | 0.077 | 287.65 | 0.4
0.05585 | 282.15 | 0.077 | 287.65 | 0.5
0.05585 | 282.15 | 0.077 | 287.65 | 0.6
0.05585 | 282.15 | 0.077 | 287.65 | 0.7
0.05585 | 282.15 | 0.077 | 287.65 | 0.8
0.05585 | 282.15 | 0.077 | 287.65 | 0.9
0.05585 | 282.15 | 0.077 | 287.65 | 1
0.05585 | 282.15 | 0.077 | 288.15 | 0.15
0.05585 | 282.15 | 0.077 | 288.15 | 0.2
0.05585 | 282.15 | 0.077 | 288.15 | 0.3
0.05585 | 282.15 | 0.077 | 288.15 | 0.4
0.05585 | 282.15 | 0.077 | 288.15 | 0.5
0.05585 | 282.15 | 0.077 | 288.15 | 0.6
0.05585 | 282.15 | 0.077 | 288.15 | 0.7
0.05585 | 282.15 | 0.077 | 288.15 | 0.8
0.05585 | 282.15 | 0.077 | 288.15 | 0.9
0.05585 | 282.15 | 0.077 | 288.15 | 1
0.05585 | 282.15 | 0.077 | 288.65 | 0.15
0.05585 | 282.15 | 0.077 | 288.65 | 0.2
0.05585 | 282.15 | 0.077 | 288.65 | 0.3
0.05585 | 282.15 | 0.077 | 288.65 | 0.4
0.05585 | 282.15 | 0.077 | 288.65 | 0.5
0.05585 | 282.15 | 0.077 | 288.65 | 0.6
0.05585 | 282.15 | 0.077 | 288.65 | 0.7
0.05585 | 282.15 | 0.077 | 288.65 | 0.8
0.05585 | 282.15 | 0.077 | 288.65 | 0.9
0.05585 | 282.15 | 0.077 | 288.65 | 1
0.05585 | 282.15 | 0.077 | 289.15 | 0.15
0.05585 | 282.15 | 0.077 | 289.15 | 0.2
0.05585 | 282.15 | 0.077 | 289.15 | 0.3
0.05585 | 282.15 | 0.077 | 289.15 | 0.4
0.05585 | 282.15 | 0.077 | 289.15 | 0.5
0.05585 | 282.15 | 0.077 | 289.15 | 0.6
0.05585 | 282.15 | 0.077 | 289.15 | 0.7
0.05585 | 282.15 | 0.077 | 289.15 | 0.8
0.05585 | 282.15 | 0.077 | 289.15 | 0.9
0.05585 | 282.15 | 0.077 | 289.15 | 1
0.05585 | 282.15 | 0.077 | 289.65 | 0.15
0.05585 | 282.15 | 0.077 | 289.65 | 0.2
0.05585 | 282.15 | 0.077 | 289.65 | 0.3
0.05585 | 282.15 | 0.077 | 289.65 | 0.4
0.05585 | 282.15 | 0.077 | 289.65 | 0.5
0.05585 | 282.15 | 0.077 | 289.65 | 0.6
0.05585 | 282.15 | 0.077 | 289.65 | 0.7
0.05585 | 282.15 | 0.077 | 289.65 | 0.8
0.05585 | 282.15 | 0.077 | 289.65 | 0.9
0.05585 | 282.15 | 0.077 | 289.65 | 1
0.05585 | 282.15 | 0.077 | 290.15 | 0.15
0.05585 | 282.15 | 0.077 | 290.15 | 0.2
0.05585 | 282.15 | 0.077 | 290.15 | 0.3
0.05585 | 282.15 | 0.077 | 290.15 | 0.4
0.05585 | 282.15 | 0.077 | 290.15 | 0.5
0.05585 | 282.15 | 0.077 | 290.15 | 0.6
0.05585 | 282.15 | 0.077 | 290.15 | 0.7
0.05585 | 282.15 | 0.077 | 290.15 | 0.8
0.05585 | 282.15 | 0.077 | 290.15 | 0.9
0.05585 | 282.15 | 0.077 | 290.15 | 1
0.05585 | 282.15 | 0.077 | 290.65 | 0.15
0.05585 | 282.15 | 0.077 | 290.65 | 0.2
0.05585 | 282.15 | 0.077 | 290.65 | 0.3
0.05585 | 282.15 | 0.077 | 290.65 | 0.4
0.05585 | 282.15 | 0.077 | 290.65 | 0.5
0.05585 | 282.15 | 0.077 | 290.65 | 0.6
0.05585 | 282.15 | 0.077 | 290.65 | 0.7
0.05585 | 282.15 | 0.077 | 290.65 | 0.8
0.05585 | 282.15 | 0.077 | 290.65 | 0.9
0.05585 | 282.15 | 0.077 | 290.65 | 1
0.05585 | 282.15 | 0.077 | 291.15 | 0.15
0.05585 | 282.15 | 0.077 | 291.15 | 0.2
0.05585 | 282.15 | 0.077 | 291.15 | 0.3
0.05585 | 282.15 | 0.077 | 291.15 | 0.4
0.05585 | 282.15 | 0.077 | 291.15 | 0.5
0.05585 | 282.15 | 0.077 | 291.15 | 0.6
0.05585 | 282.15 | 0.077 | 291.15 | 0.7
0.05585 | 282.15 | 0.077 | 291.15 | 0.8
0.05585 | 282.15 | 0.077 | 291.15 | 0.9
0.05585 | 282.15 | 0.077 | 291.15 | 1
0.05585 | 282.15 | 0.077 | 294.15 | 0.15
0.05585 | 282.15 | 0.077 | 294.15 | 0.2
0.05585 | 282.15 | 0.077 | 294.15 | 0.3
0.05585 | 282.15 | 0.077 | 294.15 | 0.4
0.05585 | 282.15 | 0.077 | 294.15 | 0.5
0.05585 | 282.15 | 0.077 | 294.15 | 0.6
0.05585 | 282.15 | 0.077 | 294.15 | 0.7
0.05585 | 282.15 | 0.077 | 294.15 | 0.8
0.05585 | 282.15 | 0.077 | 294.15 | 0.9
0.05585 | 282.15 | 0.077 | 294.15 | 1
0.05585 | 282.15 | 0.077 | 297.15 | 0.15
0.05585 | 282.15 | 0.077 | 297.15 | 0.2
0.05585 | 282.15 | 0.077 | 297.15 | 0.3
0.05585 | 282.15 | 0.077 | 297.15 | 0.4
0.05585 | 282.15 | 0.077 | 297.15 | 0.5
0.05585 | 282.15 | 0.077 | 297.15 | 0.6
0.05585 | 282.15 | 0.077 | 297.15 | 0.7
0.05585 | 282.15 | 0.077 | 297.15 | 0.8
0.05585 | 282.15 | 0.077 | 297.15 | 0.9
0.05585 | 282.15 | 0.077 | 297.15 | 1
0.05585 | 282.15 | 0.077 | 300.15 | 0.15
0.05585 | 282.15 | 0.077 | 300.15 | 0.2
0.05585 | 282.15 | 0.077 | 300.15 | 0.3
0.05585 | 282.15 | 0.077 | 300.15 | 0.4
0.05585 | 282.15 | 0.077 | 300.15 | 0.5
0.05585 | 282.15 | 0.077 | 300.15 | 0.6
0.05585 | 282.15 | 0.077 | 300.15 | 0.7
0.05585 | 282.15 | 0.077 | 300.15 | 0.8
0.05585 | 282.15 | 0.077 | 300.15 | 0.9
0.05585 | 282.15 | 0.077 | 300.15 | 1
0.05585 | 282.15 | 0.077 | 303.15 | 0.15
0.05585 | 282.15 | 0.077 | 303.15 | 0.2
0.05585 | 282.15 | 0.077 | 303.15 | 0.3
0.05585 | 282.15 | 0.077 | 303.15 | 0.4
0.05585 | 282.15 | 0.077 | 303.15 | 0.5
0.05585 | 282.15 | 0.077 | 303.15 | 0.6
0.05585 | 282.15 | 0.077 | 303.15 | 0.7
0.05585 | 282.15 | 0.077 | 303.15 | 0.8
0.05585 | 282.15 | 0.077 | 303.15 | 0.9
0.05585 | 282.15 | 0.077 | 303.15 | 1
0.05585 | 282.15 | 0.09437 | 283.65 | 0.15
0.05585 | 282.15 | 0.09437 | 283.65 | 0.2
0.05585 | 282.15 | 0.09437 | 283.65 | 0.3
0.05585 | 282.15 | 0.09437 | 283.65 | 0.4
0.05585 | 282.15 | 0.09437 | 283.65 | 0.5
0.05585 | 282.15 | 0.09437 | 283.65 | 0.6
0.05585 | 282.15 | 0.09437 | 283.65 | 0.7
0.05585 | 282.15 | 0.09437 | 283.65 | 0.8
0.05585 | 282.15 | 0.09437 | 283.65 | 0.9
0.05585 | 282.15 | 0.09437 | 283.65 | 1
0.05585 | 282.15 | 0.09437 | 284.15 | 0.15
0.05585 | 282.15 | 0.09437 | 284.15 | 0.2
0.05585 | 282.15 | 0.09437 | 284.15 | 0.3
0.05585 | 282.15 | 0.09437 | 284.15 | 0.4
0.05585 | 282.15 | 0.09437 | 284.15 | 0.5
0.05585 | 282.15 | 0.09437 | 284.15 | 0.6
0.05585 | 282.15 | 0.09437 | 284.15 | 0.7
0.05585 | 282.15 | 0.09437 | 284.15 | 0.8
0.05585 | 282.15 | 0.09437 | 284.15 | 0.9
0.05585 | 282.15 | 0.09437 | 284.15 | 1
0.05585 | 282.15 | 0.09437 | 284.65 | 0.15
0.05585 | 282.15 | 0.09437 | 284.65 | 0.2
0.05585 | 282.15 | 0.09437 | 284.65 | 0.3
0.05585 | 282.15 | 0.09437 | 284.65 | 0.4
0.05585 | 282.15 | 0.09437 | 284.65 | 0.5
0.05585 | 282.15 | 0.09437 | 284.65 | 0.6
0.05585 | 282.15 | 0.09437 | 284.65 | 0.7
0.05585 | 282.15 | 0.09437 | 284.65 | 0.8
0.05585 | 282.15 | 0.09437 | 284.65 | 0.9
0.05585 | 282.15 | 0.09437 | 284.65 | 1
0.05585 | 282.15 | 0.09437 | 285.15 | 0.15
0.05585 | 282.15 | 0.09437 | 285.15 | 0.2
0.05585 | 282.15 | 0.09437 | 285.15 | 0.3
0.05585 | 282.15 | 0.09437 | 285.15 | 0.4
0.05585 | 282.15 | 0.09437 | 285.15 | 0.5
0.05585 | 282.15 | 0.09437 | 285.15 | 0.6
0.05585 | 282.15 | 0.09437 | 285.15 | 0.7
0.05585 | 282.15 | 0.09437 | 285.15 | 0.8
0.05585 | 282.15 | 0.09437 | 285.15 | 0.9
0.05585 | 282.15 | 0.09437 | 285.15 | 1
0.05585 | 282.15 | 0.09437 | 285.65 | 0.15
0.05585 | 282.15 | 0.09437 | 285.65 | 0.2
0.05585 | 282.15 | 0.09437 | 285.65 | 0.3
0.05585 | 282.15 | 0.09437 | 285.65 | 0.4
0.05585 | 282.15 | 0.09437 | 285.65 | 0.5
0.05585 | 282.15 | 0.09437 | 285.65 | 0.6
0.05585 | 282.15 | 0.09437 | 285.65 | 0.7
0.05585 | 282.15 | 0.09437 | 285.65 | 0.8
0.05585 | 282.15 | 0.09437 | 285.65 | 0.9
0.05585 | 282.15 | 0.09437 | 285.65 | 1
0.05585 | 282.15 | 0.09437 | 286.15 | 0.15
0.05585 | 282.15 | 0.09437 | 286.15 | 0.2
0.05585 | 282.15 | 0.09437 | 286.15 | 0.3
0.05585 | 282.15 | 0.09437 | 286.15 | 0.4
0.05585 | 282.15 | 0.09437 | 286.15 | 0.5
0.05585 | 282.15 | 0.09437 | 286.15 | 0.6
0.05585 | 282.15 | 0.09437 | 286.15 | 0.7
0.05585 | 282.15 | 0.09437 | 286.15 | 0.8
0.05585 | 282.15 | 0.09437 | 286.15 | 0.9
0.05585 | 282.15 | 0.09437 | 286.15 | 1
0.05585 | 282.15 | 0.09437 | 286.65 | 0.15
0.05585 | 282.15 | 0.09437 | 286.65 | 0.2
0.05585 | 282.15 | 0.09437 | 286.65 | 0.3
0.05585 | 282.15 | 0.09437 | 286.65 | 0.4
0.05585 | 282.15 | 0.09437 | 286.65 | 0.5
0.05585 | 282.15 | 0.09437 | 286.65 | 0.6
0.05585 | 282.15 | 0.09437 | 286.65 | 0.7
0.05585 | 282.15 | 0.09437 | 286.65 | 0.8
0.05585 | 282.15 | 0.09437 | 286.65 | 0.9
0.05585 | 282.15 | 0.09437 | 286.65 | 1
0.05585 | 282.15 | 0.09437 | 287.15 | 0.15
0.05585 | 282.15 | 0.09437 | 287.15 | 0.2
0.05585 | 282.15 | 0.09437 | 287.15 | 0.3
0.05585 | 282.15 | 0.09437 | 287.15 | 0.4
0.05585 | 282.15 | 0.09437 | 287.15 | 0.5
0.05585 | 282.15 | 0.09437 | 287.15 | 0.6
0.05585 | 282.15 | 0.09437 | 287.15 | 0.7
0.05585 | 282.15 | 0.09437 | 287.15 | 0.8
0.05585 | 282.15 | 0.09437 | 287.15 | 0.9
0.05585 | 282.15 | 0.09437 | 287.15 | 1
0.05585 | 282.15 | 0.09437 | 287.65 | 0.15
0.05585 | 282.15 | 0.09437 | 287.65 | 0.2
0.05585 | 282.15 | 0.09437 | 287.65 | 0.3
0.05585 | 282.15 | 0.09437 | 287.65 | 0.4
0.05585 | 282.15 | 0.09437 | 287.65 | 0.5
0.05585 | 282.15 | 0.09437 | 287.65 | 0.6
0.05585 | 282.15 | 0.09437 | 287.65 | 0.7
0.05585 | 282.15 | 0.09437 | 287.65 | 0.8
0.05585 | 282.15 | 0.09437 | 287.65 | 0.9
0.05585 | 282.15 | 0.09437 | 287.65 | 1
0.05585 | 282.15 | 0.09437 | 288.15 | 0.15
0.05585 | 282.15 | 0.09437 | 288.15 | 0.2
0.05585 | 282.15 | 0.09437 | 288.15 | 0.3
0.05585 | 282.15 | 0.09437 | 288.15 | 0.4
0.05585 | 282.15 | 0.09437 | 288.15 | 0.5
0.05585 | 282.15 | 0.09437 | 288.15 | 0.6
0.05585 | 282.15 | 0.09437 | 288.15 | 0.7
0.05585 | 282.15 | 0.09437 | 288.15 | 0.8
0.05585 | 282.15 | 0.09437 | 288.15 | 0.9
0.05585 | 282.15 | 0.09437 | 288.15 | 1
0.05585 | 282.15 | 0.09437 | 288.65 | 0.15
0.05585 | 282.15 | 0.09437 | 288.65 | 0.2
0.05585 | 282.15 | 0.09437 | 288.65 | 0.3
0.05585 | 282.15 | 0.09437 | 288.65 | 0.4
0.05585 | 282.15 | 0.09437 | 288.65 | 0.5
0.05585 | 282.15 | 0.09437 | 288.65 | 0.6
0.05585 | 282.15 | 0.09437 | 288.65 | 0.7
0.05585 | 282.15 | 0.09437 | 288.65 | 0.8
0.05585 | 282.15 | 0.09437 | 288.65 | 0.9
0.05585 | 282.15 | 0.09437 | 288.65 | 1
0.05585 | 282.15 | 0.09437 | 289.15 | 0.15
0.05585 | 282.15 | 0.09437 | 289.15 | 0.2
0.05585 | 282.15 | 0.09437 | 289.15 | 0.3
0.05585 | 282.15 | 0.09437 | 289.15 | 0.4
0.05585 | 282.15 | 0.09437 | 289.15 | 0.5
0.05585 | 282.15 | 0.09437 | 289.15 | 0.6
0.05585 | 282.15 | 0.09437 | 289.15 | 0.7
0.05585 | 282.15 | 0.09437 | 289.15 | 0.8
0.05585 | 282.15 | 0.09437 | 289.15 | 0.9
0.05585 | 282.15 | 0.09437 | 289.15 | 1
0.05585 | 282.15 | 0.09437 | 289.65 | 0.15
0.05585 | 282.15 | 0.09437 | 289.65 | 0.2
0.05585 | 282.15 | 0.09437 | 289.65 | 0.3
0.05585 | 282.15 | 0.09437 | 289.65 | 0.4
0.05585 | 282.15 | 0.09437 | 289.65 | 0.5
0.05585 | 282.15 | 0.09437 | 289.65 | 0.6
0.05585 | 282.15 | 0.09437 | 289.65 | 0.7
0.05585 | 282.15 | 0.09437 | 289.65 | 0.8
0.05585 | 282.15 | 0.09437 | 289.65 | 0.9
0.05585 | 282.15 | 0.09437 | 289.65 | 1
0.05585 | 282.15 | 0.09437 | 290.15 | 0.15
0.05585 | 282.15 | 0.09437 | 290.15 | 0.2
0.05585 | 282.15 | 0.09437 | 290.15 | 0.3
0.05585 | 282.15 | 0.09437 | 290.15 | 0.4
0.05585 | 282.15 | 0.09437 | 290.15 | 0.5
0.05585 | 282.15 | 0.09437 | 290.15 | 0.6
0.05585 | 282.15 | 0.09437 | 290.15 | 0.7
0.05585 | 282.15 | 0.09437 | 290.15 | 0.8
0.05585 | 282.15 | 0.09437 | 290.15 | 0.9
0.05585 | 282.15 | 0.09437 | 290.15 | 1
0.05585 | 282.15 | 0.09437 | 290.65 | 0.15
0.05585 | 282.15 | 0.09437 | 290.65 | 0.2
0.05585 | 282.15 | 0.09437 | 290.65 | 0.3
0.05585 | 282.15 | 0.09437 | 290.65 | 0.4
0.05585 | 282.15 | 0.09437 | 290.65 | 0.5
0.05585 | 282.15 | 0.09437 | 290.65 | 0.6
0.05585 | 282.15 | 0.09437 | 290.65 | 0.7
0.05585 | 282.15 | 0.09437 | 290.65 | 0.8
0.05585 | 282.15 | 0.09437 | 290.65 | 0.9
0.05585 | 282.15 | 0.09437 | 290.65 | 1
0.05585 | 282.15 | 0.09437 | 291.15 | 0.15
0.05585 | 282.15 | 0.09437 | 291.15 | 0.2
0.05585 | 282.15 | 0.09437 | 291.15 | 0.3
0.05585 | 282.15 | 0.09437 | 291.15 | 0.4
0.05585 | 282.15 | 0.09437 | 291.15 | 0.5
0.05585 | 282.15 | 0.09437 | 291.15 | 0.6
0.05585 | 282.15 | 0.09437 | 291.15 | 0.7
0.05585 | 282.15 | 0.09437 | 291.15 | 0.8
0.05585 | 282.15 | 0.09437 | 291.15 | 0.9
0.05585 | 282.15 | 0.09437 | 291.15 | 1
0.05585 | 282.15 | 0.09437 | 294.15 | 0.15
0.05585 | 282.15 | 0.09437 | 294.15 | 0.2
0.05585 | 282.15 | 0.09437 | 294.15 | 0.3
0.05585 | 282.15 | 0.09437 | 294.15 | 0.4
0.05585 | 282.15 | 0.09437 | 294.15 | 0.5
0.05585 | 282.15 | 0.09437 | 294.15 | 0.6
0.05585 | 282.15 | 0.09437 | 294.15 | 0.7
0.05585 | 282.15 | 0.09437 | 294.15 | 0.8
0.05585 | 282.15 | 0.09437 | 294.15 | 0.9
0.05585 | 282.15 | 0.09437 | 294.15 | 1
0.05585 | 282.15 | 0.09437 | 297.15 | 0.15
0.05585 | 282.15 | 0.09437 | 297.15 | 0.2
0.05585 | 282.15 | 0.09437 | 297.15 | 0.3
0.05585 | 282.15 | 0.09437 | 297.15 | 0.4
0.05585 | 282.15 | 0.09437 | 297.15 | 0.5
0.05585 | 282.15 | 0.09437 | 297.15 | 0.6
0.05585 | 282.15 | 0.09437 | 297.15 | 0.7
0.05585 | 282.15 | 0.09437 | 297.15 | 0.8
0.05585 | 282.15 | 0.09437 | 297.15 | 0.9
0.05585 | 282.15 | 0.09437 | 297.15 | 1
0.05585 | 282.15 | 0.09437 | 300.15 | 0.15
0.05585 | 282.15 | 0.09437 | 300.15 | 0.2
0.05585 | 282.15 | 0.09437 | 300.15 | 0.3
0.05585 | 282.15 | 0.09437 | 300.15 | 0.4
0.05585 | 282.15 | 0.09437 | 300.15 | 0.5
0.05585 | 282.15 | 0.09437 | 300.15 | 0.6
0.05585 | 282.15 | 0.09437 | 300.15 | 0.7
0.05585 | 282.15 | 0.09437 | 300.15 | 0.8
0.05585 | 282.15 | 0.09437 | 300.15 | 0.9
0.05585 | 282.15 | 0.09437 | 300.15 | 1
0.05585 | 282.15 | 0.09437 | 303.15 | 0.15
0.05585 | 282.15 | 0.09437 | 303.15 | 0.2
0.05585 | 282.15 | 0.09437 | 303.15 | 0.3
0.05585 | 282.15 | 0.09437 | 303.15 | 0.4
0.05585 | 282.15 | 0.09437 | 303.15 | 0.5
0.05585 | 282.15 | 0.09437 | 303.15 | 0.6
0.05585 | 282.15 | 0.09437 | 303.15 | 0.7
0.05585 | 282.15 | 0.09437 | 303.15 | 0.8
0.05585 | 282.15 | 0.09437 | 303.15 | 0.9
0.05585 | 282.15 | 0.09437 | 303.15 | 1
0.05585 | 282.15 | 0.09644 | 283.65 | 0.15
0.05585 | 282.15 | 0.09644 | 283.65 | 0.2
0.05585 | 282.15 | 0.09644 | 283.65 | 0.3
0.05585 | 282.15 | 0.09644 | 283.65 | 0.4
0.05585 | 282.15 | 0.09644 | 283.65 | 0.5
0.05585 | 282.15 | 0.09644 | 283.65 | 0.6
0.05585 | 282.15 | 0.09644 | 283.65 | 0.7
0.05585 | 282.15 | 0.09644 | 283.65 | 0.8
0.05585 | 282.15 | 0.09644 | 283.65 | 0.9
0.05585 | 282.15 | 0.09644 | 283.65 | 1
0.05585 | 282.15 | 0.09644 | 284.15 | 0.15
0.05585 | 282.15 | 0.09644 | 284.15 | 0.2
0.05585 | 282.15 | 0.09644 | 284.15 | 0.3
0.05585 | 282.15 | 0.09644 | 284.15 | 0.4
0.05585 | 282.15 | 0.09644 | 284.15 | 0.5
0.05585 | 282.15 | 0.09644 | 284.15 | 0.6
0.05585 | 282.15 | 0.09644 | 284.15 | 0.7
0.05585 | 282.15 | 0.09644 | 284.15 | 0.8
0.05585 | 282.15 | 0.09644 | 284.15 | 0.9
0.05585 | 282.15 | 0.09644 | 284.15 | 1
0.05585 | 282.15 | 0.09644 | 284.65 | 0.15
0.05585 | 282.15 | 0.09644 | 284.65 | 0.2
0.05585 | 282.15 | 0.09644 | 284.65 | 0.3
0.05585 | 282.15 | 0.09644 | 284.65 | 0.4
0.05585 | 282.15 | 0.09644 | 284.65 | 0.5
0.05585 | 282.15 | 0.09644 | 284.65 | 0.6
0.05585 | 282.15 | 0.09644 | 284.65 | 0.7
0.05585 | 282.15 | 0.09644 | 284.65 | 0.8
0.05585 | 282.15 | 0.09644 | 284.65 | 0.9
0.05585 | 282.15 | 0.09644 | 284.65 | 1
0.05585 | 282.15 | 0.09644 | 285.15 | 0.15
0.05585 | 282.15 | 0.09644 | 285.15 | 0.2
0.05585 | 282.15 | 0.09644 | 285.15 | 0.3
0.05585 | 282.15 | 0.09644 | 285.15 | 0.4
0.05585 | 282.15 | 0.09644 | 285.15 | 0.5
0.05585 | 282.15 | 0.09644 | 285.15 | 0.6
0.05585 | 282.15 | 0.09644 | 285.15 | 0.7
0.05585 | 282.15 | 0.09644 | 285.15 | 0.8
0.05585 | 282.15 | 0.09644 | 285.15 | 0.9
0.05585 | 282.15 | 0.09644 | 285.15 | 1
0.05585 | 282.15 | 0.09644 | 285.65 | 0.15
0.05585 | 282.15 | 0.09644 | 285.65 | 0.2
0.05585 | 282.15 | 0.09644 | 285.65 | 0.3
0.05585 | 282.15 | 0.09644 | 285.65 | 0.4
0.05585 | 282.15 | 0.09644 | 285.65 | 0.5
0.05585 | 282.15 | 0.09644 | 285.65 | 0.6
0.05585 | 282.15 | 0.09644 | 285.65 | 0.7
0.05585 | 282.15 | 0.09644 | 285.65 | 0.8
0.05585 | 282.15 | 0.09644 | 285.65 | 0.9
0.05585 | 282.15 | 0.09644 | 285.65 | 1
0.05585 | 282.15 | 0.09644 | 286.15 | 0.15
0.05585 | 282.15 | 0.09644 | 286.15 | 0.2
0.05585 | 282.15 | 0.09644 | 286.15 | 0.3
0.05585 | 282.15 | 0.09644 | 286.15 | 0.4
0.05585 | 282.15 | 0.09644 | 286.15 | 0.5
0.05585 | 282.15 | 0.09644 | 286.15 | 0.6
0.05585 | 282.15 | 0.09644 | 286.15 | 0.7
0.05585 | 282.15 | 0.09644 | 286.15 | 0.8
0.05585 | 282.15 | 0.09644 | 286.15 | 0.9
0.05585 | 282.15 | 0.09644 | 286.15 | 1
0.05585 | 282.15 | 0.09644 | 286.65 | 0.15
0.05585 | 282.15 | 0.09644 | 286.65 | 0.2
0.05585 | 282.15 | 0.09644 | 286.65 | 0.3
0.05585 | 282.15 | 0.09644 | 286.65 | 0.4
0.05585 | 282.15 | 0.09644 | 286.65 | 0.5
0.05585 | 282.15 | 0.09644 | 286.65 | 0.6
0.05585 | 282.15 | 0.09644 | 286.65 | 0.7
0.05585 | 282.15 | 0.09644 | 286.65 | 0.8
0.05585 | 282.15 | 0.09644 | 286.65 | 0.9
0.05585 | 282.15 | 0.09644 | 286.65 | 1
0.05585 | 282.15 | 0.09644 | 287.15 | 0.15
0.05585 | 282.15 | 0.09644 | 287.15 | 0.2
0.05585 | 282.15 | 0.09644 | 287.15 | 0.3
0.05585 | 282.15 | 0.09644 | 287.15 | 0.4
0.05585 | 282.15 | 0.09644 | 287.15 | 0.5
0.05585 | 282.15 | 0.09644 | 287.15 | 0.6
0.05585 | 282.15 | 0.09644 | 287.15 | 0.7
0.05585 | 282.15 | 0.09644 | 287.15 | 0.8
0.05585 | 282.15 | 0.09644 | 287.15 | 0.9
0.05585 | 282.15 | 0.09644 | 287.15 | 1
0.05585 | 282.15 | 0.09644 | 287.65 | 0.15
0.05585 | 282.15 | 0.09644 | 287.65 | 0.2
0.05585 | 282.15 | 0.09644 | 287.65 | 0.3
0.05585 | 282.15 | 0.09644 | 287.65 | 0.4
0.05585 | 282.15 | 0.09644 | 287.65 | 0.5
0.05585 | 282.15 | 0.09644 | 287.65 | 0.6
0.05585 | 282.15 | 0.09644 | 287.65 | 0.7
0.05585 | 282.15 | 0.09644 | 287.65 | 0.8
0.05585 | 282.15 | 0.09644 | 287.65 | 0.9
0.05585 | 282.15 | 0.09644 | 287.65 | 1
0.05585 | 282.15 | 0.09644 | 288.15 | 0.15
0.05585 | 282.15 | 0.09644 | 288.15 | 0.2
0.05585 | 282.15 | 0.09644 | 288.15 | 0.3
0.05585 | 282.15 | 0.09644 | 288.15 | 0.4
0.05585 | 282.15 | 0.09644 | 288.15 | 0.5
0.05585 | 282.15 | 0.09644 | 288.15 | 0.6
0.05585 | 282.15 | 0.09644 | 288.15 | 0.7
0.05585 | 282.15 | 0.09644 | 288.15 | 0.8
0.05585 | 282.15 | 0.09644 | 288.15 | 0.9
0.05585 | 282.15 | 0.09644 | 288.15 | 1
0.05585 | 282.15 | 0.09644 | 288.65 | 0.15
0.05585 | 282.15 | 0.09644 | 288.65 | 0.2
0.05585 | 282.15 | 0.09644 | 288.65 | 0.3
0.05585 | 282.15 | 0.09644 | 288.65 | 0.4
0.05585 | 282.15 | 0.09644 | 288.65 | 0.5
0.05585 | 282.15 | 0.09644 | 288.65 | 0.6
0.05585 | 282.15 | 0.09644 | 288.65 | 0.7
0.05585 | 282.15 | 0.09644 | 288.65 | 0.8
0.05585 | 282.15 | 0.09644 | 288.65 | 0.9
0.05585 | 282.15 | 0.09644 | 288.65 | 1
0.05585 | 282.15 | 0.09644 | 289.15 | 0.15
0.05585 | 282.15 | 0.09644 | 289.15 | 0.2
0.05585 | 282.15 | 0.09644 | 289.15 | 0.3
0.05585 | 282.15 | 0.09644 | 289.15 | 0.4
0.05585 | 282.15 | 0.09644 | 289.15 | 0.5
0.05585 | 282.15 | 0.09644 | 289.15 | 0.6
0.05585 | 282.15 | 0.09644 | 289.15 | 0.7
0.05585 | 282.15 | 0.09644 | 289.15 | 0.8
0.05585 | 282.15 | 0.09644 | 289.15 | 0.9
0.05585 | 282.15 | 0.09644 | 289.15 | 1
0.05585 | 282.15 | 0.09644 | 289.65 | 0.15
0.05585 | 282.15 | 0.09644 | 289.65 | 0.2
0.05585 | 282.15 | 0.09644 | 289.65 | 0.3
0.05585 | 282.15 | 0.09644 | 289.65 | 0.4
0.05585 | 282.15 | 0.09644 | 289.65 | 0.5
0.05585 | 282.15 | 0.09644 | 289.65 | 0.6
0.05585 | 282.15 | 0.09644 | 289.65 | 0.7
0.05585 | 282.15 | 0.09644 | 289.65 | 0.8
0.05585 | 282.15 | 0.09644 | 289.65 | 0.9
0.05585 | 282.15 | 0.09644 | 289.65 | 1
0.05585 | 282.15 | 0.09644 | 290.15 | 0.15
0.05585 | 282.15 | 0.09644 | 290.15 | 0.2
0.05585 | 282.15 | 0.09644 | 290.15 | 0.3
0.05585 | 282.15 | 0.09644 | 290.15 | 0.4
0.05585 | 282.15 | 0.09644 | 290.15 | 0.5
0.05585 | 282.15 | 0.09644 | 290.15 | 0.6
0.05585 | 282.15 | 0.09644 | 290.15 | 0.7
0.05585 | 282.15 | 0.09644 | 290.15 | 0.8
0.05585 | 282.15 | 0.09644 | 290.15 | 0.9
0.05585 | 282.15 | 0.09644 | 290.15 | 1
0.05585 | 282.15 | 0.09644 | 290.65 | 0.15
0.05585 | 282.15 | 0.09644 | 290.65 | 0.2
0.05585 | 282.15 | 0.09644 | 290.65 | 0.3
0.05585 | 282.15 | 0.09644 | 290.65 | 0.4
0.05585 | 282.15 | 0.09644 | 290.65 | 0.5
0.05585 | 282.15 | 0.09644 | 290.65 | 0.6
0.05585 | 282.15 | 0.09644 | 290.65 | 0.7
0.05585 | 282.15 | 0.09644 | 290.65 | 0.8
0.05585 | 282.15 | 0.09644 | 290.65 | 0.9
0.05585 | 282.15 | 0.09644 | 290.65 | 1
0.05585 | 282.15 | 0.09644 | 291.15 | 0.15
0.05585 | 282.15 | 0.09644 | 291.15 | 0.2
0.05585 | 282.15 | 0.09644 | 291.15 | 0.3
0.05585 | 282.15 | 0.09644 | 291.15 | 0.4
0.05585 | 282.15 | 0.09644 | 291.15 | 0.5
0.05585 | 282.15 | 0.09644 | 291.15 | 0.6
0.05585 | 282.15 | 0.09644 | 291.15 | 0.7
0.05585 | 282.15 | 0.09644 | 291.15 | 0.8
0.05585 | 282.15 | 0.09644 | 291.15 | 0.9
0.05585 | 282.15 | 0.09644 | 291.15 | 1
0.05585 | 282.15 | 0.09644 | 294.15 | 0.15
0.05585 | 282.15 | 0.09644 | 294.15 | 0.2
0.05585 | 282.15 | 0.09644 | 294.15 | 0.3
0.05585 | 282.15 | 0.09644 | 294.15 | 0.4
0.05585 | 282.15 | 0.09644 | 294.15 | 0.5
0.05585 | 282.15 | 0.09644 | 294.15 | 0.6
0.05585 | 282.15 | 0.09644 | 294.15 | 0.7
0.05585 | 282.15 | 0.09644 | 294.15 | 0.8
0.05585 | 282.15 | 0.09644 | 294.15 | 0.9
0.05585 | 282.15 | 0.09644 | 294.15 | 1
0.05585 | 282.15 | 0.09644 | 297.15 | 0.15
0.05585 | 282.15 | 0.09644 | 297.15 | 0.2
0.05585 | 282.15 | 0.09644 | 297.15 | 0.3
0.05585 | 282.15 | 0.09644 | 297.15 | 0.4
0.05585 | 282.15 | 0.09644 | 297.15 | 0.5
0.05585 | 282.15 | 0.09644 | 297.15 | 0.6
0.05585 | 282.15 | 0.09644 | 297.15 | 0.7
0.05585 | 282.15 | 0.09644 | 297.15 | 0.8
0.05585 | 282.15 | 0.09644 | 297.15 | 0.9
0.05585 | 282.15 | 0.09644 | 297.15 | 1
0.05585 | 282.15 | 0.09644 | 300.15 | 0.15
0.05585 | 282.15 | 0.09644 | 300.15 | 0.2
0.05585 | 282.15 | 0.09644 | 300.15 | 0.3
0.05585 | 282.15 | 0.09644 | 300.15 | 0.4
0.05585 | 282.15 | 0.09644 | 300.15 | 0.5
0.05585 | 282.15 | 0.09644 | 300.15 | 0.6
0.05585 | 282.15 | 0.09644 | 300.15 | 0.7
0.05585 | 282.15 | 0.09644 | 300.15 | 0.8
0.05585 | 282.15 | 0.09644 | 300.15 | 0.9
0.05585 | 282.15 | 0.09644 | 300.15 | 1
0.05585 | 282.15 | 0.09644 | 303.15 | 0.15
0.05585 | 282.15 | 0.09644 | 303.15 | 0.2
0.05585 | 282.15 | 0.09644 | 303.15 | 0.3
0.05585 | 282.15 | 0.09644 | 303.15 | 0.4
0.05585 | 282.15 | 0.09644 | 303.15 | 0.5
0.05585 | 282.15 | 0.09644 | 303.15 | 0.6
0.05585 | 282.15 | 0.09644 | 303.15 | 0.7
0.05585 | 282.15 | 0.09644 | 303.15 | 0.8
0.05585 | 282.15 | 0.09644 | 303.15 | 0.9
0.05585 | 282.15 | 0.09644 | 303.15 | 1
0.05585 | 282.15 | 0.09737 | 283.65 | 0.15
0.05585 | 282.15 | 0.09737 | 283.65 | 0.2
0.05585 | 282.15 | 0.09737 | 283.65 | 0.3
0.05585 | 282.15 | 0.09737 | 283.65 | 0.4
0.05585 | 282.15 | 0.09737 | 283.65 | 0.5
0.05585 | 282.15 | 0.09737 | 283.65 | 0.6
0.05585 | 282.15 | 0.09737 | 283.65 | 0.7
0.05585 | 282.15 | 0.09737 | 283.65 | 0.8
0.05585 | 282.15 | 0.09737 | 283.65 | 0.9
0.05585 | 282.15 | 0.09737 | 283.65 | 1
0.05585 | 282.15 | 0.09737 | 284.15 | 0.15
0.05585 | 282.15 | 0.09737 | 284.15 | 0.2
0.05585 | 282.15 | 0.09737 | 284.15 | 0.3
0.05585 | 282.15 | 0.09737 | 284.15 | 0.4
0.05585 | 282.15 | 0.09737 | 284.15 | 0.5
0.05585 | 282.15 | 0.09737 | 284.15 | 0.6
0.05585 | 282.15 | 0.09737 | 284.15 | 0.7
0.05585 | 282.15 | 0.09737 | 284.15 | 0.8
0.05585 | 282.15 | 0.09737 | 284.15 | 0.9
0.05585 | 282.15 | 0.09737 | 284.15 | 1
0.05585 | 282.15 | 0.09737 | 284.65 | 0.15
0.05585 | 282.15 | 0.09737 | 284.65 | 0.2
0.05585 | 282.15 | 0.09737 | 284.65 | 0.3
0.05585 | 282.15 | 0.09737 | 284.65 | 0.4
0.05585 | 282.15 | 0.09737 | 284.65 | 0.5
0.05585 | 282.15 | 0.09737 | 284.65 | 0.6
0.05585 | 282.15 | 0.09737 | 284.65 | 0.7
0.05585 | 282.15 | 0.09737 | 284.65 | 0.8
0.05585 | 282.15 | 0.09737 | 284.65 | 0.9
0.05585 | 282.15 | 0.09737 | 284.65 | 1
0.05585 | 282.15 | 0.09737 | 285.15 | 0.15
0.05585 | 282.15 | 0.09737 | 285.15 | 0.2
0.05585 | 282.15 | 0.09737 | 285.15 | 0.3
0.05585 | 282.15 | 0.09737 | 285.15 | 0.4
0.05585 | 282.15 | 0.09737 | 285.15 | 0.5
0.05585 | 282.15 | 0.09737 | 285.15 | 0.6
0.05585 | 282.15 | 0.09737 | 285.15 | 0.7
0.05585 | 282.15 | 0.09737 | 285.15 | 0.8
0.05585 | 282.15 | 0.09737 | 285.15 | 0.9
0.05585 | 282.15 | 0.09737 | 285.15 | 1
0.05585 | 282.15 | 0.09737 | 285.65 | 0.15
0.05585 | 282.15 | 0.09737 | 285.65 | 0.2
0.05585 | 282.15 | 0.09737 | 285.65 | 0.3
0.05585 | 282.15 | 0.09737 | 285.65 | 0.4
0.05585 | 282.15 | 0.09737 | 285.65 | 0.5
0.05585 | 282.15 | 0.09737 | 285.65 | 0.6
0.05585 | 282.15 | 0.09737 | 285.65 | 0.7
0.05585 | 282.15 | 0.09737 | 285.65 | 0.8
0.05585 | 282.15 | 0.09737 | 285.65 | 0.9
0.05585 | 282.15 | 0.09737 | 285.65 | 1
0.05585 | 282.15 | 0.09737 | 286.15 | 0.15
0.05585 | 282.15 | 0.09737 | 286.15 | 0.2
0.05585 | 282.15 | 0.09737 | 286.15 | 0.3
0.05585 | 282.15 | 0.09737 | 286.15 | 0.4
0.05585 | 282.15 | 0.09737 | 286.15 | 0.5
0.05585 | 282.15 | 0.09737 | 286.15 | 0.6
0.05585 | 282.15 | 0.09737 | 286.15 | 0.7
0.05585 | 282.15 | 0.09737 | 286.15 | 0.8
0.05585 | 282.15 | 0.09737 | 286.15 | 0.9
0.05585 | 282.15 | 0.09737 | 286.15 | 1
0.05585 | 282.15 | 0.09737 | 286.65 | 0.15
0.05585 | 282.15 | 0.09737 | 286.65 | 0.2
0.05585 | 282.15 | 0.09737 | 286.65 | 0.3
0.05585 | 282.15 | 0.09737 | 286.65 | 0.4
0.05585 | 282.15 | 0.09737 | 286.65 | 0.5
0.05585 | 282.15 | 0.09737 | 286.65 | 0.6
0.05585 | 282.15 | 0.09737 | 286.65 | 0.7
0.05585 | 282.15 | 0.09737 | 286.65 | 0.8
0.05585 | 282.15 | 0.09737 | 286.65 | 0.9
0.05585 | 282.15 | 0.09737 | 286.65 | 1
0.05585 | 282.15 | 0.09737 | 287.15 | 0.15
0.05585 | 282.15 | 0.09737 | 287.15 | 0.2
0.05585 | 282.15 | 0.09737 | 287.15 | 0.3
0.05585 | 282.15 | 0.09737 | 287.15 | 0.4
0.05585 | 282.15 | 0.09737 | 287.15 | 0.5
0.05585 | 282.15 | 0.09737 | 287.15 | 0.6
0.05585 | 282.15 | 0.09737 | 287.15 | 0.7
0.05585 | 282.15 | 0.09737 | 287.15 | 0.8
0.05585 | 282.15 | 0.09737 | 287.15 | 0.9
0.05585 | 282.15 | 0.09737 | 287.15 | 1
0.05585 | 282.15 | 0.09737 | 287.65 | 0.15
0.05585 | 282.15 | 0.09737 | 287.65 | 0.2
0.05585 | 282.15 | 0.09737 | 287.65 | 0.3
0.05585 | 282.15 | 0.09737 | 287.65 | 0.4
0.05585 | 282.15 | 0.09737 | 287.65 | 0.5
0.05585 | 282.15 | 0.09737 | 287.65 | 0.6
0.05585 | 282.15 | 0.09737 | 287.65 | 0.7
0.05585 | 282.15 | 0.09737 | 287.65 | 0.8
0.05585 | 282.15 | 0.09737 | 287.65 | 0.9
0.05585 | 282.15 | 0.09737 | 287.65 | 1
0.05585 | 282.15 | 0.09737 | 288.15 | 0.15
0.05585 | 282.15 | 0.09737 | 288.15 | 0.2
0.05585 | 282.15 | 0.09737 | 288.15 | 0.3
0.05585 | 282.15 | 0.09737 | 288.15 | 0.4
0.05585 | 282.15 | 0.09737 | 288.15 | 0.5
0.05585 | 282.15 | 0.09737 | 288.15 | 0.6
0.05585 | 282.15 | 0.09737 | 288.15 | 0.7
0.05585 | 282.15 | 0.09737 | 288.15 | 0.8
0.05585 | 282.15 | 0.09737 | 288.15 | 0.9
0.05585 | 282.15 | 0.09737 | 288.15 | 1
0.05585 | 282.15 | 0.09737 | 288.65 | 0.15
0.05585 | 282.15 | 0.09737 | 288.65 | 0.2
0.05585 | 282.15 | 0.09737 | 288.65 | 0.3
0.05585 | 282.15 | 0.09737 | 288.65 | 0.4
0.05585 | 282.15 | 0.09737 | 288.65 | 0.5
0.05585 | 282.15 | 0.09737 | 288.65 | 0.6
0.05585 | 282.15 | 0.09737 | 288.65 | 0.7
0.05585 | 282.15 | 0.09737 | 288.65 | 0.8
0.05585 | 282.15 | 0.09737 | 288.65 | 0.9
0.05585 | 282.15 | 0.09737 | 288.65 | 1
0.05585 | 282.15 | 0.09737 | 289.15 | 0.15
0.05585 | 282.15 | 0.09737 | 289.15 | 0.2
0.05585 | 282.15 | 0.09737 | 289.15 | 0.3
0.05585 | 282.15 | 0.09737 | 289.15 | 0.4
0.05585 | 282.15 | 0.09737 | 289.15 | 0.5
0.05585 | 282.15 | 0.09737 | 289.15 | 0.6
0.05585 | 282.15 | 0.09737 | 289.15 | 0.7
0.05585 | 282.15 | 0.09737 | 289.15 | 0.8
0.05585 | 282.15 | 0.09737 | 289.15 | 0.9
0.05585 | 282.15 | 0.09737 | 289.15 | 1
0.05585 | 282.15 | 0.09737 | 289.65 | 0.15
0.05585 | 282.15 | 0.09737 | 289.65 | 0.2
0.05585 | 282.15 | 0.09737 | 289.65 | 0.3
0.05585 | 282.15 | 0.09737 | 289.65 | 0.4
0.05585 | 282.15 | 0.09737 | 289.65 | 0.5
0.05585 | 282.15 | 0.09737 | 289.65 | 0.6
0.05585 | 282.15 | 0.09737 | 289.65 | 0.7
0.05585 | 282.15 | 0.09737 | 289.65 | 0.8
0.05585 | 282.15 | 0.09737 | 289.65 | 0.9
0.05585 | 282.15 | 0.09737 | 289.65 | 1
0.05585 | 282.15 | 0.09737 | 290.15 | 0.15
0.05585 | 282.15 | 0.09737 | 290.15 | 0.2
0.05585 | 282.15 | 0.09737 | 290.15 | 0.3
0.05585 | 282.15 | 0.09737 | 290.15 | 0.4
0.05585 | 282.15 | 0.09737 | 290.15 | 0.5
0.05585 | 282.15 | 0.09737 | 290.15 | 0.6
0.05585 | 282.15 | 0.09737 | 290.15 | 0.7
0.05585 | 282.15 | 0.09737 | 290.15 | 0.8
0.05585 | 282.15 | 0.09737 | 290.15 | 0.9
0.05585 | 282.15 | 0.09737 | 290.15 | 1
0.05585 | 282.15 | 0.09737 | 290.65 | 0.15
0.05585 | 282.15 | 0.09737 | 290.65 | 0.2
0.05585 | 282.15 | 0.09737 | 290.65 | 0.3
0.05585 | 282.15 | 0.09737 | 290.65 | 0.4
0.05585 | 282.15 | 0.09737 | 290.65 | 0.5
0.05585 | 282.15 | 0.09737 | 290.65 | 0.6
0.05585 | 282.15 | 0.09737 | 290.65 | 0.7
0.05585 | 282.15 | 0.09737 | 290.65 | 0.8
0.05585 | 282.15 | 0.09737 | 290.65 | 0.9
0.05585 | 282.15 | 0.09737 | 290.65 | 1
0.05585 | 282.15 | 0.09737 | 291.15 | 0.15
0.05585 | 282.15 | 0.09737 | 291.15 | 0.2
0.05585 | 282.15 | 0.09737 | 291.15 | 0.3
0.05585 | 282.15 | 0.09737 | 291.15 | 0.4
0.05585 | 282.15 | 0.09737 | 291.15 | 0.5
0.05585 | 282.15 | 0.09737 | 291.15 | 0.6
0.05585 | 282.15 | 0.09737 | 291.15 | 0.7
0.05585 | 282.15 | 0.09737 | 291.15 | 0.8
0.05585 | 282.15 | 0.09737 | 291.15 | 0.9
0.05585 | 282.15 | 0.09737 | 291.15 | 1
0.05585 | 282.15 | 0.09737 | 294.15 | 0.15
0.05585 | 282.15 | 0.09737 | 294.15 | 0.2
0.05585 | 282.15 | 0.09737 | 294.15 | 0.3
0.05585 | 282.15 | 0.09737 | 294.15 | 0.4
0.05585 | 282.15 | 0.09737 | 294.15 | 0.5
0.05585 | 282.15 | 0.09737 | 294.15 | 0.6
0.05585 | 282.15 | 0.09737 | 294.15 | 0.7
0.05585 | 282.15 | 0.09737 | 294.15 | 0.8
0.05585 | 282.15 | 0.09737 | 294.15 | 0.9
0.05585 | 282.15 | 0.09737 | 294.15 | 1
0.05585 | 282.15 | 0.09737 | 297.15 | 0.15
0.05585 | 282.15 | 0.09737 | 297.15 | 0.2
0.05585 | 282.15 | 0.09737 | 297.15 | 0.3
0.05585 | 282.15 | 0.09737 | 297.15 | 0.4
0.05585 | 282.15 | 0.09737 | 297.15 | 0.5
0.05585 | 282.15 | 0.09737 | 297.15 | 0.6
0.05585 | 282.15 | 0.09737 | 297.15 | 0.7
0.05585 | 282.15 | 0.09737 | 297.15 | 0.8
0.05585 | 282.15 | 0.09737 | 297.15 | 0.9
0.05585 | 282.15 | 0.09737 | 297.15 | 1
0.05585 | 282.15 | 0.09737 | 300.15 | 0.15
0.05585 | 282.15 | 0.09737 | 300.15 | 0.2
0.05585 | 282.15 | 0.09737 | 300.15 | 0.3
0.05585 | 282.15 | 0.09737 | 300.15 | 0.4
0.05585 | 282.15 | 0.09737 | 300.15 | 0.5
0.05585 | 282.15 | 0.09737 | 300.15 | 0.6
0.05585 | 282.15 | 0.09737 | 300.15 | 0.7
0.05585 | 282.15 | 0.09737 | 300.15 | 0.8
0.05585 | 282.15 | 0.09737 | 300.15 | 0.9
0.05585 | 282.15 | 0.09737 | 300.15 | 1
0.05585 | 282.15 | 0.09737 | 303.15 | 0.15
0.05585 | 282.15 | 0.09737 | 303.15 | 0.2
0.05585 | 282.15 | 0.09737 | 303.15 | 0.3
0.05585 | 282.15 | 0.09737 | 303.15 | 0.4
0.05585 | 282.15 | 0.09737 | 303.15 | 0.5
0.05585 | 282.15 | 0.09737 | 303.15 | 0.6
0.05585 | 282.15 | 0.09737 | 303.15 | 0.7
0.05585 | 282.15 | 0.09737 | 303.15 | 0.8
0.05585 | 282.15 | 0.09737 | 303.15 | 0.9
0.05585 | 282.15 | 0.09737 | 303.15 | 1
0.05585 | 282.15 | 0.115 | 283.65 | 0.15
0.05585 | 282.15 | 0.115 | 283.65 | 0.2
0.05585 | 282.15 | 0.115 | 283.65 | 0.3
0.05585 | 282.15 | 0.115 | 283.65 | 0.4
0.05585 | 282.15 | 0.115 | 283.65 | 0.5
0.05585 | 282.15 | 0.115 | 283.65 | 0.6
0.05585 | 282.15 | 0.115 | 283.65 | 0.7
0.05585 | 282.15 | 0.115 | 283.65 | 0.8
0.05585 | 282.15 | 0.115 | 283.65 | 0.9
0.05585 | 282.15 | 0.115 | 283.65 | 1
0.05585 | 282.15 | 0.115 | 284.15 | 0.15
0.05585 | 282.15 | 0.115 | 284.15 | 0.2
0.05585 | 282.15 | 0.115 | 284.15 | 0.3
0.05585 | 282.15 | 0.115 | 284.15 | 0.4
0.05585 | 282.15 | 0.115 | 284.15 | 0.5
0.05585 | 282.15 | 0.115 | 284.15 | 0.6
0.05585 | 282.15 | 0.115 | 284.15 | 0.7
0.05585 | 282.15 | 0.115 | 284.15 | 0.8
0.05585 | 282.15 | 0.115 | 284.15 | 0.9
0.05585 | 282.15 | 0.115 | 284.15 | 1
0.05585 | 282.15 | 0.115 | 284.65 | 0.15
0.05585 | 282.15 | 0.115 | 284.65 | 0.2
0.05585 | 282.15 | 0.115 | 284.65 | 0.3
0.05585 | 282.15 | 0.115 | 284.65 | 0.4
0.05585 | 282.15 | 0.115 | 284.65 | 0.5
0.05585 | 282.15 | 0.115 | 284.65 | 0.6
0.05585 | 282.15 | 0.115 | 284.65 | 0.7
0.05585 | 282.15 | 0.115 | 284.65 | 0.8
0.05585 | 282.15 | 0.115 | 284.65 | 0.9
0.05585 | 282.15 | 0.115 | 284.65 | 1
0.05585 | 282.15 | 0.115 | 285.15 | 0.15
0.05585 | 282.15 | 0.115 | 285.15 | 0.2
0.05585 | 282.15 | 0.115 | 285.15 | 0.3
0.05585 | 282.15 | 0.115 | 285.15 | 0.4
0.05585 | 282.15 | 0.115 | 285.15 | 0.5
0.05585 | 282.15 | 0.115 | 285.15 | 0.6
0.05585 | 282.15 | 0.115 | 285.15 | 0.7
0.05585 | 282.15 | 0.115 | 285.15 | 0.8
0.05585 | 282.15 | 0.115 | 285.15 | 0.9
0.05585 | 282.15 | 0.115 | 285.15 | 1
0.05585 | 282.15 | 0.115 | 285.65 | 0.15
0.05585 | 282.15 | 0.115 | 285.65 | 0.2
0.05585 | 282.15 | 0.115 | 285.65 | 0.3
0.05585 | 282.15 | 0.115 | 285.65 | 0.4
0.05585 | 282.15 | 0.115 | 285.65 | 0.5
0.05585 | 282.15 | 0.115 | 285.65 | 0.6
0.05585 | 282.15 | 0.115 | 285.65 | 0.7
0.05585 | 282.15 | 0.115 | 285.65 | 0.8
0.05585 | 282.15 | 0.115 | 285.65 | 0.9
0.05585 | 282.15 | 0.115 | 285.65 | 1
0.05585 | 282.15 | 0.115 | 286.15 | 0.15
0.05585 | 282.15 | 0.115 | 286.15 | 0.2
0.05585 | 282.15 | 0.115 | 286.15 | 0.3
0.05585 | 282.15 | 0.115 | 286.15 | 0.4
0.05585 | 282.15 | 0.115 | 286.15 | 0.5
0.05585 | 282.15 | 0.115 | 286.15 | 0.6
0.05585 | 282.15 | 0.115 | 286.15 | 0.7
0.05585 | 282.15 | 0.115 | 286.15 | 0.8
0.05585 | 282.15 | 0.115 | 286.15 | 0.9
0.05585 | 282.15 | 0.115 | 286.15 | 1
0.05585 | 282.15 | 0.115 | 286.65 | 0.15
0.05585 | 282.15 | 0.115 | 286.65 | 0.2
0.05585 | 282.15 | 0.115 | 286.65 | 0.3
0.05585 | 282.15 | 0.115 | 286.65 | 0.4
0.05585 | 282.15 | 0.115 | 286.65 | 0.5
0.05585 | 282.15 | 0.115 | 286.65 | 0.6
0.05585 | 282.15 | 0.115 | 286.65 | 0.7
0.05585 | 282.15 | 0.115 | 286.65 | 0.8
0.05585 | 282.15 | 0.115 | 286.65 | 0.9
0.05585 | 282.15 | 0.115 | 286.65 | 1
0.05585 | 282.15 | 0.115 | 287.15 | 0.15
0.05585 | 282.15 | 0.115 | 287.15 | 0.2
0.05585 | 282.15 | 0.115 | 287.15 | 0.3
0.05585 | 282.15 | 0.115 | 287.15 | 0.4
0.05585 | 282.15 | 0.115 | 287.15 | 0.5
0.05585 | 282.15 | 0.115 | 287.15 | 0.6
0.05585 | 282.15 | 0.115 | 287.15 | 0.7
0.05585 | 282.15 | 0.115 | 287.15 | 0.8
0.05585 | 282.15 | 0.115 | 287.15 | 0.9
0.05585 | 282.15 | 0.115 | 287.15 | 1
0.05585 | 282.15 | 0.115 | 287.65 | 0.15
0.05585 | 282.15 | 0.115 | 287.65 | 0.2
0.05585 | 282.15 | 0.115 | 287.65 | 0.3
0.05585 | 282.15 | 0.115 | 287.65 | 0.4
0.05585 | 282.15 | 0.115 | 287.65 | 0.5
0.05585 | 282.15 | 0.115 | 287.65 | 0.6
0.05585 | 282.15 | 0.115 | 287.65 | 0.7
0.05585 | 282.15 | 0.115 | 287.65 | 0.8
0.05585 | 282.15 | 0.115 | 287.65 | 0.9
0.05585 | 282.15 | 0.115 | 287.65 | 1
0.05585 | 282.15 | 0.115 | 288.15 | 0.15
0.05585 | 282.15 | 0.115 | 288.15 | 0.2
0.05585 | 282.15 | 0.115 | 288.15 | 0.3
0.05585 | 282.15 | 0.115 | 288.15 | 0.4
0.05585 | 282.15 | 0.115 | 288.15 | 0.5
0.05585 | 282.15 | 0.115 | 288.15 | 0.6
0.05585 | 282.15 | 0.115 | 288.15 | 0.7
0.05585 | 282.15 | 0.115 | 288.15 | 0.8
0.05585 | 282.15 | 0.115 | 288.15 | 0.9
0.05585 | 282.15 | 0.115 | 288.15 | 1
0.05585 | 282.15 | 0.115 | 288.65 | 0.15
0.05585 | 282.15 | 0.115 | 288.65 | 0.2
0.05585 | 282.15 | 0.115 | 288.65 | 0.3
0.05585 | 282.15 | 0.115 | 288.65 | 0.4
0.05585 | 282.15 | 0.115 | 288.65 | 0.5
0.05585 | 282.15 | 0.115 | 288.65 | 0.6
0.05585 | 282.15 | 0.115 | 288.65 | 0.7
0.05585 | 282.15 | 0.115 | 288.65 | 0.8
0.05585 | 282.15 | 0.115 | 288.65 | 0.9
0.05585 | 282.15 | 0.115 | 288.65 | 1
0.05585 | 282.15 | 0.115 | 289.15 | 0.15
0.05585 | 282.15 | 0.115 | 289.15 | 0.2
0.05585 | 282.15 | 0.115 | 289.15 | 0.3
0.05585 | 282.15 | 0.115 | 289.15 | 0.4
0.05585 | 282.15 | 0.115 | 289.15 | 0.5
0.05585 | 282.15 | 0.115 | 289.15 | 0.6
0.05585 | 282.15 | 0.115 | 289.15 | 0.7
0.05585 | 282.15 | 0.115 | 289.15 | 0.8
0.05585 | 282.15 | 0.115 | 289.15 | 0.9
0.05585 | 282.15 | 0.115 | 289.15 | 1
0.05585 | 282.15 | 0.115 | 289.65 | 0.15
0.05585 | 282.15 | 0.115 | 289.65 | 0.2
0.05585 | 282.15 | 0.115 | 289.65 | 0.3
0.05585 | 282.15 | 0.115 | 289.65 | 0.4
0.05585 | 282.15 | 0.115 | 289.65 | 0.5
0.05585 | 282.15 | 0.115 | 289.65 | 0.6
0.05585 | 282.15 | 0.115 | 289.65 | 0.7
0.05585 | 282.15 | 0.115 | 289.65 | 0.8
0.05585 | 282.15 | 0.115 | 289.65 | 0.9
0.05585 | 282.15 | 0.115 | 289.65 | 1
0.05585 | 282.15 | 0.115 | 290.15 | 0.15
0.05585 | 282.15 | 0.115 | 290.15 | 0.2
0.05585 | 282.15 | 0.115 | 290.15 | 0.3
0.05585 | 282.15 | 0.115 | 290.15 | 0.4
0.05585 | 282.15 | 0.115 | 290.15 | 0.5
0.05585 | 282.15 | 0.115 | 290.15 | 0.6
0.05585 | 282.15 | 0.115 | 290.15 | 0.7
0.05585 | 282.15 | 0.115 | 290.15 | 0.8
0.05585 | 282.15 | 0.115 | 290.15 | 0.9
0.05585 | 282.15 | 0.115 | 290.15 | 1
0.05585 | 282.15 | 0.115 | 290.65 | 0.15
0.05585 | 282.15 | 0.115 | 290.65 | 0.2
0.05585 | 282.15 | 0.115 | 290.65 | 0.3
0.05585 | 282.15 | 0.115 | 290.65 | 0.4
0.05585 | 282.15 | 0.115 | 290.65 | 0.5
0.05585 | 282.15 | 0.115 | 290.65 | 0.6
0.05585 | 282.15 | 0.115 | 290.65 | 0.7
0.05585 | 282.15 | 0.115 | 290.65 | 0.8
0.05585 | 282.15 | 0.115 | 290.65 | 0.9
0.05585 | 282.15 | 0.115 | 290.65 | 1
0.05585 | 282.15 | 0.115 | 291.15 | 0.15
0.05585 | 282.15 | 0.115 | 291.15 | 0.2
0.05585 | 282.15 | 0.115 | 291.15 | 0.3
0.05585 | 282.15 | 0.115 | 291.15 | 0.4
0.05585 | 282.15 | 0.115 | 291.15 | 0.5
0.05585 | 282.15 | 0.115 | 291.15 | 0.6
0.05585 | 282.15 | 0.115 | 291.15 | 0.7
0.05585 | 282.15 | 0.115 | 291.15 | 0.8
0.05585 | 282.15 | 0.115 | 291.15 | 0.9
0.05585 | 282.15 | 0.115 | 291.15 | 1
0.05585 | 282.15 | 0.115 | 294.15 | 0.15
0.05585 | 282.15 | 0.115 | 294.15 | 0.2
0.05585 | 282.15 | 0.115 | 294.15 | 0.3
0.05585 | 282.15 | 0.115 | 294.15 | 0.4
0.05585 | 282.15 | 0.115 | 294.15 | 0.5
0.05585 | 282.15 | 0.115 | 294.15 | 0.6
0.05585 | 282.15 | 0.115 | 294.15 | 0.7
0.05585 | 282.15 | 0.115 | 294.15 | 0.8
0.05585 | 282.15 | 0.115 | 294.15 | 0.9
0.05585 | 282.15 | 0.115 | 294.15 | 1
0.05585 | 282.15 | 0.115 | 297.15 | 0.15
0.05585 | 282.15 | 0.115 | 297.15 | 0.2
0.05585 | 282.15 | 0.115 | 297.15 | 0.3
0.05585 | 282.15 | 0.115 | 297.15 | 0.4
0.05585 | 282.15 | 0.115 | 297.15 | 0.5
0.05585 | 282.15 | 0.115 | 297.15 | 0.6
0.05585 | 282.15 | 0.115 | 297.15 | 0.7
0.05585 | 282.15 | 0.115 | 297.15 | 0.8
0.05585 | 282.15 | 0.115 | 297.15 | 0.9
0.05585 | 282.15 | 0.115 | 297.15 | 1
0.05585 | 282.15 | 0.115 | 300.15 | 0.15
0.05585 | 282.15 | 0.115 | 300.15 | 0.2
0.05585 | 282.15 | 0.115 | 300.15 | 0.3
0.05585 | 282.15 | 0.115 | 300.15 | 0.4
0.05585 | 282.15 | 0.115 | 300.15 | 0.5
0.05585 | 282.15 | 0.115 | 300.15 | 0.6
0.05585 | 282.15 | 0.115 | 300.15 | 0.7
0.05585 | 282.15 | 0.115 | 300.15 | 0.8
0.05585 | 282.15 | 0.115 | 300.15 | 0.9
0.05585 | 282.15 | 0.115 | 300.15 | 1
0.05585 | 282.15 | 0.115 | 303.15 | 0.15
0.05585 | 282.15 | 0.115 | 303.15 | 0.2
0.05585 | 282.15 | 0.115 | 303.15 | 0.3
0.05585 | 282.15 | 0.115 | 303.15 | 0.4
0.05585 | 282.15 | 0.115 | 303.15 | 0.5
0.05585 | 282.15 | 0.115 | 303.15 | 0.6
0.05585 | 282.15 | 0.115 | 303.15 | 0.7
0.05585 | 282.15 | 0.115 | 303.15 | 0.8
0.05585 | 282.15 | 0.115 | 303.15 | 0.9
0.05585 | 282.15 | 0.115 | 303.15 | 1
0.05737 | 278.15 | 0.00115 | 283.65 | 0.15
0.05737 | 278.15 | 0.00115 | 283.65 | 0.2
0.05737 | 278.15 | 0.00115 | 283.65 | 0.3
0.05737 | 278.15 | 0.00115 | 283.65 | 0.4
0.05737 | 278.15 | 0.00115 | 283.65 | 0.5
0.05737 | 278.15 | 0.00115 | 283.65 | 0.6
0.05737 | 278.15 | 0.00115 | 283.65 | 0.7
0.05737 | 278.15 | 0.00115 | 283.65 | 0.8
0.05737 | 278.15 | 0.00115 | 283.65 | 0.9
0.05737 | 278.15 | 0.00115 | 283.65 | 1
0.05737 | 278.15 | 0.00115 | 284.15 | 0.15
0.05737 | 278.15 | 0.00115 | 284.15 | 0.2
0.05737 | 278.15 | 0.00115 | 284.15 | 0.3
0.05737 | 278.15 | 0.00115 | 284.15 | 0.4
0.05737 | 278.15 | 0.00115 | 284.15 | 0.5
0.05737 | 278.15 | 0.00115 | 284.15 | 0.6
0.05737 | 278.15 | 0.00115 | 284.15 | 0.7
0.05737 | 278.15 | 0.00115 | 284.15 | 0.8
0.05737 | 278.15 | 0.00115 | 284.15 | 0.9
0.05737 | 278.15 | 0.00115 | 284.15 | 1
0.05737 | 278.15 | 0.00115 | 284.65 | 0.15
0.05737 | 278.15 | 0.00115 | 284.65 | 0.2
0.05737 | 278.15 | 0.00115 | 284.65 | 0.3
0.05737 | 278.15 | 0.00115 | 284.65 | 0.4
0.05737 | 278.15 | 0.00115 | 284.65 | 0.5
0.05737 | 278.15 | 0.00115 | 284.65 | 0.6
0.05737 | 278.15 | 0.00115 | 284.65 | 0.7
0.05737 | 278.15 | 0.00115 | 284.65 | 0.8
0.05737 | 278.15 | 0.00115 | 284.65 | 0.9
0.05737 | 278.15 | 0.00115 | 284.65 | 1
0.05737 | 278.15 | 0.00115 | 285.15 | 0.15
0.05737 | 278.15 | 0.00115 | 285.15 | 0.2
0.05737 | 278.15 | 0.00115 | 285.15 | 0.3
0.05737 | 278.15 | 0.00115 | 285.15 | 0.4
0.05737 | 278.15 | 0.00115 | 285.15 | 0.5
0.05737 | 278.15 | 0.00115 | 285.15 | 0.6
0.05737 | 278.15 | 0.00115 | 285.15 | 0.7
0.05737 | 278.15 | 0.00115 | 285.15 | 0.8
0.05737 | 278.15 | 0.00115 | 285.15 | 0.9
0.05737 | 278.15 | 0.00115 | 285.15 | 1
0.05737 | 278.15 | 0.00115 | 285.65 | 0.15
0.05737 | 278.15 | 0.00115 | 285.65 | 0.2
0.05737 | 278.15 | 0.00115 | 285.65 | 0.3
0.05737 | 278.15 | 0.00115 | 285.65 | 0.4
0.05737 | 278.15 | 0.00115 | 285.65 | 0.5
0.05737 | 278.15 | 0.00115 | 285.65 | 0.6
0.05737 | 278.15 | 0.00115 | 285.65 | 0.7
0.05737 | 278.15 | 0.00115 | 285.65 | 0.8
0.05737 | 278.15 | 0.00115 | 285.65 | 0.9
0.05737 | 278.15 | 0.00115 | 285.65 | 1
0.05737 | 278.15 | 0.00115 | 286.15 | 0.15
0.05737 | 278.15 | 0.00115 | 286.15 | 0.2
0.05737 | 278.15 | 0.00115 | 286.15 | 0.3
0.05737 | 278.15 | 0.00115 | 286.15 | 0.4
0.05737 | 278.15 | 0.00115 | 286.15 | 0.5
0.05737 | 278.15 | 0.00115 | 286.15 | 0.6
0.05737 | 278.15 | 0.00115 | 286.15 | 0.7
0.05737 | 278.15 | 0.00115 | 286.15 | 0.8
0.05737 | 278.15 | 0.00115 | 286.15 | 0.9
0.05737 | 278.15 | 0.00115 | 286.15 | 1
0.05737 | 278.15 | 0.00115 | 286.65 | 0.15
0.05737 | 278.15 | 0.00115 | 286.65 | 0.2
0.05737 | 278.15 | 0.00115 | 286.65 | 0.3
0.05737 | 278.15 | 0.00115 | 286.65 | 0.4
0.05737 | 278.15 | 0.00115 | 286.65 | 0.5
0.05737 | 278.15 | 0.00115 | 286.65 | 0.6
0.05737 | 278.15 | 0.00115 | 286.65 | 0.7
0.05737 | 278.15 | 0.00115 | 286.65 | 0.8
0.05737 | 278.15 | 0.00115 | 286.65 | 0.9
0.05737 | 278.15 | 0.00115 | 286.65 | 1
0.05737 | 278.15 | 0.00115 | 287.15 | 0.15
0.05737 | 278.15 | 0.00115 | 287.15 | 0.2
0.05737 | 278.15 | 0.00115 | 287.15 | 0.3
0.05737 | 278.15 | 0.00115 | 287.15 | 0.4
0.05737 | 278.15 | 0.00115 | 287.15 | 0.5
0.05737 | 278.15 | 0.00115 | 287.15 | 0.6
0.05737 | 278.15 | 0.00115 | 287.15 | 0.7
0.05737 | 278.15 | 0.00115 | 287.15 | 0.8
0.05737 | 278.15 | 0.00115 | 287.15 | 0.9
0.05737 | 278.15 | 0.00115 | 287.15 | 1
0.05737 | 278.15 | 0.00115 | 287.65 | 0.15
0.05737 | 278.15 | 0.00115 | 287.65 | 0.2
0.05737 | 278.15 | 0.00115 | 287.65 | 0.3
0.05737 | 278.15 | 0.00115 | 287.65 | 0.4
0.05737 | 278.15 | 0.00115 | 287.65 | 0.5
0.05737 | 278.15 | 0.00115 | 287.65 | 0.6
0.05737 | 278.15 | 0.00115 | 287.65 | 0.7
0.05737 | 278.15 | 0.00115 | 287.65 | 0.8
0.05737 | 278.15 | 0.00115 | 287.65 | 0.9
0.05737 | 278.15 | 0.00115 | 287.65 | 1
0.05737 | 278.15 | 0.00115 | 288.15 | 0.15
0.05737 | 278.15 | 0.00115 | 288.15 | 0.2
0.05737 | 278.15 | 0.00115 | 288.15 | 0.3
0.05737 | 278.15 | 0.00115 | 288.15 | 0.4
0.05737 | 278.15 | 0.00115 | 288.15 | 0.5
0.05737 | 278.15 | 0.00115 | 288.15 | 0.6
0.05737 | 278.15 | 0.00115 | 288.15 | 0.7
0.05737 | 278.15 | 0.00115 | 288.15 | 0.8
0.05737 | 278.15 | 0.00115 | 288.15 | 0.9
0.05737 | 278.15 | 0.00115 | 288.15 | 1
0.05737 | 278.15 | 0.00115 | 288.65 | 0.15
0.05737 | 278.15 | 0.00115 | 288.65 | 0.2
0.05737 | 278.15 | 0.00115 | 288.65 | 0.3
0.05737 | 278.15 | 0.00115 | 288.65 | 0.4
0.05737 | 278.15 | 0.00115 | 288.65 | 0.5
0.05737 | 278.15 | 0.00115 | 288.65 | 0.6
0.05737 | 278.15 | 0.00115 | 288.65 | 0.7
0.05737 | 278.15 | 0.00115 | 288.65 | 0.8
0.05737 | 278.15 | 0.00115 | 288.65 | 0.9
0.05737 | 278.15 | 0.00115 | 288.65 | 1
0.05737 | 278.15 | 0.00115 | 289.15 | 0.15
0.05737 | 278.15 | 0.00115 | 289.15 | 0.2
0.05737 | 278.15 | 0.00115 | 289.15 | 0.3
0.05737 | 278.15 | 0.00115 | 289.15 | 0.4
0.05737 | 278.15 | 0.00115 | 289.15 | 0.5
0.05737 | 278.15 | 0.00115 | 289.15 | 0.6
0.05737 | 278.15 | 0.00115 | 289.15 | 0.7
0.05737 | 278.15 | 0.00115 | 289.15 | 0.8
0.05737 | 278.15 | 0.00115 | 289.15 | 0.9
0.05737 | 278.15 | 0.00115 | 289.15 | 1
0.05737 | 278.15 | 0.00115 | 289.65 | 0.15
0.05737 | 278.15 | 0.00115 | 289.65 | 0.2
0.05737 | 278.15 | 0.00115 | 289.65 | 0.3
0.05737 | 278.15 | 0.00115 | 289.65 | 0.4
0.05737 | 278.15 | 0.00115 | 289.65 | 0.5
0.05737 | 278.15 | 0.00115 | 289.65 | 0.6
0.05737 | 278.15 | 0.00115 | 289.65 | 0.7
0.05737 | 278.15 | 0.00115 | 289.65 | 0.8
0.05737 | 278.15 | 0.00115 | 289.65 | 0.9
0.05737 | 278.15 | 0.00115 | 289.65 | 1
0.05737 | 278.15 | 0.00115 | 290.15 | 0.15
0.05737 | 278.15 | 0.00115 | 290.15 | 0.2
0.05737 | 278.15 | 0.00115 | 290.15 | 0.3
0.05737 | 278.15 | 0.00115 | 290.15 | 0.4
0.05737 | 278.15 | 0.00115 | 290.15 | 0.5
0.05737 | 278.15 | 0.00115 | 290.15 | 0.6
0.05737 | 278.15 | 0.00115 | 290.15 | 0.7
0.05737 | 278.15 | 0.00115 | 290.15 | 0.8
0.05737 | 278.15 | 0.00115 | 290.15 | 0.9
0.05737 | 278.15 | 0.00115 | 290.15 | 1
0.05737 | 278.15 | 0.00115 | 290.65 | 0.15
0.05737 | 278.15 | 0.00115 | 290.65 | 0.2
0.05737 | 278.15 | 0.00115 | 290.65 | 0.3
0.05737 | 278.15 | 0.00115 | 290.65 | 0.4
0.05737 | 278.15 | 0.00115 | 290.65 | 0.5
0.05737 | 278.15 | 0.00115 | 290.65 | 0.6
0.05737 | 278.15 | 0.00115 | 290.65 | 0.7
0.05737 | 278.15 | 0.00115 | 290.65 | 0.8
0.05737 | 278.15 | 0.00115 | 290.65 | 0.9
0.05737 | 278.15 | 0.00115 | 290.65 | 1
0.05737 | 278.15 | 0.00115 | 291.15 | 0.15
0.05737 | 278.15 | 0.00115 | 291.15 | 0.2
0.05737 | 278.15 | 0.00115 | 291.15 | 0.3
0.05737 | 278.15 | 0.00115 | 291.15 | 0.4
0.05737 | 278.15 | 0.00115 | 291.15 | 0.5
0.05737 | 278.15 | 0.00115 | 291.15 | 0.6
0.05737 | 278.15 | 0.00115 | 291.15 | 0.7
0.05737 | 278.15 | 0.00115 | 291.15 | 0.8
0.05737 | 278.15 | 0.00115 | 291.15 | 0.9
0.05737 | 278.15 | 0.00115 | 291.15 | 1
0.05737 | 278.15 | 0.00115 | 294.15 | 0.15
0.05737 | 278.15 | 0.00115 | 294.15 | 0.2
0.05737 | 278.15 | 0.00115 | 294.15 | 0.3
0.05737 | 278.15 | 0.00115 | 294.15 | 0.4
0.05737 | 278.15 | 0.00115 | 294.15 | 0.5
0.05737 | 278.15 | 0.00115 | 294.15 | 0.6
0.05737 | 278.15 | 0.00115 | 294.15 | 0.7
0.05737 | 278.15 | 0.00115 | 294.15 | 0.8
0.05737 | 278.15 | 0.00115 | 294.15 | 0.9
0.05737 | 278.15 | 0.00115 | 294.15 | 1
0.05737 | 278.15 | 0.00115 | 297.15 | 0.15
0.05737 | 278.15 | 0.00115 | 297.15 | 0.2
0.05737 | 278.15 | 0.00115 | 297.15 | 0.3
0.05737 | 278.15 | 0.00115 | 297.15 | 0.4
0.05737 | 278.15 | 0.00115 | 297.15 | 0.5
0.05737 | 278.15 | 0.00115 | 297.15 | 0.6
0.05737 | 278.15 | 0.00115 | 297.15 | 0.7
0.05737 | 278.15 | 0.00115 | 297.15 | 0.8
0.05737 | 278.15 | 0.00115 | 297.15 | 0.9
0.05737 | 278.15 | 0.00115 | 297.15 | 1
0.05737 | 278.15 | 0.00115 | 300.15 | 0.15
0.05737 | 278.15 | 0.00115 | 300.15 | 0.2
0.05737 | 278.15 | 0.00115 | 300.15 | 0.3
0.05737 | 278.15 | 0.00115 | 300.15 | 0.4
0.05737 | 278.15 | 0.00115 | 300.15 | 0.5
0.05737 | 278.15 | 0.00115 | 300.15 | 0.6
0.05737 | 278.15 | 0.00115 | 300.15 | 0.7
0.05737 | 278.15 | 0.00115 | 300.15 | 0.8
0.05737 | 278.15 | 0.00115 | 300.15 | 0.9
0.05737 | 278.15 | 0.00115 | 300.15 | 1
0.05737 | 278.15 | 0.00115 | 303.15 | 0.15
0.05737 | 278.15 | 0.00115 | 303.15 | 0.2
0.05737 | 278.15 | 0.00115 | 303.15 | 0.3
0.05737 | 278.15 | 0.00115 | 303.15 | 0.4
0.05737 | 278.15 | 0.00115 | 303.15 | 0.5
0.05737 | 278.15 | 0.00115 | 303.15 | 0.6
0.05737 | 278.15 | 0.00115 | 303.15 | 0.7
0.05737 | 278.15 | 0.00115 | 303.15 | 0.8
0.05737 | 278.15 | 0.00115 | 303.15 | 0.9
0.05737 | 278.15 | 0.00115 | 303.15 | 1
0.05737 | 278.15 | 0.077 | 283.65 | 0.15
0.05737 | 278.15 | 0.077 | 283.65 | 0.2
0.05737 | 278.15 | 0.077 | 283.65 | 0.3
0.05737 | 278.15 | 0.077 | 283.65 | 0.4
0.05737 | 278.15 | 0.077 | 283.65 | 0.5
0.05737 | 278.15 | 0.077 | 283.65 | 0.6
0.05737 | 278.15 | 0.077 | 283.65 | 0.7
0.05737 | 278.15 | 0.077 | 283.65 | 0.8
0.05737 | 278.15 | 0.077 | 283.65 | 0.9
0.05737 | 278.15 | 0.077 | 283.65 | 1
0.05737 | 278.15 | 0.077 | 284.15 | 0.15
0.05737 | 278.15 | 0.077 | 284.15 | 0.2
0.05737 | 278.15 | 0.077 | 284.15 | 0.3
0.05737 | 278.15 | 0.077 | 284.15 | 0.4
0.05737 | 278.15 | 0.077 | 284.15 | 0.5
0.05737 | 278.15 | 0.077 | 284.15 | 0.6
0.05737 | 278.15 | 0.077 | 284.15 | 0.7
0.05737 | 278.15 | 0.077 | 284.15 | 0.8
0.05737 | 278.15 | 0.077 | 284.15 | 0.9
0.05737 | 278.15 | 0.077 | 284.15 | 1
0.05737 | 278.15 | 0.077 | 284.65 | 0.15
0.05737 | 278.15 | 0.077 | 284.65 | 0.2
0.05737 | 278.15 | 0.077 | 284.65 | 0.3
0.05737 | 278.15 | 0.077 | 284.65 | 0.4
0.05737 | 278.15 | 0.077 | 284.65 | 0.5
0.05737 | 278.15 | 0.077 | 284.65 | 0.6
0.05737 | 278.15 | 0.077 | 284.65 | 0.7
0.05737 | 278.15 | 0.077 | 284.65 | 0.8
0.05737 | 278.15 | 0.077 | 284.65 | 0.9
0.05737 | 278.15 | 0.077 | 284.65 | 1
0.05737 | 278.15 | 0.077 | 285.15 | 0.15
0.05737 | 278.15 | 0.077 | 285.15 | 0.2
0.05737 | 278.15 | 0.077 | 285.15 | 0.3
0.05737 | 278.15 | 0.077 | 285.15 | 0.4
0.05737 | 278.15 | 0.077 | 285.15 | 0.5
0.05737 | 278.15 | 0.077 | 285.15 | 0.6
0.05737 | 278.15 | 0.077 | 285.15 | 0.7
0.05737 | 278.15 | 0.077 | 285.15 | 0.8
0.05737 | 278.15 | 0.077 | 285.15 | 0.9
0.05737 | 278.15 | 0.077 | 285.15 | 1
0.05737 | 278.15 | 0.077 | 285.65 | 0.15
0.05737 | 278.15 | 0.077 | 285.65 | 0.2
0.05737 | 278.15 | 0.077 | 285.65 | 0.3
0.05737 | 278.15 | 0.077 | 285.65 | 0.4
0.05737 | 278.15 | 0.077 | 285.65 | 0.5
0.05737 | 278.15 | 0.077 | 285.65 | 0.6
0.05737 | 278.15 | 0.077 | 285.65 | 0.7
0.05737 | 278.15 | 0.077 | 285.65 | 0.8
0.05737 | 278.15 | 0.077 | 285.65 | 0.9
0.05737 | 278.15 | 0.077 | 285.65 | 1
0.05737 | 278.15 | 0.077 | 286.15 | 0.15
0.05737 | 278.15 | 0.077 | 286.15 | 0.2
0.05737 | 278.15 | 0.077 | 286.15 | 0.3
0.05737 | 278.15 | 0.077 | 286.15 | 0.4
0.05737 | 278.15 | 0.077 | 286.15 | 0.5
0.05737 | 278.15 | 0.077 | 286.15 | 0.6
0.05737 | 278.15 | 0.077 | 286.15 | 0.7
0.05737 | 278.15 | 0.077 | 286.15 | 0.8
0.05737 | 278.15 | 0.077 | 286.15 | 0.9
0.05737 | 278.15 | 0.077 | 286.15 | 1
0.05737 | 278.15 | 0.077 | 286.65 | 0.15
0.05737 | 278.15 | 0.077 | 286.65 | 0.2
0.05737 | 278.15 | 0.077 | 286.65 | 0.3
0.05737 | 278.15 | 0.077 | 286.65 | 0.4
0.05737 | 278.15 | 0.077 | 286.65 | 0.5
0.05737 | 278.15 | 0.077 | 286.65 | 0.6
0.05737 | 278.15 | 0.077 | 286.65 | 0.7
0.05737 | 278.15 | 0.077 | 286.65 | 0.8
0.05737 | 278.15 | 0.077 | 286.65 | 0.9
0.05737 | 278.15 | 0.077 | 286.65 | 1
0.05737 | 278.15 | 0.077 | 287.15 | 0.15
0.05737 | 278.15 | 0.077 | 287.15 | 0.2
0.05737 | 278.15 | 0.077 | 287.15 | 0.3
0.05737 | 278.15 | 0.077 | 287.15 | 0.4
0.05737 | 278.15 | 0.077 | 287.15 | 0.5
0.05737 | 278.15 | 0.077 | 287.15 | 0.6
0.05737 | 278.15 | 0.077 | 287.15 | 0.7
0.05737 | 278.15 | 0.077 | 287.15 | 0.8
0.05737 | 278.15 | 0.077 | 287.15 | 0.9
0.05737 | 278.15 | 0.077 | 287.15 | 1
0.05737 | 278.15 | 0.077 | 287.65 | 0.15
0.05737 | 278.15 | 0.077 | 287.65 | 0.2
0.05737 | 278.15 | 0.077 | 287.65 | 0.3
0.05737 | 278.15 | 0.077 | 287.65 | 0.4
0.05737 | 278.15 | 0.077 | 287.65 | 0.5
0.05737 | 278.15 | 0.077 | 287.65 | 0.6
0.05737 | 278.15 | 0.077 | 287.65 | 0.7
0.05737 | 278.15 | 0.077 | 287.65 | 0.8
0.05737 | 278.15 | 0.077 | 287.65 | 0.9
0.05737 | 278.15 | 0.077 | 287.65 | 1
0.05737 | 278.15 | 0.077 | 288.15 | 0.15
0.05737 | 278.15 | 0.077 | 288.15 | 0.2
0.05737 | 278.15 | 0.077 | 288.15 | 0.3
0.05737 | 278.15 | 0.077 | 288.15 | 0.4
0.05737 | 278.15 | 0.077 | 288.15 | 0.5
0.05737 | 278.15 | 0.077 | 288.15 | 0.6
0.05737 | 278.15 | 0.077 | 288.15 | 0.7
0.05737 | 278.15 | 0.077 | 288.15 | 0.8
0.05737 | 278.15 | 0.077 | 288.15 | 0.9
0.05737 | 278.15 | 0.077 | 288.15 | 1
0.05737 | 278.15 | 0.077 | 288.65 | 0.15
0.05737 | 278.15 | 0.077 | 288.65 | 0.2
0.05737 | 278.15 | 0.077 | 288.65 | 0.3
0.05737 | 278.15 | 0.077 | 288.65 | 0.4
0.05737 | 278.15 | 0.077 | 288.65 | 0.5
0.05737 | 278.15 | 0.077 | 288.65 | 0.6
0.05737 | 278.15 | 0.077 | 288.65 | 0.7
0.05737 | 278.15 | 0.077 | 288.65 | 0.8
0.05737 | 278.15 | 0.077 | 288.65 | 0.9
0.05737 | 278.15 | 0.077 | 288.65 | 1
0.05737 | 278.15 | 0.077 | 289.15 | 0.15
0.05737 | 278.15 | 0.077 | 289.15 | 0.2
0.05737 | 278.15 | 0.077 | 289.15 | 0.3
0.05737 | 278.15 | 0.077 | 289.15 | 0.4
0.05737 | 278.15 | 0.077 | 289.15 | 0.5
0.05737 | 278.15 | 0.077 | 289.15 | 0.6
0.05737 | 278.15 | 0.077 | 289.15 | 0.7
0.05737 | 278.15 | 0.077 | 289.15 | 0.8
0.05737 | 278.15 | 0.077 | 289.15 | 0.9
0.05737 | 278.15 | 0.077 | 289.15 | 1
0.05737 | 278.15 | 0.077 | 289.65 | 0.15
0.05737 | 278.15 | 0.077 | 289.65 | 0.2
0.05737 | 278.15 | 0.077 | 289.65 | 0.3
0.05737 | 278.15 | 0.077 | 289.65 | 0.4
0.05737 | 278.15 | 0.077 | 289.65 | 0.5
0.05737 | 278.15 | 0.077 | 289.65 | 0.6
0.05737 | 278.15 | 0.077 | 289.65 | 0.7
0.05737 | 278.15 | 0.077 | 289.65 | 0.8
0.05737 | 278.15 | 0.077 | 289.65 | 0.9
0.05737 | 278.15 | 0.077 | 289.65 | 1
0.05737 | 278.15 | 0.077 | 290.15 | 0.15
0.05737 | 278.15 | 0.077 | 290.15 | 0.2
0.05737 | 278.15 | 0.077 | 290.15 | 0.3
0.05737 | 278.15 | 0.077 | 290.15 | 0.4
0.05737 | 278.15 | 0.077 | 290.15 | 0.5
0.05737 | 278.15 | 0.077 | 290.15 | 0.6
0.05737 | 278.15 | 0.077 | 290.15 | 0.7
0.05737 | 278.15 | 0.077 | 290.15 | 0.8
0.05737 | 278.15 | 0.077 | 290.15 | 0.9
0.05737 | 278.15 | 0.077 | 290.15 | 1
0.05737 | 278.15 | 0.077 | 290.65 | 0.15
0.05737 | 278.15 | 0.077 | 290.65 | 0.2
0.05737 | 278.15 | 0.077 | 290.65 | 0.3
0.05737 | 278.15 | 0.077 | 290.65 | 0.4
0.05737 | 278.15 | 0.077 | 290.65 | 0.5
0.05737 | 278.15 | 0.077 | 290.65 | 0.6
0.05737 | 278.15 | 0.077 | 290.65 | 0.7
0.05737 | 278.15 | 0.077 | 290.65 | 0.8
0.05737 | 278.15 | 0.077 | 290.65 | 0.9
0.05737 | 278.15 | 0.077 | 290.65 | 1
0.05737 | 278.15 | 0.077 | 291.15 | 0.15
0.05737 | 278.15 | 0.077 | 291.15 | 0.2
0.05737 | 278.15 | 0.077 | 291.15 | 0.3
0.05737 | 278.15 | 0.077 | 291.15 | 0.4
0.05737 | 278.15 | 0.077 | 291.15 | 0.5
0.05737 | 278.15 | 0.077 | 291.15 | 0.6
0.05737 | 278.15 | 0.077 | 291.15 | 0.7
0.05737 | 278.15 | 0.077 | 291.15 | 0.8
0.05737 | 278.15 | 0.077 | 291.15 | 0.9
0.05737 | 278.15 | 0.077 | 291.15 | 1
0.05737 | 278.15 | 0.077 | 294.15 | 0.15
0.05737 | 278.15 | 0.077 | 294.15 | 0.2
0.05737 | 278.15 | 0.077 | 294.15 | 0.3
0.05737 | 278.15 | 0.077 | 294.15 | 0.4
0.05737 | 278.15 | 0.077 | 294.15 | 0.5
0.05737 | 278.15 | 0.077 | 294.15 | 0.6
0.05737 | 278.15 | 0.077 | 294.15 | 0.7
0.05737 | 278.15 | 0.077 | 294.15 | 0.8
0.05737 | 278.15 | 0.077 | 294.15 | 0.9
0.05737 | 278.15 | 0.077 | 294.15 | 1
0.05737 | 278.15 | 0.077 | 297.15 | 0.15
0.05737 | 278.15 | 0.077 | 297.15 | 0.2
0.05737 | 278.15 | 0.077 | 297.15 | 0.3
0.05737 | 278.15 | 0.077 | 297.15 | 0.4
0.05737 | 278.15 | 0.077 | 297.15 | 0.5
0.05737 | 278.15 | 0.077 | 297.15 | 0.6
0.05737 | 278.15 | 0.077 | 297.15 | 0.7
0.05737 | 278.15 | 0.077 | 297.15 | 0.8
0.05737 | 278.15 | 0.077 | 297.15 | 0.9
0.05737 | 278.15 | 0.077 | 297.15 | 1
0.05737 | 278.15 | 0.077 | 300.15 | 0.15
0.05737 | 278.15 | 0.077 | 300.15 | 0.2
0.05737 | 278.15 | 0.077 | 300.15 | 0.3
0.05737 | 278.15 | 0.077 | 300.15 | 0.4
0.05737 | 278.15 | 0.077 | 300.15 | 0.5
0.05737 | 278.15 | 0.077 | 300.15 | 0.6
0.05737 | 278.15 | 0.077 | 300.15 | 0.7
0.05737 | 278.15 | 0.077 | 300.15 | 0.8
0.05737 | 278.15 | 0.077 | 300.15 | 0.9
0.05737 | 278.15 | 0.077 | 300.15 | 1
0.05737 | 278.15 | 0.077 | 303.15 | 0.15
0.05737 | 278.15 | 0.077 | 303.15 | 0.2
0.05737 | 278.15 | 0.077 | 303.15 | 0.3
0.05737 | 278.15 | 0.077 | 303.15 | 0.4
0.05737 | 278.15 | 0.077 | 303.15 | 0.5
0.05737 | 278.15 | 0.077 | 303.15 | 0.6
0.05737 | 278.15 | 0.077 | 303.15 | 0.7
0.05737 | 278.15 | 0.077 | 303.15 | 0.8
0.05737 | 278.15 | 0.077 | 303.15 | 0.9
0.05737 | 278.15 | 0.077 | 303.15 | 1
0.05737 | 278.15 | 0.09437 | 283.65 | 0.15
0.05737 | 278.15 | 0.09437 | 283.65 | 0.2
0.05737 | 278.15 | 0.09437 | 283.65 | 0.3
0.05737 | 278.15 | 0.09437 | 283.65 | 0.4
0.05737 | 278.15 | 0.09437 | 283.65 | 0.5
0.05737 | 278.15 | 0.09437 | 283.65 | 0.6
0.05737 | 278.15 | 0.09437 | 283.65 | 0.7
0.05737 | 278.15 | 0.09437 | 283.65 | 0.8
0.05737 | 278.15 | 0.09437 | 283.65 | 0.9
0.05737 | 278.15 | 0.09437 | 283.65 | 1
0.05737 | 278.15 | 0.09437 | 284.15 | 0.15
0.05737 | 278.15 | 0.09437 | 284.15 | 0.2
0.05737 | 278.15 | 0.09437 | 284.15 | 0.3
0.05737 | 278.15 | 0.09437 | 284.15 | 0.4
0.05737 | 278.15 | 0.09437 | 284.15 | 0.5
0.05737 | 278.15 | 0.09437 | 284.15 | 0.6
0.05737 | 278.15 | 0.09437 | 284.15 | 0.7
0.05737 | 278.15 | 0.09437 | 284.15 | 0.8
0.05737 | 278.15 | 0.09437 | 284.15 | 0.9
0.05737 | 278.15 | 0.09437 | 284.15 | 1
0.05737 | 278.15 | 0.09437 | 284.65 | 0.15
0.05737 | 278.15 | 0.09437 | 284.65 | 0.2
0.05737 | 278.15 | 0.09437 | 284.65 | 0.3
0.05737 | 278.15 | 0.09437 | 284.65 | 0.4
0.05737 | 278.15 | 0.09437 | 284.65 | 0.5
0.05737 | 278.15 | 0.09437 | 284.65 | 0.6
0.05737 | 278.15 | 0.09437 | 284.65 | 0.7
0.05737 | 278.15 | 0.09437 | 284.65 | 0.8
0.05737 | 278.15 | 0.09437 | 284.65 | 0.9
0.05737 | 278.15 | 0.09437 | 284.65 | 1
0.05737 | 278.15 | 0.09437 | 285.15 | 0.15
0.05737 | 278.15 | 0.09437 | 285.15 | 0.2
0.05737 | 278.15 | 0.09437 | 285.15 | 0.3
0.05737 | 278.15 | 0.09437 | 285.15 | 0.4
0.05737 | 278.15 | 0.09437 | 285.15 | 0.5
0.05737 | 278.15 | 0.09437 | 285.15 | 0.6
0.05737 | 278.15 | 0.09437 | 285.15 | 0.7
0.05737 | 278.15 | 0.09437 | 285.15 | 0.8
0.05737 | 278.15 | 0.09437 | 285.15 | 0.9
0.05737 | 278.15 | 0.09437 | 285.15 | 1
0.05737 | 278.15 | 0.09437 | 285.65 | 0.15
0.05737 | 278.15 | 0.09437 | 285.65 | 0.2
0.05737 | 278.15 | 0.09437 | 285.65 | 0.3
0.05737 | 278.15 | 0.09437 | 285.65 | 0.4
0.05737 | 278.15 | 0.09437 | 285.65 | 0.5
0.05737 | 278.15 | 0.09437 | 285.65 | 0.6
0.05737 | 278.15 | 0.09437 | 285.65 | 0.7
0.05737 | 278.15 | 0.09437 | 285.65 | 0.8
0.05737 | 278.15 | 0.09437 | 285.65 | 0.9
0.05737 | 278.15 | 0.09437 | 285.65 | 1
0.05737 | 278.15 | 0.09437 | 286.15 | 0.15
0.05737 | 278.15 | 0.09437 | 286.15 | 0.2
0.05737 | 278.15 | 0.09437 | 286.15 | 0.3
0.05737 | 278.15 | 0.09437 | 286.15 | 0.4
0.05737 | 278.15 | 0.09437 | 286.15 | 0.5
0.05737 | 278.15 | 0.09437 | 286.15 | 0.6
0.05737 | 278.15 | 0.09437 | 286.15 | 0.7
0.05737 | 278.15 | 0.09437 | 286.15 | 0.8
0.05737 | 278.15 | 0.09437 | 286.15 | 0.9
0.05737 | 278.15 | 0.09437 | 286.15 | 1
0.05737 | 278.15 | 0.09437 | 286.65 | 0.15
0.05737 | 278.15 | 0.09437 | 286.65 | 0.2
0.05737 | 278.15 | 0.09437 | 286.65 | 0.3
0.05737 | 278.15 | 0.09437 | 286.65 | 0.4
0.05737 | 278.15 | 0.09437 | 286.65 | 0.5
0.05737 | 278.15 | 0.09437 | 286.65 | 0.6
0.05737 | 278.15 | 0.09437 | 286.65 | 0.7
0.05737 | 278.15 | 0.09437 | 286.65 | 0.8
0.05737 | 278.15 | 0.09437 | 286.65 | 0.9
0.05737 | 278.15 | 0.09437 | 286.65 | 1
0.05737 | 278.15 | 0.09437 | 287.15 | 0.15
0.05737 | 278.15 | 0.09437 | 287.15 | 0.2
0.05737 | 278.15 | 0.09437 | 287.15 | 0.3
0.05737 | 278.15 | 0.09437 | 287.15 | 0.4
0.05737 | 278.15 | 0.09437 | 287.15 | 0.5
0.05737 | 278.15 | 0.09437 | 287.15 | 0.6
0.05737 | 278.15 | 0.09437 | 287.15 | 0.7
0.05737 | 278.15 | 0.09437 | 287.15 | 0.8
0.05737 | 278.15 | 0.09437 | 287.15 | 0.9
0.05737 | 278.15 | 0.09437 | 287.15 | 1
0.05737 | 278.15 | 0.09437 | 287.65 | 0.15
0.05737 | 278.15 | 0.09437 | 287.65 | 0.2
0.05737 | 278.15 | 0.09437 | 287.65 | 0.3
0.05737 | 278.15 | 0.09437 | 287.65 | 0.4
0.05737 | 278.15 | 0.09437 | 287.65 | 0.5
0.05737 | 278.15 | 0.09437 | 287.65 | 0.6
0.05737 | 278.15 | 0.09437 | 287.65 | 0.7
0.05737 | 278.15 | 0.09437 | 287.65 | 0.8
0.05737 | 278.15 | 0.09437 | 287.65 | 0.9
0.05737 | 278.15 | 0.09437 | 287.65 | 1
0.05737 | 278.15 | 0.09437 | 288.15 | 0.15
0.05737 | 278.15 | 0.09437 | 288.15 | 0.2
0.05737 | 278.15 | 0.09437 | 288.15 | 0.3
0.05737 | 278.15 | 0.09437 | 288.15 | 0.4
0.05737 | 278.15 | 0.09437 | 288.15 | 0.5
0.05737 | 278.15 | 0.09437 | 288.15 | 0.6
0.05737 | 278.15 | 0.09437 | 288.15 | 0.7
0.05737 | 278.15 | 0.09437 | 288.15 | 0.8
0.05737 | 278.15 | 0.09437 | 288.15 | 0.9
0.05737 | 278.15 | 0.09437 | 288.15 | 1
0.05737 | 278.15 | 0.09437 | 288.65 | 0.15
0.05737 | 278.15 | 0.09437 | 288.65 | 0.2
0.05737 | 278.15 | 0.09437 | 288.65 | 0.3
0.05737 | 278.15 | 0.09437 | 288.65 | 0.4
0.05737 | 278.15 | 0.09437 | 288.65 | 0.5
0.05737 | 278.15 | 0.09437 | 288.65 | 0.6
0.05737 | 278.15 | 0.09437 | 288.65 | 0.7
0.05737 | 278.15 | 0.09437 | 288.65 | 0.8
0.05737 | 278.15 | 0.09437 | 288.65 | 0.9
0.05737 | 278.15 | 0.09437 | 288.65 | 1
0.05737 | 278.15 | 0.09437 | 289.15 | 0.15
0.05737 | 278.15 | 0.09437 | 289.15 | 0.2
0.05737 | 278.15 | 0.09437 | 289.15 | 0.3
0.05737 | 278.15 | 0.09437 | 289.15 | 0.4
0.05737 | 278.15 | 0.09437 | 289.15 | 0.5
0.05737 | 278.15 | 0.09437 | 289.15 | 0.6
0.05737 | 278.15 | 0.09437 | 289.15 | 0.7
0.05737 | 278.15 | 0.09437 | 289.15 | 0.8
0.05737 | 278.15 | 0.09437 | 289.15 | 0.9
0.05737 | 278.15 | 0.09437 | 289.15 | 1
0.05737 | 278.15 | 0.09437 | 289.65 | 0.15
0.05737 | 278.15 | 0.09437 | 289.65 | 0.2
0.05737 | 278.15 | 0.09437 | 289.65 | 0.3
0.05737 | 278.15 | 0.09437 | 289.65 | 0.4
0.05737 | 278.15 | 0.09437 | 289.65 | 0.5
0.05737 | 278.15 | 0.09437 | 289.65 | 0.6
0.05737 | 278.15 | 0.09437 | 289.65 | 0.7
0.05737 | 278.15 | 0.09437 | 289.65 | 0.8
0.05737 | 278.15 | 0.09437 | 289.65 | 0.9
0.05737 | 278.15 | 0.09437 | 289.65 | 1
0.05737 | 278.15 | 0.09437 | 290.15 | 0.15
0.05737 | 278.15 | 0.09437 | 290.15 | 0.2
0.05737 | 278.15 | 0.09437 | 290.15 | 0.3
0.05737 | 278.15 | 0.09437 | 290.15 | 0.4
0.05737 | 278.15 | 0.09437 | 290.15 | 0.5
0.05737 | 278.15 | 0.09437 | 290.15 | 0.6
0.05737 | 278.15 | 0.09437 | 290.15 | 0.7
0.05737 | 278.15 | 0.09437 | 290.15 | 0.8
0.05737 | 278.15 | 0.09437 | 290.15 | 0.9
0.05737 | 278.15 | 0.09437 | 290.15 | 1
0.05737 | 278.15 | 0.09437 | 290.65 | 0.15
0.05737 | 278.15 | 0.09437 | 290.65 | 0.2
0.05737 | 278.15 | 0.09437 | 290.65 | 0.3
0.05737 | 278.15 | 0.09437 | 290.65 | 0.4
0.05737 | 278.15 | 0.09437 | 290.65 | 0.5
0.05737 | 278.15 | 0.09437 | 290.65 | 0.6
0.05737 | 278.15 | 0.09437 | 290.65 | 0.7
0.05737 | 278.15 | 0.09437 | 290.65 | 0.8
0.05737 | 278.15 | 0.09437 | 290.65 | 0.9
0.05737 | 278.15 | 0.09437 | 290.65 | 1
0.05737 | 278.15 | 0.09437 | 291.15 | 0.15
0.05737 | 278.15 | 0.09437 | 291.15 | 0.2
0.05737 | 278.15 | 0.09437 | 291.15 | 0.3
0.05737 | 278.15 | 0.09437 | 291.15 | 0.4
0.05737 | 278.15 | 0.09437 | 291.15 | 0.5
0.05737 | 278.15 | 0.09437 | 291.15 | 0.6
0.05737 | 278.15 | 0.09437 | 291.15 | 0.7
0.05737 | 278.15 | 0.09437 | 291.15 | 0.8
0.05737 | 278.15 | 0.09437 | 291.15 | 0.9
0.05737 | 278.15 | 0.09437 | 291.15 | 1
0.05737 | 278.15 | 0.09437 | 294.15 | 0.15
0.05737 | 278.15 | 0.09437 | 294.15 | 0.2
0.05737 | 278.15 | 0.09437 | 294.15 | 0.3
0.05737 | 278.15 | 0.09437 | 294.15 | 0.4
0.05737 | 278.15 | 0.09437 | 294.15 | 0.5
0.05737 | 278.15 | 0.09437 | 294.15 | 0.6
0.05737 | 278.15 | 0.09437 | 294.15 | 0.7
0.05737 | 278.15 | 0.09437 | 294.15 | 0.8
0.05737 | 278.15 | 0.09437 | 294.15 | 0.9
0.05737 | 278.15 | 0.09437 | 294.15 | 1
0.05737 | 278.15 | 0.09437 | 297.15 | 0.15
0.05737 | 278.15 | 0.09437 | 297.15 | 0.2
0.05737 | 278.15 | 0.09437 | 297.15 | 0.3
0.05737 | 278.15 | 0.09437 | 297.15 | 0.4
0.05737 | 278.15 | 0.09437 | 297.15 | 0.5
0.05737 | 278.15 | 0.09437 | 297.15 | 0.6
0.05737 | 278.15 | 0.09437 | 297.15 | 0.7
0.05737 | 278.15 | 0.09437 | 297.15 | 0.8
0.05737 | 278.15 | 0.09437 | 297.15 | 0.9
0.05737 | 278.15 | 0.09437 | 297.15 | 1
0.05737 | 278.15 | 0.09437 | 300.15 | 0.15
0.05737 | 278.15 | 0.09437 | 300.15 | 0.2
0.05737 | 278.15 | 0.09437 | 300.15 | 0.3
0.05737 | 278.15 | 0.09437 | 300.15 | 0.4
0.05737 | 278.15 | 0.09437 | 300.15 | 0.5
0.05737 | 278.15 | 0.09437 | 300.15 | 0.6
0.05737 | 278.15 | 0.09437 | 300.15 | 0.7
0.05737 | 278.15 | 0.09437 | 300.15 | 0.8
0.05737 | 278.15 | 0.09437 | 300.15 | 0.9
0.05737 | 278.15 | 0.09437 | 300.15 | 1
0.05737 | 278.15 | 0.09437 | 303.15 | 0.15
0.05737 | 278.15 | 0.09437 | 303.15 | 0.2
0.05737 | 278.15 | 0.09437 | 303.15 | 0.3
0.05737 | 278.15 | 0.09437 | 303.15 | 0.4
0.05737 | 278.15 | 0.09437 | 303.15 | 0.5
0.05737 | 278.15 | 0.09437 | 303.15 | 0.6
0.05737 | 278.15 | 0.09437 | 303.15 | 0.7
0.05737 | 278.15 | 0.09437 | 303.15 | 0.8
0.05737 | 278.15 | 0.09437 | 303.15 | 0.9
0.05737 | 278.15 | 0.09437 | 303.15 | 1
0.05737 | 278.15 | 0.09644 | 283.65 | 0.15
0.05737 | 278.15 | 0.09644 | 283.65 | 0.2
0.05737 | 278.15 | 0.09644 | 283.65 | 0.3
0.05737 | 278.15 | 0.09644 | 283.65 | 0.4
0.05737 | 278.15 | 0.09644 | 283.65 | 0.5
0.05737 | 278.15 | 0.09644 | 283.65 | 0.6
0.05737 | 278.15 | 0.09644 | 283.65 | 0.7
0.05737 | 278.15 | 0.09644 | 283.65 | 0.8
0.05737 | 278.15 | 0.09644 | 283.65 | 0.9
0.05737 | 278.15 | 0.09644 | 283.65 | 1
0.05737 | 278.15 | 0.09644 | 284.15 | 0.15
0.05737 | 278.15 | 0.09644 | 284.15 | 0.2
0.05737 | 278.15 | 0.09644 | 284.15 | 0.3
0.05737 | 278.15 | 0.09644 | 284.15 | 0.4
0.05737 | 278.15 | 0.09644 | 284.15 | 0.5
0.05737 | 278.15 | 0.09644 | 284.15 | 0.6
0.05737 | 278.15 | 0.09644 | 284.15 | 0.7
0.05737 | 278.15 | 0.09644 | 284.15 | 0.8
0.05737 | 278.15 | 0.09644 | 284.15 | 0.9
0.05737 | 278.15 | 0.09644 | 284.15 | 1
0.05737 | 278.15 | 0.09644 | 284.65 | 0.15
0.05737 | 278.15 | 0.09644 | 284.65 | 0.2
0.05737 | 278.15 | 0.09644 | 284.65 | 0.3
0.05737 | 278.15 | 0.09644 | 284.65 | 0.4
0.05737 | 278.15 | 0.09644 | 284.65 | 0.5
0.05737 | 278.15 | 0.09644 | 284.65 | 0.6
0.05737 | 278.15 | 0.09644 | 284.65 | 0.7
0.05737 | 278.15 | 0.09644 | 284.65 | 0.8
0.05737 | 278.15 | 0.09644 | 284.65 | 0.9
0.05737 | 278.15 | 0.09644 | 284.65 | 1
0.05737 | 278.15 | 0.09644 | 285.15 | 0.15
0.05737 | 278.15 | 0.09644 | 285.15 | 0.2
0.05737 | 278.15 | 0.09644 | 285.15 | 0.3
0.05737 | 278.15 | 0.09644 | 285.15 | 0.4
0.05737 | 278.15 | 0.09644 | 285.15 | 0.5
0.05737 | 278.15 | 0.09644 | 285.15 | 0.6
0.05737 | 278.15 | 0.09644 | 285.15 | 0.7
0.05737 | 278.15 | 0.09644 | 285.15 | 0.8
0.05737 | 278.15 | 0.09644 | 285.15 | 0.9
0.05737 | 278.15 | 0.09644 | 285.15 | 1
0.05737 | 278.15 | 0.09644 | 285.65 | 0.15
0.05737 | 278.15 | 0.09644 | 285.65 | 0.2
0.05737 | 278.15 | 0.09644 | 285.65 | 0.3
0.05737 | 278.15 | 0.09644 | 285.65 | 0.4
0.05737 | 278.15 | 0.09644 | 285.65 | 0.5
0.05737 | 278.15 | 0.09644 | 285.65 | 0.6
0.05737 | 278.15 | 0.09644 | 285.65 | 0.7
0.05737 | 278.15 | 0.09644 | 285.65 | 0.8
0.05737 | 278.15 | 0.09644 | 285.65 | 0.9
0.05737 | 278.15 | 0.09644 | 285.65 | 1
0.05737 | 278.15 | 0.09644 | 286.15 | 0.15
0.05737 | 278.15 | 0.09644 | 286.15 | 0.2
0.05737 | 278.15 | 0.09644 | 286.15 | 0.3
0.05737 | 278.15 | 0.09644 | 286.15 | 0.4
0.05737 | 278.15 | 0.09644 | 286.15 | 0.5
0.05737 | 278.15 | 0.09644 | 286.15 | 0.6
0.05737 | 278.15 | 0.09644 | 286.15 | 0.7
0.05737 | 278.15 | 0.09644 | 286.15 | 0.8
0.05737 | 278.15 | 0.09644 | 286.15 | 0.9
0.05737 | 278.15 | 0.09644 | 286.15 | 1
0.05737 | 278.15 | 0.09644 | 286.65 | 0.15
0.05737 | 278.15 | 0.09644 | 286.65 | 0.2
0.05737 | 278.15 | 0.09644 | 286.65 | 0.3
0.05737 | 278.15 | 0.09644 | 286.65 | 0.4
0.05737 | 278.15 | 0.09644 | 286.65 | 0.5
0.05737 | 278.15 | 0.09644 | 286.65 | 0.6
0.05737 | 278.15 | 0.09644 | 286.65 | 0.7
0.05737 | 278.15 | 0.09644 | 286.65 | 0.8
0.05737 | 278.15 | 0.09644 | 286.65 | 0.9
0.05737 | 278.15 | 0.09644 | 286.65 | 1
0.05737 | 278.15 | 0.09644 | 287.15 | 0.15
0.05737 | 278.15 | 0.09644 | 287.15 | 0.2
0.05737 | 278.15 | 0.09644 | 287.15 | 0.3
0.05737 | 278.15 | 0.09644 | 287.15 | 0.4
0.05737 | 278.15 | 0.09644 | 287.15 | 0.5
0.05737 | 278.15 | 0.09644 | 287.15 | 0.6
0.05737 | 278.15 | 0.09644 | 287.15 | 0.7
0.05737 | 278.15 | 0.09644 | 287.15 | 0.8
0.05737 | 278.15 | 0.09644 | 287.15 | 0.9
0.05737 | 278.15 | 0.09644 | 287.15 | 1
0.05737 | 278.15 | 0.09644 | 287.65 | 0.15
0.05737 | 278.15 | 0.09644 | 287.65 | 0.2
0.05737 | 278.15 | 0.09644 | 287.65 | 0.3
0.05737 | 278.15 | 0.09644 | 287.65 | 0.4
0.05737 | 278.15 | 0.09644 | 287.65 | 0.5
0.05737 | 278.15 | 0.09644 | 287.65 | 0.6
0.05737 | 278.15 | 0.09644 | 287.65 | 0.7
0.05737 | 278.15 | 0.09644 | 287.65 | 0.8
0.05737 | 278.15 | 0.09644 | 287.65 | 0.9
0.05737 | 278.15 | 0.09644 | 287.65 | 1
0.05737 | 278.15 | 0.09644 | 288.15 | 0.15
0.05737 | 278.15 | 0.09644 | 288.15 | 0.2
0.05737 | 278.15 | 0.09644 | 288.15 | 0.3
0.05737 | 278.15 | 0.09644 | 288.15 | 0.4
0.05737 | 278.15 | 0.09644 | 288.15 | 0.5
0.05737 | 278.15 | 0.09644 | 288.15 | 0.6
0.05737 | 278.15 | 0.09644 | 288.15 | 0.7
0.05737 | 278.15 | 0.09644 | 288.15 | 0.8
0.05737 | 278.15 | 0.09644 | 288.15 | 0.9
0.05737 | 278.15 | 0.09644 | 288.15 | 1
0.05737 | 278.15 | 0.09644 | 288.65 | 0.15
0.05737 | 278.15 | 0.09644 | 288.65 | 0.2
0.05737 | 278.15 | 0.09644 | 288.65 | 0.3
0.05737 | 278.15 | 0.09644 | 288.65 | 0.4
0.05737 | 278.15 | 0.09644 | 288.65 | 0.5
0.05737 | 278.15 | 0.09644 | 288.65 | 0.6
0.05737 | 278.15 | 0.09644 | 288.65 | 0.7
0.05737 | 278.15 | 0.09644 | 288.65 | 0.8
0.05737 | 278.15 | 0.09644 | 288.65 | 0.9
0.05737 | 278.15 | 0.09644 | 288.65 | 1
0.05737 | 278.15 | 0.09644 | 289.15 | 0.15
0.05737 | 278.15 | 0.09644 | 289.15 | 0.2
0.05737 | 278.15 | 0.09644 | 289.15 | 0.3
0.05737 | 278.15 | 0.09644 | 289.15 | 0.4
0.05737 | 278.15 | 0.09644 | 289.15 | 0.5
0.05737 | 278.15 | 0.09644 | 289.15 | 0.6
0.05737 | 278.15 | 0.09644 | 289.15 | 0.7
0.05737 | 278.15 | 0.09644 | 289.15 | 0.8
0.05737 | 278.15 | 0.09644 | 289.15 | 0.9
0.05737 | 278.15 | 0.09644 | 289.15 | 1
0.05737 | 278.15 | 0.09644 | 289.65 | 0.15
0.05737 | 278.15 | 0.09644 | 289.65 | 0.2
0.05737 | 278.15 | 0.09644 | 289.65 | 0.3
0.05737 | 278.15 | 0.09644 | 289.65 | 0.4
0.05737 | 278.15 | 0.09644 | 289.65 | 0.5
0.05737 | 278.15 | 0.09644 | 289.65 | 0.6
0.05737 | 278.15 | 0.09644 | 289.65 | 0.7
0.05737 | 278.15 | 0.09644 | 289.65 | 0.8
0.05737 | 278.15 | 0.09644 | 289.65 | 0.9
0.05737 | 278.15 | 0.09644 | 289.65 | 1
0.05737 | 278.15 | 0.09644 | 290.15 | 0.15
0.05737 | 278.15 | 0.09644 | 290.15 | 0.2
0.05737 | 278.15 | 0.09644 | 290.15 | 0.3
0.05737 | 278.15 | 0.09644 | 290.15 | 0.4
0.05737 | 278.15 | 0.09644 | 290.15 | 0.5
0.05737 | 278.15 | 0.09644 | 290.15 | 0.6
0.05737 | 278.15 | 0.09644 | 290.15 | 0.7
0.05737 | 278.15 | 0.09644 | 290.15 | 0.8
0.05737 | 278.15 | 0.09644 | 290.15 | 0.9
0.05737 | 278.15 | 0.09644 | 290.15 | 1
0.05737 | 278.15 | 0.09644 | 290.65 | 0.15
0.05737 | 278.15 | 0.09644 | 290.65 | 0.2
0.05737 | 278.15 | 0.09644 | 290.65 | 0.3
0.05737 | 278.15 | 0.09644 | 290.65 | 0.4
0.05737 | 278.15 | 0.09644 | 290.65 | 0.5
0.05737 | 278.15 | 0.09644 | 290.65 | 0.6
0.05737 | 278.15 | 0.09644 | 290.65 | 0.7
0.05737 | 278.15 | 0.09644 | 290.65 | 0.8
0.05737 | 278.15 | 0.09644 | 290.65 | 0.9
0.05737 | 278.15 | 0.09644 | 290.65 | 1
0.05737 | 278.15 | 0.09644 | 291.15 | 0.15
0.05737 | 278.15 | 0.09644 | 291.15 | 0.2
0.05737 | 278.15 | 0.09644 | 291.15 | 0.3
0.05737 | 278.15 | 0.09644 | 291.15 | 0.4
0.05737 | 278.15 | 0.09644 | 291.15 | 0.5
0.05737 | 278.15 | 0.09644 | 291.15 | 0.6
0.05737 | 278.15 | 0.09644 | 291.15 | 0.7
0.05737 | 278.15 | 0.09644 | 291.15 | 0.8
0.05737 | 278.15 | 0.09644 | 291.15 | 0.9
0.05737 | 278.15 | 0.09644 | 291.15 | 1
0.05737 | 278.15 | 0.09644 | 294.15 | 0.15
0.05737 | 278.15 | 0.09644 | 294.15 | 0.2
0.05737 | 278.15 | 0.09644 | 294.15 | 0.3
0.05737 | 278.15 | 0.09644 | 294.15 | 0.4
0.05737 | 278.15 | 0.09644 | 294.15 | 0.5
0.05737 | 278.15 | 0.09644 | 294.15 | 0.6
0.05737 | 278.15 | 0.09644 | 294.15 | 0.7
0.05737 | 278.15 | 0.09644 | 294.15 | 0.8
0.05737 | 278.15 | 0.09644 | 294.15 | 0.9
0.05737 | 278.15 | 0.09644 | 294.15 | 1
0.05737 | 278.15 | 0.09644 | 297.15 | 0.15
0.05737 | 278.15 | 0.09644 | 297.15 | 0.2
0.05737 | 278.15 | 0.09644 | 297.15 | 0.3
0.05737 | 278.15 | 0.09644 | 297.15 | 0.4
0.05737 | 278.15 | 0.09644 | 297.15 | 0.5
0.05737 | 278.15 | 0.09644 | 297.15 | 0.6
0.05737 | 278.15 | 0.09644 | 297.15 | 0.7
0.05737 | 278.15 | 0.09644 | 297.15 | 0.8
0.05737 | 278.15 | 0.09644 | 297.15 | 0.9
0.05737 | 278.15 | 0.09644 | 297.15 | 1
0.05737 | 278.15 | 0.09644 | 300.15 | 0.15
0.05737 | 278.15 | 0.09644 | 300.15 | 0.2
0.05737 | 278.15 | 0.09644 | 300.15 | 0.3
0.05737 | 278.15 | 0.09644 | 300.15 | 0.4
0.05737 | 278.15 | 0.09644 | 300.15 | 0.5
0.05737 | 278.15 | 0.09644 | 300.15 | 0.6
0.05737 | 278.15 | 0.09644 | 300.15 | 0.7
0.05737 | 278.15 | 0.09644 | 300.15 | 0.8
0.05737 | 278.15 | 0.09644 | 300.15 | 0.9
0.05737 | 278.15 | 0.09644 | 300.15 | 1
0.05737 | 278.15 | 0.09644 | 303.15 | 0.15
0.05737 | 278.15 | 0.09644 | 303.15 | 0.2
0.05737 | 278.15 | 0.09644 | 303.15 | 0.3
0.05737 | 278.15 | 0.09644 | 303.15 | 0.4
0.05737 | 278.15 | 0.09644 | 303.15 | 0.5
0.05737 | 278.15 | 0.09644 | 303.15 | 0.6
0.05737 | 278.15 | 0.09644 | 303.15 | 0.7
0.05737 | 278.15 | 0.09644 | 303.15 | 0.8
0.05737 | 278.15 | 0.09644 | 303.15 | 0.9
0.05737 | 278.15 | 0.09644 | 303.15 | 1
0.05737 | 278.15 | 0.09737 | 283.65 | 0.15
0.05737 | 278.15 | 0.09737 | 283.65 | 0.2
0.05737 | 278.15 | 0.09737 | 283.65 | 0.3
0.05737 | 278.15 | 0.09737 | 283.65 | 0.4
0.05737 | 278.15 | 0.09737 | 283.65 | 0.5
0.05737 | 278.15 | 0.09737 | 283.65 | 0.6
0.05737 | 278.15 | 0.09737 | 283.65 | 0.7
0.05737 | 278.15 | 0.09737 | 283.65 | 0.8
0.05737 | 278.15 | 0.09737 | 283.65 | 0.9
0.05737 | 278.15 | 0.09737 | 283.65 | 1
0.05737 | 278.15 | 0.09737 | 284.15 | 0.15
0.05737 | 278.15 | 0.09737 | 284.15 | 0.2
0.05737 | 278.15 | 0.09737 | 284.15 | 0.3
0.05737 | 278.15 | 0.09737 | 284.15 | 0.4
0.05737 | 278.15 | 0.09737 | 284.15 | 0.5
0.05737 | 278.15 | 0.09737 | 284.15 | 0.6
0.05737 | 278.15 | 0.09737 | 284.15 | 0.7
0.05737 | 278.15 | 0.09737 | 284.15 | 0.8
0.05737 | 278.15 | 0.09737 | 284.15 | 0.9
0.05737 | 278.15 | 0.09737 | 284.15 | 1
0.05737 | 278.15 | 0.09737 | 284.65 | 0.15
0.05737 | 278.15 | 0.09737 | 284.65 | 0.2
0.05737 | 278.15 | 0.09737 | 284.65 | 0.3
0.05737 | 278.15 | 0.09737 | 284.65 | 0.4
0.05737 | 278.15 | 0.09737 | 284.65 | 0.5
0.05737 | 278.15 | 0.09737 | 284.65 | 0.6
0.05737 | 278.15 | 0.09737 | 284.65 | 0.7
0.05737 | 278.15 | 0.09737 | 284.65 | 0.8
0.05737 | 278.15 | 0.09737 | 284.65 | 0.9
0.05737 | 278.15 | 0.09737 | 284.65 | 1
0.05737 | 278.15 | 0.09737 | 285.15 | 0.15
0.05737 | 278.15 | 0.09737 | 285.15 | 0.2
0.05737 | 278.15 | 0.09737 | 285.15 | 0.3
0.05737 | 278.15 | 0.09737 | 285.15 | 0.4
0.05737 | 278.15 | 0.09737 | 285.15 | 0.5
0.05737 | 278.15 | 0.09737 | 285.15 | 0.6
0.05737 | 278.15 | 0.09737 | 285.15 | 0.7
0.05737 | 278.15 | 0.09737 | 285.15 | 0.8
0.05737 | 278.15 | 0.09737 | 285.15 | 0.9
0.05737 | 278.15 | 0.09737 | 285.15 | 1
0.05737 | 278.15 | 0.09737 | 285.65 | 0.15
0.05737 | 278.15 | 0.09737 | 285.65 | 0.2
0.05737 | 278.15 | 0.09737 | 285.65 | 0.3
0.05737 | 278.15 | 0.09737 | 285.65 | 0.4
0.05737 | 278.15 | 0.09737 | 285.65 | 0.5
0.05737 | 278.15 | 0.09737 | 285.65 | 0.6
0.05737 | 278.15 | 0.09737 | 285.65 | 0.7
0.05737 | 278.15 | 0.09737 | 285.65 | 0.8
0.05737 | 278.15 | 0.09737 | 285.65 | 0.9
0.05737 | 278.15 | 0.09737 | 285.65 | 1
0.05737 | 278.15 | 0.09737 | 286.15 | 0.15
0.05737 | 278.15 | 0.09737 | 286.15 | 0.2
0.05737 | 278.15 | 0.09737 | 286.15 | 0.3
0.05737 | 278.15 | 0.09737 | 286.15 | 0.4
0.05737 | 278.15 | 0.09737 | 286.15 | 0.5
0.05737 | 278.15 | 0.09737 | 286.15 | 0.6
0.05737 | 278.15 | 0.09737 | 286.15 | 0.7
0.05737 | 278.15 | 0.09737 | 286.15 | 0.8
0.05737 | 278.15 | 0.09737 | 286.15 | 0.9
0.05737 | 278.15 | 0.09737 | 286.15 | 1
0.05737 | 278.15 | 0.09737 | 286.65 | 0.15
0.05737 | 278.15 | 0.09737 | 286.65 | 0.2
0.05737 | 278.15 | 0.09737 | 286.65 | 0.3
0.05737 | 278.15 | 0.09737 | 286.65 | 0.4
0.05737 | 278.15 | 0.09737 | 286.65 | 0.5
0.05737 | 278.15 | 0.09737 | 286.65 | 0.6
0.05737 | 278.15 | 0.09737 | 286.65 | 0.7
0.05737 | 278.15 | 0.09737 | 286.65 | 0.8
0.05737 | 278.15 | 0.09737 | 286.65 | 0.9
0.05737 | 278.15 | 0.09737 | 286.65 | 1
0.05737 | 278.15 | 0.09737 | 287.15 | 0.15
0.05737 | 278.15 | 0.09737 | 287.15 | 0.2
0.05737 | 278.15 | 0.09737 | 287.15 | 0.3
0.05737 | 278.15 | 0.09737 | 287.15 | 0.4
0.05737 | 278.15 | 0.09737 | 287.15 | 0.5
0.05737 | 278.15 | 0.09737 | 287.15 | 0.6
0.05737 | 278.15 | 0.09737 | 287.15 | 0.7
0.05737 | 278.15 | 0.09737 | 287.15 | 0.8
0.05737 | 278.15 | 0.09737 | 287.15 | 0.9
0.05737 | 278.15 | 0.09737 | 287.15 | 1
0.05737 | 278.15 | 0.09737 | 287.65 | 0.15
0.05737 | 278.15 | 0.09737 | 287.65 | 0.2
0.05737 | 278.15 | 0.09737 | 287.65 | 0.3
0.05737 | 278.15 | 0.09737 | 287.65 | 0.4
0.05737 | 278.15 | 0.09737 | 287.65 | 0.5
0.05737 | 278.15 | 0.09737 | 287.65 | 0.6
0.05737 | 278.15 | 0.09737 | 287.65 | 0.7
0.05737 | 278.15 | 0.09737 | 287.65 | 0.8
0.05737 | 278.15 | 0.09737 | 287.65 | 0.9
0.05737 | 278.15 | 0.09737 | 287.65 | 1
0.05737 | 278.15 | 0.09737 | 288.15 | 0.15
0.05737 | 278.15 | 0.09737 | 288.15 | 0.2
0.05737 | 278.15 | 0.09737 | 288.15 | 0.3
0.05737 | 278.15 | 0.09737 | 288.15 | 0.4
0.05737 | 278.15 | 0.09737 | 288.15 | 0.5
0.05737 | 278.15 | 0.09737 | 288.15 | 0.6
0.05737 | 278.15 | 0.09737 | 288.15 | 0.7
0.05737 | 278.15 | 0.09737 | 288.15 | 0.8
0.05737 | 278.15 | 0.09737 | 288.15 | 0.9
0.05737 | 278.15 | 0.09737 | 288.15 | 1
0.05737 | 278.15 | 0.09737 | 288.65 | 0.15
0.05737 | 278.15 | 0.09737 | 288.65 | 0.2
0.05737 | 278.15 | 0.09737 | 288.65 | 0.3
0.05737 | 278.15 | 0.09737 | 288.65 | 0.4
0.05737 | 278.15 | 0.09737 | 288.65 | 0.5
0.05737 | 278.15 | 0.09737 | 288.65 | 0.6
0.05737 | 278.15 | 0.09737 | 288.65 | 0.7
0.05737 | 278.15 | 0.09737 | 288.65 | 0.8
0.05737 | 278.15 | 0.09737 | 288.65 | 0.9
0.05737 | 278.15 | 0.09737 | 288.65 | 1
0.05737 | 278.15 | 0.09737 | 289.15 | 0.15
0.05737 | 278.15 | 0.09737 | 289.15 | 0.2
0.05737 | 278.15 | 0.09737 | 289.15 | 0.3
0.05737 | 278.15 | 0.09737 | 289.15 | 0.4
0.05737 | 278.15 | 0.09737 | 289.15 | 0.5
0.05737 | 278.15 | 0.09737 | 289.15 | 0.6
0.05737 | 278.15 | 0.09737 | 289.15 | 0.7
0.05737 | 278.15 | 0.09737 | 289.15 | 0.8
0.05737 | 278.15 | 0.09737 | 289.15 | 0.9
0.05737 | 278.15 | 0.09737 | 289.15 | 1
0.05737 | 278.15 | 0.09737 | 289.65 | 0.15
0.05737 | 278.15 | 0.09737 | 289.65 | 0.2
0.05737 | 278.15 | 0.09737 | 289.65 | 0.3
0.05737 | 278.15 | 0.09737 | 289.65 | 0.4
0.05737 | 278.15 | 0.09737 | 289.65 | 0.5
0.05737 | 278.15 | 0.09737 | 289.65 | 0.6
0.05737 | 278.15 | 0.09737 | 289.65 | 0.7
0.05737 | 278.15 | 0.09737 | 289.65 | 0.8
0.05737 | 278.15 | 0.09737 | 289.65 | 0.9
0.05737 | 278.15 | 0.09737 | 289.65 | 1
0.05737 | 278.15 | 0.09737 | 290.15 | 0.15
0.05737 | 278.15 | 0.09737 | 290.15 | 0.2
0.05737 | 278.15 | 0.09737 | 290.15 | 0.3
0.05737 | 278.15 | 0.09737 | 290.15 | 0.4
0.05737 | 278.15 | 0.09737 | 290.15 | 0.5
0.05737 | 278.15 | 0.09737 | 290.15 | 0.6
0.05737 | 278.15 | 0.09737 | 290.15 | 0.7
0.05737 | 278.15 | 0.09737 | 290.15 | 0.8
0.05737 | 278.15 | 0.09737 | 290.15 | 0.9
0.05737 | 278.15 | 0.09737 | 290.15 | 1
0.05737 | 278.15 | 0.09737 | 290.65 | 0.15
0.05737 | 278.15 | 0.09737 | 290.65 | 0.2
0.05737 | 278.15 | 0.09737 | 290.65 | 0.3
0.05737 | 278.15 | 0.09737 | 290.65 | 0.4
0.05737 | 278.15 | 0.09737 | 290.65 | 0.5
0.05737 | 278.15 | 0.09737 | 290.65 | 0.6
0.05737 | 278.15 | 0.09737 | 290.65 | 0.7
0.05737 | 278.15 | 0.09737 | 290.65 | 0.8
0.05737 | 278.15 | 0.09737 | 290.65 | 0.9
0.05737 | 278.15 | 0.09737 | 290.65 | 1
0.05737 | 278.15 | 0.09737 | 291.15 | 0.15
0.05737 | 278.15 | 0.09737 | 291.15 | 0.2
0.05737 | 278.15 | 0.09737 | 291.15 | 0.3
0.05737 | 278.15 | 0.09737 | 291.15 | 0.4
0.05737 | 278.15 | 0.09737 | 291.15 | 0.5
0.05737 | 278.15 | 0.09737 | 291.15 | 0.6
0.05737 | 278.15 | 0.09737 | 291.15 | 0.7
0.05737 | 278.15 | 0.09737 | 291.15 | 0.8
0.05737 | 278.15 | 0.09737 | 291.15 | 0.9
0.05737 | 278.15 | 0.09737 | 291.15 | 1
0.05737 | 278.15 | 0.09737 | 294.15 | 0.15
0.05737 | 278.15 | 0.09737 | 294.15 | 0.2
0.05737 | 278.15 | 0.09737 | 294.15 | 0.3
0.05737 | 278.15 | 0.09737 | 294.15 | 0.4
0.05737 | 278.15 | 0.09737 | 294.15 | 0.5
0.05737 | 278.15 | 0.09737 | 294.15 | 0.6
0.05737 | 278.15 | 0.09737 | 294.15 | 0.7
0.05737 | 278.15 | 0.09737 | 294.15 | 0.8
0.05737 | 278.15 | 0.09737 | 294.15 | 0.9
0.05737 | 278.15 | 0.09737 | 294.15 | 1
0.05737 | 278.15 | 0.09737 | 297.15 | 0.15
0.05737 | 278.15 | 0.09737 | 297.15 | 0.2
0.05737 | 278.15 | 0.09737 | 297.15 | 0.3
0.05737 | 278.15 | 0.09737 | 297.15 | 0.4
0.05737 | 278.15 | 0.09737 | 297.15 | 0.5
0.05737 | 278.15 | 0.09737 | 297.15 | 0.6
0.05737 | 278.15 | 0.09737 | 297.15 | 0.7
0.05737 | 278.15 | 0.09737 | 297.15 | 0.8
0.05737 | 278.15 | 0.09737 | 297.15 | 0.9
0.05737 | 278.15 | 0.09737 | 297.15 | 1
0.05737 | 278.15 | 0.09737 | 300.15 | 0.15
0.05737 | 278.15 | 0.09737 | 300.15 | 0.2
0.05737 | 278.15 | 0.09737 | 300.15 | 0.3
0.05737 | 278.15 | 0.09737 | 300.15 | 0.4
0.05737 | 278.15 | 0.09737 | 300.15 | 0.5
0.05737 | 278.15 | 0.09737 | 300.15 | 0.6
0.05737 | 278.15 | 0.09737 | 300.15 | 0.7
0.05737 | 278.15 | 0.09737 | 300.15 | 0.8
0.05737 | 278.15 | 0.09737 | 300.15 | 0.9
0.05737 | 278.15 | 0.09737 | 300.15 | 1
0.05737 | 278.15 | 0.09737 | 303.15 | 0.15
0.05737 | 278.15 | 0.09737 | 303.15 | 0.2
0.05737 | 278.15 | 0.09737 | 303.15 | 0.3
0.05737 | 278.15 | 0.09737 | 303.15 | 0.4
0.05737 | 278.15 | 0.09737 | 303.15 | 0.5
0.05737 | 278.15 | 0.09737 | 303.15 | 0.6
0.05737 | 278.15 | 0.09737 | 303.15 | 0.7
0.05737 | 278.15 | 0.09737 | 303.15 | 0.8
0.05737 | 278.15 | 0.09737 | 303.15 | 0.9
0.05737 | 278.15 | 0.09737 | 303.15 | 1
0.05737 | 278.15 | 0.115 | 283.65 | 0.15
0.05737 | 278.15 | 0.115 | 283.65 | 0.2
0.05737 | 278.15 | 0.115 | 283.65 | 0.3
0.05737 | 278.15 | 0.115 | 283.65 | 0.4
0.05737 | 278.15 | 0.115 | 283.65 | 0.5
0.05737 | 278.15 | 0.115 | 283.65 | 0.6
0.05737 | 278.15 | 0.115 | 283.65 | 0.7
0.05737 | 278.15 | 0.115 | 283.65 | 0.8
0.05737 | 278.15 | 0.115 | 283.65 | 0.9
0.05737 | 278.15 | 0.115 | 283.65 | 1
0.05737 | 278.15 | 0.115 | 284.15 | 0.15
0.05737 | 278.15 | 0.115 | 284.15 | 0.2
0.05737 | 278.15 | 0.115 | 284.15 | 0.3
0.05737 | 278.15 | 0.115 | 284.15 | 0.4
0.05737 | 278.15 | 0.115 | 284.15 | 0.5
0.05737 | 278.15 | 0.115 | 284.15 | 0.6
0.05737 | 278.15 | 0.115 | 284.15 | 0.7
0.05737 | 278.15 | 0.115 | 284.15 | 0.8
0.05737 | 278.15 | 0.115 | 284.15 | 0.9
0.05737 | 278.15 | 0.115 | 284.15 | 1
0.05737 | 278.15 | 0.115 | 284.65 | 0.15
0.05737 | 278.15 | 0.115 | 284.65 | 0.2
0.05737 | 278.15 | 0.115 | 284.65 | 0.3
0.05737 | 278.15 | 0.115 | 284.65 | 0.4
0.05737 | 278.15 | 0.115 | 284.65 | 0.5
0.05737 | 278.15 | 0.115 | 284.65 | 0.6
0.05737 | 278.15 | 0.115 | 284.65 | 0.7
0.05737 | 278.15 | 0.115 | 284.65 | 0.8
0.05737 | 278.15 | 0.115 | 284.65 | 0.9
0.05737 | 278.15 | 0.115 | 284.65 | 1
0.05737 | 278.15 | 0.115 | 285.15 | 0.15
0.05737 | 278.15 | 0.115 | 285.15 | 0.2
0.05737 | 278.15 | 0.115 | 285.15 | 0.3
0.05737 | 278.15 | 0.115 | 285.15 | 0.4
0.05737 | 278.15 | 0.115 | 285.15 | 0.5
0.05737 | 278.15 | 0.115 | 285.15 | 0.6
0.05737 | 278.15 | 0.115 | 285.15 | 0.7
0.05737 | 278.15 | 0.115 | 285.15 | 0.8
0.05737 | 278.15 | 0.115 | 285.15 | 0.9
0.05737 | 278.15 | 0.115 | 285.15 | 1
0.05737 | 278.15 | 0.115 | 285.65 | 0.15
0.05737 | 278.15 | 0.115 | 285.65 | 0.2
0.05737 | 278.15 | 0.115 | 285.65 | 0.3
0.05737 | 278.15 | 0.115 | 285.65 | 0.4
0.05737 | 278.15 | 0.115 | 285.65 | 0.5
0.05737 | 278.15 | 0.115 | 285.65 | 0.6
0.05737 | 278.15 | 0.115 | 285.65 | 0.7
0.05737 | 278.15 | 0.115 | 285.65 | 0.8
0.05737 | 278.15 | 0.115 | 285.65 | 0.9
0.05737 | 278.15 | 0.115 | 285.65 | 1
0.05737 | 278.15 | 0.115 | 286.15 | 0.15
0.05737 | 278.15 | 0.115 | 286.15 | 0.2
0.05737 | 278.15 | 0.115 | 286.15 | 0.3
0.05737 | 278.15 | 0.115 | 286.15 | 0.4
0.05737 | 278.15 | 0.115 | 286.15 | 0.5
0.05737 | 278.15 | 0.115 | 286.15 | 0.6
0.05737 | 278.15 | 0.115 | 286.15 | 0.7
0.05737 | 278.15 | 0.115 | 286.15 | 0.8
0.05737 | 278.15 | 0.115 | 286.15 | 0.9
0.05737 | 278.15 | 0.115 | 286.15 | 1
0.05737 | 278.15 | 0.115 | 286.65 | 0.15
0.05737 | 278.15 | 0.115 | 286.65 | 0.2
0.05737 | 278.15 | 0.115 | 286.65 | 0.3
0.05737 | 278.15 | 0.115 | 286.65 | 0.4
0.05737 | 278.15 | 0.115 | 286.65 | 0.5
0.05737 | 278.15 | 0.115 | 286.65 | 0.6
0.05737 | 278.15 | 0.115 | 286.65 | 0.7
0.05737 | 278.15 | 0.115 | 286.65 | 0.8
0.05737 | 278.15 | 0.115 | 286.65 | 0.9
0.05737 | 278.15 | 0.115 | 286.65 | 1
0.05737 | 278.15 | 0.115 | 287.15 | 0.15
0.05737 | 278.15 | 0.115 | 287.15 | 0.2
0.05737 | 278.15 | 0.115 | 287.15 | 0.3
0.05737 | 278.15 | 0.115 | 287.15 | 0.4
0.05737 | 278.15 | 0.115 | 287.15 | 0.5
0.05737 | 278.15 | 0.115 | 287.15 | 0.6
0.05737 | 278.15 | 0.115 | 287.15 | 0.7
0.05737 | 278.15 | 0.115 | 287.15 | 0.8
0.05737 | 278.15 | 0.115 | 287.15 | 0.9
0.05737 | 278.15 | 0.115 | 287.15 | 1
0.05737 | 278.15 | 0.115 | 287.65 | 0.15
0.05737 | 278.15 | 0.115 | 287.65 | 0.2
0.05737 | 278.15 | 0.115 | 287.65 | 0.3
0.05737 | 278.15 | 0.115 | 287.65 | 0.4
0.05737 | 278.15 | 0.115 | 287.65 | 0.5
0.05737 | 278.15 | 0.115 | 287.65 | 0.6
0.05737 | 278.15 | 0.115 | 287.65 | 0.7
0.05737 | 278.15 | 0.115 | 287.65 | 0.8
0.05737 | 278.15 | 0.115 | 287.65 | 0.9
0.05737 | 278.15 | 0.115 | 287.65 | 1
0.05737 | 278.15 | 0.115 | 288.15 | 0.15
0.05737 | 278.15 | 0.115 | 288.15 | 0.2
0.05737 | 278.15 | 0.115 | 288.15 | 0.3
0.05737 | 278.15 | 0.115 | 288.15 | 0.4
0.05737 | 278.15 | 0.115 | 288.15 | 0.5
0.05737 | 278.15 | 0.115 | 288.15 | 0.6
0.05737 | 278.15 | 0.115 | 288.15 | 0.7
0.05737 | 278.15 | 0.115 | 288.15 | 0.8
0.05737 | 278.15 | 0.115 | 288.15 | 0.9
0.05737 | 278.15 | 0.115 | 288.15 | 1
0.05737 | 278.15 | 0.115 | 288.65 | 0.15
0.05737 | 278.15 | 0.115 | 288.65 | 0.2
0.05737 | 278.15 | 0.115 | 288.65 | 0.3
0.05737 | 278.15 | 0.115 | 288.65 | 0.4
0.05737 | 278.15 | 0.115 | 288.65 | 0.5
0.05737 | 278.15 | 0.115 | 288.65 | 0.6
0.05737 | 278.15 | 0.115 | 288.65 | 0.7
0.05737 | 278.15 | 0.115 | 288.65 | 0.8
0.05737 | 278.15 | 0.115 | 288.65 | 0.9
0.05737 | 278.15 | 0.115 | 288.65 | 1
0.05737 | 278.15 | 0.115 | 289.15 | 0.15
0.05737 | 278.15 | 0.115 | 289.15 | 0.2
0.05737 | 278.15 | 0.115 | 289.15 | 0.3
0.05737 | 278.15 | 0.115 | 289.15 | 0.4
0.05737 | 278.15 | 0.115 | 289.15 | 0.5
0.05737 | 278.15 | 0.115 | 289.15 | 0.6
0.05737 | 278.15 | 0.115 | 289.15 | 0.7
0.05737 | 278.15 | 0.115 | 289.15 | 0.8
0.05737 | 278.15 | 0.115 | 289.15 | 0.9
0.05737 | 278.15 | 0.115 | 289.15 | 1
0.05737 | 278.15 | 0.115 | 289.65 | 0.15
0.05737 | 278.15 | 0.115 | 289.65 | 0.2
0.05737 | 278.15 | 0.115 | 289.65 | 0.3
0.05737 | 278.15 | 0.115 | 289.65 | 0.4
0.05737 | 278.15 | 0.115 | 289.65 | 0.5
0.05737 | 278.15 | 0.115 | 289.65 | 0.6
0.05737 | 278.15 | 0.115 | 289.65 | 0.7
0.05737 | 278.15 | 0.115 | 289.65 | 0.8
0.05737 | 278.15 | 0.115 | 289.65 | 0.9
0.05737 | 278.15 | 0.115 | 289.65 | 1
0.05737 | 278.15 | 0.115 | 290.15 | 0.15
0.05737 | 278.15 | 0.115 | 290.15 | 0.2
0.05737 | 278.15 | 0.115 | 290.15 | 0.3
0.05737 | 278.15 | 0.115 | 290.15 | 0.4
0.05737 | 278.15 | 0.115 | 290.15 | 0.5
0.05737 | 278.15 | 0.115 | 290.15 | 0.6
0.05737 | 278.15 | 0.115 | 290.15 | 0.7
0.05737 | 278.15 | 0.115 | 290.15 | 0.8
0.05737 | 278.15 | 0.115 | 290.15 | 0.9
0.05737 | 278.15 | 0.115 | 290.15 | 1
0.05737 | 278.15 | 0.115 | 290.65 | 0.15
0.05737 | 278.15 | 0.115 | 290.65 | 0.2
0.05737 | 278.15 | 0.115 | 290.65 | 0.3
0.05737 | 278.15 | 0.115 | 290.65 | 0.4
0.05737 | 278.15 | 0.115 | 290.65 | 0.5
0.05737 | 278.15 | 0.115 | 290.65 | 0.6
0.05737 | 278.15 | 0.115 | 290.65 | 0.7
0.05737 | 278.15 | 0.115 | 290.65 | 0.8
0.05737 | 278.15 | 0.115 | 290.65 | 0.9
0.05737 | 278.15 | 0.115 | 290.65 | 1
0.05737 | 278.15 | 0.115 | 291.15 | 0.15
0.05737 | 278.15 | 0.115 | 291.15 | 0.2
0.05737 | 278.15 | 0.115 | 291.15 | 0.3
0.05737 | 278.15 | 0.115 | 291.15 | 0.4
0.05737 | 278.15 | 0.115 | 291.15 | 0.5
0.05737 | 278.15 | 0.115 | 291.15 | 0.6
0.05737 | 278.15 | 0.115 | 291.15 | 0.7
0.05737 | 278.15 | 0.115 | 291.15 | 0.8
0.05737 | 278.15 | 0.115 | 291.15 | 0.9
0.05737 | 278.15 | 0.115 | 291.15 | 1
0.05737 | 278.15 | 0.115 | 294.15 | 0.15
0.05737 | 278.15 | 0.115 | 294.15 | 0.2
0.05737 | 278.15 | 0.115 | 294.15 | 0.3
0.05737 | 278.15 | 0.115 | 294.15 | 0.4
0.05737 | 278.15 | 0.115 | 294.15 | 0.5
0.05737 | 278.15 | 0.115 | 294.15 | 0.6
0.05737 | 278.15 | 0.115 | 294.15 | 0.7
0.05737 | 278.15 | 0.115 | 294.15 | 0.8
0.05737 | 278.15 | 0.115 | 294.15 | 0.9
0.05737 | 278.15 | 0.115 | 294.15 | 1
0.05737 | 278.15 | 0.115 | 297.15 | 0.15
0.05737 | 278.15 | 0.115 | 297.15 | 0.2
0.05737 | 278.15 | 0.115 | 297.15 | 0.3
0.05737 | 278.15 | 0.115 | 297.15 | 0.4
0.05737 | 278.15 | 0.115 | 297.15 | 0.5
0.05737 | 278.15 | 0.115 | 297.15 | 0.6
0.05737 | 278.15 | 0.115 | 297.15 | 0.7
0.05737 | 278.15 | 0.115 | 297.15 | 0.8
0.05737 | 278.15 | 0.115 | 297.15 | 0.9
0.05737 | 278.15 | 0.115 | 297.15 | 1
0.05737 | 278.15 | 0.115 | 300.15 | 0.15
0.05737 | 278.15 | 0.115 | 300.15 | 0.2
0.05737 | 278.15 | 0.115 | 300.15 | 0.3
0.05737 | 278.15 | 0.115 | 300.15 | 0.4
0.05737 | 278.15 | 0.115 | 300.15 | 0.5
0.05737 | 278.15 | 0.115 | 300.15 | 0.6
0.05737 | 278.15 | 0.115 | 300.15 | 0.7
0.05737 | 278.15 | 0.115 | 300.15 | 0.8
0.05737 | 278.15 | 0.115 | 300.15 | 0.9
0.05737 | 278.15 | 0.115 | 300.15 | 1
0.05737 | 278.15 | 0.115 | 303.15 | 0.15
0.05737 | 278.15 | 0.115 | 303.15 | 0.2
0.05737 | 278.15 | 0.115 | 303.15 | 0.3
0.05737 | 278.15 | 0.115 | 303.15 | 0.4
0.05737 | 278.15 | 0.115 | 303.15 | 0.5
0.05737 | 278.15 | 0.115 | 303.15 | 0.6
0.05737 | 278.15 | 0.115 | 303.15 | 0.7
0.05737 | 278.15 | 0.115 | 303.15 | 0.8
0.05737 | 278.15 | 0.115 | 303.15 | 0.9
0.05737 | 278.15 | 0.115 | 303.15 | 1
0.05737 | 280.15 | 0.00115 | 283.65 | 0.15
0.05737 | 280.15 | 0.00115 | 283.65 | 0.2
0.05737 | 280.15 | 0.00115 | 283.65 | 0.3
0.05737 | 280.15 | 0.00115 | 283.65 | 0.4
0.05737 | 280.15 | 0.00115 | 283.65 | 0.5
0.05737 | 280.15 | 0.00115 | 283.65 | 0.6
0.05737 | 280.15 | 0.00115 | 283.65 | 0.7
0.05737 | 280.15 | 0.00115 | 283.65 | 0.8
0.05737 | 280.15 | 0.00115 | 283.65 | 0.9
0.05737 | 280.15 | 0.00115 | 283.65 | 1
0.05737 | 280.15 | 0.00115 | 284.15 | 0.15
0.05737 | 280.15 | 0.00115 | 284.15 | 0.2
0.05737 | 280.15 | 0.00115 | 284.15 | 0.3
0.05737 | 280.15 | 0.00115 | 284.15 | 0.4
0.05737 | 280.15 | 0.00115 | 284.15 | 0.5
0.05737 | 280.15 | 0.00115 | 284.15 | 0.6
0.05737 | 280.15 | 0.00115 | 284.15 | 0.7
0.05737 | 280.15 | 0.00115 | 284.15 | 0.8
0.05737 | 280.15 | 0.00115 | 284.15 | 0.9
0.05737 | 280.15 | 0.00115 | 284.15 | 1
0.05737 | 280.15 | 0.00115 | 284.65 | 0.15
0.05737 | 280.15 | 0.00115 | 284.65 | 0.2
0.05737 | 280.15 | 0.00115 | 284.65 | 0.3
0.05737 | 280.15 | 0.00115 | 284.65 | 0.4
0.05737 | 280.15 | 0.00115 | 284.65 | 0.5
0.05737 | 280.15 | 0.00115 | 284.65 | 0.6
0.05737 | 280.15 | 0.00115 | 284.65 | 0.7
0.05737 | 280.15 | 0.00115 | 284.65 | 0.8
0.05737 | 280.15 | 0.00115 | 284.65 | 0.9
0.05737 | 280.15 | 0.00115 | 284.65 | 1
0.05737 | 280.15 | 0.00115 | 285.15 | 0.15
0.05737 | 280.15 | 0.00115 | 285.15 | 0.2
0.05737 | 280.15 | 0.00115 | 285.15 | 0.3
0.05737 | 280.15 | 0.00115 | 285.15 | 0.4
0.05737 | 280.15 | 0.00115 | 285.15 | 0.5
0.05737 | 280.15 | 0.00115 | 285.15 | 0.6
0.05737 | 280.15 | 0.00115 | 285.15 | 0.7
0.05737 | 280.15 | 0.00115 | 285.15 | 0.8
0.05737 | 280.15 | 0.00115 | 285.15 | 0.9
0.05737 | 280.15 | 0.00115 | 285.15 | 1
0.05737 | 280.15 | 0.00115 | 285.65 | 0.15
0.05737 | 280.15 | 0.00115 | 285.65 | 0.2
0.05737 | 280.15 | 0.00115 | 285.65 | 0.3
0.05737 | 280.15 | 0.00115 | 285.65 | 0.4
0.05737 | 280.15 | 0.00115 | 285.65 | 0.5
0.05737 | 280.15 | 0.00115 | 285.65 | 0.6
0.05737 | 280.15 | 0.00115 | 285.65 | 0.7
0.05737 | 280.15 | 0.00115 | 285.65 | 0.8
0.05737 | 280.15 | 0.00115 | 285.65 | 0.9
0.05737 | 280.15 | 0.00115 | 285.65 | 1
0.05737 | 280.15 | 0.00115 | 286.15 | 0.15
0.05737 | 280.15 | 0.00115 | 286.15 | 0.2
0.05737 | 280.15 | 0.00115 | 286.15 | 0.3
0.05737 | 280.15 | 0.00115 | 286.15 | 0.4
0.05737 | 280.15 | 0.00115 | 286.15 | 0.5
0.05737 | 280.15 | 0.00115 | 286.15 | 0.6
0.05737 | 280.15 | 0.00115 | 286.15 | 0.7
0.05737 | 280.15 | 0.00115 | 286.15 | 0.8
0.05737 | 280.15 | 0.00115 | 286.15 | 0.9
0.05737 | 280.15 | 0.00115 | 286.15 | 1
0.05737 | 280.15 | 0.00115 | 286.65 | 0.15
0.05737 | 280.15 | 0.00115 | 286.65 | 0.2
0.05737 | 280.15 | 0.00115 | 286.65 | 0.3
0.05737 | 280.15 | 0.00115 | 286.65 | 0.4
0.05737 | 280.15 | 0.00115 | 286.65 | 0.5
0.05737 | 280.15 | 0.00115 | 286.65 | 0.6
0.05737 | 280.15 | 0.00115 | 286.65 | 0.7
0.05737 | 280.15 | 0.00115 | 286.65 | 0.8
0.05737 | 280.15 | 0.00115 | 286.65 | 0.9
0.05737 | 280.15 | 0.00115 | 286.65 | 1
0.05737 | 280.15 | 0.00115 | 287.15 | 0.15
0.05737 | 280.15 | 0.00115 | 287.15 | 0.2
0.05737 | 280.15 | 0.00115 | 287.15 | 0.3
0.05737 | 280.15 | 0.00115 | 287.15 | 0.4
0.05737 | 280.15 | 0.00115 | 287.15 | 0.5
0.05737 | 280.15 | 0.00115 | 287.15 | 0.6
0.05737 | 280.15 | 0.00115 | 287.15 | 0.7
0.05737 | 280.15 | 0.00115 | 287.15 | 0.8
0.05737 | 280.15 | 0.00115 | 287.15 | 0.9
0.05737 | 280.15 | 0.00115 | 287.15 | 1
0.05737 | 280.15 | 0.00115 | 287.65 | 0.15
0.05737 | 280.15 | 0.00115 | 287.65 | 0.2
0.05737 | 280.15 | 0.00115 | 287.65 | 0.3
0.05737 | 280.15 | 0.00115 | 287.65 | 0.4
0.05737 | 280.15 | 0.00115 | 287.65 | 0.5
0.05737 | 280.15 | 0.00115 | 287.65 | 0.6
0.05737 | 280.15 | 0.00115 | 287.65 | 0.7
0.05737 | 280.15 | 0.00115 | 287.65 | 0.8
0.05737 | 280.15 | 0.00115 | 287.65 | 0.9
0.05737 | 280.15 | 0.00115 | 287.65 | 1
0.05737 | 280.15 | 0.00115 | 288.15 | 0.15
0.05737 | 280.15 | 0.00115 | 288.15 | 0.2
0.05737 | 280.15 | 0.00115 | 288.15 | 0.3
0.05737 | 280.15 | 0.00115 | 288.15 | 0.4
0.05737 | 280.15 | 0.00115 | 288.15 | 0.5
0.05737 | 280.15 | 0.00115 | 288.15 | 0.6
0.05737 | 280.15 | 0.00115 | 288.15 | 0.7
0.05737 | 280.15 | 0.00115 | 288.15 | 0.8
0.05737 | 280.15 | 0.00115 | 288.15 | 0.9
0.05737 | 280.15 | 0.00115 | 288.15 | 1
0.05737 | 280.15 | 0.00115 | 288.65 | 0.15
0.05737 | 280.15 | 0.00115 | 288.65 | 0.2
0.05737 | 280.15 | 0.00115 | 288.65 | 0.3
0.05737 | 280.15 | 0.00115 | 288.65 | 0.4
0.05737 | 280.15 | 0.00115 | 288.65 | 0.5
0.05737 | 280.15 | 0.00115 | 288.65 | 0.6
0.05737 | 280.15 | 0.00115 | 288.65 | 0.7
0.05737 | 280.15 | 0.00115 | 288.65 | 0.8
0.05737 | 280.15 | 0.00115 | 288.65 | 0.9
0.05737 | 280.15 | 0.00115 | 288.65 | 1
0.05737 | 280.15 | 0.00115 | 289.15 | 0.15
0.05737 | 280.15 | 0.00115 | 289.15 | 0.2
0.05737 | 280.15 | 0.00115 | 289.15 | 0.3
0.05737 | 280.15 | 0.00115 | 289.15 | 0.4
0.05737 | 280.15 | 0.00115 | 289.15 | 0.5
0.05737 | 280.15 | 0.00115 | 289.15 | 0.6
0.05737 | 280.15 | 0.00115 | 289.15 | 0.7
0.05737 | 280.15 | 0.00115 | 289.15 | 0.8
0.05737 | 280.15 | 0.00115 | 289.15 | 0.9
0.05737 | 280.15 | 0.00115 | 289.15 | 1
0.05737 | 280.15 | 0.00115 | 289.65 | 0.15
0.05737 | 280.15 | 0.00115 | 289.65 | 0.2
0.05737 | 280.15 | 0.00115 | 289.65 | 0.3
0.05737 | 280.15 | 0.00115 | 289.65 | 0.4
0.05737 | 280.15 | 0.00115 | 289.65 | 0.5
0.05737 | 280.15 | 0.00115 | 289.65 | 0.6
0.05737 | 280.15 | 0.00115 | 289.65 | 0.7
0.05737 | 280.15 | 0.00115 | 289.65 | 0.8
0.05737 | 280.15 | 0.00115 | 289.65 | 0.9
0.05737 | 280.15 | 0.00115 | 289.65 | 1
0.05737 | 280.15 | 0.00115 | 290.15 | 0.15
0.05737 | 280.15 | 0.00115 | 290.15 | 0.2
0.05737 | 280.15 | 0.00115 | 290.15 | 0.3
0.05737 | 280.15 | 0.00115 | 290.15 | 0.4
0.05737 | 280.15 | 0.00115 | 290.15 | 0.5
0.05737 | 280.15 | 0.00115 | 290.15 | 0.6
0.05737 | 280.15 | 0.00115 | 290.15 | 0.7
0.05737 | 280.15 | 0.00115 | 290.15 | 0.8
0.05737 | 280.15 | 0.00115 | 290.15 | 0.9
0.05737 | 280.15 | 0.00115 | 290.15 | 1
0.05737 | 280.15 | 0.00115 | 290.65 | 0.15
0.05737 | 280.15 | 0.00115 | 290.65 | 0.2
0.05737 | 280.15 | 0.00115 | 290.65 | 0.3
0.05737 | 280.15 | 0.00115 | 290.65 | 0.4
0.05737 | 280.15 | 0.00115 | 290.65 | 0.5
0.05737 | 280.15 | 0.00115 | 290.65 | 0.6
0.05737 | 280.15 | 0.00115 | 290.65 | 0.7
0.05737 | 280.15 | 0.00115 | 290.65 | 0.8
0.05737 | 280.15 | 0.00115 | 290.65 | 0.9
0.05737 | 280.15 | 0.00115 | 290.65 | 1
0.05737 | 280.15 | 0.00115 | 291.15 | 0.15
0.05737 | 280.15 | 0.00115 | 291.15 | 0.2
0.05737 | 280.15 | 0.00115 | 291.15 | 0.3
0.05737 | 280.15 | 0.00115 | 291.15 | 0.4
0.05737 | 280.15 | 0.00115 | 291.15 | 0.5
0.05737 | 280.15 | 0.00115 | 291.15 | 0.6
0.05737 | 280.15 | 0.00115 | 291.15 | 0.7
0.05737 | 280.15 | 0.00115 | 291.15 | 0.8
0.05737 | 280.15 | 0.00115 | 291.15 | 0.9
0.05737 | 280.15 | 0.00115 | 291.15 | 1
0.05737 | 280.15 | 0.00115 | 294.15 | 0.15
0.05737 | 280.15 | 0.00115 | 294.15 | 0.2
0.05737 | 280.15 | 0.00115 | 294.15 | 0.3
0.05737 | 280.15 | 0.00115 | 294.15 | 0.4
0.05737 | 280.15 | 0.00115 | 294.15 | 0.5
0.05737 | 280.15 | 0.00115 | 294.15 | 0.6
0.05737 | 280.15 | 0.00115 | 294.15 | 0.7
0.05737 | 280.15 | 0.00115 | 294.15 | 0.8
0.05737 | 280.15 | 0.00115 | 294.15 | 0.9
0.05737 | 280.15 | 0.00115 | 294.15 | 1
0.05737 | 280.15 | 0.00115 | 297.15 | 0.15
0.05737 | 280.15 | 0.00115 | 297.15 | 0.2
0.05737 | 280.15 | 0.00115 | 297.15 | 0.3
0.05737 | 280.15 | 0.00115 | 297.15 | 0.4
0.05737 | 280.15 | 0.00115 | 297.15 | 0.5
0.05737 | 280.15 | 0.00115 | 297.15 | 0.6
0.05737 | 280.15 | 0.00115 | 297.15 | 0.7
0.05737 | 280.15 | 0.00115 | 297.15 | 0.8
0.05737 | 280.15 | 0.00115 | 297.15 | 0.9
0.05737 | 280.15 | 0.00115 | 297.15 | 1
0.05737 | 280.15 | 0.00115 | 300.15 | 0.15
0.05737 | 280.15 | 0.00115 | 300.15 | 0.2
0.05737 | 280.15 | 0.00115 | 300.15 | 0.3
0.05737 | 280.15 | 0.00115 | 300.15 | 0.4
0.05737 | 280.15 | 0.00115 | 300.15 | 0.5
0.05737 | 280.15 | 0.00115 | 300.15 | 0.6
0.05737 | 280.15 | 0.00115 | 300.15 | 0.7
0.05737 | 280.15 | 0.00115 | 300.15 | 0.8
0.05737 | 280.15 | 0.00115 | 300.15 | 0.9
0.05737 | 280.15 | 0.00115 | 300.15 | 1
0.05737 | 280.15 | 0.00115 | 303.15 | 0.15
0.05737 | 280.15 | 0.00115 | 303.15 | 0.2
0.05737 | 280.15 | 0.00115 | 303.15 | 0.3
0.05737 | 280.15 | 0.00115 | 303.15 | 0.4
0.05737 | 280.15 | 0.00115 | 303.15 | 0.5
0.05737 | 280.15 | 0.00115 | 303.15 | 0.6
0.05737 | 280.15 | 0.00115 | 303.15 | 0.7
0.05737 | 280.15 | 0.00115 | 303.15 | 0.8
0.05737 | 280.15 | 0.00115 | 303.15 | 0.9
0.05737 | 280.15 | 0.00115 | 303.15 | 1
0.05737 | 280.15 | 0.077 | 283.65 | 0.15
0.05737 | 280.15 | 0.077 | 283.65 | 0.2
0.05737 | 280.15 | 0.077 | 283.65 | 0.3
0.05737 | 280.15 | 0.077 | 283.65 | 0.4
0.05737 | 280.15 | 0.077 | 283.65 | 0.5
0.05737 | 280.15 | 0.077 | 283.65 | 0.6
0.05737 | 280.15 | 0.077 | 283.65 | 0.7
0.05737 | 280.15 | 0.077 | 283.65 | 0.8
0.05737 | 280.15 | 0.077 | 283.65 | 0.9
0.05737 | 280.15 | 0.077 | 283.65 | 1
0.05737 | 280.15 | 0.077 | 284.15 | 0.15
0.05737 | 280.15 | 0.077 | 284.15 | 0.2
0.05737 | 280.15 | 0.077 | 284.15 | 0.3
0.05737 | 280.15 | 0.077 | 284.15 | 0.4
0.05737 | 280.15 | 0.077 | 284.15 | 0.5
0.05737 | 280.15 | 0.077 | 284.15 | 0.6
0.05737 | 280.15 | 0.077 | 284.15 | 0.7
0.05737 | 280.15 | 0.077 | 284.15 | 0.8
0.05737 | 280.15 | 0.077 | 284.15 | 0.9
0.05737 | 280.15 | 0.077 | 284.15 | 1
0.05737 | 280.15 | 0.077 | 284.65 | 0.15
0.05737 | 280.15 | 0.077 | 284.65 | 0.2
0.05737 | 280.15 | 0.077 | 284.65 | 0.3
0.05737 | 280.15 | 0.077 | 284.65 | 0.4
0.05737 | 280.15 | 0.077 | 284.65 | 0.5
0.05737 | 280.15 | 0.077 | 284.65 | 0.6
0.05737 | 280.15 | 0.077 | 284.65 | 0.7
0.05737 | 280.15 | 0.077 | 284.65 | 0.8
0.05737 | 280.15 | 0.077 | 284.65 | 0.9
0.05737 | 280.15 | 0.077 | 284.65 | 1
0.05737 | 280.15 | 0.077 | 285.15 | 0.15
0.05737 | 280.15 | 0.077 | 285.15 | 0.2
0.05737 | 280.15 | 0.077 | 285.15 | 0.3
0.05737 | 280.15 | 0.077 | 285.15 | 0.4
0.05737 | 280.15 | 0.077 | 285.15 | 0.5
0.05737 | 280.15 | 0.077 | 285.15 | 0.6
0.05737 | 280.15 | 0.077 | 285.15 | 0.7
0.05737 | 280.15 | 0.077 | 285.15 | 0.8
0.05737 | 280.15 | 0.077 | 285.15 | 0.9
0.05737 | 280.15 | 0.077 | 285.15 | 1
0.05737 | 280.15 | 0.077 | 285.65 | 0.15
0.05737 | 280.15 | 0.077 | 285.65 | 0.2
0.05737 | 280.15 | 0.077 | 285.65 | 0.3
0.05737 | 280.15 | 0.077 | 285.65 | 0.4
0.05737 | 280.15 | 0.077 | 285.65 | 0.5
0.05737 | 280.15 | 0.077 | 285.65 | 0.6
0.05737 | 280.15 | 0.077 | 285.65 | 0.7
0.05737 | 280.15 | 0.077 | 285.65 | 0.8
0.05737 | 280.15 | 0.077 | 285.65 | 0.9
0.05737 | 280.15 | 0.077 | 285.65 | 1
0.05737 | 280.15 | 0.077 | 286.15 | 0.15
0.05737 | 280.15 | 0.077 | 286.15 | 0.2
0.05737 | 280.15 | 0.077 | 286.15 | 0.3
0.05737 | 280.15 | 0.077 | 286.15 | 0.4
0.05737 | 280.15 | 0.077 | 286.15 | 0.5
0.05737 | 280.15 | 0.077 | 286.15 | 0.6
0.05737 | 280.15 | 0.077 | 286.15 | 0.7
0.05737 | 280.15 | 0.077 | 286.15 | 0.8
0.05737 | 280.15 | 0.077 | 286.15 | 0.9
0.05737 | 280.15 | 0.077 | 286.15 | 1
0.05737 | 280.15 | 0.077 | 286.65 | 0.15
0.05737 | 280.15 | 0.077 | 286.65 | 0.2
0.05737 | 280.15 | 0.077 | 286.65 | 0.3
0.05737 | 280.15 | 0.077 | 286.65 | 0.4
0.05737 | 280.15 | 0.077 | 286.65 | 0.5
0.05737 | 280.15 | 0.077 | 286.65 | 0.6
0.05737 | 280.15 | 0.077 | 286.65 | 0.7
0.05737 | 280.15 | 0.077 | 286.65 | 0.8
0.05737 | 280.15 | 0.077 | 286.65 | 0.9
0.05737 | 280.15 | 0.077 | 286.65 | 1
0.05737 | 280.15 | 0.077 | 287.15 | 0.15
0.05737 | 280.15 | 0.077 | 287.15 | 0.2
0.05737 | 280.15 | 0.077 | 287.15 | 0.3
0.05737 | 280.15 | 0.077 | 287.15 | 0.4
0.05737 | 280.15 | 0.077 | 287.15 | 0.5
0.05737 | 280.15 | 0.077 | 287.15 | 0.6
0.05737 | 280.15 | 0.077 | 287.15 | 0.7
0.05737 | 280.15 | 0.077 | 287.15 | 0.8
0.05737 | 280.15 | 0.077 | 287.15 | 0.9
0.05737 | 280.15 | 0.077 | 287.15 | 1
0.05737 | 280.15 | 0.077 | 287.65 | 0.15
0.05737 | 280.15 | 0.077 | 287.65 | 0.2
0.05737 | 280.15 | 0.077 | 287.65 | 0.3
0.05737 | 280.15 | 0.077 | 287.65 | 0.4
0.05737 | 280.15 | 0.077 | 287.65 | 0.5
0.05737 | 280.15 | 0.077 | 287.65 | 0.6
0.05737 | 280.15 | 0.077 | 287.65 | 0.7
0.05737 | 280.15 | 0.077 | 287.65 | 0.8
0.05737 | 280.15 | 0.077 | 287.65 | 0.9
0.05737 | 280.15 | 0.077 | 287.65 | 1
0.05737 | 280.15 | 0.077 | 288.15 | 0.15
0.05737 | 280.15 | 0.077 | 288.15 | 0.2
0.05737 | 280.15 | 0.077 | 288.15 | 0.3
0.05737 | 280.15 | 0.077 | 288.15 | 0.4
0.05737 | 280.15 | 0.077 | 288.15 | 0.5
0.05737 | 280.15 | 0.077 | 288.15 | 0.6
0.05737 | 280.15 | 0.077 | 288.15 | 0.7
0.05737 | 280.15 | 0.077 | 288.15 | 0.8
0.05737 | 280.15 | 0.077 | 288.15 | 0.9
0.05737 | 280.15 | 0.077 | 288.15 | 1
0.05737 | 280.15 | 0.077 | 288.65 | 0.15
0.05737 | 280.15 | 0.077 | 288.65 | 0.2
0.05737 | 280.15 | 0.077 | 288.65 | 0.3
0.05737 | 280.15 | 0.077 | 288.65 | 0.4
0.05737 | 280.15 | 0.077 | 288.65 | 0.5
0.05737 | 280.15 | 0.077 | 288.65 | 0.6
0.05737 | 280.15 | 0.077 | 288.65 | 0.7
0.05737 | 280.15 | 0.077 | 288.65 | 0.8
0.05737 | 280.15 | 0.077 | 288.65 | 0.9
0.05737 | 280.15 | 0.077 | 288.65 | 1
0.05737 | 280.15 | 0.077 | 289.15 | 0.15
0.05737 | 280.15 | 0.077 | 289.15 | 0.2
0.05737 | 280.15 | 0.077 | 289.15 | 0.3
0.05737 | 280.15 | 0.077 | 289.15 | 0.4
0.05737 | 280.15 | 0.077 | 289.15 | 0.5
0.05737 | 280.15 | 0.077 | 289.15 | 0.6
0.05737 | 280.15 | 0.077 | 289.15 | 0.7
0.05737 | 280.15 | 0.077 | 289.15 | 0.8
0.05737 | 280.15 | 0.077 | 289.15 | 0.9
0.05737 | 280.15 | 0.077 | 289.15 | 1
0.05737 | 280.15 | 0.077 | 289.65 | 0.15
0.05737 | 280.15 | 0.077 | 289.65 | 0.2
0.05737 | 280.15 | 0.077 | 289.65 | 0.3
0.05737 | 280.15 | 0.077 | 289.65 | 0.4
0.05737 | 280.15 | 0.077 | 289.65 | 0.5
0.05737 | 280.15 | 0.077 | 289.65 | 0.6
0.05737 | 280.15 | 0.077 | 289.65 | 0.7
0.05737 | 280.15 | 0.077 | 289.65 | 0.8
0.05737 | 280.15 | 0.077 | 289.65 | 0.9
0.05737 | 280.15 | 0.077 | 289.65 | 1
0.05737 | 280.15 | 0.077 | 290.15 | 0.15
0.05737 | 280.15 | 0.077 | 290.15 | 0.2
0.05737 | 280.15 | 0.077 | 290.15 | 0.3
0.05737 | 280.15 | 0.077 | 290.15 | 0.4
0.05737 | 280.15 | 0.077 | 290.15 | 0.5
0.05737 | 280.15 | 0.077 | 290.15 | 0.6
0.05737 | 280.15 | 0.077 | 290.15 | 0.7
0.05737 | 280.15 | 0.077 | 290.15 | 0.8
0.05737 | 280.15 | 0.077 | 290.15 | 0.9
0.05737 | 280.15 | 0.077 | 290.15 | 1
0.05737 | 280.15 | 0.077 | 290.65 | 0.15
0.05737 | 280.15 | 0.077 | 290.65 | 0.2
0.05737 | 280.15 | 0.077 | 290.65 | 0.3
0.05737 | 280.15 | 0.077 | 290.65 | 0.4
0.05737 | 280.15 | 0.077 | 290.65 | 0.5
0.05737 | 280.15 | 0.077 | 290.65 | 0.6
0.05737 | 280.15 | 0.077 | 290.65 | 0.7
0.05737 | 280.15 | 0.077 | 290.65 | 0.8
0.05737 | 280.15 | 0.077 | 290.65 | 0.9
0.05737 | 280.15 | 0.077 | 290.65 | 1
0.05737 | 280.15 | 0.077 | 291.15 | 0.15
0.05737 | 280.15 | 0.077 | 291.15 | 0.2
0.05737 | 280.15 | 0.077 | 291.15 | 0.3
0.05737 | 280.15 | 0.077 | 291.15 | 0.4
0.05737 | 280.15 | 0.077 | 291.15 | 0.5
0.05737 | 280.15 | 0.077 | 291.15 | 0.6
0.05737 | 280.15 | 0.077 | 291.15 | 0.7
0.05737 | 280.15 | 0.077 | 291.15 | 0.8
0.05737 | 280.15 | 0.077 | 291.15 | 0.9
0.05737 | 280.15 | 0.077 | 291.15 | 1
0.05737 | 280.15 | 0.077 | 294.15 | 0.15
0.05737 | 280.15 | 0.077 | 294.15 | 0.2
0.05737 | 280.15 | 0.077 | 294.15 | 0.3
0.05737 | 280.15 | 0.077 | 294.15 | 0.4
0.05737 | 280.15 | 0.077 | 294.15 | 0.5
0.05737 | 280.15 | 0.077 | 294.15 | 0.6
0.05737 | 280.15 | 0.077 | 294.15 | 0.7
0.05737 | 280.15 | 0.077 | 294.15 | 0.8
0.05737 | 280.15 | 0.077 | 294.15 | 0.9
0.05737 | 280.15 | 0.077 | 294.15 | 1
0.05737 | 280.15 | 0.077 | 297.15 | 0.15
0.05737 | 280.15 | 0.077 | 297.15 | 0.2
0.05737 | 280.15 | 0.077 | 297.15 | 0.3
0.05737 | 280.15 | 0.077 | 297.15 | 0.4
0.05737 | 280.15 | 0.077 | 297.15 | 0.5
0.05737 | 280.15 | 0.077 | 297.15 | 0.6
0.05737 | 280.15 | 0.077 | 297.15 | 0.7
0.05737 | 280.15 | 0.077 | 297.15 | 0.8
0.05737 | 280.15 | 0.077 | 297.15 | 0.9
0.05737 | 280.15 | 0.077 | 297.15 | 1
0.05737 | 280.15 | 0.077 | 300.15 | 0.15
0.05737 | 280.15 | 0.077 | 300.15 | 0.2
0.05737 | 280.15 | 0.077 | 300.15 | 0.3
0.05737 | 280.15 | 0.077 | 300.15 | 0.4
0.05737 | 280.15 | 0.077 | 300.15 | 0.5
0.05737 | 280.15 | 0.077 | 300.15 | 0.6
0.05737 | 280.15 | 0.077 | 300.15 | 0.7
0.05737 | 280.15 | 0.077 | 300.15 | 0.8
0.05737 | 280.15 | 0.077 | 300.15 | 0.9
0.05737 | 280.15 | 0.077 | 300.15 | 1
0.05737 | 280.15 | 0.077 | 303.15 | 0.15
0.05737 | 280.15 | 0.077 | 303.15 | 0.2
0.05737 | 280.15 | 0.077 | 303.15 | 0.3
0.05737 | 280.15 | 0.077 | 303.15 | 0.4
0.05737 | 280.15 | 0.077 | 303.15 | 0.5
0.05737 | 280.15 | 0.077 | 303.15 | 0.6
0.05737 | 280.15 | 0.077 | 303.15 | 0.7
0.05737 | 280.15 | 0.077 | 303.15 | 0.8
0.05737 | 280.15 | 0.077 | 303.15 | 0.9
0.05737 | 280.15 | 0.077 | 303.15 | 1
0.05737 | 280.15 | 0.09437 | 283.65 | 0.15
0.05737 | 280.15 | 0.09437 | 283.65 | 0.2
0.05737 | 280.15 | 0.09437 | 283.65 | 0.3
0.05737 | 280.15 | 0.09437 | 283.65 | 0.4
0.05737 | 280.15 | 0.09437 | 283.65 | 0.5
0.05737 | 280.15 | 0.09437 | 283.65 | 0.6
0.05737 | 280.15 | 0.09437 | 283.65 | 0.7
0.05737 | 280.15 | 0.09437 | 283.65 | 0.8
0.05737 | 280.15 | 0.09437 | 283.65 | 0.9
0.05737 | 280.15 | 0.09437 | 283.65 | 1
0.05737 | 280.15 | 0.09437 | 284.15 | 0.15
0.05737 | 280.15 | 0.09437 | 284.15 | 0.2
0.05737 | 280.15 | 0.09437 | 284.15 | 0.3
0.05737 | 280.15 | 0.09437 | 284.15 | 0.4
0.05737 | 280.15 | 0.09437 | 284.15 | 0.5
0.05737 | 280.15 | 0.09437 | 284.15 | 0.6
0.05737 | 280.15 | 0.09437 | 284.15 | 0.7
0.05737 | 280.15 | 0.09437 | 284.15 | 0.8
0.05737 | 280.15 | 0.09437 | 284.15 | 0.9
0.05737 | 280.15 | 0.09437 | 284.15 | 1
0.05737 | 280.15 | 0.09437 | 284.65 | 0.15
0.05737 | 280.15 | 0.09437 | 284.65 | 0.2
0.05737 | 280.15 | 0.09437 | 284.65 | 0.3
0.05737 | 280.15 | 0.09437 | 284.65 | 0.4
0.05737 | 280.15 | 0.09437 | 284.65 | 0.5
0.05737 | 280.15 | 0.09437 | 284.65 | 0.6
0.05737 | 280.15 | 0.09437 | 284.65 | 0.7
0.05737 | 280.15 | 0.09437 | 284.65 | 0.8
0.05737 | 280.15 | 0.09437 | 284.65 | 0.9
0.05737 | 280.15 | 0.09437 | 284.65 | 1
0.05737 | 280.15 | 0.09437 | 285.15 | 0.15
0.05737 | 280.15 | 0.09437 | 285.15 | 0.2
0.05737 | 280.15 | 0.09437 | 285.15 | 0.3
0.05737 | 280.15 | 0.09437 | 285.15 | 0.4
0.05737 | 280.15 | 0.09437 | 285.15 | 0.5
0.05737 | 280.15 | 0.09437 | 285.15 | 0.6
0.05737 | 280.15 | 0.09437 | 285.15 | 0.7
0.05737 | 280.15 | 0.09437 | 285.15 | 0.8
0.05737 | 280.15 | 0.09437 | 285.15 | 0.9
0.05737 | 280.15 | 0.09437 | 285.15 | 1
0.05737 | 280.15 | 0.09437 | 285.65 | 0.15
0.05737 | 280.15 | 0.09437 | 285.65 | 0.2
0.05737 | 280.15 | 0.09437 | 285.65 | 0.3
0.05737 | 280.15 | 0.09437 | 285.65 | 0.4
0.05737 | 280.15 | 0.09437 | 285.65 | 0.5
0.05737 | 280.15 | 0.09437 | 285.65 | 0.6
0.05737 | 280.15 | 0.09437 | 285.65 | 0.7
0.05737 | 280.15 | 0.09437 | 285.65 | 0.8
0.05737 | 280.15 | 0.09437 | 285.65 | 0.9
0.05737 | 280.15 | 0.09437 | 285.65 | 1
0.05737 | 280.15 | 0.09437 | 286.15 | 0.15
0.05737 | 280.15 | 0.09437 | 286.15 | 0.2
0.05737 | 280.15 | 0.09437 | 286.15 | 0.3
0.05737 | 280.15 | 0.09437 | 286.15 | 0.4
0.05737 | 280.15 | 0.09437 | 286.15 | 0.5
0.05737 | 280.15 | 0.09437 | 286.15 | 0.6
0.05737 | 280.15 | 0.09437 | 286.15 | 0.7
0.05737 | 280.15 | 0.09437 | 286.15 | 0.8
0.05737 | 280.15 | 0.09437 | 286.15 | 0.9
0.05737 | 280.15 | 0.09437 | 286.15 | 1
0.05737 | 280.15 | 0.09437 | 286.65 | 0.15
0.05737 | 280.15 | 0.09437 | 286.65 | 0.2
0.05737 | 280.15 | 0.09437 | 286.65 | 0.3
0.05737 | 280.15 | 0.09437 | 286.65 | 0.4
0.05737 | 280.15 | 0.09437 | 286.65 | 0.5
0.05737 | 280.15 | 0.09437 | 286.65 | 0.6
0.05737 | 280.15 | 0.09437 | 286.65 | 0.7
0.05737 | 280.15 | 0.09437 | 286.65 | 0.8
0.05737 | 280.15 | 0.09437 | 286.65 | 0.9
0.05737 | 280.15 | 0.09437 | 286.65 | 1
0.05737 | 280.15 | 0.09437 | 287.15 | 0.15
0.05737 | 280.15 | 0.09437 | 287.15 | 0.2
0.05737 | 280.15 | 0.09437 | 287.15 | 0.3
0.05737 | 280.15 | 0.09437 | 287.15 | 0.4
0.05737 | 280.15 | 0.09437 | 287.15 | 0.5
0.05737 | 280.15 | 0.09437 | 287.15 | 0.6
0.05737 | 280.15 | 0.09437 | 287.15 | 0.7
0.05737 | 280.15 | 0.09437 | 287.15 | 0.8
0.05737 | 280.15 | 0.09437 | 287.15 | 0.9
0.05737 | 280.15 | 0.09437 | 287.15 | 1
0.05737 | 280.15 | 0.09437 | 287.65 | 0.15
0.05737 | 280.15 | 0.09437 | 287.65 | 0.2
0.05737 | 280.15 | 0.09437 | 287.65 | 0.3
0.05737 | 280.15 | 0.09437 | 287.65 | 0.4
0.05737 | 280.15 | 0.09437 | 287.65 | 0.5
0.05737 | 280.15 | 0.09437 | 287.65 | 0.6
0.05737 | 280.15 | 0.09437 | 287.65 | 0.7
0.05737 | 280.15 | 0.09437 | 287.65 | 0.8
0.05737 | 280.15 | 0.09437 | 287.65 | 0.9
0.05737 | 280.15 | 0.09437 | 287.65 | 1
0.05737 | 280.15 | 0.09437 | 288.15 | 0.15
0.05737 | 280.15 | 0.09437 | 288.15 | 0.2
0.05737 | 280.15 | 0.09437 | 288.15 | 0.3
0.05737 | 280.15 | 0.09437 | 288.15 | 0.4
0.05737 | 280.15 | 0.09437 | 288.15 | 0.5
0.05737 | 280.15 | 0.09437 | 288.15 | 0.6
0.05737 | 280.15 | 0.09437 | 288.15 | 0.7
0.05737 | 280.15 | 0.09437 | 288.15 | 0.8
0.05737 | 280.15 | 0.09437 | 288.15 | 0.9
0.05737 | 280.15 | 0.09437 | 288.15 | 1
0.05737 | 280.15 | 0.09437 | 288.65 | 0.15
0.05737 | 280.15 | 0.09437 | 288.65 | 0.2
0.05737 | 280.15 | 0.09437 | 288.65 | 0.3
0.05737 | 280.15 | 0.09437 | 288.65 | 0.4
0.05737 | 280.15 | 0.09437 | 288.65 | 0.5
0.05737 | 280.15 | 0.09437 | 288.65 | 0.6
0.05737 | 280.15 | 0.09437 | 288.65 | 0.7
0.05737 | 280.15 | 0.09437 | 288.65 | 0.8
0.05737 | 280.15 | 0.09437 | 288.65 | 0.9
0.05737 | 280.15 | 0.09437 | 288.65 | 1
0.05737 | 280.15 | 0.09437 | 289.15 | 0.15
0.05737 | 280.15 | 0.09437 | 289.15 | 0.2
0.05737 | 280.15 | 0.09437 | 289.15 | 0.3
0.05737 | 280.15 | 0.09437 | 289.15 | 0.4
0.05737 | 280.15 | 0.09437 | 289.15 | 0.5
0.05737 | 280.15 | 0.09437 | 289.15 | 0.6
0.05737 | 280.15 | 0.09437 | 289.15 | 0.7
0.05737 | 280.15 | 0.09437 | 289.15 | 0.8
0.05737 | 280.15 | 0.09437 | 289.15 | 0.9
0.05737 | 280.15 | 0.09437 | 289.15 | 1
0.05737 | 280.15 | 0.09437 | 289.65 | 0.15
0.05737 | 280.15 | 0.09437 | 289.65 | 0.2
0.05737 | 280.15 | 0.09437 | 289.65 | 0.3
0.05737 | 280.15 | 0.09437 | 289.65 | 0.4
0.05737 | 280.15 | 0.09437 | 289.65 | 0.5
0.05737 | 280.15 | 0.09437 | 289.65 | 0.6
0.05737 | 280.15 | 0.09437 | 289.65 | 0.7
0.05737 | 280.15 | 0.09437 | 289.65 | 0.8
0.05737 | 280.15 | 0.09437 | 289.65 | 0.9
0.05737 | 280.15 | 0.09437 | 289.65 | 1
0.05737 | 280.15 | 0.09437 | 290.15 | 0.15
0.05737 | 280.15 | 0.09437 | 290.15 | 0.2
0.05737 | 280.15 | 0.09437 | 290.15 | 0.3
0.05737 | 280.15 | 0.09437 | 290.15 | 0.4
0.05737 | 280.15 | 0.09437 | 290.15 | 0.5
0.05737 | 280.15 | 0.09437 | 290.15 | 0.6
0.05737 | 280.15 | 0.09437 | 290.15 | 0.7
0.05737 | 280.15 | 0.09437 | 290.15 | 0.8
0.05737 | 280.15 | 0.09437 | 290.15 | 0.9
0.05737 | 280.15 | 0.09437 | 290.15 | 1
0.05737 | 280.15 | 0.09437 | 290.65 | 0.15
0.05737 | 280.15 | 0.09437 | 290.65 | 0.2
0.05737 | 280.15 | 0.09437 | 290.65 | 0.3
0.05737 | 280.15 | 0.09437 | 290.65 | 0.4
0.05737 | 280.15 | 0.09437 | 290.65 | 0.5
0.05737 | 280.15 | 0.09437 | 290.65 | 0.6
0.05737 | 280.15 | 0.09437 | 290.65 | 0.7
0.05737 | 280.15 | 0.09437 | 290.65 | 0.8
0.05737 | 280.15 | 0.09437 | 290.65 | 0.9
0.05737 | 280.15 | 0.09437 | 290.65 | 1
0.05737 | 280.15 | 0.09437 | 291.15 | 0.15
0.05737 | 280.15 | 0.09437 | 291.15 | 0.2
0.05737 | 280.15 | 0.09437 | 291.15 | 0.3
0.05737 | 280.15 | 0.09437 | 291.15 | 0.4
0.05737 | 280.15 | 0.09437 | 291.15 | 0.5
0.05737 | 280.15 | 0.09437 | 291.15 | 0.6
0.05737 | 280.15 | 0.09437 | 291.15 | 0.7
0.05737 | 280.15 | 0.09437 | 291.15 | 0.8
0.05737 | 280.15 | 0.09437 | 291.15 | 0.9
0.05737 | 280.15 | 0.09437 | 291.15 | 1
0.05737 | 280.15 | 0.09437 | 294.15 | 0.15
0.05737 | 280.15 | 0.09437 | 294.15 | 0.2
0.05737 | 280.15 | 0.09437 | 294.15 | 0.3
0.05737 | 280.15 | 0.09437 | 294.15 | 0.4
0.05737 | 280.15 | 0.09437 | 294.15 | 0.5
0.05737 | 280.15 | 0.09437 | 294.15 | 0.6
0.05737 | 280.15 | 0.09437 | 294.15 | 0.7
0.05737 | 280.15 | 0.09437 | 294.15 | 0.8
0.05737 | 280.15 | 0.09437 | 294.15 | 0.9
0.05737 | 280.15 | 0.09437 | 294.15 | 1
0.05737 | 280.15 | 0.09437 | 297.15 | 0.15
0.05737 | 280.15 | 0.09437 | 297.15 | 0.2
0.05737 | 280.15 | 0.09437 | 297.15 | 0.3
0.05737 | 280.15 | 0.09437 | 297.15 | 0.4
0.05737 | 280.15 | 0.09437 | 297.15 | 0.5
0.05737 | 280.15 | 0.09437 | 297.15 | 0.6
0.05737 | 280.15 | 0.09437 | 297.15 | 0.7
0.05737 | 280.15 | 0.09437 | 297.15 | 0.8
0.05737 | 280.15 | 0.09437 | 297.15 | 0.9
0.05737 | 280.15 | 0.09437 | 297.15 | 1
0.05737 | 280.15 | 0.09437 | 300.15 | 0.15
0.05737 | 280.15 | 0.09437 | 300.15 | 0.2
0.05737 | 280.15 | 0.09437 | 300.15 | 0.3
0.05737 | 280.15 | 0.09437 | 300.15 | 0.4
0.05737 | 280.15 | 0.09437 | 300.15 | 0.5
0.05737 | 280.15 | 0.09437 | 300.15 | 0.6
0.05737 | 280.15 | 0.09437 | 300.15 | 0.7
0.05737 | 280.15 | 0.09437 | 300.15 | 0.8
0.05737 | 280.15 | 0.09437 | 300.15 | 0.9
0.05737 | 280.15 | 0.09437 | 300.15 | 1
0.05737 | 280.15 | 0.09437 | 303.15 | 0.15
0.05737 | 280.15 | 0.09437 | 303.15 | 0.2
0.05737 | 280.15 | 0.09437 | 303.15 | 0.3
0.05737 | 280.15 | 0.09437 | 303.15 | 0.4
0.05737 | 280.15 | 0.09437 | 303.15 | 0.5
0.05737 | 280.15 | 0.09437 | 303.15 | 0.6
0.05737 | 280.15 | 0.09437 | 303.15 | 0.7
0.05737 | 280.15 | 0.09437 | 303.15 | 0.8
0.05737 | 280.15 | 0.09437 | 303.15 | 0.9
0.05737 | 280.15 | 0.09437 | 303.15 | 1
0.05737 | 280.15 | 0.09644 | 283.65 | 0.15
0.05737 | 280.15 | 0.09644 | 283.65 | 0.2
0.05737 | 280.15 | 0.09644 | 283.65 | 0.3
0.05737 | 280.15 | 0.09644 | 283.65 | 0.4
0.05737 | 280.15 | 0.09644 | 283.65 | 0.5
0.05737 | 280.15 | 0.09644 | 283.65 | 0.6
0.05737 | 280.15 | 0.09644 | 283.65 | 0.7
0.05737 | 280.15 | 0.09644 | 283.65 | 0.8
0.05737 | 280.15 | 0.09644 | 283.65 | 0.9
0.05737 | 280.15 | 0.09644 | 283.65 | 1
0.05737 | 280.15 | 0.09644 | 284.15 | 0.15
0.05737 | 280.15 | 0.09644 | 284.15 | 0.2
0.05737 | 280.15 | 0.09644 | 284.15 | 0.3
0.05737 | 280.15 | 0.09644 | 284.15 | 0.4
0.05737 | 280.15 | 0.09644 | 284.15 | 0.5
0.05737 | 280.15 | 0.09644 | 284.15 | 0.6
0.05737 | 280.15 | 0.09644 | 284.15 | 0.7
0.05737 | 280.15 | 0.09644 | 284.15 | 0.8
0.05737 | 280.15 | 0.09644 | 284.15 | 0.9
0.05737 | 280.15 | 0.09644 | 284.15 | 1
0.05737 | 280.15 | 0.09644 | 284.65 | 0.15
0.05737 | 280.15 | 0.09644 | 284.65 | 0.2
0.05737 | 280.15 | 0.09644 | 284.65 | 0.3
0.05737 | 280.15 | 0.09644 | 284.65 | 0.4
0.05737 | 280.15 | 0.09644 | 284.65 | 0.5
0.05737 | 280.15 | 0.09644 | 284.65 | 0.6
0.05737 | 280.15 | 0.09644 | 284.65 | 0.7
0.05737 | 280.15 | 0.09644 | 284.65 | 0.8
0.05737 | 280.15 | 0.09644 | 284.65 | 0.9
0.05737 | 280.15 | 0.09644 | 284.65 | 1
0.05737 | 280.15 | 0.09644 | 285.15 | 0.15
0.05737 | 280.15 | 0.09644 | 285.15 | 0.2
0.05737 | 280.15 | 0.09644 | 285.15 | 0.3
0.05737 | 280.15 | 0.09644 | 285.15 | 0.4
0.05737 | 280.15 | 0.09644 | 285.15 | 0.5
0.05737 | 280.15 | 0.09644 | 285.15 | 0.6
0.05737 | 280.15 | 0.09644 | 285.15 | 0.7
0.05737 | 280.15 | 0.09644 | 285.15 | 0.8
0.05737 | 280.15 | 0.09644 | 285.15 | 0.9
0.05737 | 280.15 | 0.09644 | 285.15 | 1
0.05737 | 280.15 | 0.09644 | 285.65 | 0.15
0.05737 | 280.15 | 0.09644 | 285.65 | 0.2
0.05737 | 280.15 | 0.09644 | 285.65 | 0.3
0.05737 | 280.15 | 0.09644 | 285.65 | 0.4
0.05737 | 280.15 | 0.09644 | 285.65 | 0.5
0.05737 | 280.15 | 0.09644 | 285.65 | 0.6
0.05737 | 280.15 | 0.09644 | 285.65 | 0.7
0.05737 | 280.15 | 0.09644 | 285.65 | 0.8
0.05737 | 280.15 | 0.09644 | 285.65 | 0.9
0.05737 | 280.15 | 0.09644 | 285.65 | 1
0.05737 | 280.15 | 0.09644 | 286.15 | 0.15
0.05737 | 280.15 | 0.09644 | 286.15 | 0.2
0.05737 | 280.15 | 0.09644 | 286.15 | 0.3
0.05737 | 280.15 | 0.09644 | 286.15 | 0.4
0.05737 | 280.15 | 0.09644 | 286.15 | 0.5
0.05737 | 280.15 | 0.09644 | 286.15 | 0.6
0.05737 | 280.15 | 0.09644 | 286.15 | 0.7
0.05737 | 280.15 | 0.09644 | 286.15 | 0.8
0.05737 | 280.15 | 0.09644 | 286.15 | 0.9
0.05737 | 280.15 | 0.09644 | 286.15 | 1
0.05737 | 280.15 | 0.09644 | 286.65 | 0.15
0.05737 | 280.15 | 0.09644 | 286.65 | 0.2
0.05737 | 280.15 | 0.09644 | 286.65 | 0.3
0.05737 | 280.15 | 0.09644 | 286.65 | 0.4
0.05737 | 280.15 | 0.09644 | 286.65 | 0.5
0.05737 | 280.15 | 0.09644 | 286.65 | 0.6
0.05737 | 280.15 | 0.09644 | 286.65 | 0.7
0.05737 | 280.15 | 0.09644 | 286.65 | 0.8
0.05737 | 280.15 | 0.09644 | 286.65 | 0.9
0.05737 | 280.15 | 0.09644 | 286.65 | 1
0.05737 | 280.15 | 0.09644 | 287.15 | 0.15
0.05737 | 280.15 | 0.09644 | 287.15 | 0.2
0.05737 | 280.15 | 0.09644 | 287.15 | 0.3
0.05737 | 280.15 | 0.09644 | 287.15 | 0.4
0.05737 | 280.15 | 0.09644 | 287.15 | 0.5
0.05737 | 280.15 | 0.09644 | 287.15 | 0.6
0.05737 | 280.15 | 0.09644 | 287.15 | 0.7
0.05737 | 280.15 | 0.09644 | 287.15 | 0.8
0.05737 | 280.15 | 0.09644 | 287.15 | 0.9
0.05737 | 280.15 | 0.09644 | 287.15 | 1
0.05737 | 280.15 | 0.09644 | 287.65 | 0.15
0.05737 | 280.15 | 0.09644 | 287.65 | 0.2
0.05737 | 280.15 | 0.09644 | 287.65 | 0.3
0.05737 | 280.15 | 0.09644 | 287.65 | 0.4
0.05737 | 280.15 | 0.09644 | 287.65 | 0.5
0.05737 | 280.15 | 0.09644 | 287.65 | 0.6
0.05737 | 280.15 | 0.09644 | 287.65 | 0.7
0.05737 | 280.15 | 0.09644 | 287.65 | 0.8
0.05737 | 280.15 | 0.09644 | 287.65 | 0.9
0.05737 | 280.15 | 0.09644 | 287.65 | 1
0.05737 | 280.15 | 0.09644 | 288.15 | 0.15
0.05737 | 280.15 | 0.09644 | 288.15 | 0.2
0.05737 | 280.15 | 0.09644 | 288.15 | 0.3
0.05737 | 280.15 | 0.09644 | 288.15 | 0.4
0.05737 | 280.15 | 0.09644 | 288.15 | 0.5
0.05737 | 280.15 | 0.09644 | 288.15 | 0.6
0.05737 | 280.15 | 0.09644 | 288.15 | 0.7
0.05737 | 280.15 | 0.09644 | 288.15 | 0.8
0.05737 | 280.15 | 0.09644 | 288.15 | 0.9
0.05737 | 280.15 | 0.09644 | 288.15 | 1
0.05737 | 280.15 | 0.09644 | 288.65 | 0.15
0.05737 | 280.15 | 0.09644 | 288.65 | 0.2
0.05737 | 280.15 | 0.09644 | 288.65 | 0.3
0.05737 | 280.15 | 0.09644 | 288.65 | 0.4
0.05737 | 280.15 | 0.09644 | 288.65 | 0.5
0.05737 | 280.15 | 0.09644 | 288.65 | 0.6
0.05737 | 280.15 | 0.09644 | 288.65 | 0.7
0.05737 | 280.15 | 0.09644 | 288.65 | 0.8
0.05737 | 280.15 | 0.09644 | 288.65 | 0.9
0.05737 | 280.15 | 0.09644 | 288.65 | 1
0.05737 | 280.15 | 0.09644 | 289.15 | 0.15
0.05737 | 280.15 | 0.09644 | 289.15 | 0.2
0.05737 | 280.15 | 0.09644 | 289.15 | 0.3
0.05737 | 280.15 | 0.09644 | 289.15 | 0.4
0.05737 | 280.15 | 0.09644 | 289.15 | 0.5
0.05737 | 280.15 | 0.09644 | 289.15 | 0.6
0.05737 | 280.15 | 0.09644 | 289.15 | 0.7
0.05737 | 280.15 | 0.09644 | 289.15 | 0.8
0.05737 | 280.15 | 0.09644 | 289.15 | 0.9
0.05737 | 280.15 | 0.09644 | 289.15 | 1
0.05737 | 280.15 | 0.09644 | 289.65 | 0.15
0.05737 | 280.15 | 0.09644 | 289.65 | 0.2
0.05737 | 280.15 | 0.09644 | 289.65 | 0.3
0.05737 | 280.15 | 0.09644 | 289.65 | 0.4
0.05737 | 280.15 | 0.09644 | 289.65 | 0.5
0.05737 | 280.15 | 0.09644 | 289.65 | 0.6
0.05737 | 280.15 | 0.09644 | 289.65 | 0.7
0.05737 | 280.15 | 0.09644 | 289.65 | 0.8
0.05737 | 280.15 | 0.09644 | 289.65 | 0.9
0.05737 | 280.15 | 0.09644 | 289.65 | 1
0.05737 | 280.15 | 0.09644 | 290.15 | 0.15
0.05737 | 280.15 | 0.09644 | 290.15 | 0.2
0.05737 | 280.15 | 0.09644 | 290.15 | 0.3
0.05737 | 280.15 | 0.09644 | 290.15 | 0.4
0.05737 | 280.15 | 0.09644 | 290.15 | 0.5
0.05737 | 280.15 | 0.09644 | 290.15 | 0.6
0.05737 | 280.15 | 0.09644 | 290.15 | 0.7
0.05737 | 280.15 | 0.09644 | 290.15 | 0.8
0.05737 | 280.15 | 0.09644 | 290.15 | 0.9
0.05737 | 280.15 | 0.09644 | 290.15 | 1
0.05737 | 280.15 | 0.09644 | 290.65 | 0.15
0.05737 | 280.15 | 0.09644 | 290.65 | 0.2
0.05737 | 280.15 | 0.09644 | 290.65 | 0.3
0.05737 | 280.15 | 0.09644 | 290.65 | 0.4
0.05737 | 280.15 | 0.09644 | 290.65 | 0.5
0.05737 | 280.15 | 0.09644 | 290.65 | 0.6
0.05737 | 280.15 | 0.09644 | 290.65 | 0.7
0.05737 | 280.15 | 0.09644 | 290.65 | 0.8
0.05737 | 280.15 | 0.09644 | 290.65 | 0.9
0.05737 | 280.15 | 0.09644 | 290.65 | 1
0.05737 | 280.15 | 0.09644 | 291.15 | 0.15
0.05737 | 280.15 | 0.09644 | 291.15 | 0.2
0.05737 | 280.15 | 0.09644 | 291.15 | 0.3
0.05737 | 280.15 | 0.09644 | 291.15 | 0.4
0.05737 | 280.15 | 0.09644 | 291.15 | 0.5
0.05737 | 280.15 | 0.09644 | 291.15 | 0.6
0.05737 | 280.15 | 0.09644 | 291.15 | 0.7
0.05737 | 280.15 | 0.09644 | 291.15 | 0.8
0.05737 | 280.15 | 0.09644 | 291.15 | 0.9
0.05737 | 280.15 | 0.09644 | 291.15 | 1
0.05737 | 280.15 | 0.09644 | 294.15 | 0.15
0.05737 | 280.15 | 0.09644 | 294.15 | 0.2
0.05737 | 280.15 | 0.09644 | 294.15 | 0.3
0.05737 | 280.15 | 0.09644 | 294.15 | 0.4
0.05737 | 280.15 | 0.09644 | 294.15 | 0.5
0.05737 | 280.15 | 0.09644 | 294.15 | 0.6
0.05737 | 280.15 | 0.09644 | 294.15 | 0.7
0.05737 | 280.15 | 0.09644 | 294.15 | 0.8
0.05737 | 280.15 | 0.09644 | 294.15 | 0.9
0.05737 | 280.15 | 0.09644 | 294.15 | 1
0.05737 | 280.15 | 0.09644 | 297.15 | 0.15
0.05737 | 280.15 | 0.09644 | 297.15 | 0.2
0.05737 | 280.15 | 0.09644 | 297.15 | 0.3
0.05737 | 280.15 | 0.09644 | 297.15 | 0.4
0.05737 | 280.15 | 0.09644 | 297.15 | 0.5
0.05737 | 280.15 | 0.09644 | 297.15 | 0.6
0.05737 | 280.15 | 0.09644 | 297.15 | 0.7
0.05737 | 280.15 | 0.09644 | 297.15 | 0.8
0.05737 | 280.15 | 0.09644 | 297.15 | 0.9
0.05737 | 280.15 | 0.09644 | 297.15 | 1
0.05737 | 280.15 | 0.09644 | 300.15 | 0.15
0.05737 | 280.15 | 0.09644 | 300.15 | 0.2
0.05737 | 280.15 | 0.09644 | 300.15 | 0.3
0.05737 | 280.15 | 0.09644 | 300.15 | 0.4
0.05737 | 280.15 | 0.09644 | 300.15 | 0.5
0.05737 | 280.15 | 0.09644 | 300.15 | 0.6
0.05737 | 280.15 | 0.09644 | 300.15 | 0.7
0.05737 | 280.15 | 0.09644 | 300.15 | 0.8
0.05737 | 280.15 | 0.09644 | 300.15 | 0.9
0.05737 | 280.15 | 0.09644 | 300.15 | 1
0.05737 | 280.15 | 0.09644 | 303.15 | 0.15
0.05737 | 280.15 | 0.09644 | 303.15 | 0.2
0.05737 | 280.15 | 0.09644 | 303.15 | 0.3
0.05737 | 280.15 | 0.09644 | 303.15 | 0.4
0.05737 | 280.15 | 0.09644 | 303.15 | 0.5
0.05737 | 280.15 | 0.09644 | 303.15 | 0.6
0.05737 | 280.15 | 0.09644 | 303.15 | 0.7
0.05737 | 280.15 | 0.09644 | 303.15 | 0.8
0.05737 | 280.15 | 0.09644 | 303.15 | 0.9
0.05737 | 280.15 | 0.09644 | 303.15 | 1
0.05737 | 280.15 | 0.09737 | 283.65 | 0.15
0.05737 | 280.15 | 0.09737 | 283.65 | 0.2
0.05737 | 280.15 | 0.09737 | 283.65 | 0.3
0.05737 | 280.15 | 0.09737 | 283.65 | 0.4
0.05737 | 280.15 | 0.09737 | 283.65 | 0.5
0.05737 | 280.15 | 0.09737 | 283.65 | 0.6
0.05737 | 280.15 | 0.09737 | 283.65 | 0.7
0.05737 | 280.15 | 0.09737 | 283.65 | 0.8
0.05737 | 280.15 | 0.09737 | 283.65 | 0.9
0.05737 | 280.15 | 0.09737 | 283.65 | 1
0.05737 | 280.15 | 0.09737 | 284.15 | 0.15
0.05737 | 280.15 | 0.09737 | 284.15 | 0.2
0.05737 | 280.15 | 0.09737 | 284.15 | 0.3
0.05737 | 280.15 | 0.09737 | 284.15 | 0.4
0.05737 | 280.15 | 0.09737 | 284.15 | 0.5
0.05737 | 280.15 | 0.09737 | 284.15 | 0.6
0.05737 | 280.15 | 0.09737 | 284.15 | 0.7
0.05737 | 280.15 | 0.09737 | 284.15 | 0.8
0.05737 | 280.15 | 0.09737 | 284.15 | 0.9
0.05737 | 280.15 | 0.09737 | 284.15 | 1
0.05737 | 280.15 | 0.09737 | 284.65 | 0.15
0.05737 | 280.15 | 0.09737 | 284.65 | 0.2
0.05737 | 280.15 | 0.09737 | 284.65 | 0.3
0.05737 | 280.15 | 0.09737 | 284.65 | 0.4
0.05737 | 280.15 | 0.09737 | 284.65 | 0.5
0.05737 | 280.15 | 0.09737 | 284.65 | 0.6
0.05737 | 280.15 | 0.09737 | 284.65 | 0.7
0.05737 | 280.15 | 0.09737 | 284.65 | 0.8
0.05737 | 280.15 | 0.09737 | 284.65 | 0.9
0.05737 | 280.15 | 0.09737 | 284.65 | 1
0.05737 | 280.15 | 0.09737 | 285.15 | 0.15
0.05737 | 280.15 | 0.09737 | 285.15 | 0.2
0.05737 | 280.15 | 0.09737 | 285.15 | 0.3
0.05737 | 280.15 | 0.09737 | 285.15 | 0.4
0.05737 | 280.15 | 0.09737 | 285.15 | 0.5
0.05737 | 280.15 | 0.09737 | 285.15 | 0.6
0.05737 | 280.15 | 0.09737 | 285.15 | 0.7
0.05737 | 280.15 | 0.09737 | 285.15 | 0.8
0.05737 | 280.15 | 0.09737 | 285.15 | 0.9
0.05737 | 280.15 | 0.09737 | 285.15 | 1
0.05737 | 280.15 | 0.09737 | 285.65 | 0.15
0.05737 | 280.15 | 0.09737 | 285.65 | 0.2
0.05737 | 280.15 | 0.09737 | 285.65 | 0.3
0.05737 | 280.15 | 0.09737 | 285.65 | 0.4
0.05737 | 280.15 | 0.09737 | 285.65 | 0.5
0.05737 | 280.15 | 0.09737 | 285.65 | 0.6
0.05737 | 280.15 | 0.09737 | 285.65 | 0.7
0.05737 | 280.15 | 0.09737 | 285.65 | 0.8
0.05737 | 280.15 | 0.09737 | 285.65 | 0.9
0.05737 | 280.15 | 0.09737 | 285.65 | 1
0.05737 | 280.15 | 0.09737 | 286.15 | 0.15
0.05737 | 280.15 | 0.09737 | 286.15 | 0.2
0.05737 | 280.15 | 0.09737 | 286.15 | 0.3
0.05737 | 280.15 | 0.09737 | 286.15 | 0.4
0.05737 | 280.15 | 0.09737 | 286.15 | 0.5
0.05737 | 280.15 | 0.09737 | 286.15 | 0.6
0.05737 | 280.15 | 0.09737 | 286.15 | 0.7
0.05737 | 280.15 | 0.09737 | 286.15 | 0.8
0.05737 | 280.15 | 0.09737 | 286.15 | 0.9
0.05737 | 280.15 | 0.09737 | 286.15 | 1
0.05737 | 280.15 | 0.09737 | 286.65 | 0.15
0.05737 | 280.15 | 0.09737 | 286.65 | 0.2
0.05737 | 280.15 | 0.09737 | 286.65 | 0.3
0.05737 | 280.15 | 0.09737 | 286.65 | 0.4
0.05737 | 280.15 | 0.09737 | 286.65 | 0.5
0.05737 | 280.15 | 0.09737 | 286.65 | 0.6
0.05737 | 280.15 | 0.09737 | 286.65 | 0.7
0.05737 | 280.15 | 0.09737 | 286.65 | 0.8
0.05737 | 280.15 | 0.09737 | 286.65 | 0.9
0.05737 | 280.15 | 0.09737 | 286.65 | 1
0.05737 | 280.15 | 0.09737 | 287.15 | 0.15
0.05737 | 280.15 | 0.09737 | 287.15 | 0.2
0.05737 | 280.15 | 0.09737 | 287.15 | 0.3
0.05737 | 280.15 | 0.09737 | 287.15 | 0.4
0.05737 | 280.15 | 0.09737 | 287.15 | 0.5
0.05737 | 280.15 | 0.09737 | 287.15 | 0.6
0.05737 | 280.15 | 0.09737 | 287.15 | 0.7
0.05737 | 280.15 | 0.09737 | 287.15 | 0.8
0.05737 | 280.15 | 0.09737 | 287.15 | 0.9
0.05737 | 280.15 | 0.09737 | 287.15 | 1
0.05737 | 280.15 | 0.09737 | 287.65 | 0.15
0.05737 | 280.15 | 0.09737 | 287.65 | 0.2
0.05737 | 280.15 | 0.09737 | 287.65 | 0.3
0.05737 | 280.15 | 0.09737 | 287.65 | 0.4
0.05737 | 280.15 | 0.09737 | 287.65 | 0.5
0.05737 | 280.15 | 0.09737 | 287.65 | 0.6
0.05737 | 280.15 | 0.09737 | 287.65 | 0.7
0.05737 | 280.15 | 0.09737 | 287.65 | 0.8
0.05737 | 280.15 | 0.09737 | 287.65 | 0.9
0.05737 | 280.15 | 0.09737 | 287.65 | 1
0.05737 | 280.15 | 0.09737 | 288.15 | 0.15
0.05737 | 280.15 | 0.09737 | 288.15 | 0.2
0.05737 | 280.15 | 0.09737 | 288.15 | 0.3
0.05737 | 280.15 | 0.09737 | 288.15 | 0.4
0.05737 | 280.15 | 0.09737 | 288.15 | 0.5
0.05737 | 280.15 | 0.09737 | 288.15 | 0.6
0.05737 | 280.15 | 0.09737 | 288.15 | 0.7
0.05737 | 280.15 | 0.09737 | 288.15 | 0.8
0.05737 | 280.15 | 0.09737 | 288.15 | 0.9
0.05737 | 280.15 | 0.09737 | 288.15 | 1
0.05737 | 280.15 | 0.09737 | 288.65 | 0.15
0.05737 | 280.15 | 0.09737 | 288.65 | 0.2
0.05737 | 280.15 | 0.09737 | 288.65 | 0.3
0.05737 | 280.15 | 0.09737 | 288.65 | 0.4
0.05737 | 280.15 | 0.09737 | 288.65 | 0.5
0.05737 | 280.15 | 0.09737 | 288.65 | 0.6
0.05737 | 280.15 | 0.09737 | 288.65 | 0.7
0.05737 | 280.15 | 0.09737 | 288.65 | 0.8
0.05737 | 280.15 | 0.09737 | 288.65 | 0.9
0.05737 | 280.15 | 0.09737 | 288.65 | 1
0.05737 | 280.15 | 0.09737 | 289.15 | 0.15
0.05737 | 280.15 | 0.09737 | 289.15 | 0.2
0.05737 | 280.15 | 0.09737 | 289.15 | 0.3
0.05737 | 280.15 | 0.09737 | 289.15 | 0.4
0.05737 | 280.15 | 0.09737 | 289.15 | 0.5
0.05737 | 280.15 | 0.09737 | 289.15 | 0.6
0.05737 | 280.15 | 0.09737 | 289.15 | 0.7
0.05737 | 280.15 | 0.09737 | 289.15 | 0.8
0.05737 | 280.15 | 0.09737 | 289.15 | 0.9
0.05737 | 280.15 | 0.09737 | 289.15 | 1
0.05737 | 280.15 | 0.09737 | 289.65 | 0.15
0.05737 | 280.15 | 0.09737 | 289.65 | 0.2
0.05737 | 280.15 | 0.09737 | 289.65 | 0.3
0.05737 | 280.15 | 0.09737 | 289.65 | 0.4
0.05737 | 280.15 | 0.09737 | 289.65 | 0.5
0.05737 | 280.15 | 0.09737 | 289.65 | 0.6
0.05737 | 280.15 | 0.09737 | 289.65 | 0.7
0.05737 | 280.15 | 0.09737 | 289.65 | 0.8
0.05737 | 280.15 | 0.09737 | 289.65 | 0.9
0.05737 | 280.15 | 0.09737 | 289.65 | 1
0.05737 | 280.15 | 0.09737 | 290.15 | 0.15
0.05737 | 280.15 | 0.09737 | 290.15 | 0.2
0.05737 | 280.15 | 0.09737 | 290.15 | 0.3
0.05737 | 280.15 | 0.09737 | 290.15 | 0.4
0.05737 | 280.15 | 0.09737 | 290.15 | 0.5
0.05737 | 280.15 | 0.09737 | 290.15 | 0.6
0.05737 | 280.15 | 0.09737 | 290.15 | 0.7
0.05737 | 280.15 | 0.09737 | 290.15 | 0.8
0.05737 | 280.15 | 0.09737 | 290.15 | 0.9
0.05737 | 280.15 | 0.09737 | 290.15 | 1
0.05737 | 280.15 | 0.09737 | 290.65 | 0.15
0.05737 | 280.15 | 0.09737 | 290.65 | 0.2
0.05737 | 280.15 | 0.09737 | 290.65 | 0.3
0.05737 | 280.15 | 0.09737 | 290.65 | 0.4
0.05737 | 280.15 | 0.09737 | 290.65 | 0.5
0.05737 | 280.15 | 0.09737 | 290.65 | 0.6
0.05737 | 280.15 | 0.09737 | 290.65 | 0.7
0.05737 | 280.15 | 0.09737 | 290.65 | 0.8
0.05737 | 280.15 | 0.09737 | 290.65 | 0.9
0.05737 | 280.15 | 0.09737 | 290.65 | 1
0.05737 | 280.15 | 0.09737 | 291.15 | 0.15
0.05737 | 280.15 | 0.09737 | 291.15 | 0.2
0.05737 | 280.15 | 0.09737 | 291.15 | 0.3
0.05737 | 280.15 | 0.09737 | 291.15 | 0.4
0.05737 | 280.15 | 0.09737 | 291.15 | 0.5
0.05737 | 280.15 | 0.09737 | 291.15 | 0.6
0.05737 | 280.15 | 0.09737 | 291.15 | 0.7
0.05737 | 280.15 | 0.09737 | 291.15 | 0.8
0.05737 | 280.15 | 0.09737 | 291.15 | 0.9
0.05737 | 280.15 | 0.09737 | 291.15 | 1
0.05737 | 280.15 | 0.09737 | 294.15 | 0.15
0.05737 | 280.15 | 0.09737 | 294.15 | 0.2
0.05737 | 280.15 | 0.09737 | 294.15 | 0.3
0.05737 | 280.15 | 0.09737 | 294.15 | 0.4
0.05737 | 280.15 | 0.09737 | 294.15 | 0.5
0.05737 | 280.15 | 0.09737 | 294.15 | 0.6
0.05737 | 280.15 | 0.09737 | 294.15 | 0.7
0.05737 | 280.15 | 0.09737 | 294.15 | 0.8
0.05737 | 280.15 | 0.09737 | 294.15 | 0.9
0.05737 | 280.15 | 0.09737 | 294.15 | 1
0.05737 | 280.15 | 0.09737 | 297.15 | 0.15
0.05737 | 280.15 | 0.09737 | 297.15 | 0.2
0.05737 | 280.15 | 0.09737 | 297.15 | 0.3
0.05737 | 280.15 | 0.09737 | 297.15 | 0.4
0.05737 | 280.15 | 0.09737 | 297.15 | 0.5
0.05737 | 280.15 | 0.09737 | 297.15 | 0.6
0.05737 | 280.15 | 0.09737 | 297.15 | 0.7
0.05737 | 280.15 | 0.09737 | 297.15 | 0.8
0.05737 | 280.15 | 0.09737 | 297.15 | 0.9
0.05737 | 280.15 | 0.09737 | 297.15 | 1
0.05737 | 280.15 | 0.09737 | 300.15 | 0.15
0.05737 | 280.15 | 0.09737 | 300.15 | 0.2
0.05737 | 280.15 | 0.09737 | 300.15 | 0.3
0.05737 | 280.15 | 0.09737 | 300.15 | 0.4
0.05737 | 280.15 | 0.09737 | 300.15 | 0.5
0.05737 | 280.15 | 0.09737 | 300.15 | 0.6
0.05737 | 280.15 | 0.09737 | 300.15 | 0.7
0.05737 | 280.15 | 0.09737 | 300.15 | 0.8
0.05737 | 280.15 | 0.09737 | 300.15 | 0.9
0.05737 | 280.15 | 0.09737 | 300.15 | 1
0.05737 | 280.15 | 0.09737 | 303.15 | 0.15
0.05737 | 280.15 | 0.09737 | 303.15 | 0.2
0.05737 | 280.15 | 0.09737 | 303.15 | 0.3
0.05737 | 280.15 | 0.09737 | 303.15 | 0.4
0.05737 | 280.15 | 0.09737 | 303.15 | 0.5
0.05737 | 280.15 | 0.09737 | 303.15 | 0.6
0.05737 | 280.15 | 0.09737 | 303.15 | 0.7
0.05737 | 280.15 | 0.09737 | 303.15 | 0.8
0.05737 | 280.15 | 0.09737 | 303.15 | 0.9
0.05737 | 280.15 | 0.09737 | 303.15 | 1
0.05737 | 280.15 | 0.115 | 283.65 | 0.15
0.05737 | 280.15 | 0.115 | 283.65 | 0.2
0.05737 | 280.15 | 0.115 | 283.65 | 0.3
0.05737 | 280.15 | 0.115 | 283.65 | 0.4
0.05737 | 280.15 | 0.115 | 283.65 | 0.5
0.05737 | 280.15 | 0.115 | 283.65 | 0.6
0.05737 | 280.15 | 0.115 | 283.65 | 0.7
0.05737 | 280.15 | 0.115 | 283.65 | 0.8
0.05737 | 280.15 | 0.115 | 283.65 | 0.9
0.05737 | 280.15 | 0.115 | 283.65 | 1
0.05737 | 280.15 | 0.115 | 284.15 | 0.15
0.05737 | 280.15 | 0.115 | 284.15 | 0.2
0.05737 | 280.15 | 0.115 | 284.15 | 0.3
0.05737 | 280.15 | 0.115 | 284.15 | 0.4
0.05737 | 280.15 | 0.115 | 284.15 | 0.5
0.05737 | 280.15 | 0.115 | 284.15 | 0.6
0.05737 | 280.15 | 0.115 | 284.15 | 0.7
0.05737 | 280.15 | 0.115 | 284.15 | 0.8
0.05737 | 280.15 | 0.115 | 284.15 | 0.9
0.05737 | 280.15 | 0.115 | 284.15 | 1
0.05737 | 280.15 | 0.115 | 284.65 | 0.15
0.05737 | 280.15 | 0.115 | 284.65 | 0.2
0.05737 | 280.15 | 0.115 | 284.65 | 0.3
0.05737 | 280.15 | 0.115 | 284.65 | 0.4
0.05737 | 280.15 | 0.115 | 284.65 | 0.5
0.05737 | 280.15 | 0.115 | 284.65 | 0.6
0.05737 | 280.15 | 0.115 | 284.65 | 0.7
0.05737 | 280.15 | 0.115 | 284.65 | 0.8
0.05737 | 280.15 | 0.115 | 284.65 | 0.9
0.05737 | 280.15 | 0.115 | 284.65 | 1
0.05737 | 280.15 | 0.115 | 285.15 | 0.15
0.05737 | 280.15 | 0.115 | 285.15 | 0.2
0.05737 | 280.15 | 0.115 | 285.15 | 0.3
0.05737 | 280.15 | 0.115 | 285.15 | 0.4
0.05737 | 280.15 | 0.115 | 285.15 | 0.5
0.05737 | 280.15 | 0.115 | 285.15 | 0.6
0.05737 | 280.15 | 0.115 | 285.15 | 0.7
0.05737 | 280.15 | 0.115 | 285.15 | 0.8
0.05737 | 280.15 | 0.115 | 285.15 | 0.9
0.05737 | 280.15 | 0.115 | 285.15 | 1
0.05737 | 280.15 | 0.115 | 285.65 | 0.15
0.05737 | 280.15 | 0.115 | 285.65 | 0.2
0.05737 | 280.15 | 0.115 | 285.65 | 0.3
0.05737 | 280.15 | 0.115 | 285.65 | 0.4
0.05737 | 280.15 | 0.115 | 285.65 | 0.5
0.05737 | 280.15 | 0.115 | 285.65 | 0.6
0.05737 | 280.15 | 0.115 | 285.65 | 0.7
0.05737 | 280.15 | 0.115 | 285.65 | 0.8
0.05737 | 280.15 | 0.115 | 285.65 | 0.9
0.05737 | 280.15 | 0.115 | 285.65 | 1
0.05737 | 280.15 | 0.115 | 286.15 | 0.15
0.05737 | 280.15 | 0.115 | 286.15 | 0.2
0.05737 | 280.15 | 0.115 | 286.15 | 0.3
0.05737 | 280.15 | 0.115 | 286.15 | 0.4
0.05737 | 280.15 | 0.115 | 286.15 | 0.5
0.05737 | 280.15 | 0.115 | 286.15 | 0.6
0.05737 | 280.15 | 0.115 | 286.15 | 0.7
0.05737 | 280.15 | 0.115 | 286.15 | 0.8
0.05737 | 280.15 | 0.115 | 286.15 | 0.9
0.05737 | 280.15 | 0.115 | 286.15 | 1
0.05737 | 280.15 | 0.115 | 286.65 | 0.15
0.05737 | 280.15 | 0.115 | 286.65 | 0.2
0.05737 | 280.15 | 0.115 | 286.65 | 0.3
0.05737 | 280.15 | 0.115 | 286.65 | 0.4
0.05737 | 280.15 | 0.115 | 286.65 | 0.5
0.05737 | 280.15 | 0.115 | 286.65 | 0.6
0.05737 | 280.15 | 0.115 | 286.65 | 0.7
0.05737 | 280.15 | 0.115 | 286.65 | 0.8
0.05737 | 280.15 | 0.115 | 286.65 | 0.9
0.05737 | 280.15 | 0.115 | 286.65 | 1
0.05737 | 280.15 | 0.115 | 287.15 | 0.15
0.05737 | 280.15 | 0.115 | 287.15 | 0.2
0.05737 | 280.15 | 0.115 | 287.15 | 0.3
0.05737 | 280.15 | 0.115 | 287.15 | 0.4
0.05737 | 280.15 | 0.115 | 287.15 | 0.5
0.05737 | 280.15 | 0.115 | 287.15 | 0.6
0.05737 | 280.15 | 0.115 | 287.15 | 0.7
0.05737 | 280.15 | 0.115 | 287.15 | 0.8
0.05737 | 280.15 | 0.115 | 287.15 | 0.9
0.05737 | 280.15 | 0.115 | 287.15 | 1
0.05737 | 280.15 | 0.115 | 287.65 | 0.15
0.05737 | 280.15 | 0.115 | 287.65 | 0.2
0.05737 | 280.15 | 0.115 | 287.65 | 0.3
0.05737 | 280.15 | 0.115 | 287.65 | 0.4
0.05737 | 280.15 | 0.115 | 287.65 | 0.5
0.05737 | 280.15 | 0.115 | 287.65 | 0.6
0.05737 | 280.15 | 0.115 | 287.65 | 0.7
0.05737 | 280.15 | 0.115 | 287.65 | 0.8
0.05737 | 280.15 | 0.115 | 287.65 | 0.9
0.05737 | 280.15 | 0.115 | 287.65 | 1
0.05737 | 280.15 | 0.115 | 288.15 | 0.15
0.05737 | 280.15 | 0.115 | 288.15 | 0.2
0.05737 | 280.15 | 0.115 | 288.15 | 0.3
0.05737 | 280.15 | 0.115 | 288.15 | 0.4
0.05737 | 280.15 | 0.115 | 288.15 | 0.5
0.05737 | 280.15 | 0.115 | 288.15 | 0.6
0.05737 | 280.15 | 0.115 | 288.15 | 0.7
0.05737 | 280.15 | 0.115 | 288.15 | 0.8
0.05737 | 280.15 | 0.115 | 288.15 | 0.9
0.05737 | 280.15 | 0.115 | 288.15 | 1
0.05737 | 280.15 | 0.115 | 288.65 | 0.15
0.05737 | 280.15 | 0.115 | 288.65 | 0.2
0.05737 | 280.15 | 0.115 | 288.65 | 0.3
0.05737 | 280.15 | 0.115 | 288.65 | 0.4
0.05737 | 280.15 | 0.115 | 288.65 | 0.5
0.05737 | 280.15 | 0.115 | 288.65 | 0.6
0.05737 | 280.15 | 0.115 | 288.65 | 0.7
0.05737 | 280.15 | 0.115 | 288.65 | 0.8
0.05737 | 280.15 | 0.115 | 288.65 | 0.9
0.05737 | 280.15 | 0.115 | 288.65 | 1
0.05737 | 280.15 | 0.115 | 289.15 | 0.15
0.05737 | 280.15 | 0.115 | 289.15 | 0.2
0.05737 | 280.15 | 0.115 | 289.15 | 0.3
0.05737 | 280.15 | 0.115 | 289.15 | 0.4
0.05737 | 280.15 | 0.115 | 289.15 | 0.5
0.05737 | 280.15 | 0.115 | 289.15 | 0.6
0.05737 | 280.15 | 0.115 | 289.15 | 0.7
0.05737 | 280.15 | 0.115 | 289.15 | 0.8
0.05737 | 280.15 | 0.115 | 289.15 | 0.9
0.05737 | 280.15 | 0.115 | 289.15 | 1
0.05737 | 280.15 | 0.115 | 289.65 | 0.15
0.05737 | 280.15 | 0.115 | 289.65 | 0.2
0.05737 | 280.15 | 0.115 | 289.65 | 0.3
0.05737 | 280.15 | 0.115 | 289.65 | 0.4
0.05737 | 280.15 | 0.115 | 289.65 | 0.5
0.05737 | 280.15 | 0.115 | 289.65 | 0.6
0.05737 | 280.15 | 0.115 | 289.65 | 0.7
0.05737 | 280.15 | 0.115 | 289.65 | 0.8
0.05737 | 280.15 | 0.115 | 289.65 | 0.9
0.05737 | 280.15 | 0.115 | 289.65 | 1
0.05737 | 280.15 | 0.115 | 290.15 | 0.15
0.05737 | 280.15 | 0.115 | 290.15 | 0.2
0.05737 | 280.15 | 0.115 | 290.15 | 0.3
0.05737 | 280.15 | 0.115 | 290.15 | 0.4
0.05737 | 280.15 | 0.115 | 290.15 | 0.5
0.05737 | 280.15 | 0.115 | 290.15 | 0.6
0.05737 | 280.15 | 0.115 | 290.15 | 0.7
0.05737 | 280.15 | 0.115 | 290.15 | 0.8
0.05737 | 280.15 | 0.115 | 290.15 | 0.9
0.05737 | 280.15 | 0.115 | 290.15 | 1
0.05737 | 280.15 | 0.115 | 290.65 | 0.15
0.05737 | 280.15 | 0.115 | 290.65 | 0.2
0.05737 | 280.15 | 0.115 | 290.65 | 0.3
0.05737 | 280.15 | 0.115 | 290.65 | 0.4
0.05737 | 280.15 | 0.115 | 290.65 | 0.5
0.05737 | 280.15 | 0.115 | 290.65 | 0.6
0.05737 | 280.15 | 0.115 | 290.65 | 0.7
0.05737 | 280.15 | 0.115 | 290.65 | 0.8
0.05737 | 280.15 | 0.115 | 290.65 | 0.9
0.05737 | 280.15 | 0.115 | 290.65 | 1
0.05737 | 280.15 | 0.115 | 291.15 | 0.15
0.05737 | 280.15 | 0.115 | 291.15 | 0.2
0.05737 | 280.15 | 0.115 | 291.15 | 0.3
0.05737 | 280.15 | 0.115 | 291.15 | 0.4
0.05737 | 280.15 | 0.115 | 291.15 | 0.5
0.05737 | 280.15 | 0.115 | 291.15 | 0.6
0.05737 | 280.15 | 0.115 | 291.15 | 0.7
0.05737 | 280.15 | 0.115 | 291.15 | 0.8
0.05737 | 280.15 | 0.115 | 291.15 | 0.9
0.05737 | 280.15 | 0.115 | 291.15 | 1
0.05737 | 280.15 | 0.115 | 294.15 | 0.15
0.05737 | 280.15 | 0.115 | 294.15 | 0.2
0.05737 | 280.15 | 0.115 | 294.15 | 0.3
0.05737 | 280.15 | 0.115 | 294.15 | 0.4
0.05737 | 280.15 | 0.115 | 294.15 | 0.5
0.05737 | 280.15 | 0.115 | 294.15 | 0.6
0.05737 | 280.15 | 0.115 | 294.15 | 0.7
0.05737 | 280.15 | 0.115 | 294.15 | 0.8
0.05737 | 280.15 | 0.115 | 294.15 | 0.9
0.05737 | 280.15 | 0.115 | 294.15 | 1
0.05737 | 280.15 | 0.115 | 297.15 | 0.15
0.05737 | 280.15 | 0.115 | 297.15 | 0.2
0.05737 | 280.15 | 0.115 | 297.15 | 0.3
0.05737 | 280.15 | 0.115 | 297.15 | 0.4
0.05737 | 280.15 | 0.115 | 297.15 | 0.5
0.05737 | 280.15 | 0.115 | 297.15 | 0.6
0.05737 | 280.15 | 0.115 | 297.15 | 0.7
0.05737 | 280.15 | 0.115 | 297.15 | 0.8
0.05737 | 280.15 | 0.115 | 297.15 | 0.9
0.05737 | 280.15 | 0.115 | 297.15 | 1
0.05737 | 280.15 | 0.115 | 300.15 | 0.15
0.05737 | 280.15 | 0.115 | 300.15 | 0.2
0.05737 | 280.15 | 0.115 | 300.15 | 0.3
0.05737 | 280.15 | 0.115 | 300.15 | 0.4
0.05737 | 280.15 | 0.115 | 300.15 | 0.5
0.05737 | 280.15 | 0.115 | 300.15 | 0.6
0.05737 | 280.15 | 0.115 | 300.15 | 0.7
0.05737 | 280.15 | 0.115 | 300.15 | 0.8
0.05737 | 280.15 | 0.115 | 300.15 | 0.9
0.05737 | 280.15 | 0.115 | 300.15 | 1
0.05737 | 280.15 | 0.115 | 303.15 | 0.15
0.05737 | 280.15 | 0.115 | 303.15 | 0.2
0.05737 | 280.15 | 0.115 | 303.15 | 0.3
0.05737 | 280.15 | 0.115 | 303.15 | 0.4
0.05737 | 280.15 | 0.115 | 303.15 | 0.5
0.05737 | 280.15 | 0.115 | 303.15 | 0.6
0.05737 | 280.15 | 0.115 | 303.15 | 0.7
0.05737 | 280.15 | 0.115 | 303.15 | 0.8
0.05737 | 280.15 | 0.115 | 303.15 | 0.9
0.05737 | 280.15 | 0.115 | 303.15 | 1
0.05737 | 282.15 | 0.00115 | 283.65 | 0.15
0.05737 | 282.15 | 0.00115 | 283.65 | 0.2
0.05737 | 282.15 | 0.00115 | 283.65 | 0.3
0.05737 | 282.15 | 0.00115 | 283.65 | 0.4
0.05737 | 282.15 | 0.00115 | 283.65 | 0.5
0.05737 | 282.15 | 0.00115 | 283.65 | 0.6
0.05737 | 282.15 | 0.00115 | 283.65 | 0.7
0.05737 | 282.15 | 0.00115 | 283.65 | 0.8
0.05737 | 282.15 | 0.00115 | 283.65 | 0.9
0.05737 | 282.15 | 0.00115 | 283.65 | 1
0.05737 | 282.15 | 0.00115 | 284.15 | 0.15
0.05737 | 282.15 | 0.00115 | 284.15 | 0.2
0.05737 | 282.15 | 0.00115 | 284.15 | 0.3
0.05737 | 282.15 | 0.00115 | 284.15 | 0.4
0.05737 | 282.15 | 0.00115 | 284.15 | 0.5
0.05737 | 282.15 | 0.00115 | 284.15 | 0.6
0.05737 | 282.15 | 0.00115 | 284.15 | 0.7
0.05737 | 282.15 | 0.00115 | 284.15 | 0.8
0.05737 | 282.15 | 0.00115 | 284.15 | 0.9
0.05737 | 282.15 | 0.00115 | 284.15 | 1
0.05737 | 282.15 | 0.00115 | 284.65 | 0.15
0.05737 | 282.15 | 0.00115 | 284.65 | 0.2
0.05737 | 282.15 | 0.00115 | 284.65 | 0.3
0.05737 | 282.15 | 0.00115 | 284.65 | 0.4
0.05737 | 282.15 | 0.00115 | 284.65 | 0.5
0.05737 | 282.15 | 0.00115 | 284.65 | 0.6
0.05737 | 282.15 | 0.00115 | 284.65 | 0.7
0.05737 | 282.15 | 0.00115 | 284.65 | 0.8
0.05737 | 282.15 | 0.00115 | 284.65 | 0.9
0.05737 | 282.15 | 0.00115 | 284.65 | 1
0.05737 | 282.15 | 0.00115 | 285.15 | 0.15
0.05737 | 282.15 | 0.00115 | 285.15 | 0.2
0.05737 | 282.15 | 0.00115 | 285.15 | 0.3
0.05737 | 282.15 | 0.00115 | 285.15 | 0.4
0.05737 | 282.15 | 0.00115 | 285.15 | 0.5
0.05737 | 282.15 | 0.00115 | 285.15 | 0.6
0.05737 | 282.15 | 0.00115 | 285.15 | 0.7
0.05737 | 282.15 | 0.00115 | 285.15 | 0.8
0.05737 | 282.15 | 0.00115 | 285.15 | 0.9
0.05737 | 282.15 | 0.00115 | 285.15 | 1
0.05737 | 282.15 | 0.00115 | 285.65 | 0.15
0.05737 | 282.15 | 0.00115 | 285.65 | 0.2
0.05737 | 282.15 | 0.00115 | 285.65 | 0.3
0.05737 | 282.15 | 0.00115 | 285.65 | 0.4
0.05737 | 282.15 | 0.00115 | 285.65 | 0.5
0.05737 | 282.15 | 0.00115 | 285.65 | 0.6
0.05737 | 282.15 | 0.00115 | 285.65 | 0.7
0.05737 | 282.15 | 0.00115 | 285.65 | 0.8
0.05737 | 282.15 | 0.00115 | 285.65 | 0.9
0.05737 | 282.15 | 0.00115 | 285.65 | 1
0.05737 | 282.15 | 0.00115 | 286.15 | 0.15
0.05737 | 282.15 | 0.00115 | 286.15 | 0.2
0.05737 | 282.15 | 0.00115 | 286.15 | 0.3
0.05737 | 282.15 | 0.00115 | 286.15 | 0.4
0.05737 | 282.15 | 0.00115 | 286.15 | 0.5
0.05737 | 282.15 | 0.00115 | 286.15 | 0.6
0.05737 | 282.15 | 0.00115 | 286.15 | 0.7
0.05737 | 282.15 | 0.00115 | 286.15 | 0.8
0.05737 | 282.15 | 0.00115 | 286.15 | 0.9
0.05737 | 282.15 | 0.00115 | 286.15 | 1
0.05737 | 282.15 | 0.00115 | 286.65 | 0.15
0.05737 | 282.15 | 0.00115 | 286.65 | 0.2
0.05737 | 282.15 | 0.00115 | 286.65 | 0.3
0.05737 | 282.15 | 0.00115 | 286.65 | 0.4
0.05737 | 282.15 | 0.00115 | 286.65 | 0.5
0.05737 | 282.15 | 0.00115 | 286.65 | 0.6
0.05737 | 282.15 | 0.00115 | 286.65 | 0.7
0.05737 | 282.15 | 0.00115 | 286.65 | 0.8
0.05737 | 282.15 | 0.00115 | 286.65 | 0.9
0.05737 | 282.15 | 0.00115 | 286.65 | 1
0.05737 | 282.15 | 0.00115 | 287.15 | 0.15
0.05737 | 282.15 | 0.00115 | 287.15 | 0.2
0.05737 | 282.15 | 0.00115 | 287.15 | 0.3
0.05737 | 282.15 | 0.00115 | 287.15 | 0.4
0.05737 | 282.15 | 0.00115 | 287.15 | 0.5
0.05737 | 282.15 | 0.00115 | 287.15 | 0.6
0.05737 | 282.15 | 0.00115 | 287.15 | 0.7
0.05737 | 282.15 | 0.00115 | 287.15 | 0.8
0.05737 | 282.15 | 0.00115 | 287.15 | 0.9
0.05737 | 282.15 | 0.00115 | 287.15 | 1
0.05737 | 282.15 | 0.00115 | 287.65 | 0.15
0.05737 | 282.15 | 0.00115 | 287.65 | 0.2
0.05737 | 282.15 | 0.00115 | 287.65 | 0.3
0.05737 | 282.15 | 0.00115 | 287.65 | 0.4
0.05737 | 282.15 | 0.00115 | 287.65 | 0.5
0.05737 | 282.15 | 0.00115 | 287.65 | 0.6
0.05737 | 282.15 | 0.00115 | 287.65 | 0.7
0.05737 | 282.15 | 0.00115 | 287.65 | 0.8
0.05737 | 282.15 | 0.00115 | 287.65 | 0.9
0.05737 | 282.15 | 0.00115 | 287.65 | 1
0.05737 | 282.15 | 0.00115 | 288.15 | 0.15
0.05737 | 282.15 | 0.00115 | 288.15 | 0.2
0.05737 | 282.15 | 0.00115 | 288.15 | 0.3
0.05737 | 282.15 | 0.00115 | 288.15 | 0.4
0.05737 | 282.15 | 0.00115 | 288.15 | 0.5
0.05737 | 282.15 | 0.00115 | 288.15 | 0.6
0.05737 | 282.15 | 0.00115 | 288.15 | 0.7
0.05737 | 282.15 | 0.00115 | 288.15 | 0.8
0.05737 | 282.15 | 0.00115 | 288.15 | 0.9
0.05737 | 282.15 | 0.00115 | 288.15 | 1
0.05737 | 282.15 | 0.00115 | 288.65 | 0.15
0.05737 | 282.15 | 0.00115 | 288.65 | 0.2
0.05737 | 282.15 | 0.00115 | 288.65 | 0.3
0.05737 | 282.15 | 0.00115 | 288.65 | 0.4
0.05737 | 282.15 | 0.00115 | 288.65 | 0.5
0.05737 | 282.15 | 0.00115 | 288.65 | 0.6
0.05737 | 282.15 | 0.00115 | 288.65 | 0.7
0.05737 | 282.15 | 0.00115 | 288.65 | 0.8
0.05737 | 282.15 | 0.00115 | 288.65 | 0.9
0.05737 | 282.15 | 0.00115 | 288.65 | 1
0.05737 | 282.15 | 0.00115 | 289.15 | 0.15
0.05737 | 282.15 | 0.00115 | 289.15 | 0.2
0.05737 | 282.15 | 0.00115 | 289.15 | 0.3
0.05737 | 282.15 | 0.00115 | 289.15 | 0.4
0.05737 | 282.15 | 0.00115 | 289.15 | 0.5
0.05737 | 282.15 | 0.00115 | 289.15 | 0.6
0.05737 | 282.15 | 0.00115 | 289.15 | 0.7
0.05737 | 282.15 | 0.00115 | 289.15 | 0.8
0.05737 | 282.15 | 0.00115 | 289.15 | 0.9
0.05737 | 282.15 | 0.00115 | 289.15 | 1
0.05737 | 282.15 | 0.00115 | 289.65 | 0.15
0.05737 | 282.15 | 0.00115 | 289.65 | 0.2
0.05737 | 282.15 | 0.00115 | 289.65 | 0.3
0.05737 | 282.15 | 0.00115 | 289.65 | 0.4
0.05737 | 282.15 | 0.00115 | 289.65 | 0.5
0.05737 | 282.15 | 0.00115 | 289.65 | 0.6
0.05737 | 282.15 | 0.00115 | 289.65 | 0.7
0.05737 | 282.15 | 0.00115 | 289.65 | 0.8
0.05737 | 282.15 | 0.00115 | 289.65 | 0.9
0.05737 | 282.15 | 0.00115 | 289.65 | 1
0.05737 | 282.15 | 0.00115 | 290.15 | 0.15
0.05737 | 282.15 | 0.00115 | 290.15 | 0.2
0.05737 | 282.15 | 0.00115 | 290.15 | 0.3
0.05737 | 282.15 | 0.00115 | 290.15 | 0.4
0.05737 | 282.15 | 0.00115 | 290.15 | 0.5
0.05737 | 282.15 | 0.00115 | 290.15 | 0.6
0.05737 | 282.15 | 0.00115 | 290.15 | 0.7
0.05737 | 282.15 | 0.00115 | 290.15 | 0.8
0.05737 | 282.15 | 0.00115 | 290.15 | 0.9
0.05737 | 282.15 | 0.00115 | 290.15 | 1
0.05737 | 282.15 | 0.00115 | 290.65 | 0.15
0.05737 | 282.15 | 0.00115 | 290.65 | 0.2
0.05737 | 282.15 | 0.00115 | 290.65 | 0.3
0.05737 | 282.15 | 0.00115 | 290.65 | 0.4
0.05737 | 282.15 | 0.00115 | 290.65 | 0.5
0.05737 | 282.15 | 0.00115 | 290.65 | 0.6
0.05737 | 282.15 | 0.00115 | 290.65 | 0.7
0.05737 | 282.15 | 0.00115 | 290.65 | 0.8
0.05737 | 282.15 | 0.00115 | 290.65 | 0.9
0.05737 | 282.15 | 0.00115 | 290.65 | 1
0.05737 | 282.15 | 0.00115 | 291.15 | 0.15
0.05737 | 282.15 | 0.00115 | 291.15 | 0.2
0.05737 | 282.15 | 0.00115 | 291.15 | 0.3
0.05737 | 282.15 | 0.00115 | 291.15 | 0.4
0.05737 | 282.15 | 0.00115 | 291.15 | 0.5
0.05737 | 282.15 | 0.00115 | 291.15 | 0.6
0.05737 | 282.15 | 0.00115 | 291.15 | 0.7
0.05737 | 282.15 | 0.00115 | 291.15 | 0.8
0.05737 | 282.15 | 0.00115 | 291.15 | 0.9
0.05737 | 282.15 | 0.00115 | 291.15 | 1
0.05737 | 282.15 | 0.00115 | 294.15 | 0.15
0.05737 | 282.15 | 0.00115 | 294.15 | 0.2
0.05737 | 282.15 | 0.00115 | 294.15 | 0.3
0.05737 | 282.15 | 0.00115 | 294.15 | 0.4
0.05737 | 282.15 | 0.00115 | 294.15 | 0.5
0.05737 | 282.15 | 0.00115 | 294.15 | 0.6
0.05737 | 282.15 | 0.00115 | 294.15 | 0.7
0.05737 | 282.15 | 0.00115 | 294.15 | 0.8
0.05737 | 282.15 | 0.00115 | 294.15 | 0.9
0.05737 | 282.15 | 0.00115 | 294.15 | 1
0.05737 | 282.15 | 0.00115 | 297.15 | 0.15
0.05737 | 282.15 | 0.00115 | 297.15 | 0.2
0.05737 | 282.15 | 0.00115 | 297.15 | 0.3
0.05737 | 282.15 | 0.00115 | 297.15 | 0.4
0.05737 | 282.15 | 0.00115 | 297.15 | 0.5
0.05737 | 282.15 | 0.00115 | 297.15 | 0.6
0.05737 | 282.15 | 0.00115 | 297.15 | 0.7
0.05737 | 282.15 | 0.00115 | 297.15 | 0.8
0.05737 | 282.15 | 0.00115 | 297.15 | 0.9
0.05737 | 282.15 | 0.00115 | 297.15 | 1
0.05737 | 282.15 | 0.00115 | 300.15 | 0.15
0.05737 | 282.15 | 0.00115 | 300.15 | 0.2
0.05737 | 282.15 | 0.00115 | 300.15 | 0.3
0.05737 | 282.15 | 0.00115 | 300.15 | 0.4
0.05737 | 282.15 | 0.00115 | 300.15 | 0.5
0.05737 | 282.15 | 0.00115 | 300.15 | 0.6
0.05737 | 282.15 | 0.00115 | 300.15 | 0.7
0.05737 | 282.15 | 0.00115 | 300.15 | 0.8
0.05737 | 282.15 | 0.00115 | 300.15 | 0.9
0.05737 | 282.15 | 0.00115 | 300.15 | 1
0.05737 | 282.15 | 0.00115 | 303.15 | 0.15
0.05737 | 282.15 | 0.00115 | 303.15 | 0.2
0.05737 | 282.15 | 0.00115 | 303.15 | 0.3
0.05737 | 282.15 | 0.00115 | 303.15 | 0.4
0.05737 | 282.15 | 0.00115 | 303.15 | 0.5
0.05737 | 282.15 | 0.00115 | 303.15 | 0.6
0.05737 | 282.15 | 0.00115 | 303.15 | 0.7
0.05737 | 282.15 | 0.00115 | 303.15 | 0.8
0.05737 | 282.15 | 0.00115 | 303.15 | 0.9
0.05737 | 282.15 | 0.00115 | 303.15 | 1
0.05737 | 282.15 | 0.077 | 283.65 | 0.15
0.05737 | 282.15 | 0.077 | 283.65 | 0.2
0.05737 | 282.15 | 0.077 | 283.65 | 0.3
0.05737 | 282.15 | 0.077 | 283.65 | 0.4
0.05737 | 282.15 | 0.077 | 283.65 | 0.5
0.05737 | 282.15 | 0.077 | 283.65 | 0.6
0.05737 | 282.15 | 0.077 | 283.65 | 0.7
0.05737 | 282.15 | 0.077 | 283.65 | 0.8
0.05737 | 282.15 | 0.077 | 283.65 | 0.9
0.05737 | 282.15 | 0.077 | 283.65 | 1
0.05737 | 282.15 | 0.077 | 284.15 | 0.15
0.05737 | 282.15 | 0.077 | 284.15 | 0.2
0.05737 | 282.15 | 0.077 | 284.15 | 0.3
0.05737 | 282.15 | 0.077 | 284.15 | 0.4
0.05737 | 282.15 | 0.077 | 284.15 | 0.5
0.05737 | 282.15 | 0.077 | 284.15 | 0.6
0.05737 | 282.15 | 0.077 | 284.15 | 0.7
0.05737 | 282.15 | 0.077 | 284.15 | 0.8
0.05737 | 282.15 | 0.077 | 284.15 | 0.9
0.05737 | 282.15 | 0.077 | 284.15 | 1
0.05737 | 282.15 | 0.077 | 284.65 | 0.15
0.05737 | 282.15 | 0.077 | 284.65 | 0.2
0.05737 | 282.15 | 0.077 | 284.65 | 0.3
0.05737 | 282.15 | 0.077 | 284.65 | 0.4
0.05737 | 282.15 | 0.077 | 284.65 | 0.5
0.05737 | 282.15 | 0.077 | 284.65 | 0.6
0.05737 | 282.15 | 0.077 | 284.65 | 0.7
0.05737 | 282.15 | 0.077 | 284.65 | 0.8
0.05737 | 282.15 | 0.077 | 284.65 | 0.9
0.05737 | 282.15 | 0.077 | 284.65 | 1
0.05737 | 282.15 | 0.077 | 285.15 | 0.15
0.05737 | 282.15 | 0.077 | 285.15 | 0.2
0.05737 | 282.15 | 0.077 | 285.15 | 0.3
0.05737 | 282.15 | 0.077 | 285.15 | 0.4
0.05737 | 282.15 | 0.077 | 285.15 | 0.5
0.05737 | 282.15 | 0.077 | 285.15 | 0.6
0.05737 | 282.15 | 0.077 | 285.15 | 0.7
0.05737 | 282.15 | 0.077 | 285.15 | 0.8
0.05737 | 282.15 | 0.077 | 285.15 | 0.9
0.05737 | 282.15 | 0.077 | 285.15 | 1
0.05737 | 282.15 | 0.077 | 285.65 | 0.15
0.05737 | 282.15 | 0.077 | 285.65 | 0.2
0.05737 | 282.15 | 0.077 | 285.65 | 0.3
0.05737 | 282.15 | 0.077 | 285.65 | 0.4
0.05737 | 282.15 | 0.077 | 285.65 | 0.5
0.05737 | 282.15 | 0.077 | 285.65 | 0.6
0.05737 | 282.15 | 0.077 | 285.65 | 0.7
0.05737 | 282.15 | 0.077 | 285.65 | 0.8
0.05737 | 282.15 | 0.077 | 285.65 | 0.9
0.05737 | 282.15 | 0.077 | 285.65 | 1
0.05737 | 282.15 | 0.077 | 286.15 | 0.15
0.05737 | 282.15 | 0.077 | 286.15 | 0.2
0.05737 | 282.15 | 0.077 | 286.15 | 0.3
0.05737 | 282.15 | 0.077 | 286.15 | 0.4
0.05737 | 282.15 | 0.077 | 286.15 | 0.5
0.05737 | 282.15 | 0.077 | 286.15 | 0.6
0.05737 | 282.15 | 0.077 | 286.15 | 0.7
0.05737 | 282.15 | 0.077 | 286.15 | 0.8
0.05737 | 282.15 | 0.077 | 286.15 | 0.9
0.05737 | 282.15 | 0.077 | 286.15 | 1
0.05737 | 282.15 | 0.077 | 286.65 | 0.15
0.05737 | 282.15 | 0.077 | 286.65 | 0.2
0.05737 | 282.15 | 0.077 | 286.65 | 0.3
0.05737 | 282.15 | 0.077 | 286.65 | 0.4
0.05737 | 282.15 | 0.077 | 286.65 | 0.5
0.05737 | 282.15 | 0.077 | 286.65 | 0.6
0.05737 | 282.15 | 0.077 | 286.65 | 0.7
0.05737 | 282.15 | 0.077 | 286.65 | 0.8
0.05737 | 282.15 | 0.077 | 286.65 | 0.9
0.05737 | 282.15 | 0.077 | 286.65 | 1
0.05737 | 282.15 | 0.077 | 287.15 | 0.15
0.05737 | 282.15 | 0.077 | 287.15 | 0.2
0.05737 | 282.15 | 0.077 | 287.15 | 0.3
0.05737 | 282.15 | 0.077 | 287.15 | 0.4
0.05737 | 282.15 | 0.077 | 287.15 | 0.5
0.05737 | 282.15 | 0.077 | 287.15 | 0.6
0.05737 | 282.15 | 0.077 | 287.15 | 0.7
0.05737 | 282.15 | 0.077 | 287.15 | 0.8
0.05737 | 282.15 | 0.077 | 287.15 | 0.9
0.05737 | 282.15 | 0.077 | 287.15 | 1
0.05737 | 282.15 | 0.077 | 287.65 | 0.15
0.05737 | 282.15 | 0.077 | 287.65 | 0.2
0.05737 | 282.15 | 0.077 | 287.65 | 0.3
0.05737 | 282.15 | 0.077 | 287.65 | 0.4
0.05737 | 282.15 | 0.077 | 287.65 | 0.5
0.05737 | 282.15 | 0.077 | 287.65 | 0.6
0.05737 | 282.15 | 0.077 | 287.65 | 0.7
0.05737 | 282.15 | 0.077 | 287.65 | 0.8
0.05737 | 282.15 | 0.077 | 287.65 | 0.9
0.05737 | 282.15 | 0.077 | 287.65 | 1
0.05737 | 282.15 | 0.077 | 288.15 | 0.15
0.05737 | 282.15 | 0.077 | 288.15 | 0.2
0.05737 | 282.15 | 0.077 | 288.15 | 0.3
0.05737 | 282.15 | 0.077 | 288.15 | 0.4
0.05737 | 282.15 | 0.077 | 288.15 | 0.5
0.05737 | 282.15 | 0.077 | 288.15 | 0.6
0.05737 | 282.15 | 0.077 | 288.15 | 0.7
0.05737 | 282.15 | 0.077 | 288.15 | 0.8
0.05737 | 282.15 | 0.077 | 288.15 | 0.9
0.05737 | 282.15 | 0.077 | 288.15 | 1
0.05737 | 282.15 | 0.077 | 288.65 | 0.15
0.05737 | 282.15 | 0.077 | 288.65 | 0.2
0.05737 | 282.15 | 0.077 | 288.65 | 0.3
0.05737 | 282.15 | 0.077 | 288.65 | 0.4
0.05737 | 282.15 | 0.077 | 288.65 | 0.5
0.05737 | 282.15 | 0.077 | 288.65 | 0.6
0.05737 | 282.15 | 0.077 | 288.65 | 0.7
0.05737 | 282.15 | 0.077 | 288.65 | 0.8
0.05737 | 282.15 | 0.077 | 288.65 | 0.9
0.05737 | 282.15 | 0.077 | 288.65 | 1
0.05737 | 282.15 | 0.077 | 289.15 | 0.15
0.05737 | 282.15 | 0.077 | 289.15 | 0.2
0.05737 | 282.15 | 0.077 | 289.15 | 0.3
0.05737 | 282.15 | 0.077 | 289.15 | 0.4
0.05737 | 282.15 | 0.077 | 289.15 | 0.5
0.05737 | 282.15 | 0.077 | 289.15 | 0.6
0.05737 | 282.15 | 0.077 | 289.15 | 0.7
0.05737 | 282.15 | 0.077 | 289.15 | 0.8
0.05737 | 282.15 | 0.077 | 289.15 | 0.9
0.05737 | 282.15 | 0.077 | 289.15 | 1
0.05737 | 282.15 | 0.077 | 289.65 | 0.15
0.05737 | 282.15 | 0.077 | 289.65 | 0.2
0.05737 | 282.15 | 0.077 | 289.65 | 0.3
0.05737 | 282.15 | 0.077 | 289.65 | 0.4
0.05737 | 282.15 | 0.077 | 289.65 | 0.5
0.05737 | 282.15 | 0.077 | 289.65 | 0.6
0.05737 | 282.15 | 0.077 | 289.65 | 0.7
0.05737 | 282.15 | 0.077 | 289.65 | 0.8
0.05737 | 282.15 | 0.077 | 289.65 | 0.9
0.05737 | 282.15 | 0.077 | 289.65 | 1
0.05737 | 282.15 | 0.077 | 290.15 | 0.15
0.05737 | 282.15 | 0.077 | 290.15 | 0.2
0.05737 | 282.15 | 0.077 | 290.15 | 0.3
0.05737 | 282.15 | 0.077 | 290.15 | 0.4
0.05737 | 282.15 | 0.077 | 290.15 | 0.5
0.05737 | 282.15 | 0.077 | 290.15 | 0.6
0.05737 | 282.15 | 0.077 | 290.15 | 0.7
0.05737 | 282.15 | 0.077 | 290.15 | 0.8
0.05737 | 282.15 | 0.077 | 290.15 | 0.9
0.05737 | 282.15 | 0.077 | 290.15 | 1
0.05737 | 282.15 | 0.077 | 290.65 | 0.15
0.05737 | 282.15 | 0.077 | 290.65 | 0.2
0.05737 | 282.15 | 0.077 | 290.65 | 0.3
0.05737 | 282.15 | 0.077 | 290.65 | 0.4
0.05737 | 282.15 | 0.077 | 290.65 | 0.5
0.05737 | 282.15 | 0.077 | 290.65 | 0.6
0.05737 | 282.15 | 0.077 | 290.65 | 0.7
0.05737 | 282.15 | 0.077 | 290.65 | 0.8
0.05737 | 282.15 | 0.077 | 290.65 | 0.9
0.05737 | 282.15 | 0.077 | 290.65 | 1
0.05737 | 282.15 | 0.077 | 291.15 | 0.15
0.05737 | 282.15 | 0.077 | 291.15 | 0.2
0.05737 | 282.15 | 0.077 | 291.15 | 0.3
0.05737 | 282.15 | 0.077 | 291.15 | 0.4
0.05737 | 282.15 | 0.077 | 291.15 | 0.5
0.05737 | 282.15 | 0.077 | 291.15 | 0.6
0.05737 | 282.15 | 0.077 | 291.15 | 0.7
0.05737 | 282.15 | 0.077 | 291.15 | 0.8
0.05737 | 282.15 | 0.077 | 291.15 | 0.9
0.05737 | 282.15 | 0.077 | 291.15 | 1
0.05737 | 282.15 | 0.077 | 294.15 | 0.15
0.05737 | 282.15 | 0.077 | 294.15 | 0.2
0.05737 | 282.15 | 0.077 | 294.15 | 0.3
0.05737 | 282.15 | 0.077 | 294.15 | 0.4
0.05737 | 282.15 | 0.077 | 294.15 | 0.5
0.05737 | 282.15 | 0.077 | 294.15 | 0.6
0.05737 | 282.15 | 0.077 | 294.15 | 0.7
0.05737 | 282.15 | 0.077 | 294.15 | 0.8
0.05737 | 282.15 | 0.077 | 294.15 | 0.9
0.05737 | 282.15 | 0.077 | 294.15 | 1
0.05737 | 282.15 | 0.077 | 297.15 | 0.15
0.05737 | 282.15 | 0.077 | 297.15 | 0.2
0.05737 | 282.15 | 0.077 | 297.15 | 0.3
0.05737 | 282.15 | 0.077 | 297.15 | 0.4
0.05737 | 282.15 | 0.077 | 297.15 | 0.5
0.05737 | 282.15 | 0.077 | 297.15 | 0.6
0.05737 | 282.15 | 0.077 | 297.15 | 0.7
0.05737 | 282.15 | 0.077 | 297.15 | 0.8
0.05737 | 282.15 | 0.077 | 297.15 | 0.9
0.05737 | 282.15 | 0.077 | 297.15 | 1
0.05737 | 282.15 | 0.077 | 300.15 | 0.15
0.05737 | 282.15 | 0.077 | 300.15 | 0.2
0.05737 | 282.15 | 0.077 | 300.15 | 0.3
0.05737 | 282.15 | 0.077 | 300.15 | 0.4
0.05737 | 282.15 | 0.077 | 300.15 | 0.5
0.05737 | 282.15 | 0.077 | 300.15 | 0.6
0.05737 | 282.15 | 0.077 | 300.15 | 0.7
0.05737 | 282.15 | 0.077 | 300.15 | 0.8
0.05737 | 282.15 | 0.077 | 300.15 | 0.9
0.05737 | 282.15 | 0.077 | 300.15 | 1
0.05737 | 282.15 | 0.077 | 303.15 | 0.15
0.05737 | 282.15 | 0.077 | 303.15 | 0.2
0.05737 | 282.15 | 0.077 | 303.15 | 0.3
0.05737 | 282.15 | 0.077 | 303.15 | 0.4
0.05737 | 282.15 | 0.077 | 303.15 | 0.5
0.05737 | 282.15 | 0.077 | 303.15 | 0.6
0.05737 | 282.15 | 0.077 | 303.15 | 0.7
0.05737 | 282.15 | 0.077 | 303.15 | 0.8
0.05737 | 282.15 | 0.077 | 303.15 | 0.9
0.05737 | 282.15 | 0.077 | 303.15 | 1
0.05737 | 282.15 | 0.09437 | 283.65 | 0.15
0.05737 | 282.15 | 0.09437 | 283.65 | 0.2
0.05737 | 282.15 | 0.09437 | 283.65 | 0.3
0.05737 | 282.15 | 0.09437 | 283.65 | 0.4
0.05737 | 282.15 | 0.09437 | 283.65 | 0.5
0.05737 | 282.15 | 0.09437 | 283.65 | 0.6
0.05737 | 282.15 | 0.09437 | 283.65 | 0.7
0.05737 | 282.15 | 0.09437 | 283.65 | 0.8
0.05737 | 282.15 | 0.09437 | 283.65 | 0.9
0.05737 | 282.15 | 0.09437 | 283.65 | 1
0.05737 | 282.15 | 0.09437 | 284.15 | 0.15
0.05737 | 282.15 | 0.09437 | 284.15 | 0.2
0.05737 | 282.15 | 0.09437 | 284.15 | 0.3
0.05737 | 282.15 | 0.09437 | 284.15 | 0.4
0.05737 | 282.15 | 0.09437 | 284.15 | 0.5
0.05737 | 282.15 | 0.09437 | 284.15 | 0.6
0.05737 | 282.15 | 0.09437 | 284.15 | 0.7
0.05737 | 282.15 | 0.09437 | 284.15 | 0.8
0.05737 | 282.15 | 0.09437 | 284.15 | 0.9
0.05737 | 282.15 | 0.09437 | 284.15 | 1
0.05737 | 282.15 | 0.09437 | 284.65 | 0.15
0.05737 | 282.15 | 0.09437 | 284.65 | 0.2
0.05737 | 282.15 | 0.09437 | 284.65 | 0.3
0.05737 | 282.15 | 0.09437 | 284.65 | 0.4
0.05737 | 282.15 | 0.09437 | 284.65 | 0.5
0.05737 | 282.15 | 0.09437 | 284.65 | 0.6
0.05737 | 282.15 | 0.09437 | 284.65 | 0.7
0.05737 | 282.15 | 0.09437 | 284.65 | 0.8
0.05737 | 282.15 | 0.09437 | 284.65 | 0.9
0.05737 | 282.15 | 0.09437 | 284.65 | 1
0.05737 | 282.15 | 0.09437 | 285.15 | 0.15
0.05737 | 282.15 | 0.09437 | 285.15 | 0.2
0.05737 | 282.15 | 0.09437 | 285.15 | 0.3
0.05737 | 282.15 | 0.09437 | 285.15 | 0.4
0.05737 | 282.15 | 0.09437 | 285.15 | 0.5
0.05737 | 282.15 | 0.09437 | 285.15 | 0.6
0.05737 | 282.15 | 0.09437 | 285.15 | 0.7
0.05737 | 282.15 | 0.09437 | 285.15 | 0.8
0.05737 | 282.15 | 0.09437 | 285.15 | 0.9
0.05737 | 282.15 | 0.09437 | 285.15 | 1
0.05737 | 282.15 | 0.09437 | 285.65 | 0.15
0.05737 | 282.15 | 0.09437 | 285.65 | 0.2
0.05737 | 282.15 | 0.09437 | 285.65 | 0.3
0.05737 | 282.15 | 0.09437 | 285.65 | 0.4
0.05737 | 282.15 | 0.09437 | 285.65 | 0.5
0.05737 | 282.15 | 0.09437 | 285.65 | 0.6
0.05737 | 282.15 | 0.09437 | 285.65 | 0.7
0.05737 | 282.15 | 0.09437 | 285.65 | 0.8
0.05737 | 282.15 | 0.09437 | 285.65 | 0.9
0.05737 | 282.15 | 0.09437 | 285.65 | 1
0.05737 | 282.15 | 0.09437 | 286.15 | 0.15
0.05737 | 282.15 | 0.09437 | 286.15 | 0.2
0.05737 | 282.15 | 0.09437 | 286.15 | 0.3
0.05737 | 282.15 | 0.09437 | 286.15 | 0.4
0.05737 | 282.15 | 0.09437 | 286.15 | 0.5
0.05737 | 282.15 | 0.09437 | 286.15 | 0.6
0.05737 | 282.15 | 0.09437 | 286.15 | 0.7
0.05737 | 282.15 | 0.09437 | 286.15 | 0.8
0.05737 | 282.15 | 0.09437 | 286.15 | 0.9
0.05737 | 282.15 | 0.09437 | 286.15 | 1
0.05737 | 282.15 | 0.09437 | 286.65 | 0.15
0.05737 | 282.15 | 0.09437 | 286.65 | 0.2
0.05737 | 282.15 | 0.09437 | 286.65 | 0.3
0.05737 | 282.15 | 0.09437 | 286.65 | 0.4
0.05737 | 282.15 | 0.09437 | 286.65 | 0.5
0.05737 | 282.15 | 0.09437 | 286.65 | 0.6
0.05737 | 282.15 | 0.09437 | 286.65 | 0.7
0.05737 | 282.15 | 0.09437 | 286.65 | 0.8
0.05737 | 282.15 | 0.09437 | 286.65 | 0.9
0.05737 | 282.15 | 0.09437 | 286.65 | 1
0.05737 | 282.15 | 0.09437 | 287.15 | 0.15
0.05737 | 282.15 | 0.09437 | 287.15 | 0.2
0.05737 | 282.15 | 0.09437 | 287.15 | 0.3
0.05737 | 282.15 | 0.09437 | 287.15 | 0.4
0.05737 | 282.15 | 0.09437 | 287.15 | 0.5
0.05737 | 282.15 | 0.09437 | 287.15 | 0.6
0.05737 | 282.15 | 0.09437 | 287.15 | 0.7
0.05737 | 282.15 | 0.09437 | 287.15 | 0.8
0.05737 | 282.15 | 0.09437 | 287.15 | 0.9
0.05737 | 282.15 | 0.09437 | 287.15 | 1
0.05737 | 282.15 | 0.09437 | 287.65 | 0.15
0.05737 | 282.15 | 0.09437 | 287.65 | 0.2
0.05737 | 282.15 | 0.09437 | 287.65 | 0.3
0.05737 | 282.15 | 0.09437 | 287.65 | 0.4
0.05737 | 282.15 | 0.09437 | 287.65 | 0.5
0.05737 | 282.15 | 0.09437 | 287.65 | 0.6
0.05737 | 282.15 | 0.09437 | 287.65 | 0.7
0.05737 | 282.15 | 0.09437 | 287.65 | 0.8
0.05737 | 282.15 | 0.09437 | 287.65 | 0.9
0.05737 | 282.15 | 0.09437 | 287.65 | 1
0.05737 | 282.15 | 0.09437 | 288.15 | 0.15
0.05737 | 282.15 | 0.09437 | 288.15 | 0.2
0.05737 | 282.15 | 0.09437 | 288.15 | 0.3
0.05737 | 282.15 | 0.09437 | 288.15 | 0.4
0.05737 | 282.15 | 0.09437 | 288.15 | 0.5
0.05737 | 282.15 | 0.09437 | 288.15 | 0.6
0.05737 | 282.15 | 0.09437 | 288.15 | 0.7
0.05737 | 282.15 | 0.09437 | 288.15 | 0.8
0.05737 | 282.15 | 0.09437 | 288.15 | 0.9
0.05737 | 282.15 | 0.09437 | 288.15 | 1
0.05737 | 282.15 | 0.09437 | 288.65 | 0.15
0.05737 | 282.15 | 0.09437 | 288.65 | 0.2
0.05737 | 282.15 | 0.09437 | 288.65 | 0.3
0.05737 | 282.15 | 0.09437 | 288.65 | 0.4
0.05737 | 282.15 | 0.09437 | 288.65 | 0.5
0.05737 | 282.15 | 0.09437 | 288.65 | 0.6
0.05737 | 282.15 | 0.09437 | 288.65 | 0.7
0.05737 | 282.15 | 0.09437 | 288.65 | 0.8
0.05737 | 282.15 | 0.09437 | 288.65 | 0.9
0.05737 | 282.15 | 0.09437 | 288.65 | 1
0.05737 | 282.15 | 0.09437 | 289.15 | 0.15
0.05737 | 282.15 | 0.09437 | 289.15 | 0.2
0.05737 | 282.15 | 0.09437 | 289.15 | 0.3
0.05737 | 282.15 | 0.09437 | 289.15 | 0.4
0.05737 | 282.15 | 0.09437 | 289.15 | 0.5
0.05737 | 282.15 | 0.09437 | 289.15 | 0.6
0.05737 | 282.15 | 0.09437 | 289.15 | 0.7
0.05737 | 282.15 | 0.09437 | 289.15 | 0.8
0.05737 | 282.15 | 0.09437 | 289.15 | 0.9
0.05737 | 282.15 | 0.09437 | 289.15 | 1
0.05737 | 282.15 | 0.09437 | 289.65 | 0.15
0.05737 | 282.15 | 0.09437 | 289.65 | 0.2
0.05737 | 282.15 | 0.09437 | 289.65 | 0.3
0.05737 | 282.15 | 0.09437 | 289.65 | 0.4
0.05737 | 282.15 | 0.09437 | 289.65 | 0.5
0.05737 | 282.15 | 0.09437 | 289.65 | 0.6
0.05737 | 282.15 | 0.09437 | 289.65 | 0.7
0.05737 | 282.15 | 0.09437 | 289.65 | 0.8
0.05737 | 282.15 | 0.09437 | 289.65 | 0.9
0.05737 | 282.15 | 0.09437 | 289.65 | 1
0.05737 | 282.15 | 0.09437 | 290.15 | 0.15
0.05737 | 282.15 | 0.09437 | 290.15 | 0.2
0.05737 | 282.15 | 0.09437 | 290.15 | 0.3
0.05737 | 282.15 | 0.09437 | 290.15 | 0.4
0.05737 | 282.15 | 0.09437 | 290.15 | 0.5
0.05737 | 282.15 | 0.09437 | 290.15 | 0.6
0.05737 | 282.15 | 0.09437 | 290.15 | 0.7
0.05737 | 282.15 | 0.09437 | 290.15 | 0.8
0.05737 | 282.15 | 0.09437 | 290.15 | 0.9
0.05737 | 282.15 | 0.09437 | 290.15 | 1
0.05737 | 282.15 | 0.09437 | 290.65 | 0.15
0.05737 | 282.15 | 0.09437 | 290.65 | 0.2
0.05737 | 282.15 | 0.09437 | 290.65 | 0.3
0.05737 | 282.15 | 0.09437 | 290.65 | 0.4
0.05737 | 282.15 | 0.09437 | 290.65 | 0.5
0.05737 | 282.15 | 0.09437 | 290.65 | 0.6
0.05737 | 282.15 | 0.09437 | 290.65 | 0.7
0.05737 | 282.15 | 0.09437 | 290.65 | 0.8
0.05737 | 282.15 | 0.09437 | 290.65 | 0.9
0.05737 | 282.15 | 0.09437 | 290.65 | 1
0.05737 | 282.15 | 0.09437 | 291.15 | 0.15
0.05737 | 282.15 | 0.09437 | 291.15 | 0.2
0.05737 | 282.15 | 0.09437 | 291.15 | 0.3
0.05737 | 282.15 | 0.09437 | 291.15 | 0.4
0.05737 | 282.15 | 0.09437 | 291.15 | 0.5
0.05737 | 282.15 | 0.09437 | 291.15 | 0.6
0.05737 | 282.15 | 0.09437 | 291.15 | 0.7
0.05737 | 282.15 | 0.09437 | 291.15 | 0.8
0.05737 | 282.15 | 0.09437 | 291.15 | 0.9
0.05737 | 282.15 | 0.09437 | 291.15 | 1
0.05737 | 282.15 | 0.09437 | 294.15 | 0.15
0.05737 | 282.15 | 0.09437 | 294.15 | 0.2
0.05737 | 282.15 | 0.09437 | 294.15 | 0.3
0.05737 | 282.15 | 0.09437 | 294.15 | 0.4
0.05737 | 282.15 | 0.09437 | 294.15 | 0.5
0.05737 | 282.15 | 0.09437 | 294.15 | 0.6
0.05737 | 282.15 | 0.09437 | 294.15 | 0.7
0.05737 | 282.15 | 0.09437 | 294.15 | 0.8
0.05737 | 282.15 | 0.09437 | 294.15 | 0.9
0.05737 | 282.15 | 0.09437 | 294.15 | 1
0.05737 | 282.15 | 0.09437 | 297.15 | 0.15
0.05737 | 282.15 | 0.09437 | 297.15 | 0.2
0.05737 | 282.15 | 0.09437 | 297.15 | 0.3
0.05737 | 282.15 | 0.09437 | 297.15 | 0.4
0.05737 | 282.15 | 0.09437 | 297.15 | 0.5
0.05737 | 282.15 | 0.09437 | 297.15 | 0.6
0.05737 | 282.15 | 0.09437 | 297.15 | 0.7
0.05737 | 282.15 | 0.09437 | 297.15 | 0.8
0.05737 | 282.15 | 0.09437 | 297.15 | 0.9
0.05737 | 282.15 | 0.09437 | 297.15 | 1
0.05737 | 282.15 | 0.09437 | 300.15 | 0.15
0.05737 | 282.15 | 0.09437 | 300.15 | 0.2
0.05737 | 282.15 | 0.09437 | 300.15 | 0.3
0.05737 | 282.15 | 0.09437 | 300.15 | 0.4
0.05737 | 282.15 | 0.09437 | 300.15 | 0.5
0.05737 | 282.15 | 0.09437 | 300.15 | 0.6
0.05737 | 282.15 | 0.09437 | 300.15 | 0.7
0.05737 | 282.15 | 0.09437 | 300.15 | 0.8
0.05737 | 282.15 | 0.09437 | 300.15 | 0.9
0.05737 | 282.15 | 0.09437 | 300.15 | 1
0.05737 | 282.15 | 0.09437 | 303.15 | 0.15
0.05737 | 282.15 | 0.09437 | 303.15 | 0.2
0.05737 | 282.15 | 0.09437 | 303.15 | 0.3
0.05737 | 282.15 | 0.09437 | 303.15 | 0.4
0.05737 | 282.15 | 0.09437 | 303.15 | 0.5
0.05737 | 282.15 | 0.09437 | 303.15 | 0.6
0.05737 | 282.15 | 0.09437 | 303.15 | 0.7
0.05737 | 282.15 | 0.09437 | 303.15 | 0.8
0.05737 | 282.15 | 0.09437 | 303.15 | 0.9
0.05737 | 282.15 | 0.09437 | 303.15 | 1
0.05737 | 282.15 | 0.09644 | 283.65 | 0.15
0.05737 | 282.15 | 0.09644 | 283.65 | 0.2
0.05737 | 282.15 | 0.09644 | 283.65 | 0.3
0.05737 | 282.15 | 0.09644 | 283.65 | 0.4
0.05737 | 282.15 | 0.09644 | 283.65 | 0.5
0.05737 | 282.15 | 0.09644 | 283.65 | 0.6
0.05737 | 282.15 | 0.09644 | 283.65 | 0.7
0.05737 | 282.15 | 0.09644 | 283.65 | 0.8
0.05737 | 282.15 | 0.09644 | 283.65 | 0.9
0.05737 | 282.15 | 0.09644 | 283.65 | 1
0.05737 | 282.15 | 0.09644 | 284.15 | 0.15
0.05737 | 282.15 | 0.09644 | 284.15 | 0.2
0.05737 | 282.15 | 0.09644 | 284.15 | 0.3
0.05737 | 282.15 | 0.09644 | 284.15 | 0.4
0.05737 | 282.15 | 0.09644 | 284.15 | 0.5
0.05737 | 282.15 | 0.09644 | 284.15 | 0.6
0.05737 | 282.15 | 0.09644 | 284.15 | 0.7
0.05737 | 282.15 | 0.09644 | 284.15 | 0.8
0.05737 | 282.15 | 0.09644 | 284.15 | 0.9
0.05737 | 282.15 | 0.09644 | 284.15 | 1
0.05737 | 282.15 | 0.09644 | 284.65 | 0.15
0.05737 | 282.15 | 0.09644 | 284.65 | 0.2
0.05737 | 282.15 | 0.09644 | 284.65 | 0.3
0.05737 | 282.15 | 0.09644 | 284.65 | 0.4
0.05737 | 282.15 | 0.09644 | 284.65 | 0.5
0.05737 | 282.15 | 0.09644 | 284.65 | 0.6
0.05737 | 282.15 | 0.09644 | 284.65 | 0.7
0.05737 | 282.15 | 0.09644 | 284.65 | 0.8
0.05737 | 282.15 | 0.09644 | 284.65 | 0.9
0.05737 | 282.15 | 0.09644 | 284.65 | 1
0.05737 | 282.15 | 0.09644 | 285.15 | 0.15
0.05737 | 282.15 | 0.09644 | 285.15 | 0.2
0.05737 | 282.15 | 0.09644 | 285.15 | 0.3
0.05737 | 282.15 | 0.09644 | 285.15 | 0.4
0.05737 | 282.15 | 0.09644 | 285.15 | 0.5
0.05737 | 282.15 | 0.09644 | 285.15 | 0.6
0.05737 | 282.15 | 0.09644 | 285.15 | 0.7
0.05737 | 282.15 | 0.09644 | 285.15 | 0.8
0.05737 | 282.15 | 0.09644 | 285.15 | 0.9
0.05737 | 282.15 | 0.09644 | 285.15 | 1
0.05737 | 282.15 | 0.09644 | 285.65 | 0.15
0.05737 | 282.15 | 0.09644 | 285.65 | 0.2
0.05737 | 282.15 | 0.09644 | 285.65 | 0.3
0.05737 | 282.15 | 0.09644 | 285.65 | 0.4
0.05737 | 282.15 | 0.09644 | 285.65 | 0.5
0.05737 | 282.15 | 0.09644 | 285.65 | 0.6
0.05737 | 282.15 | 0.09644 | 285.65 | 0.7
0.05737 | 282.15 | 0.09644 | 285.65 | 0.8
0.05737 | 282.15 | 0.09644 | 285.65 | 0.9
0.05737 | 282.15 | 0.09644 | 285.65 | 1
0.05737 | 282.15 | 0.09644 | 286.15 | 0.15
0.05737 | 282.15 | 0.09644 | 286.15 | 0.2
0.05737 | 282.15 | 0.09644 | 286.15 | 0.3
0.05737 | 282.15 | 0.09644 | 286.15 | 0.4
0.05737 | 282.15 | 0.09644 | 286.15 | 0.5
0.05737 | 282.15 | 0.09644 | 286.15 | 0.6
0.05737 | 282.15 | 0.09644 | 286.15 | 0.7
0.05737 | 282.15 | 0.09644 | 286.15 | 0.8
0.05737 | 282.15 | 0.09644 | 286.15 | 0.9
0.05737 | 282.15 | 0.09644 | 286.15 | 1
0.05737 | 282.15 | 0.09644 | 286.65 | 0.15
0.05737 | 282.15 | 0.09644 | 286.65 | 0.2
0.05737 | 282.15 | 0.09644 | 286.65 | 0.3
0.05737 | 282.15 | 0.09644 | 286.65 | 0.4
0.05737 | 282.15 | 0.09644 | 286.65 | 0.5
0.05737 | 282.15 | 0.09644 | 286.65 | 0.6
0.05737 | 282.15 | 0.09644 | 286.65 | 0.7
0.05737 | 282.15 | 0.09644 | 286.65 | 0.8
0.05737 | 282.15 | 0.09644 | 286.65 | 0.9
0.05737 | 282.15 | 0.09644 | 286.65 | 1
0.05737 | 282.15 | 0.09644 | 287.15 | 0.15
0.05737 | 282.15 | 0.09644 | 287.15 | 0.2
0.05737 | 282.15 | 0.09644 | 287.15 | 0.3
0.05737 | 282.15 | 0.09644 | 287.15 | 0.4
0.05737 | 282.15 | 0.09644 | 287.15 | 0.5
0.05737 | 282.15 | 0.09644 | 287.15 | 0.6
0.05737 | 282.15 | 0.09644 | 287.15 | 0.7
0.05737 | 282.15 | 0.09644 | 287.15 | 0.8
0.05737 | 282.15 | 0.09644 | 287.15 | 0.9
0.05737 | 282.15 | 0.09644 | 287.15 | 1
0.05737 | 282.15 | 0.09644 | 287.65 | 0.15
0.05737 | 282.15 | 0.09644 | 287.65 | 0.2
0.05737 | 282.15 | 0.09644 | 287.65 | 0.3
0.05737 | 282.15 | 0.09644 | 287.65 | 0.4
0.05737 | 282.15 | 0.09644 | 287.65 | 0.5
0.05737 | 282.15 | 0.09644 | 287.65 | 0.6
0.05737 | 282.15 | 0.09644 | 287.65 | 0.7
0.05737 | 282.15 | 0.09644 | 287.65 | 0.8
0.05737 | 282.15 | 0.09644 | 287.65 | 0.9
0.05737 | 282.15 | 0.09644 | 287.65 | 1
0.05737 | 282.15 | 0.09644 | 288.15 | 0.15
0.05737 | 282.15 | 0.09644 | 288.15 | 0.2
0.05737 | 282.15 | 0.09644 | 288.15 | 0.3
0.05737 | 282.15 | 0.09644 | 288.15 | 0.4
0.05737 | 282.15 | 0.09644 | 288.15 | 0.5
0.05737 | 282.15 | 0.09644 | 288.15 | 0.6
0.05737 | 282.15 | 0.09644 | 288.15 | 0.7
0.05737 | 282.15 | 0.09644 | 288.15 | 0.8
0.05737 | 282.15 | 0.09644 | 288.15 | 0.9
0.05737 | 282.15 | 0.09644 | 288.15 | 1
0.05737 | 282.15 | 0.09644 | 288.65 | 0.15
0.05737 | 282.15 | 0.09644 | 288.65 | 0.2
0.05737 | 282.15 | 0.09644 | 288.65 | 0.3
0.05737 | 282.15 | 0.09644 | 288.65 | 0.4
0.05737 | 282.15 | 0.09644 | 288.65 | 0.5
0.05737 | 282.15 | 0.09644 | 288.65 | 0.6
0.05737 | 282.15 | 0.09644 | 288.65 | 0.7
0.05737 | 282.15 | 0.09644 | 288.65 | 0.8
0.05737 | 282.15 | 0.09644 | 288.65 | 0.9
0.05737 | 282.15 | 0.09644 | 288.65 | 1
0.05737 | 282.15 | 0.09644 | 289.15 | 0.15
0.05737 | 282.15 | 0.09644 | 289.15 | 0.2
0.05737 | 282.15 | 0.09644 | 289.15 | 0.3
0.05737 | 282.15 | 0.09644 | 289.15 | 0.4
0.05737 | 282.15 | 0.09644 | 289.15 | 0.5
0.05737 | 282.15 | 0.09644 | 289.15 | 0.6
0.05737 | 282.15 | 0.09644 | 289.15 | 0.7
0.05737 | 282.15 | 0.09644 | 289.15 | 0.8
0.05737 | 282.15 | 0.09644 | 289.15 | 0.9
0.05737 | 282.15 | 0.09644 | 289.15 | 1
0.05737 | 282.15 | 0.09644 | 289.65 | 0.15
0.05737 | 282.15 | 0.09644 | 289.65 | 0.2
0.05737 | 282.15 | 0.09644 | 289.65 | 0.3
0.05737 | 282.15 | 0.09644 | 289.65 | 0.4
0.05737 | 282.15 | 0.09644 | 289.65 | 0.5
0.05737 | 282.15 | 0.09644 | 289.65 | 0.6
0.05737 | 282.15 | 0.09644 | 289.65 | 0.7
0.05737 | 282.15 | 0.09644 | 289.65 | 0.8
0.05737 | 282.15 | 0.09644 | 289.65 | 0.9
0.05737 | 282.15 | 0.09644 | 289.65 | 1
0.05737 | 282.15 | 0.09644 | 290.15 | 0.15
0.05737 | 282.15 | 0.09644 | 290.15 | 0.2
0.05737 | 282.15 | 0.09644 | 290.15 | 0.3
0.05737 | 282.15 | 0.09644 | 290.15 | 0.4
0.05737 | 282.15 | 0.09644 | 290.15 | 0.5
0.05737 | 282.15 | 0.09644 | 290.15 | 0.6
0.05737 | 282.15 | 0.09644 | 290.15 | 0.7
0.05737 | 282.15 | 0.09644 | 290.15 | 0.8
0.05737 | 282.15 | 0.09644 | 290.15 | 0.9
0.05737 | 282.15 | 0.09644 | 290.15 | 1
0.05737 | 282.15 | 0.09644 | 290.65 | 0.15
0.05737 | 282.15 | 0.09644 | 290.65 | 0.2
0.05737 | 282.15 | 0.09644 | 290.65 | 0.3
0.05737 | 282.15 | 0.09644 | 290.65 | 0.4
0.05737 | 282.15 | 0.09644 | 290.65 | 0.5
0.05737 | 282.15 | 0.09644 | 290.65 | 0.6
0.05737 | 282.15 | 0.09644 | 290.65 | 0.7
0.05737 | 282.15 | 0.09644 | 290.65 | 0.8
0.05737 | 282.15 | 0.09644 | 290.65 | 0.9
0.05737 | 282.15 | 0.09644 | 290.65 | 1
0.05737 | 282.15 | 0.09644 | 291.15 | 0.15
0.05737 | 282.15 | 0.09644 | 291.15 | 0.2
0.05737 | 282.15 | 0.09644 | 291.15 | 0.3
0.05737 | 282.15 | 0.09644 | 291.15 | 0.4
0.05737 | 282.15 | 0.09644 | 291.15 | 0.5
0.05737 | 282.15 | 0.09644 | 291.15 | 0.6
0.05737 | 282.15 | 0.09644 | 291.15 | 0.7
0.05737 | 282.15 | 0.09644 | 291.15 | 0.8
0.05737 | 282.15 | 0.09644 | 291.15 | 0.9
0.05737 | 282.15 | 0.09644 | 291.15 | 1
0.05737 | 282.15 | 0.09644 | 294.15 | 0.15
0.05737 | 282.15 | 0.09644 | 294.15 | 0.2
0.05737 | 282.15 | 0.09644 | 294.15 | 0.3
0.05737 | 282.15 | 0.09644 | 294.15 | 0.4
0.05737 | 282.15 | 0.09644 | 294.15 | 0.5
0.05737 | 282.15 | 0.09644 | 294.15 | 0.6
0.05737 | 282.15 | 0.09644 | 294.15 | 0.7
0.05737 | 282.15 | 0.09644 | 294.15 | 0.8
0.05737 | 282.15 | 0.09644 | 294.15 | 0.9
0.05737 | 282.15 | 0.09644 | 294.15 | 1
0.05737 | 282.15 | 0.09644 | 297.15 | 0.15
0.05737 | 282.15 | 0.09644 | 297.15 | 0.2
0.05737 | 282.15 | 0.09644 | 297.15 | 0.3
0.05737 | 282.15 | 0.09644 | 297.15 | 0.4
0.05737 | 282.15 | 0.09644 | 297.15 | 0.5
0.05737 | 282.15 | 0.09644 | 297.15 | 0.6
0.05737 | 282.15 | 0.09644 | 297.15 | 0.7
0.05737 | 282.15 | 0.09644 | 297.15 | 0.8
0.05737 | 282.15 | 0.09644 | 297.15 | 0.9
0.05737 | 282.15 | 0.09644 | 297.15 | 1
0.05737 | 282.15 | 0.09644 | 300.15 | 0.15
0.05737 | 282.15 | 0.09644 | 300.15 | 0.2
0.05737 | 282.15 | 0.09644 | 300.15 | 0.3
0.05737 | 282.15 | 0.09644 | 300.15 | 0.4
0.05737 | 282.15 | 0.09644 | 300.15 | 0.5
0.05737 | 282.15 | 0.09644 | 300.15 | 0.6
0.05737 | 282.15 | 0.09644 | 300.15 | 0.7
0.05737 | 282.15 | 0.09644 | 300.15 | 0.8
0.05737 | 282.15 | 0.09644 | 300.15 | 0.9
0.05737 | 282.15 | 0.09644 | 300.15 | 1
0.05737 | 282.15 | 0.09644 | 303.15 | 0.15
0.05737 | 282.15 | 0.09644 | 303.15 | 0.2
0.05737 | 282.15 | 0.09644 | 303.15 | 0.3
0.05737 | 282.15 | 0.09644 | 303.15 | 0.4
0.05737 | 282.15 | 0.09644 | 303.15 | 0.5
0.05737 | 282.15 | 0.09644 | 303.15 | 0.6
0.05737 | 282.15 | 0.09644 | 303.15 | 0.7
0.05737 | 282.15 | 0.09644 | 303.15 | 0.8
0.05737 | 282.15 | 0.09644 | 303.15 | 0.9
0.05737 | 282.15 | 0.09644 | 303.15 | 1
0.05737 | 282.15 | 0.09737 | 283.65 | 0.15
0.05737 | 282.15 | 0.09737 | 283.65 | 0.2
0.05737 | 282.15 | 0.09737 | 283.65 | 0.3
0.05737 | 282.15 | 0.09737 | 283.65 | 0.4
0.05737 | 282.15 | 0.09737 | 283.65 | 0.5
0.05737 | 282.15 | 0.09737 | 283.65 | 0.6
0.05737 | 282.15 | 0.09737 | 283.65 | 0.7
0.05737 | 282.15 | 0.09737 | 283.65 | 0.8
0.05737 | 282.15 | 0.09737 | 283.65 | 0.9
0.05737 | 282.15 | 0.09737 | 283.65 | 1
0.05737 | 282.15 | 0.09737 | 284.15 | 0.15
0.05737 | 282.15 | 0.09737 | 284.15 | 0.2
0.05737 | 282.15 | 0.09737 | 284.15 | 0.3
0.05737 | 282.15 | 0.09737 | 284.15 | 0.4
0.05737 | 282.15 | 0.09737 | 284.15 | 0.5
0.05737 | 282.15 | 0.09737 | 284.15 | 0.6
0.05737 | 282.15 | 0.09737 | 284.15 | 0.7
0.05737 | 282.15 | 0.09737 | 284.15 | 0.8
0.05737 | 282.15 | 0.09737 | 284.15 | 0.9
0.05737 | 282.15 | 0.09737 | 284.15 | 1
0.05737 | 282.15 | 0.09737 | 284.65 | 0.15
0.05737 | 282.15 | 0.09737 | 284.65 | 0.2
0.05737 | 282.15 | 0.09737 | 284.65 | 0.3
0.05737 | 282.15 | 0.09737 | 284.65 | 0.4
0.05737 | 282.15 | 0.09737 | 284.65 | 0.5
0.05737 | 282.15 | 0.09737 | 284.65 | 0.6
0.05737 | 282.15 | 0.09737 | 284.65 | 0.7
0.05737 | 282.15 | 0.09737 | 284.65 | 0.8
0.05737 | 282.15 | 0.09737 | 284.65 | 0.9
0.05737 | 282.15 | 0.09737 | 284.65 | 1
0.05737 | 282.15 | 0.09737 | 285.15 | 0.15
0.05737 | 282.15 | 0.09737 | 285.15 | 0.2
0.05737 | 282.15 | 0.09737 | 285.15 | 0.3
0.05737 | 282.15 | 0.09737 | 285.15 | 0.4
0.05737 | 282.15 | 0.09737 | 285.15 | 0.5
0.05737 | 282.15 | 0.09737 | 285.15 | 0.6
0.05737 | 282.15 | 0.09737 | 285.15 | 0.7
0.05737 | 282.15 | 0.09737 | 285.15 | 0.8
0.05737 | 282.15 | 0.09737 | 285.15 | 0.9
0.05737 | 282.15 | 0.09737 | 285.15 | 1
0.05737 | 282.15 | 0.09737 | 285.65 | 0.15
0.05737 | 282.15 | 0.09737 | 285.65 | 0.2
0.05737 | 282.15 | 0.09737 | 285.65 | 0.3
0.05737 | 282.15 | 0.09737 | 285.65 | 0.4
0.05737 | 282.15 | 0.09737 | 285.65 | 0.5
0.05737 | 282.15 | 0.09737 | 285.65 | 0.6
0.05737 | 282.15 | 0.09737 | 285.65 | 0.7
0.05737 | 282.15 | 0.09737 | 285.65 | 0.8
0.05737 | 282.15 | 0.09737 | 285.65 | 0.9
0.05737 | 282.15 | 0.09737 | 285.65 | 1
0.05737 | 282.15 | 0.09737 | 286.15 | 0.15
0.05737 | 282.15 | 0.09737 | 286.15 | 0.2
0.05737 | 282.15 | 0.09737 | 286.15 | 0.3
0.05737 | 282.15 | 0.09737 | 286.15 | 0.4
0.05737 | 282.15 | 0.09737 | 286.15 | 0.5
0.05737 | 282.15 | 0.09737 | 286.15 | 0.6
0.05737 | 282.15 | 0.09737 | 286.15 | 0.7
0.05737 | 282.15 | 0.09737 | 286.15 | 0.8
0.05737 | 282.15 | 0.09737 | 286.15 | 0.9
0.05737 | 282.15 | 0.09737 | 286.15 | 1
0.05737 | 282.15 | 0.09737 | 286.65 | 0.15
0.05737 | 282.15 | 0.09737 | 286.65 | 0.2
0.05737 | 282.15 | 0.09737 | 286.65 | 0.3
0.05737 | 282.15 | 0.09737 | 286.65 | 0.4
0.05737 | 282.15 | 0.09737 | 286.65 | 0.5
0.05737 | 282.15 | 0.09737 | 286.65 | 0.6
0.05737 | 282.15 | 0.09737 | 286.65 | 0.7
0.05737 | 282.15 | 0.09737 | 286.65 | 0.8
0.05737 | 282.15 | 0.09737 | 286.65 | 0.9
0.05737 | 282.15 | 0.09737 | 286.65 | 1
0.05737 | 282.15 | 0.09737 | 287.15 | 0.15
0.05737 | 282.15 | 0.09737 | 287.15 | 0.2
0.05737 | 282.15 | 0.09737 | 287.15 | 0.3
0.05737 | 282.15 | 0.09737 | 287.15 | 0.4
0.05737 | 282.15 | 0.09737 | 287.15 | 0.5
0.05737 | 282.15 | 0.09737 | 287.15 | 0.6
0.05737 | 282.15 | 0.09737 | 287.15 | 0.7
0.05737 | 282.15 | 0.09737 | 287.15 | 0.8
0.05737 | 282.15 | 0.09737 | 287.15 | 0.9
0.05737 | 282.15 | 0.09737 | 287.15 | 1
0.05737 | 282.15 | 0.09737 | 287.65 | 0.15
0.05737 | 282.15 | 0.09737 | 287.65 | 0.2
0.05737 | 282.15 | 0.09737 | 287.65 | 0.3
0.05737 | 282.15 | 0.09737 | 287.65 | 0.4
0.05737 | 282.15 | 0.09737 | 287.65 | 0.5
0.05737 | 282.15 | 0.09737 | 287.65 | 0.6
0.05737 | 282.15 | 0.09737 | 287.65 | 0.7
0.05737 | 282.15 | 0.09737 | 287.65 | 0.8
0.05737 | 282.15 | 0.09737 | 287.65 | 0.9
0.05737 | 282.15 | 0.09737 | 287.65 | 1
0.05737 | 282.15 | 0.09737 | 288.15 | 0.15
0.05737 | 282.15 | 0.09737 | 288.15 | 0.2
0.05737 | 282.15 | 0.09737 | 288.15 | 0.3
0.05737 | 282.15 | 0.09737 | 288.15 | 0.4
0.05737 | 282.15 | 0.09737 | 288.15 | 0.5
0.05737 | 282.15 | 0.09737 | 288.15 | 0.6
0.05737 | 282.15 | 0.09737 | 288.15 | 0.7
0.05737 | 282.15 | 0.09737 | 288.15 | 0.8
0.05737 | 282.15 | 0.09737 | 288.15 | 0.9
0.05737 | 282.15 | 0.09737 | 288.15 | 1
0.05737 | 282.15 | 0.09737 | 288.65 | 0.15
0.05737 | 282.15 | 0.09737 | 288.65 | 0.2
0.05737 | 282.15 | 0.09737 | 288.65 | 0.3
0.05737 | 282.15 | 0.09737 | 288.65 | 0.4
0.05737 | 282.15 | 0.09737 | 288.65 | 0.5
0.05737 | 282.15 | 0.09737 | 288.65 | 0.6
0.05737 | 282.15 | 0.09737 | 288.65 | 0.7
0.05737 | 282.15 | 0.09737 | 288.65 | 0.8
0.05737 | 282.15 | 0.09737 | 288.65 | 0.9
0.05737 | 282.15 | 0.09737 | 288.65 | 1
0.05737 | 282.15 | 0.09737 | 289.15 | 0.15
0.05737 | 282.15 | 0.09737 | 289.15 | 0.2
0.05737 | 282.15 | 0.09737 | 289.15 | 0.3
0.05737 | 282.15 | 0.09737 | 289.15 | 0.4
0.05737 | 282.15 | 0.09737 | 289.15 | 0.5
0.05737 | 282.15 | 0.09737 | 289.15 | 0.6
0.05737 | 282.15 | 0.09737 | 289.15 | 0.7
0.05737 | 282.15 | 0.09737 | 289.15 | 0.8
0.05737 | 282.15 | 0.09737 | 289.15 | 0.9
0.05737 | 282.15 | 0.09737 | 289.15 | 1
0.05737 | 282.15 | 0.09737 | 289.65 | 0.15
0.05737 | 282.15 | 0.09737 | 289.65 | 0.2
0.05737 | 282.15 | 0.09737 | 289.65 | 0.3
0.05737 | 282.15 | 0.09737 | 289.65 | 0.4
0.05737 | 282.15 | 0.09737 | 289.65 | 0.5
0.05737 | 282.15 | 0.09737 | 289.65 | 0.6
0.05737 | 282.15 | 0.09737 | 289.65 | 0.7
0.05737 | 282.15 | 0.09737 | 289.65 | 0.8
0.05737 | 282.15 | 0.09737 | 289.65 | 0.9
0.05737 | 282.15 | 0.09737 | 289.65 | 1
0.05737 | 282.15 | 0.09737 | 290.15 | 0.15
0.05737 | 282.15 | 0.09737 | 290.15 | 0.2
0.05737 | 282.15 | 0.09737 | 290.15 | 0.3
0.05737 | 282.15 | 0.09737 | 290.15 | 0.4
0.05737 | 282.15 | 0.09737 | 290.15 | 0.5
0.05737 | 282.15 | 0.09737 | 290.15 | 0.6
0.05737 | 282.15 | 0.09737 | 290.15 | 0.7
0.05737 | 282.15 | 0.09737 | 290.15 | 0.8
0.05737 | 282.15 | 0.09737 | 290.15 | 0.9
0.05737 | 282.15 | 0.09737 | 290.15 | 1
0.05737 | 282.15 | 0.09737 | 290.65 | 0.15
0.05737 | 282.15 | 0.09737 | 290.65 | 0.2
0.05737 | 282.15 | 0.09737 | 290.65 | 0.3
0.05737 | 282.15 | 0.09737 | 290.65 | 0.4
0.05737 | 282.15 | 0.09737 | 290.65 | 0.5
0.05737 | 282.15 | 0.09737 | 290.65 | 0.6
0.05737 | 282.15 | 0.09737 | 290.65 | 0.7
0.05737 | 282.15 | 0.09737 | 290.65 | 0.8
0.05737 | 282.15 | 0.09737 | 290.65 | 0.9
0.05737 | 282.15 | 0.09737 | 290.65 | 1
0.05737 | 282.15 | 0.09737 | 291.15 | 0.15
0.05737 | 282.15 | 0.09737 | 291.15 | 0.2
0.05737 | 282.15 | 0.09737 | 291.15 | 0.3
0.05737 | 282.15 | 0.09737 | 291.15 | 0.4
0.05737 | 282.15 | 0.09737 | 291.15 | 0.5
0.05737 | 282.15 | 0.09737 | 291.15 | 0.6
0.05737 | 282.15 | 0.09737 | 291.15 | 0.7
0.05737 | 282.15 | 0.09737 | 291.15 | 0.8
0.05737 | 282.15 | 0.09737 | 291.15 | 0.9
0.05737 | 282.15 | 0.09737 | 291.15 | 1
0.05737 | 282.15 | 0.09737 | 294.15 | 0.15
0.05737 | 282.15 | 0.09737 | 294.15 | 0.2
0.05737 | 282.15 | 0.09737 | 294.15 | 0.3
0.05737 | 282.15 | 0.09737 | 294.15 | 0.4
0.05737 | 282.15 | 0.09737 | 294.15 | 0.5
0.05737 | 282.15 | 0.09737 | 294.15 | 0.6
0.05737 | 282.15 | 0.09737 | 294.15 | 0.7
0.05737 | 282.15 | 0.09737 | 294.15 | 0.8
0.05737 | 282.15 | 0.09737 | 294.15 | 0.9
0.05737 | 282.15 | 0.09737 | 294.15 | 1
0.05737 | 282.15 | 0.09737 | 297.15 | 0.15
0.05737 | 282.15 | 0.09737 | 297.15 | 0.2
0.05737 | 282.15 | 0.09737 | 297.15 | 0.3
0.05737 | 282.15 | 0.09737 | 297.15 | 0.4
0.05737 | 282.15 | 0.09737 | 297.15 | 0.5
0.05737 | 282.15 | 0.09737 | 297.15 | 0.6
0.05737 | 282.15 | 0.09737 | 297.15 | 0.7
0.05737 | 282.15 | 0.09737 | 297.15 | 0.8
0.05737 | 282.15 | 0.09737 | 297.15 | 0.9
0.05737 | 282.15 | 0.09737 | 297.15 | 1
0.05737 | 282.15 | 0.09737 | 300.15 | 0.15
0.05737 | 282.15 | 0.09737 | 300.15 | 0.2
0.05737 | 282.15 | 0.09737 | 300.15 | 0.3
0.05737 | 282.15 | 0.09737 | 300.15 | 0.4
0.05737 | 282.15 | 0.09737 | 300.15 | 0.5
0.05737 | 282.15 | 0.09737 | 300.15 | 0.6
0.05737 | 282.15 | 0.09737 | 300.15 | 0.7
0.05737 | 282.15 | 0.09737 | 300.15 | 0.8
0.05737 | 282.15 | 0.09737 | 300.15 | 0.9
0.05737 | 282.15 | 0.09737 | 300.15 | 1
0.05737 | 282.15 | 0.09737 | 303.15 | 0.15
0.05737 | 282.15 | 0.09737 | 303.15 | 0.2
0.05737 | 282.15 | 0.09737 | 303.15 | 0.3
0.05737 | 282.15 | 0.09737 | 303.15 | 0.4
0.05737 | 282.15 | 0.09737 | 303.15 | 0.5
0.05737 | 282.15 | 0.09737 | 303.15 | 0.6
0.05737 | 282.15 | 0.09737 | 303.15 | 0.7
0.05737 | 282.15 | 0.09737 | 303.15 | 0.8
0.05737 | 282.15 | 0.09737 | 303.15 | 0.9
0.05737 | 282.15 | 0.09737 | 303.15 | 1
0.05737 | 282.15 | 0.115 | 283.65 | 0.15
0.05737 | 282.15 | 0.115 | 283.65 | 0.2
0.05737 | 282.15 | 0.115 | 283.65 | 0.3
0.05737 | 282.15 | 0.115 | 283.65 | 0.4
0.05737 | 282.15 | 0.115 | 283.65 | 0.5
0.05737 | 282.15 | 0.115 | 283.65 | 0.6
0.05737 | 282.15 | 0.115 | 283.65 | 0.7
0.05737 | 282.15 | 0.115 | 283.65 | 0.8
0.05737 | 282.15 | 0.115 | 283.65 | 0.9
0.05737 | 282.15 | 0.115 | 283.65 | 1
0.05737 | 282.15 | 0.115 | 284.15 | 0.15
0.05737 | 282.15 | 0.115 | 284.15 | 0.2
0.05737 | 282.15 | 0.115 | 284.15 | 0.3
0.05737 | 282.15 | 0.115 | 284.15 | 0.4
0.05737 | 282.15 | 0.115 | 284.15 | 0.5
0.05737 | 282.15 | 0.115 | 284.15 | 0.6
0.05737 | 282.15 | 0.115 | 284.15 | 0.7
0.05737 | 282.15 | 0.115 | 284.15 | 0.8
0.05737 | 282.15 | 0.115 | 284.15 | 0.9
0.05737 | 282.15 | 0.115 | 284.15 | 1
0.05737 | 282.15 | 0.115 | 284.65 | 0.15
0.05737 | 282.15 | 0.115 | 284.65 | 0.2
0.05737 | 282.15 | 0.115 | 284.65 | 0.3
0.05737 | 282.15 | 0.115 | 284.65 | 0.4
0.05737 | 282.15 | 0.115 | 284.65 | 0.5
0.05737 | 282.15 | 0.115 | 284.65 | 0.6
0.05737 | 282.15 | 0.115 | 284.65 | 0.7
0.05737 | 282.15 | 0.115 | 284.65 | 0.8
0.05737 | 282.15 | 0.115 | 284.65 | 0.9
0.05737 | 282.15 | 0.115 | 284.65 | 1
0.05737 | 282.15 | 0.115 | 285.15 | 0.15
0.05737 | 282.15 | 0.115 | 285.15 | 0.2
0.05737 | 282.15 | 0.115 | 285.15 | 0.3
0.05737 | 282.15 | 0.115 | 285.15 | 0.4
0.05737 | 282.15 | 0.115 | 285.15 | 0.5
0.05737 | 282.15 | 0.115 | 285.15 | 0.6
0.05737 | 282.15 | 0.115 | 285.15 | 0.7
0.05737 | 282.15 | 0.115 | 285.15 | 0.8
0.05737 | 282.15 | 0.115 | 285.15 | 0.9
0.05737 | 282.15 | 0.115 | 285.15 | 1
0.05737 | 282.15 | 0.115 | 285.65 | 0.15
0.05737 | 282.15 | 0.115 | 285.65 | 0.2
0.05737 | 282.15 | 0.115 | 285.65 | 0.3
0.05737 | 282.15 | 0.115 | 285.65 | 0.4
0.05737 | 282.15 | 0.115 | 285.65 | 0.5
0.05737 | 282.15 | 0.115 | 285.65 | 0.6
0.05737 | 282.15 | 0.115 | 285.65 | 0.7
0.05737 | 282.15 | 0.115 | 285.65 | 0.8
0.05737 | 282.15 | 0.115 | 285.65 | 0.9
0.05737 | 282.15 | 0.115 | 285.65 | 1
0.05737 | 282.15 | 0.115 | 286.15 | 0.15
0.05737 | 282.15 | 0.115 | 286.15 | 0.2
0.05737 | 282.15 | 0.115 | 286.15 | 0.3
0.05737 | 282.15 | 0.115 | 286.15 | 0.4
0.05737 | 282.15 | 0.115 | 286.15 | 0.5
0.05737 | 282.15 | 0.115 | 286.15 | 0.6
0.05737 | 282.15 | 0.115 | 286.15 | 0.7
0.05737 | 282.15 | 0.115 | 286.15 | 0.8
0.05737 | 282.15 | 0.115 | 286.15 | 0.9
0.05737 | 282.15 | 0.115 | 286.15 | 1
0.05737 | 282.15 | 0.115 | 286.65 | 0.15
0.05737 | 282.15 | 0.115 | 286.65 | 0.2
0.05737 | 282.15 | 0.115 | 286.65 | 0.3
0.05737 | 282.15 | 0.115 | 286.65 | 0.4
0.05737 | 282.15 | 0.115 | 286.65 | 0.5
0.05737 | 282.15 | 0.115 | 286.65 | 0.6
0.05737 | 282.15 | 0.115 | 286.65 | 0.7
0.05737 | 282.15 | 0.115 | 286.65 | 0.8
0.05737 | 282.15 | 0.115 | 286.65 | 0.9
0.05737 | 282.15 | 0.115 | 286.65 | 1
0.05737 | 282.15 | 0.115 | 287.15 | 0.15
0.05737 | 282.15 | 0.115 | 287.15 | 0.2
0.05737 | 282.15 | 0.115 | 287.15 | 0.3
0.05737 | 282.15 | 0.115 | 287.15 | 0.4
0.05737 | 282.15 | 0.115 | 287.15 | 0.5
0.05737 | 282.15 | 0.115 | 287.15 | 0.6
0.05737 | 282.15 | 0.115 | 287.15 | 0.7
0.05737 | 282.15 | 0.115 | 287.15 | 0.8
0.05737 | 282.15 | 0.115 | 287.15 | 0.9
0.05737 | 282.15 | 0.115 | 287.15 | 1
0.05737 | 282.15 | 0.115 | 287.65 | 0.15
0.05737 | 282.15 | 0.115 | 287.65 | 0.2
0.05737 | 282.15 | 0.115 | 287.65 | 0.3
0.05737 | 282.15 | 0.115 | 287.65 | 0.4
0.05737 | 282.15 | 0.115 | 287.65 | 0.5
0.05737 | 282.15 | 0.115 | 287.65 | 0.6
0.05737 | 282.15 | 0.115 | 287.65 | 0.7
0.05737 | 282.15 | 0.115 | 287.65 | 0.8
0.05737 | 282.15 | 0.115 | 287.65 | 0.9
0.05737 | 282.15 | 0.115 | 287.65 | 1
0.05737 | 282.15 | 0.115 | 288.15 | 0.15
0.05737 | 282.15 | 0.115 | 288.15 | 0.2
0.05737 | 282.15 | 0.115 | 288.15 | 0.3
0.05737 | 282.15 | 0.115 | 288.15 | 0.4
0.05737 | 282.15 | 0.115 | 288.15 | 0.5
0.05737 | 282.15 | 0.115 | 288.15 | 0.6
0.05737 | 282.15 | 0.115 | 288.15 | 0.7
0.05737 | 282.15 | 0.115 | 288.15 | 0.8
0.05737 | 282.15 | 0.115 | 288.15 | 0.9
0.05737 | 282.15 | 0.115 | 288.15 | 1
0.05737 | 282.15 | 0.115 | 288.65 | 0.15
0.05737 | 282.15 | 0.115 | 288.65 | 0.2
0.05737 | 282.15 | 0.115 | 288.65 | 0.3
0.05737 | 282.15 | 0.115 | 288.65 | 0.4
0.05737 | 282.15 | 0.115 | 288.65 | 0.5
0.05737 | 282.15 | 0.115 | 288.65 | 0.6
0.05737 | 282.15 | 0.115 | 288.65 | 0.7
0.05737 | 282.15 | 0.115 | 288.65 | 0.8
0.05737 | 282.15 | 0.115 | 288.65 | 0.9
0.05737 | 282.15 | 0.115 | 288.65 | 1
0.05737 | 282.15 | 0.115 | 289.15 | 0.15
0.05737 | 282.15 | 0.115 | 289.15 | 0.2
0.05737 | 282.15 | 0.115 | 289.15 | 0.3
0.05737 | 282.15 | 0.115 | 289.15 | 0.4
0.05737 | 282.15 | 0.115 | 289.15 | 0.5
0.05737 | 282.15 | 0.115 | 289.15 | 0.6
0.05737 | 282.15 | 0.115 | 289.15 | 0.7
0.05737 | 282.15 | 0.115 | 289.15 | 0.8
0.05737 | 282.15 | 0.115 | 289.15 | 0.9
0.05737 | 282.15 | 0.115 | 289.15 | 1
0.05737 | 282.15 | 0.115 | 289.65 | 0.15
0.05737 | 282.15 | 0.115 | 289.65 | 0.2
0.05737 | 282.15 | 0.115 | 289.65 | 0.3
0.05737 | 282.15 | 0.115 | 289.65 | 0.4
0.05737 | 282.15 | 0.115 | 289.65 | 0.5
0.05737 | 282.15 | 0.115 | 289.65 | 0.6
0.05737 | 282.15 | 0.115 | 289.65 | 0.7
0.05737 | 282.15 | 0.115 | 289.65 | 0.8
0.05737 | 282.15 | 0.115 | 289.65 | 0.9
0.05737 | 282.15 | 0.115 | 289.65 | 1
0.05737 | 282.15 | 0.115 | 290.15 | 0.15
0.05737 | 282.15 | 0.115 | 290.15 | 0.2
0.05737 | 282.15 | 0.115 | 290.15 | 0.3
0.05737 | 282.15 | 0.115 | 290.15 | 0.4
0.05737 | 282.15 | 0.115 | 290.15 | 0.5
0.05737 | 282.15 | 0.115 | 290.15 | 0.6
0.05737 | 282.15 | 0.115 | 290.15 | 0.7
0.05737 | 282.15 | 0.115 | 290.15 | 0.8
0.05737 | 282.15 | 0.115 | 290.15 | 0.9
0.05737 | 282.15 | 0.115 | 290.15 | 1
0.05737 | 282.15 | 0.115 | 290.65 | 0.15
0.05737 | 282.15 | 0.115 | 290.65 | 0.2
0.05737 | 282.15 | 0.115 | 290.65 | 0.3
0.05737 | 282.15 | 0.115 | 290.65 | 0.4
0.05737 | 282.15 | 0.115 | 290.65 | 0.5
0.05737 | 282.15 | 0.115 | 290.65 | 0.6
0.05737 | 282.15 | 0.115 | 290.65 | 0.7
0.05737 | 282.15 | 0.115 | 290.65 | 0.8
0.05737 | 282.15 | 0.115 | 290.65 | 0.9
0.05737 | 282.15 | 0.115 | 290.65 | 1
0.05737 | 282.15 | 0.115 | 291.15 | 0.15
0.05737 | 282.15 | 0.115 | 291.15 | 0.2
0.05737 | 282.15 | 0.115 | 291.15 | 0.3
0.05737 | 282.15 | 0.115 | 291.15 | 0.4
0.05737 | 282.15 | 0.115 | 291.15 | 0.5
0.05737 | 282.15 | 0.115 | 291.15 | 0.6
0.05737 | 282.15 | 0.115 | 291.15 | 0.7
0.05737 | 282.15 | 0.115 | 291.15 | 0.8
0.05737 | 282.15 | 0.115 | 291.15 | 0.9
0.05737 | 282.15 | 0.115 | 291.15 | 1
0.05737 | 282.15 | 0.115 | 294.15 | 0.15
0.05737 | 282.15 | 0.115 | 294.15 | 0.2
0.05737 | 282.15 | 0.115 | 294.15 | 0.3
0.05737 | 282.15 | 0.115 | 294.15 | 0.4
0.05737 | 282.15 | 0.115 | 294.15 | 0.5
0.05737 | 282.15 | 0.115 | 294.15 | 0.6
0.05737 | 282.15 | 0.115 | 294.15 | 0.7
0.05737 | 282.15 | 0.115 | 294.15 | 0.8
0.05737 | 282.15 | 0.115 | 294.15 | 0.9
0.05737 | 282.15 | 0.115 | 294.15 | 1
0.05737 | 282.15 | 0.115 | 297.15 | 0.15
0.05737 | 282.15 | 0.115 | 297.15 | 0.2
0.05737 | 282.15 | 0.115 | 297.15 | 0.3
0.05737 | 282.15 | 0.115 | 297.15 | 0.4
0.05737 | 282.15 | 0.115 | 297.15 | 0.5
0.05737 | 282.15 | 0.115 | 297.15 | 0.6
0.05737 | 282.15 | 0.115 | 297.15 | 0.7
0.05737 | 282.15 | 0.115 | 297.15 | 0.8
0.05737 | 282.15 | 0.115 | 297.15 | 0.9
0.05737 | 282.15 | 0.115 | 297.15 | 1
0.05737 | 282.15 | 0.115 | 300.15 | 0.15
0.05737 | 282.15 | 0.115 | 300.15 | 0.2
0.05737 | 282.15 | 0.115 | 300.15 | 0.3
0.05737 | 282.15 | 0.115 | 300.15 | 0.4
0.05737 | 282.15 | 0.115 | 300.15 | 0.5
0.05737 | 282.15 | 0.115 | 300.15 | 0.6
0.05737 | 282.15 | 0.115 | 300.15 | 0.7
0.05737 | 282.15 | 0.115 | 300.15 | 0.8
0.05737 | 282.15 | 0.115 | 300.15 | 0.9
0.05737 | 282.15 | 0.115 | 300.15 | 1
0.05737 | 282.15 | 0.115 | 303.15 | 0.15
0.05737 | 282.15 | 0.115 | 303.15 | 0.2
0.05737 | 282.15 | 0.115 | 303.15 | 0.3
0.05737 | 282.15 | 0.115 | 303.15 | 0.4
0.05737 | 282.15 | 0.115 | 303.15 | 0.5
0.05737 | 282.15 | 0.115 | 303.15 | 0.6
0.05737 | 282.15 | 0.115 | 303.15 | 0.7
0.05737 | 282.15 | 0.115 | 303.15 | 0.8
0.05737 | 282.15 | 0.115 | 303.15 | 0.9
0.05737 | 282.15 | 0.115 | 303.15 | 1
0.05856 | 278.15 | 0.00115 | 283.65 | 0.15
0.05856 | 278.15 | 0.00115 | 283.65 | 0.2
0.05856 | 278.15 | 0.00115 | 283.65 | 0.3
0.05856 | 278.15 | 0.00115 | 283.65 | 0.4
0.05856 | 278.15 | 0.00115 | 283.65 | 0.5
0.05856 | 278.15 | 0.00115 | 283.65 | 0.6
0.05856 | 278.15 | 0.00115 | 283.65 | 0.7
0.05856 | 278.15 | 0.00115 | 283.65 | 0.8
0.05856 | 278.15 | 0.00115 | 283.65 | 0.9
0.05856 | 278.15 | 0.00115 | 283.65 | 1
0.05856 | 278.15 | 0.00115 | 284.15 | 0.15
0.05856 | 278.15 | 0.00115 | 284.15 | 0.2
0.05856 | 278.15 | 0.00115 | 284.15 | 0.3
0.05856 | 278.15 | 0.00115 | 284.15 | 0.4
0.05856 | 278.15 | 0.00115 | 284.15 | 0.5
0.05856 | 278.15 | 0.00115 | 284.15 | 0.6
0.05856 | 278.15 | 0.00115 | 284.15 | 0.7
0.05856 | 278.15 | 0.00115 | 284.15 | 0.8
0.05856 | 278.15 | 0.00115 | 284.15 | 0.9
0.05856 | 278.15 | 0.00115 | 284.15 | 1
0.05856 | 278.15 | 0.00115 | 284.65 | 0.15
0.05856 | 278.15 | 0.00115 | 284.65 | 0.2
0.05856 | 278.15 | 0.00115 | 284.65 | 0.3
0.05856 | 278.15 | 0.00115 | 284.65 | 0.4
0.05856 | 278.15 | 0.00115 | 284.65 | 0.5
0.05856 | 278.15 | 0.00115 | 284.65 | 0.6
0.05856 | 278.15 | 0.00115 | 284.65 | 0.7
0.05856 | 278.15 | 0.00115 | 284.65 | 0.8
0.05856 | 278.15 | 0.00115 | 284.65 | 0.9
0.05856 | 278.15 | 0.00115 | 284.65 | 1
0.05856 | 278.15 | 0.00115 | 285.15 | 0.15
0.05856 | 278.15 | 0.00115 | 285.15 | 0.2
0.05856 | 278.15 | 0.00115 | 285.15 | 0.3
0.05856 | 278.15 | 0.00115 | 285.15 | 0.4
0.05856 | 278.15 | 0.00115 | 285.15 | 0.5
0.05856 | 278.15 | 0.00115 | 285.15 | 0.6
0.05856 | 278.15 | 0.00115 | 285.15 | 0.7
0.05856 | 278.15 | 0.00115 | 285.15 | 0.8
0.05856 | 278.15 | 0.00115 | 285.15 | 0.9
0.05856 | 278.15 | 0.00115 | 285.15 | 1
0.05856 | 278.15 | 0.00115 | 285.65 | 0.15
0.05856 | 278.15 | 0.00115 | 285.65 | 0.2
0.05856 | 278.15 | 0.00115 | 285.65 | 0.3
0.05856 | 278.15 | 0.00115 | 285.65 | 0.4
0.05856 | 278.15 | 0.00115 | 285.65 | 0.5
0.05856 | 278.15 | 0.00115 | 285.65 | 0.6
0.05856 | 278.15 | 0.00115 | 285.65 | 0.7
0.05856 | 278.15 | 0.00115 | 285.65 | 0.8
0.05856 | 278.15 | 0.00115 | 285.65 | 0.9
0.05856 | 278.15 | 0.00115 | 285.65 | 1
0.05856 | 278.15 | 0.00115 | 286.15 | 0.15
0.05856 | 278.15 | 0.00115 | 286.15 | 0.2
0.05856 | 278.15 | 0.00115 | 286.15 | 0.3
0.05856 | 278.15 | 0.00115 | 286.15 | 0.4
0.05856 | 278.15 | 0.00115 | 286.15 | 0.5
0.05856 | 278.15 | 0.00115 | 286.15 | 0.6
0.05856 | 278.15 | 0.00115 | 286.15 | 0.7
0.05856 | 278.15 | 0.00115 | 286.15 | 0.8
0.05856 | 278.15 | 0.00115 | 286.15 | 0.9
0.05856 | 278.15 | 0.00115 | 286.15 | 1
0.05856 | 278.15 | 0.00115 | 286.65 | 0.15
0.05856 | 278.15 | 0.00115 | 286.65 | 0.2
0.05856 | 278.15 | 0.00115 | 286.65 | 0.3
0.05856 | 278.15 | 0.00115 | 286.65 | 0.4
0.05856 | 278.15 | 0.00115 | 286.65 | 0.5
0.05856 | 278.15 | 0.00115 | 286.65 | 0.6
0.05856 | 278.15 | 0.00115 | 286.65 | 0.7
0.05856 | 278.15 | 0.00115 | 286.65 | 0.8
0.05856 | 278.15 | 0.00115 | 286.65 | 0.9
0.05856 | 278.15 | 0.00115 | 286.65 | 1
0.05856 | 278.15 | 0.00115 | 287.15 | 0.15
0.05856 | 278.15 | 0.00115 | 287.15 | 0.2
0.05856 | 278.15 | 0.00115 | 287.15 | 0.3
0.05856 | 278.15 | 0.00115 | 287.15 | 0.4
0.05856 | 278.15 | 0.00115 | 287.15 | 0.5
0.05856 | 278.15 | 0.00115 | 287.15 | 0.6
0.05856 | 278.15 | 0.00115 | 287.15 | 0.7
0.05856 | 278.15 | 0.00115 | 287.15 | 0.8
0.05856 | 278.15 | 0.00115 | 287.15 | 0.9
0.05856 | 278.15 | 0.00115 | 287.15 | 1
0.05856 | 278.15 | 0.00115 | 287.65 | 0.15
0.05856 | 278.15 | 0.00115 | 287.65 | 0.2
0.05856 | 278.15 | 0.00115 | 287.65 | 0.3
0.05856 | 278.15 | 0.00115 | 287.65 | 0.4
0.05856 | 278.15 | 0.00115 | 287.65 | 0.5
0.05856 | 278.15 | 0.00115 | 287.65 | 0.6
0.05856 | 278.15 | 0.00115 | 287.65 | 0.7
0.05856 | 278.15 | 0.00115 | 287.65 | 0.8
0.05856 | 278.15 | 0.00115 | 287.65 | 0.9
0.05856 | 278.15 | 0.00115 | 287.65 | 1
0.05856 | 278.15 | 0.00115 | 288.15 | 0.15
0.05856 | 278.15 | 0.00115 | 288.15 | 0.2
0.05856 | 278.15 | 0.00115 | 288.15 | 0.3
0.05856 | 278.15 | 0.00115 | 288.15 | 0.4
0.05856 | 278.15 | 0.00115 | 288.15 | 0.5
0.05856 | 278.15 | 0.00115 | 288.15 | 0.6
0.05856 | 278.15 | 0.00115 | 288.15 | 0.7
0.05856 | 278.15 | 0.00115 | 288.15 | 0.8
0.05856 | 278.15 | 0.00115 | 288.15 | 0.9
0.05856 | 278.15 | 0.00115 | 288.15 | 1
0.05856 | 278.15 | 0.00115 | 288.65 | 0.15
0.05856 | 278.15 | 0.00115 | 288.65 | 0.2
0.05856 | 278.15 | 0.00115 | 288.65 | 0.3
0.05856 | 278.15 | 0.00115 | 288.65 | 0.4
0.05856 | 278.15 | 0.00115 | 288.65 | 0.5
0.05856 | 278.15 | 0.00115 | 288.65 | 0.6
0.05856 | 278.15 | 0.00115 | 288.65 | 0.7
0.05856 | 278.15 | 0.00115 | 288.65 | 0.8
0.05856 | 278.15 | 0.00115 | 288.65 | 0.9
0.05856 | 278.15 | 0.00115 | 288.65 | 1
0.05856 | 278.15 | 0.00115 | 289.15 | 0.15
0.05856 | 278.15 | 0.00115 | 289.15 | 0.2
0.05856 | 278.15 | 0.00115 | 289.15 | 0.3
0.05856 | 278.15 | 0.00115 | 289.15 | 0.4
0.05856 | 278.15 | 0.00115 | 289.15 | 0.5
0.05856 | 278.15 | 0.00115 | 289.15 | 0.6
0.05856 | 278.15 | 0.00115 | 289.15 | 0.7
0.05856 | 278.15 | 0.00115 | 289.15 | 0.8
0.05856 | 278.15 | 0.00115 | 289.15 | 0.9
0.05856 | 278.15 | 0.00115 | 289.15 | 1
0.05856 | 278.15 | 0.00115 | 289.65 | 0.15
0.05856 | 278.15 | 0.00115 | 289.65 | 0.2
0.05856 | 278.15 | 0.00115 | 289.65 | 0.3
0.05856 | 278.15 | 0.00115 | 289.65 | 0.4
0.05856 | 278.15 | 0.00115 | 289.65 | 0.5
0.05856 | 278.15 | 0.00115 | 289.65 | 0.6
0.05856 | 278.15 | 0.00115 | 289.65 | 0.7
0.05856 | 278.15 | 0.00115 | 289.65 | 0.8
0.05856 | 278.15 | 0.00115 | 289.65 | 0.9
0.05856 | 278.15 | 0.00115 | 289.65 | 1
0.05856 | 278.15 | 0.00115 | 290.15 | 0.15
0.05856 | 278.15 | 0.00115 | 290.15 | 0.2
0.05856 | 278.15 | 0.00115 | 290.15 | 0.3
0.05856 | 278.15 | 0.00115 | 290.15 | 0.4
0.05856 | 278.15 | 0.00115 | 290.15 | 0.5
0.05856 | 278.15 | 0.00115 | 290.15 | 0.6
0.05856 | 278.15 | 0.00115 | 290.15 | 0.7
0.05856 | 278.15 | 0.00115 | 290.15 | 0.8
0.05856 | 278.15 | 0.00115 | 290.15 | 0.9
0.05856 | 278.15 | 0.00115 | 290.15 | 1
0.05856 | 278.15 | 0.00115 | 290.65 | 0.15
0.05856 | 278.15 | 0.00115 | 290.65 | 0.2
0.05856 | 278.15 | 0.00115 | 290.65 | 0.3
0.05856 | 278.15 | 0.00115 | 290.65 | 0.4
0.05856 | 278.15 | 0.00115 | 290.65 | 0.5
0.05856 | 278.15 | 0.00115 | 290.65 | 0.6
0.05856 | 278.15 | 0.00115 | 290.65 | 0.7
0.05856 | 278.15 | 0.00115 | 290.65 | 0.8
0.05856 | 278.15 | 0.00115 | 290.65 | 0.9
0.05856 | 278.15 | 0.00115 | 290.65 | 1
0.05856 | 278.15 | 0.00115 | 291.15 | 0.15
0.05856 | 278.15 | 0.00115 | 291.15 | 0.2
0.05856 | 278.15 | 0.00115 | 291.15 | 0.3
0.05856 | 278.15 | 0.00115 | 291.15 | 0.4
0.05856 | 278.15 | 0.00115 | 291.15 | 0.5
0.05856 | 278.15 | 0.00115 | 291.15 | 0.6
0.05856 | 278.15 | 0.00115 | 291.15 | 0.7
0.05856 | 278.15 | 0.00115 | 291.15 | 0.8
0.05856 | 278.15 | 0.00115 | 291.15 | 0.9
0.05856 | 278.15 | 0.00115 | 291.15 | 1
0.05856 | 278.15 | 0.00115 | 294.15 | 0.15
0.05856 | 278.15 | 0.00115 | 294.15 | 0.2
0.05856 | 278.15 | 0.00115 | 294.15 | 0.3
0.05856 | 278.15 | 0.00115 | 294.15 | 0.4
0.05856 | 278.15 | 0.00115 | 294.15 | 0.5
0.05856 | 278.15 | 0.00115 | 294.15 | 0.6
0.05856 | 278.15 | 0.00115 | 294.15 | 0.7
0.05856 | 278.15 | 0.00115 | 294.15 | 0.8
0.05856 | 278.15 | 0.00115 | 294.15 | 0.9
0.05856 | 278.15 | 0.00115 | 294.15 | 1
0.05856 | 278.15 | 0.00115 | 297.15 | 0.15
0.05856 | 278.15 | 0.00115 | 297.15 | 0.2
0.05856 | 278.15 | 0.00115 | 297.15 | 0.3
0.05856 | 278.15 | 0.00115 | 297.15 | 0.4
0.05856 | 278.15 | 0.00115 | 297.15 | 0.5
0.05856 | 278.15 | 0.00115 | 297.15 | 0.6
0.05856 | 278.15 | 0.00115 | 297.15 | 0.7
0.05856 | 278.15 | 0.00115 | 297.15 | 0.8
0.05856 | 278.15 | 0.00115 | 297.15 | 0.9
0.05856 | 278.15 | 0.00115 | 297.15 | 1
0.05856 | 278.15 | 0.00115 | 300.15 | 0.15
0.05856 | 278.15 | 0.00115 | 300.15 | 0.2
0.05856 | 278.15 | 0.00115 | 300.15 | 0.3
0.05856 | 278.15 | 0.00115 | 300.15 | 0.4
0.05856 | 278.15 | 0.00115 | 300.15 | 0.5
0.05856 | 278.15 | 0.00115 | 300.15 | 0.6
0.05856 | 278.15 | 0.00115 | 300.15 | 0.7
0.05856 | 278.15 | 0.00115 | 300.15 | 0.8
0.05856 | 278.15 | 0.00115 | 300.15 | 0.9
0.05856 | 278.15 | 0.00115 | 300.15 | 1
0.05856 | 278.15 | 0.00115 | 303.15 | 0.15
0.05856 | 278.15 | 0.00115 | 303.15 | 0.2
0.05856 | 278.15 | 0.00115 | 303.15 | 0.3
0.05856 | 278.15 | 0.00115 | 303.15 | 0.4
0.05856 | 278.15 | 0.00115 | 303.15 | 0.5
0.05856 | 278.15 | 0.00115 | 303.15 | 0.6
0.05856 | 278.15 | 0.00115 | 303.15 | 0.7
0.05856 | 278.15 | 0.00115 | 303.15 | 0.8
0.05856 | 278.15 | 0.00115 | 303.15 | 0.9
0.05856 | 278.15 | 0.00115 | 303.15 | 1
0.05856 | 278.15 | 0.077 | 283.65 | 0.15
0.05856 | 278.15 | 0.077 | 283.65 | 0.2
0.05856 | 278.15 | 0.077 | 283.65 | 0.3
0.05856 | 278.15 | 0.077 | 283.65 | 0.4
0.05856 | 278.15 | 0.077 | 283.65 | 0.5
0.05856 | 278.15 | 0.077 | 283.65 | 0.6
0.05856 | 278.15 | 0.077 | 283.65 | 0.7
0.05856 | 278.15 | 0.077 | 283.65 | 0.8
0.05856 | 278.15 | 0.077 | 283.65 | 0.9
0.05856 | 278.15 | 0.077 | 283.65 | 1
0.05856 | 278.15 | 0.077 | 284.15 | 0.15
0.05856 | 278.15 | 0.077 | 284.15 | 0.2
0.05856 | 278.15 | 0.077 | 284.15 | 0.3
0.05856 | 278.15 | 0.077 | 284.15 | 0.4
0.05856 | 278.15 | 0.077 | 284.15 | 0.5
0.05856 | 278.15 | 0.077 | 284.15 | 0.6
0.05856 | 278.15 | 0.077 | 284.15 | 0.7
0.05856 | 278.15 | 0.077 | 284.15 | 0.8
0.05856 | 278.15 | 0.077 | 284.15 | 0.9
0.05856 | 278.15 | 0.077 | 284.15 | 1
0.05856 | 278.15 | 0.077 | 284.65 | 0.15
0.05856 | 278.15 | 0.077 | 284.65 | 0.2
0.05856 | 278.15 | 0.077 | 284.65 | 0.3
0.05856 | 278.15 | 0.077 | 284.65 | 0.4
0.05856 | 278.15 | 0.077 | 284.65 | 0.5
0.05856 | 278.15 | 0.077 | 284.65 | 0.6
0.05856 | 278.15 | 0.077 | 284.65 | 0.7
0.05856 | 278.15 | 0.077 | 284.65 | 0.8
0.05856 | 278.15 | 0.077 | 284.65 | 0.9
0.05856 | 278.15 | 0.077 | 284.65 | 1
0.05856 | 278.15 | 0.077 | 285.15 | 0.15
0.05856 | 278.15 | 0.077 | 285.15 | 0.2
0.05856 | 278.15 | 0.077 | 285.15 | 0.3
0.05856 | 278.15 | 0.077 | 285.15 | 0.4
0.05856 | 278.15 | 0.077 | 285.15 | 0.5
0.05856 | 278.15 | 0.077 | 285.15 | 0.6
0.05856 | 278.15 | 0.077 | 285.15 | 0.7
0.05856 | 278.15 | 0.077 | 285.15 | 0.8
0.05856 | 278.15 | 0.077 | 285.15 | 0.9
0.05856 | 278.15 | 0.077 | 285.15 | 1
0.05856 | 278.15 | 0.077 | 285.65 | 0.15
0.05856 | 278.15 | 0.077 | 285.65 | 0.2
0.05856 | 278.15 | 0.077 | 285.65 | 0.3
0.05856 | 278.15 | 0.077 | 285.65 | 0.4
0.05856 | 278.15 | 0.077 | 285.65 | 0.5
0.05856 | 278.15 | 0.077 | 285.65 | 0.6
0.05856 | 278.15 | 0.077 | 285.65 | 0.7
0.05856 | 278.15 | 0.077 | 285.65 | 0.8
0.05856 | 278.15 | 0.077 | 285.65 | 0.9
0.05856 | 278.15 | 0.077 | 285.65 | 1
0.05856 | 278.15 | 0.077 | 286.15 | 0.15
0.05856 | 278.15 | 0.077 | 286.15 | 0.2
0.05856 | 278.15 | 0.077 | 286.15 | 0.3
0.05856 | 278.15 | 0.077 | 286.15 | 0.4
0.05856 | 278.15 | 0.077 | 286.15 | 0.5
0.05856 | 278.15 | 0.077 | 286.15 | 0.6
0.05856 | 278.15 | 0.077 | 286.15 | 0.7
0.05856 | 278.15 | 0.077 | 286.15 | 0.8
0.05856 | 278.15 | 0.077 | 286.15 | 0.9
0.05856 | 278.15 | 0.077 | 286.15 | 1
0.05856 | 278.15 | 0.077 | 286.65 | 0.15
0.05856 | 278.15 | 0.077 | 286.65 | 0.2
0.05856 | 278.15 | 0.077 | 286.65 | 0.3
0.05856 | 278.15 | 0.077 | 286.65 | 0.4
0.05856 | 278.15 | 0.077 | 286.65 | 0.5
0.05856 | 278.15 | 0.077 | 286.65 | 0.6
0.05856 | 278.15 | 0.077 | 286.65 | 0.7
0.05856 | 278.15 | 0.077 | 286.65 | 0.8
0.05856 | 278.15 | 0.077 | 286.65 | 0.9
0.05856 | 278.15 | 0.077 | 286.65 | 1
0.05856 | 278.15 | 0.077 | 287.15 | 0.15
0.05856 | 278.15 | 0.077 | 287.15 | 0.2
0.05856 | 278.15 | 0.077 | 287.15 | 0.3
0.05856 | 278.15 | 0.077 | 287.15 | 0.4
0.05856 | 278.15 | 0.077 | 287.15 | 0.5
0.05856 | 278.15 | 0.077 | 287.15 | 0.6
0.05856 | 278.15 | 0.077 | 287.15 | 0.7
0.05856 | 278.15 | 0.077 | 287.15 | 0.8
0.05856 | 278.15 | 0.077 | 287.15 | 0.9
0.05856 | 278.15 | 0.077 | 287.15 | 1
0.05856 | 278.15 | 0.077 | 287.65 | 0.15
0.05856 | 278.15 | 0.077 | 287.65 | 0.2
0.05856 | 278.15 | 0.077 | 287.65 | 0.3
0.05856 | 278.15 | 0.077 | 287.65 | 0.4
0.05856 | 278.15 | 0.077 | 287.65 | 0.5
0.05856 | 278.15 | 0.077 | 287.65 | 0.6
0.05856 | 278.15 | 0.077 | 287.65 | 0.7
0.05856 | 278.15 | 0.077 | 287.65 | 0.8
0.05856 | 278.15 | 0.077 | 287.65 | 0.9
0.05856 | 278.15 | 0.077 | 287.65 | 1
0.05856 | 278.15 | 0.077 | 288.15 | 0.15
0.05856 | 278.15 | 0.077 | 288.15 | 0.2
0.05856 | 278.15 | 0.077 | 288.15 | 0.3
0.05856 | 278.15 | 0.077 | 288.15 | 0.4
0.05856 | 278.15 | 0.077 | 288.15 | 0.5
0.05856 | 278.15 | 0.077 | 288.15 | 0.6
0.05856 | 278.15 | 0.077 | 288.15 | 0.7
0.05856 | 278.15 | 0.077 | 288.15 | 0.8
0.05856 | 278.15 | 0.077 | 288.15 | 0.9
0.05856 | 278.15 | 0.077 | 288.15 | 1
0.05856 | 278.15 | 0.077 | 288.65 | 0.15
0.05856 | 278.15 | 0.077 | 288.65 | 0.2
0.05856 | 278.15 | 0.077 | 288.65 | 0.3
0.05856 | 278.15 | 0.077 | 288.65 | 0.4
0.05856 | 278.15 | 0.077 | 288.65 | 0.5
0.05856 | 278.15 | 0.077 | 288.65 | 0.6
0.05856 | 278.15 | 0.077 | 288.65 | 0.7
0.05856 | 278.15 | 0.077 | 288.65 | 0.8
0.05856 | 278.15 | 0.077 | 288.65 | 0.9
0.05856 | 278.15 | 0.077 | 288.65 | 1
0.05856 | 278.15 | 0.077 | 289.15 | 0.15
0.05856 | 278.15 | 0.077 | 289.15 | 0.2
0.05856 | 278.15 | 0.077 | 289.15 | 0.3
0.05856 | 278.15 | 0.077 | 289.15 | 0.4
0.05856 | 278.15 | 0.077 | 289.15 | 0.5
0.05856 | 278.15 | 0.077 | 289.15 | 0.6
0.05856 | 278.15 | 0.077 | 289.15 | 0.7
0.05856 | 278.15 | 0.077 | 289.15 | 0.8
0.05856 | 278.15 | 0.077 | 289.15 | 0.9
0.05856 | 278.15 | 0.077 | 289.15 | 1
0.05856 | 278.15 | 0.077 | 289.65 | 0.15
0.05856 | 278.15 | 0.077 | 289.65 | 0.2
0.05856 | 278.15 | 0.077 | 289.65 | 0.3
0.05856 | 278.15 | 0.077 | 289.65 | 0.4
0.05856 | 278.15 | 0.077 | 289.65 | 0.5
0.05856 | 278.15 | 0.077 | 289.65 | 0.6
0.05856 | 278.15 | 0.077 | 289.65 | 0.7
0.05856 | 278.15 | 0.077 | 289.65 | 0.8
0.05856 | 278.15 | 0.077 | 289.65 | 0.9
0.05856 | 278.15 | 0.077 | 289.65 | 1
0.05856 | 278.15 | 0.077 | 290.15 | 0.15
0.05856 | 278.15 | 0.077 | 290.15 | 0.2
0.05856 | 278.15 | 0.077 | 290.15 | 0.3
0.05856 | 278.15 | 0.077 | 290.15 | 0.4
0.05856 | 278.15 | 0.077 | 290.15 | 0.5
0.05856 | 278.15 | 0.077 | 290.15 | 0.6
0.05856 | 278.15 | 0.077 | 290.15 | 0.7
0.05856 | 278.15 | 0.077 | 290.15 | 0.8
0.05856 | 278.15 | 0.077 | 290.15 | 0.9
0.05856 | 278.15 | 0.077 | 290.15 | 1
0.05856 | 278.15 | 0.077 | 290.65 | 0.15
0.05856 | 278.15 | 0.077 | 290.65 | 0.2
0.05856 | 278.15 | 0.077 | 290.65 | 0.3
0.05856 | 278.15 | 0.077 | 290.65 | 0.4
0.05856 | 278.15 | 0.077 | 290.65 | 0.5
0.05856 | 278.15 | 0.077 | 290.65 | 0.6
0.05856 | 278.15 | 0.077 | 290.65 | 0.7
0.05856 | 278.15 | 0.077 | 290.65 | 0.8
0.05856 | 278.15 | 0.077 | 290.65 | 0.9
0.05856 | 278.15 | 0.077 | 290.65 | 1
0.05856 | 278.15 | 0.077 | 291.15 | 0.15
0.05856 | 278.15 | 0.077 | 291.15 | 0.2
0.05856 | 278.15 | 0.077 | 291.15 | 0.3
0.05856 | 278.15 | 0.077 | 291.15 | 0.4
0.05856 | 278.15 | 0.077 | 291.15 | 0.5
0.05856 | 278.15 | 0.077 | 291.15 | 0.6
0.05856 | 278.15 | 0.077 | 291.15 | 0.7
0.05856 | 278.15 | 0.077 | 291.15 | 0.8
0.05856 | 278.15 | 0.077 | 291.15 | 0.9
0.05856 | 278.15 | 0.077 | 291.15 | 1
0.05856 | 278.15 | 0.077 | 294.15 | 0.15
0.05856 | 278.15 | 0.077 | 294.15 | 0.2
0.05856 | 278.15 | 0.077 | 294.15 | 0.3
0.05856 | 278.15 | 0.077 | 294.15 | 0.4
0.05856 | 278.15 | 0.077 | 294.15 | 0.5
0.05856 | 278.15 | 0.077 | 294.15 | 0.6
0.05856 | 278.15 | 0.077 | 294.15 | 0.7
0.05856 | 278.15 | 0.077 | 294.15 | 0.8
0.05856 | 278.15 | 0.077 | 294.15 | 0.9
0.05856 | 278.15 | 0.077 | 294.15 | 1
0.05856 | 278.15 | 0.077 | 297.15 | 0.15
0.05856 | 278.15 | 0.077 | 297.15 | 0.2
0.05856 | 278.15 | 0.077 | 297.15 | 0.3
0.05856 | 278.15 | 0.077 | 297.15 | 0.4
0.05856 | 278.15 | 0.077 | 297.15 | 0.5
0.05856 | 278.15 | 0.077 | 297.15 | 0.6
0.05856 | 278.15 | 0.077 | 297.15 | 0.7
0.05856 | 278.15 | 0.077 | 297.15 | 0.8
0.05856 | 278.15 | 0.077 | 297.15 | 0.9
0.05856 | 278.15 | 0.077 | 297.15 | 1
0.05856 | 278.15 | 0.077 | 300.15 | 0.15
0.05856 | 278.15 | 0.077 | 300.15 | 0.2
0.05856 | 278.15 | 0.077 | 300.15 | 0.3
0.05856 | 278.15 | 0.077 | 300.15 | 0.4
0.05856 | 278.15 | 0.077 | 300.15 | 0.5
0.05856 | 278.15 | 0.077 | 300.15 | 0.6
0.05856 | 278.15 | 0.077 | 300.15 | 0.7
0.05856 | 278.15 | 0.077 | 300.15 | 0.8
0.05856 | 278.15 | 0.077 | 300.15 | 0.9
0.05856 | 278.15 | 0.077 | 300.15 | 1
0.05856 | 278.15 | 0.077 | 303.15 | 0.15
0.05856 | 278.15 | 0.077 | 303.15 | 0.2
0.05856 | 278.15 | 0.077 | 303.15 | 0.3
0.05856 | 278.15 | 0.077 | 303.15 | 0.4
0.05856 | 278.15 | 0.077 | 303.15 | 0.5
0.05856 | 278.15 | 0.077 | 303.15 | 0.6
0.05856 | 278.15 | 0.077 | 303.15 | 0.7
0.05856 | 278.15 | 0.077 | 303.15 | 0.8
0.05856 | 278.15 | 0.077 | 303.15 | 0.9
0.05856 | 278.15 | 0.077 | 303.15 | 1
0.05856 | 278.15 | 0.09437 | 283.65 | 0.15
0.05856 | 278.15 | 0.09437 | 283.65 | 0.2
0.05856 | 278.15 | 0.09437 | 283.65 | 0.3
0.05856 | 278.15 | 0.09437 | 283.65 | 0.4
0.05856 | 278.15 | 0.09437 | 283.65 | 0.5
0.05856 | 278.15 | 0.09437 | 283.65 | 0.6
0.05856 | 278.15 | 0.09437 | 283.65 | 0.7
0.05856 | 278.15 | 0.09437 | 283.65 | 0.8
0.05856 | 278.15 | 0.09437 | 283.65 | 0.9
0.05856 | 278.15 | 0.09437 | 283.65 | 1
0.05856 | 278.15 | 0.09437 | 284.15 | 0.15
0.05856 | 278.15 | 0.09437 | 284.15 | 0.2
0.05856 | 278.15 | 0.09437 | 284.15 | 0.3
0.05856 | 278.15 | 0.09437 | 284.15 | 0.4
0.05856 | 278.15 | 0.09437 | 284.15 | 0.5
0.05856 | 278.15 | 0.09437 | 284.15 | 0.6
0.05856 | 278.15 | 0.09437 | 284.15 | 0.7
0.05856 | 278.15 | 0.09437 | 284.15 | 0.8
0.05856 | 278.15 | 0.09437 | 284.15 | 0.9
0.05856 | 278.15 | 0.09437 | 284.15 | 1
0.05856 | 278.15 | 0.09437 | 284.65 | 0.15
0.05856 | 278.15 | 0.09437 | 284.65 | 0.2
0.05856 | 278.15 | 0.09437 | 284.65 | 0.3
0.05856 | 278.15 | 0.09437 | 284.65 | 0.4
0.05856 | 278.15 | 0.09437 | 284.65 | 0.5
0.05856 | 278.15 | 0.09437 | 284.65 | 0.6
0.05856 | 278.15 | 0.09437 | 284.65 | 0.7
0.05856 | 278.15 | 0.09437 | 284.65 | 0.8
0.05856 | 278.15 | 0.09437 | 284.65 | 0.9
0.05856 | 278.15 | 0.09437 | 284.65 | 1
0.05856 | 278.15 | 0.09437 | 285.15 | 0.15
0.05856 | 278.15 | 0.09437 | 285.15 | 0.2
0.05856 | 278.15 | 0.09437 | 285.15 | 0.3
0.05856 | 278.15 | 0.09437 | 285.15 | 0.4
0.05856 | 278.15 | 0.09437 | 285.15 | 0.5
0.05856 | 278.15 | 0.09437 | 285.15 | 0.6
0.05856 | 278.15 | 0.09437 | 285.15 | 0.7
0.05856 | 278.15 | 0.09437 | 285.15 | 0.8
0.05856 | 278.15 | 0.09437 | 285.15 | 0.9
0.05856 | 278.15 | 0.09437 | 285.15 | 1
0.05856 | 278.15 | 0.09437 | 285.65 | 0.15
0.05856 | 278.15 | 0.09437 | 285.65 | 0.2
0.05856 | 278.15 | 0.09437 | 285.65 | 0.3
0.05856 | 278.15 | 0.09437 | 285.65 | 0.4
0.05856 | 278.15 | 0.09437 | 285.65 | 0.5
0.05856 | 278.15 | 0.09437 | 285.65 | 0.6
0.05856 | 278.15 | 0.09437 | 285.65 | 0.7
0.05856 | 278.15 | 0.09437 | 285.65 | 0.8
0.05856 | 278.15 | 0.09437 | 285.65 | 0.9
0.05856 | 278.15 | 0.09437 | 285.65 | 1
0.05856 | 278.15 | 0.09437 | 286.15 | 0.15
0.05856 | 278.15 | 0.09437 | 286.15 | 0.2
0.05856 | 278.15 | 0.09437 | 286.15 | 0.3
0.05856 | 278.15 | 0.09437 | 286.15 | 0.4
0.05856 | 278.15 | 0.09437 | 286.15 | 0.5
0.05856 | 278.15 | 0.09437 | 286.15 | 0.6
0.05856 | 278.15 | 0.09437 | 286.15 | 0.7
0.05856 | 278.15 | 0.09437 | 286.15 | 0.8
0.05856 | 278.15 | 0.09437 | 286.15 | 0.9
0.05856 | 278.15 | 0.09437 | 286.15 | 1
0.05856 | 278.15 | 0.09437 | 286.65 | 0.15
0.05856 | 278.15 | 0.09437 | 286.65 | 0.2
0.05856 | 278.15 | 0.09437 | 286.65 | 0.3
0.05856 | 278.15 | 0.09437 | 286.65 | 0.4
0.05856 | 278.15 | 0.09437 | 286.65 | 0.5
0.05856 | 278.15 | 0.09437 | 286.65 | 0.6
0.05856 | 278.15 | 0.09437 | 286.65 | 0.7
0.05856 | 278.15 | 0.09437 | 286.65 | 0.8
0.05856 | 278.15 | 0.09437 | 286.65 | 0.9
0.05856 | 278.15 | 0.09437 | 286.65 | 1
0.05856 | 278.15 | 0.09437 | 287.15 | 0.15
0.05856 | 278.15 | 0.09437 | 287.15 | 0.2
0.05856 | 278.15 | 0.09437 | 287.15 | 0.3
0.05856 | 278.15 | 0.09437 | 287.15 | 0.4
0.05856 | 278.15 | 0.09437 | 287.15 | 0.5
0.05856 | 278.15 | 0.09437 | 287.15 | 0.6
0.05856 | 278.15 | 0.09437 | 287.15 | 0.7
0.05856 | 278.15 | 0.09437 | 287.15 | 0.8
0.05856 | 278.15 | 0.09437 | 287.15 | 0.9
0.05856 | 278.15 | 0.09437 | 287.15 | 1
0.05856 | 278.15 | 0.09437 | 287.65 | 0.15
0.05856 | 278.15 | 0.09437 | 287.65 | 0.2
0.05856 | 278.15 | 0.09437 | 287.65 | 0.3
0.05856 | 278.15 | 0.09437 | 287.65 | 0.4
0.05856 | 278.15 | 0.09437 | 287.65 | 0.5
0.05856 | 278.15 | 0.09437 | 287.65 | 0.6
0.05856 | 278.15 | 0.09437 | 287.65 | 0.7
0.05856 | 278.15 | 0.09437 | 287.65 | 0.8
0.05856 | 278.15 | 0.09437 | 287.65 | 0.9
0.05856 | 278.15 | 0.09437 | 287.65 | 1
0.05856 | 278.15 | 0.09437 | 288.15 | 0.15
0.05856 | 278.15 | 0.09437 | 288.15 | 0.2
0.05856 | 278.15 | 0.09437 | 288.15 | 0.3
0.05856 | 278.15 | 0.09437 | 288.15 | 0.4
0.05856 | 278.15 | 0.09437 | 288.15 | 0.5
0.05856 | 278.15 | 0.09437 | 288.15 | 0.6
0.05856 | 278.15 | 0.09437 | 288.15 | 0.7
0.05856 | 278.15 | 0.09437 | 288.15 | 0.8
0.05856 | 278.15 | 0.09437 | 288.15 | 0.9
0.05856 | 278.15 | 0.09437 | 288.15 | 1
0.05856 | 278.15 | 0.09437 | 288.65 | 0.15
0.05856 | 278.15 | 0.09437 | 288.65 | 0.2
0.05856 | 278.15 | 0.09437 | 288.65 | 0.3
0.05856 | 278.15 | 0.09437 | 288.65 | 0.4
0.05856 | 278.15 | 0.09437 | 288.65 | 0.5
0.05856 | 278.15 | 0.09437 | 288.65 | 0.6
0.05856 | 278.15 | 0.09437 | 288.65 | 0.7
0.05856 | 278.15 | 0.09437 | 288.65 | 0.8
0.05856 | 278.15 | 0.09437 | 288.65 | 0.9
0.05856 | 278.15 | 0.09437 | 288.65 | 1
0.05856 | 278.15 | 0.09437 | 289.15 | 0.15
0.05856 | 278.15 | 0.09437 | 289.15 | 0.2
0.05856 | 278.15 | 0.09437 | 289.15 | 0.3
0.05856 | 278.15 | 0.09437 | 289.15 | 0.4
0.05856 | 278.15 | 0.09437 | 289.15 | 0.5
0.05856 | 278.15 | 0.09437 | 289.15 | 0.6
0.05856 | 278.15 | 0.09437 | 289.15 | 0.7
0.05856 | 278.15 | 0.09437 | 289.15 | 0.8
0.05856 | 278.15 | 0.09437 | 289.15 | 0.9
0.05856 | 278.15 | 0.09437 | 289.15 | 1
0.05856 | 278.15 | 0.09437 | 289.65 | 0.15
0.05856 | 278.15 | 0.09437 | 289.65 | 0.2
0.05856 | 278.15 | 0.09437 | 289.65 | 0.3
0.05856 | 278.15 | 0.09437 | 289.65 | 0.4
0.05856 | 278.15 | 0.09437 | 289.65 | 0.5
0.05856 | 278.15 | 0.09437 | 289.65 | 0.6
0.05856 | 278.15 | 0.09437 | 289.65 | 0.7
0.05856 | 278.15 | 0.09437 | 289.65 | 0.8
0.05856 | 278.15 | 0.09437 | 289.65 | 0.9
0.05856 | 278.15 | 0.09437 | 289.65 | 1
0.05856 | 278.15 | 0.09437 | 290.15 | 0.15
0.05856 | 278.15 | 0.09437 | 290.15 | 0.2
0.05856 | 278.15 | 0.09437 | 290.15 | 0.3
0.05856 | 278.15 | 0.09437 | 290.15 | 0.4
0.05856 | 278.15 | 0.09437 | 290.15 | 0.5
0.05856 | 278.15 | 0.09437 | 290.15 | 0.6
0.05856 | 278.15 | 0.09437 | 290.15 | 0.7
0.05856 | 278.15 | 0.09437 | 290.15 | 0.8
0.05856 | 278.15 | 0.09437 | 290.15 | 0.9
0.05856 | 278.15 | 0.09437 | 290.15 | 1
0.05856 | 278.15 | 0.09437 | 290.65 | 0.15
0.05856 | 278.15 | 0.09437 | 290.65 | 0.2
0.05856 | 278.15 | 0.09437 | 290.65 | 0.3
0.05856 | 278.15 | 0.09437 | 290.65 | 0.4
0.05856 | 278.15 | 0.09437 | 290.65 | 0.5
0.05856 | 278.15 | 0.09437 | 290.65 | 0.6
0.05856 | 278.15 | 0.09437 | 290.65 | 0.7
0.05856 | 278.15 | 0.09437 | 290.65 | 0.8
0.05856 | 278.15 | 0.09437 | 290.65 | 0.9
0.05856 | 278.15 | 0.09437 | 290.65 | 1
0.05856 | 278.15 | 0.09437 | 291.15 | 0.15
0.05856 | 278.15 | 0.09437 | 291.15 | 0.2
0.05856 | 278.15 | 0.09437 | 291.15 | 0.3
0.05856 | 278.15 | 0.09437 | 291.15 | 0.4
0.05856 | 278.15 | 0.09437 | 291.15 | 0.5
0.05856 | 278.15 | 0.09437 | 291.15 | 0.6
0.05856 | 278.15 | 0.09437 | 291.15 | 0.7
0.05856 | 278.15 | 0.09437 | 291.15 | 0.8
0.05856 | 278.15 | 0.09437 | 291.15 | 0.9
0.05856 | 278.15 | 0.09437 | 291.15 | 1
0.05856 | 278.15 | 0.09437 | 294.15 | 0.15
0.05856 | 278.15 | 0.09437 | 294.15 | 0.2
0.05856 | 278.15 | 0.09437 | 294.15 | 0.3
0.05856 | 278.15 | 0.09437 | 294.15 | 0.4
0.05856 | 278.15 | 0.09437 | 294.15 | 0.5
0.05856 | 278.15 | 0.09437 | 294.15 | 0.6
0.05856 | 278.15 | 0.09437 | 294.15 | 0.7
0.05856 | 278.15 | 0.09437 | 294.15 | 0.8
0.05856 | 278.15 | 0.09437 | 294.15 | 0.9
0.05856 | 278.15 | 0.09437 | 294.15 | 1
0.05856 | 278.15 | 0.09437 | 297.15 | 0.15
0.05856 | 278.15 | 0.09437 | 297.15 | 0.2
0.05856 | 278.15 | 0.09437 | 297.15 | 0.3
0.05856 | 278.15 | 0.09437 | 297.15 | 0.4
0.05856 | 278.15 | 0.09437 | 297.15 | 0.5
0.05856 | 278.15 | 0.09437 | 297.15 | 0.6
0.05856 | 278.15 | 0.09437 | 297.15 | 0.7
0.05856 | 278.15 | 0.09437 | 297.15 | 0.8
0.05856 | 278.15 | 0.09437 | 297.15 | 0.9
0.05856 | 278.15 | 0.09437 | 297.15 | 1
0.05856 | 278.15 | 0.09437 | 300.15 | 0.15
0.05856 | 278.15 | 0.09437 | 300.15 | 0.2
0.05856 | 278.15 | 0.09437 | 300.15 | 0.3
0.05856 | 278.15 | 0.09437 | 300.15 | 0.4
0.05856 | 278.15 | 0.09437 | 300.15 | 0.5
0.05856 | 278.15 | 0.09437 | 300.15 | 0.6
0.05856 | 278.15 | 0.09437 | 300.15 | 0.7
0.05856 | 278.15 | 0.09437 | 300.15 | 0.8
0.05856 | 278.15 | 0.09437 | 300.15 | 0.9
0.05856 | 278.15 | 0.09437 | 300.15 | 1
0.05856 | 278.15 | 0.09437 | 303.15 | 0.15
0.05856 | 278.15 | 0.09437 | 303.15 | 0.2
0.05856 | 278.15 | 0.09437 | 303.15 | 0.3
0.05856 | 278.15 | 0.09437 | 303.15 | 0.4
0.05856 | 278.15 | 0.09437 | 303.15 | 0.5
0.05856 | 278.15 | 0.09437 | 303.15 | 0.6
0.05856 | 278.15 | 0.09437 | 303.15 | 0.7
0.05856 | 278.15 | 0.09437 | 303.15 | 0.8
0.05856 | 278.15 | 0.09437 | 303.15 | 0.9
0.05856 | 278.15 | 0.09437 | 303.15 | 1
0.05856 | 278.15 | 0.09644 | 283.65 | 0.15
0.05856 | 278.15 | 0.09644 | 283.65 | 0.2
0.05856 | 278.15 | 0.09644 | 283.65 | 0.3
0.05856 | 278.15 | 0.09644 | 283.65 | 0.4
0.05856 | 278.15 | 0.09644 | 283.65 | 0.5
0.05856 | 278.15 | 0.09644 | 283.65 | 0.6
0.05856 | 278.15 | 0.09644 | 283.65 | 0.7
0.05856 | 278.15 | 0.09644 | 283.65 | 0.8
0.05856 | 278.15 | 0.09644 | 283.65 | 0.9
0.05856 | 278.15 | 0.09644 | 283.65 | 1
0.05856 | 278.15 | 0.09644 | 284.15 | 0.15
0.05856 | 278.15 | 0.09644 | 284.15 | 0.2
0.05856 | 278.15 | 0.09644 | 284.15 | 0.3
0.05856 | 278.15 | 0.09644 | 284.15 | 0.4
0.05856 | 278.15 | 0.09644 | 284.15 | 0.5
0.05856 | 278.15 | 0.09644 | 284.15 | 0.6
0.05856 | 278.15 | 0.09644 | 284.15 | 0.7
0.05856 | 278.15 | 0.09644 | 284.15 | 0.8
0.05856 | 278.15 | 0.09644 | 284.15 | 0.9
0.05856 | 278.15 | 0.09644 | 284.15 | 1
0.05856 | 278.15 | 0.09644 | 284.65 | 0.15
0.05856 | 278.15 | 0.09644 | 284.65 | 0.2
0.05856 | 278.15 | 0.09644 | 284.65 | 0.3
0.05856 | 278.15 | 0.09644 | 284.65 | 0.4
0.05856 | 278.15 | 0.09644 | 284.65 | 0.5
0.05856 | 278.15 | 0.09644 | 284.65 | 0.6
0.05856 | 278.15 | 0.09644 | 284.65 | 0.7
0.05856 | 278.15 | 0.09644 | 284.65 | 0.8
0.05856 | 278.15 | 0.09644 | 284.65 | 0.9
0.05856 | 278.15 | 0.09644 | 284.65 | 1
0.05856 | 278.15 | 0.09644 | 285.15 | 0.15
0.05856 | 278.15 | 0.09644 | 285.15 | 0.2
0.05856 | 278.15 | 0.09644 | 285.15 | 0.3
0.05856 | 278.15 | 0.09644 | 285.15 | 0.4
0.05856 | 278.15 | 0.09644 | 285.15 | 0.5
0.05856 | 278.15 | 0.09644 | 285.15 | 0.6
0.05856 | 278.15 | 0.09644 | 285.15 | 0.7
0.05856 | 278.15 | 0.09644 | 285.15 | 0.8
0.05856 | 278.15 | 0.09644 | 285.15 | 0.9
0.05856 | 278.15 | 0.09644 | 285.15 | 1
0.05856 | 278.15 | 0.09644 | 285.65 | 0.15
0.05856 | 278.15 | 0.09644 | 285.65 | 0.2
0.05856 | 278.15 | 0.09644 | 285.65 | 0.3
0.05856 | 278.15 | 0.09644 | 285.65 | 0.4
0.05856 | 278.15 | 0.09644 | 285.65 | 0.5
0.05856 | 278.15 | 0.09644 | 285.65 | 0.6
0.05856 | 278.15 | 0.09644 | 285.65 | 0.7
0.05856 | 278.15 | 0.09644 | 285.65 | 0.8
0.05856 | 278.15 | 0.09644 | 285.65 | 0.9
0.05856 | 278.15 | 0.09644 | 285.65 | 1
0.05856 | 278.15 | 0.09644 | 286.15 | 0.15
0.05856 | 278.15 | 0.09644 | 286.15 | 0.2
0.05856 | 278.15 | 0.09644 | 286.15 | 0.3
0.05856 | 278.15 | 0.09644 | 286.15 | 0.4
0.05856 | 278.15 | 0.09644 | 286.15 | 0.5
0.05856 | 278.15 | 0.09644 | 286.15 | 0.6
0.05856 | 278.15 | 0.09644 | 286.15 | 0.7
0.05856 | 278.15 | 0.09644 | 286.15 | 0.8
0.05856 | 278.15 | 0.09644 | 286.15 | 0.9
0.05856 | 278.15 | 0.09644 | 286.15 | 1
0.05856 | 278.15 | 0.09644 | 286.65 | 0.15
0.05856 | 278.15 | 0.09644 | 286.65 | 0.2
0.05856 | 278.15 | 0.09644 | 286.65 | 0.3
0.05856 | 278.15 | 0.09644 | 286.65 | 0.4
0.05856 | 278.15 | 0.09644 | 286.65 | 0.5
0.05856 | 278.15 | 0.09644 | 286.65 | 0.6
0.05856 | 278.15 | 0.09644 | 286.65 | 0.7
0.05856 | 278.15 | 0.09644 | 286.65 | 0.8
0.05856 | 278.15 | 0.09644 | 286.65 | 0.9
0.05856 | 278.15 | 0.09644 | 286.65 | 1
0.05856 | 278.15 | 0.09644 | 287.15 | 0.15
0.05856 | 278.15 | 0.09644 | 287.15 | 0.2
0.05856 | 278.15 | 0.09644 | 287.15 | 0.3
0.05856 | 278.15 | 0.09644 | 287.15 | 0.4
0.05856 | 278.15 | 0.09644 | 287.15 | 0.5
0.05856 | 278.15 | 0.09644 | 287.15 | 0.6
0.05856 | 278.15 | 0.09644 | 287.15 | 0.7
0.05856 | 278.15 | 0.09644 | 287.15 | 0.8
0.05856 | 278.15 | 0.09644 | 287.15 | 0.9
0.05856 | 278.15 | 0.09644 | 287.15 | 1
0.05856 | 278.15 | 0.09644 | 287.65 | 0.15
0.05856 | 278.15 | 0.09644 | 287.65 | 0.2
0.05856 | 278.15 | 0.09644 | 287.65 | 0.3
0.05856 | 278.15 | 0.09644 | 287.65 | 0.4
0.05856 | 278.15 | 0.09644 | 287.65 | 0.5
0.05856 | 278.15 | 0.09644 | 287.65 | 0.6
0.05856 | 278.15 | 0.09644 | 287.65 | 0.7
0.05856 | 278.15 | 0.09644 | 287.65 | 0.8
0.05856 | 278.15 | 0.09644 | 287.65 | 0.9
0.05856 | 278.15 | 0.09644 | 287.65 | 1
0.05856 | 278.15 | 0.09644 | 288.15 | 0.15
0.05856 | 278.15 | 0.09644 | 288.15 | 0.2
0.05856 | 278.15 | 0.09644 | 288.15 | 0.3
0.05856 | 278.15 | 0.09644 | 288.15 | 0.4
0.05856 | 278.15 | 0.09644 | 288.15 | 0.5
0.05856 | 278.15 | 0.09644 | 288.15 | 0.6
0.05856 | 278.15 | 0.09644 | 288.15 | 0.7
0.05856 | 278.15 | 0.09644 | 288.15 | 0.8
0.05856 | 278.15 | 0.09644 | 288.15 | 0.9
0.05856 | 278.15 | 0.09644 | 288.15 | 1
0.05856 | 278.15 | 0.09644 | 288.65 | 0.15
0.05856 | 278.15 | 0.09644 | 288.65 | 0.2
0.05856 | 278.15 | 0.09644 | 288.65 | 0.3
0.05856 | 278.15 | 0.09644 | 288.65 | 0.4
0.05856 | 278.15 | 0.09644 | 288.65 | 0.5
0.05856 | 278.15 | 0.09644 | 288.65 | 0.6
0.05856 | 278.15 | 0.09644 | 288.65 | 0.7
0.05856 | 278.15 | 0.09644 | 288.65 | 0.8
0.05856 | 278.15 | 0.09644 | 288.65 | 0.9
0.05856 | 278.15 | 0.09644 | 288.65 | 1
0.05856 | 278.15 | 0.09644 | 289.15 | 0.15
0.05856 | 278.15 | 0.09644 | 289.15 | 0.2
0.05856 | 278.15 | 0.09644 | 289.15 | 0.3
0.05856 | 278.15 | 0.09644 | 289.15 | 0.4
0.05856 | 278.15 | 0.09644 | 289.15 | 0.5
0.05856 | 278.15 | 0.09644 | 289.15 | 0.6
0.05856 | 278.15 | 0.09644 | 289.15 | 0.7
0.05856 | 278.15 | 0.09644 | 289.15 | 0.8
0.05856 | 278.15 | 0.09644 | 289.15 | 0.9
0.05856 | 278.15 | 0.09644 | 289.15 | 1
0.05856 | 278.15 | 0.09644 | 289.65 | 0.15
0.05856 | 278.15 | 0.09644 | 289.65 | 0.2
0.05856 | 278.15 | 0.09644 | 289.65 | 0.3
0.05856 | 278.15 | 0.09644 | 289.65 | 0.4
0.05856 | 278.15 | 0.09644 | 289.65 | 0.5
0.05856 | 278.15 | 0.09644 | 289.65 | 0.6
0.05856 | 278.15 | 0.09644 | 289.65 | 0.7
0.05856 | 278.15 | 0.09644 | 289.65 | 0.8
0.05856 | 278.15 | 0.09644 | 289.65 | 0.9
0.05856 | 278.15 | 0.09644 | 289.65 | 1
0.05856 | 278.15 | 0.09644 | 290.15 | 0.15
0.05856 | 278.15 | 0.09644 | 290.15 | 0.2
0.05856 | 278.15 | 0.09644 | 290.15 | 0.3
0.05856 | 278.15 | 0.09644 | 290.15 | 0.4
0.05856 | 278.15 | 0.09644 | 290.15 | 0.5
0.05856 | 278.15 | 0.09644 | 290.15 | 0.6
0.05856 | 278.15 | 0.09644 | 290.15 | 0.7
0.05856 | 278.15 | 0.09644 | 290.15 | 0.8
0.05856 | 278.15 | 0.09644 | 290.15 | 0.9
0.05856 | 278.15 | 0.09644 | 290.15 | 1
0.05856 | 278.15 | 0.09644 | 290.65 | 0.15
0.05856 | 278.15 | 0.09644 | 290.65 | 0.2
0.05856 | 278.15 | 0.09644 | 290.65 | 0.3
0.05856 | 278.15 | 0.09644 | 290.65 | 0.4
0.05856 | 278.15 | 0.09644 | 290.65 | 0.5
0.05856 | 278.15 | 0.09644 | 290.65 | 0.6
0.05856 | 278.15 | 0.09644 | 290.65 | 0.7
0.05856 | 278.15 | 0.09644 | 290.65 | 0.8
0.05856 | 278.15 | 0.09644 | 290.65 | 0.9
0.05856 | 278.15 | 0.09644 | 290.65 | 1
0.05856 | 278.15 | 0.09644 | 291.15 | 0.15
0.05856 | 278.15 | 0.09644 | 291.15 | 0.2
0.05856 | 278.15 | 0.09644 | 291.15 | 0.3
0.05856 | 278.15 | 0.09644 | 291.15 | 0.4
0.05856 | 278.15 | 0.09644 | 291.15 | 0.5
0.05856 | 278.15 | 0.09644 | 291.15 | 0.6
0.05856 | 278.15 | 0.09644 | 291.15 | 0.7
0.05856 | 278.15 | 0.09644 | 291.15 | 0.8
0.05856 | 278.15 | 0.09644 | 291.15 | 0.9
0.05856 | 278.15 | 0.09644 | 291.15 | 1
0.05856 | 278.15 | 0.09644 | 294.15 | 0.15
0.05856 | 278.15 | 0.09644 | 294.15 | 0.2
0.05856 | 278.15 | 0.09644 | 294.15 | 0.3
0.05856 | 278.15 | 0.09644 | 294.15 | 0.4
0.05856 | 278.15 | 0.09644 | 294.15 | 0.5
0.05856 | 278.15 | 0.09644 | 294.15 | 0.6
0.05856 | 278.15 | 0.09644 | 294.15 | 0.7
0.05856 | 278.15 | 0.09644 | 294.15 | 0.8
0.05856 | 278.15 | 0.09644 | 294.15 | 0.9
0.05856 | 278.15 | 0.09644 | 294.15 | 1
0.05856 | 278.15 | 0.09644 | 297.15 | 0.15
0.05856 | 278.15 | 0.09644 | 297.15 | 0.2
0.05856 | 278.15 | 0.09644 | 297.15 | 0.3
0.05856 | 278.15 | 0.09644 | 297.15 | 0.4
0.05856 | 278.15 | 0.09644 | 297.15 | 0.5
0.05856 | 278.15 | 0.09644 | 297.15 | 0.6
0.05856 | 278.15 | 0.09644 | 297.15 | 0.7
0.05856 | 278.15 | 0.09644 | 297.15 | 0.8
0.05856 | 278.15 | 0.09644 | 297.15 | 0.9
0.05856 | 278.15 | 0.09644 | 297.15 | 1
0.05856 | 278.15 | 0.09644 | 300.15 | 0.15
0.05856 | 278.15 | 0.09644 | 300.15 | 0.2
0.05856 | 278.15 | 0.09644 | 300.15 | 0.3
0.05856 | 278.15 | 0.09644 | 300.15 | 0.4
0.05856 | 278.15 | 0.09644 | 300.15 | 0.5
0.05856 | 278.15 | 0.09644 | 300.15 | 0.6
0.05856 | 278.15 | 0.09644 | 300.15 | 0.7
0.05856 | 278.15 | 0.09644 | 300.15 | 0.8
0.05856 | 278.15 | 0.09644 | 300.15 | 0.9
0.05856 | 278.15 | 0.09644 | 300.15 | 1
0.05856 | 278.15 | 0.09644 | 303.15 | 0.15
0.05856 | 278.15 | 0.09644 | 303.15 | 0.2
0.05856 | 278.15 | 0.09644 | 303.15 | 0.3
0.05856 | 278.15 | 0.09644 | 303.15 | 0.4
0.05856 | 278.15 | 0.09644 | 303.15 | 0.5
0.05856 | 278.15 | 0.09644 | 303.15 | 0.6
0.05856 | 278.15 | 0.09644 | 303.15 | 0.7
0.05856 | 278.15 | 0.09644 | 303.15 | 0.8
0.05856 | 278.15 | 0.09644 | 303.15 | 0.9
0.05856 | 278.15 | 0.09644 | 303.15 | 1
0.05856 | 278.15 | 0.09737 | 283.65 | 0.15
0.05856 | 278.15 | 0.09737 | 283.65 | 0.2
0.05856 | 278.15 | 0.09737 | 283.65 | 0.3
0.05856 | 278.15 | 0.09737 | 283.65 | 0.4
0.05856 | 278.15 | 0.09737 | 283.65 | 0.5
0.05856 | 278.15 | 0.09737 | 283.65 | 0.6
0.05856 | 278.15 | 0.09737 | 283.65 | 0.7
0.05856 | 278.15 | 0.09737 | 283.65 | 0.8
0.05856 | 278.15 | 0.09737 | 283.65 | 0.9
0.05856 | 278.15 | 0.09737 | 283.65 | 1
0.05856 | 278.15 | 0.09737 | 284.15 | 0.15
0.05856 | 278.15 | 0.09737 | 284.15 | 0.2
0.05856 | 278.15 | 0.09737 | 284.15 | 0.3
0.05856 | 278.15 | 0.09737 | 284.15 | 0.4
0.05856 | 278.15 | 0.09737 | 284.15 | 0.5
0.05856 | 278.15 | 0.09737 | 284.15 | 0.6
0.05856 | 278.15 | 0.09737 | 284.15 | 0.7
0.05856 | 278.15 | 0.09737 | 284.15 | 0.8
0.05856 | 278.15 | 0.09737 | 284.15 | 0.9
0.05856 | 278.15 | 0.09737 | 284.15 | 1
0.05856 | 278.15 | 0.09737 | 284.65 | 0.15
0.05856 | 278.15 | 0.09737 | 284.65 | 0.2
0.05856 | 278.15 | 0.09737 | 284.65 | 0.3
0.05856 | 278.15 | 0.09737 | 284.65 | 0.4
0.05856 | 278.15 | 0.09737 | 284.65 | 0.5
0.05856 | 278.15 | 0.09737 | 284.65 | 0.6
0.05856 | 278.15 | 0.09737 | 284.65 | 0.7
0.05856 | 278.15 | 0.09737 | 284.65 | 0.8
0.05856 | 278.15 | 0.09737 | 284.65 | 0.9
0.05856 | 278.15 | 0.09737 | 284.65 | 1
0.05856 | 278.15 | 0.09737 | 285.15 | 0.15
0.05856 | 278.15 | 0.09737 | 285.15 | 0.2
0.05856 | 278.15 | 0.09737 | 285.15 | 0.3
0.05856 | 278.15 | 0.09737 | 285.15 | 0.4
0.05856 | 278.15 | 0.09737 | 285.15 | 0.5
0.05856 | 278.15 | 0.09737 | 285.15 | 0.6
0.05856 | 278.15 | 0.09737 | 285.15 | 0.7
0.05856 | 278.15 | 0.09737 | 285.15 | 0.8
0.05856 | 278.15 | 0.09737 | 285.15 | 0.9
0.05856 | 278.15 | 0.09737 | 285.15 | 1
0.05856 | 278.15 | 0.09737 | 285.65 | 0.15
0.05856 | 278.15 | 0.09737 | 285.65 | 0.2
0.05856 | 278.15 | 0.09737 | 285.65 | 0.3
0.05856 | 278.15 | 0.09737 | 285.65 | 0.4
0.05856 | 278.15 | 0.09737 | 285.65 | 0.5
0.05856 | 278.15 | 0.09737 | 285.65 | 0.6
0.05856 | 278.15 | 0.09737 | 285.65 | 0.7
0.05856 | 278.15 | 0.09737 | 285.65 | 0.8
0.05856 | 278.15 | 0.09737 | 285.65 | 0.9
0.05856 | 278.15 | 0.09737 | 285.65 | 1
0.05856 | 278.15 | 0.09737 | 286.15 | 0.15
0.05856 | 278.15 | 0.09737 | 286.15 | 0.2
0.05856 | 278.15 | 0.09737 | 286.15 | 0.3
0.05856 | 278.15 | 0.09737 | 286.15 | 0.4
0.05856 | 278.15 | 0.09737 | 286.15 | 0.5
0.05856 | 278.15 | 0.09737 | 286.15 | 0.6
0.05856 | 278.15 | 0.09737 | 286.15 | 0.7
0.05856 | 278.15 | 0.09737 | 286.15 | 0.8
0.05856 | 278.15 | 0.09737 | 286.15 | 0.9
0.05856 | 278.15 | 0.09737 | 286.15 | 1
0.05856 | 278.15 | 0.09737 | 286.65 | 0.15
0.05856 | 278.15 | 0.09737 | 286.65 | 0.2
0.05856 | 278.15 | 0.09737 | 286.65 | 0.3
0.05856 | 278.15 | 0.09737 | 286.65 | 0.4
0.05856 | 278.15 | 0.09737 | 286.65 | 0.5
0.05856 | 278.15 | 0.09737 | 286.65 | 0.6
0.05856 | 278.15 | 0.09737 | 286.65 | 0.7
0.05856 | 278.15 | 0.09737 | 286.65 | 0.8
0.05856 | 278.15 | 0.09737 | 286.65 | 0.9
0.05856 | 278.15 | 0.09737 | 286.65 | 1
0.05856 | 278.15 | 0.09737 | 287.15 | 0.15
0.05856 | 278.15 | 0.09737 | 287.15 | 0.2
0.05856 | 278.15 | 0.09737 | 287.15 | 0.3
0.05856 | 278.15 | 0.09737 | 287.15 | 0.4
0.05856 | 278.15 | 0.09737 | 287.15 | 0.5
0.05856 | 278.15 | 0.09737 | 287.15 | 0.6
0.05856 | 278.15 | 0.09737 | 287.15 | 0.7
0.05856 | 278.15 | 0.09737 | 287.15 | 0.8
0.05856 | 278.15 | 0.09737 | 287.15 | 0.9
0.05856 | 278.15 | 0.09737 | 287.15 | 1
0.05856 | 278.15 | 0.09737 | 287.65 | 0.15
0.05856 | 278.15 | 0.09737 | 287.65 | 0.2
0.05856 | 278.15 | 0.09737 | 287.65 | 0.3
0.05856 | 278.15 | 0.09737 | 287.65 | 0.4
0.05856 | 278.15 | 0.09737 | 287.65 | 0.5
0.05856 | 278.15 | 0.09737 | 287.65 | 0.6
0.05856 | 278.15 | 0.09737 | 287.65 | 0.7
0.05856 | 278.15 | 0.09737 | 287.65 | 0.8
0.05856 | 278.15 | 0.09737 | 287.65 | 0.9
0.05856 | 278.15 | 0.09737 | 287.65 | 1
0.05856 | 278.15 | 0.09737 | 288.15 | 0.15
0.05856 | 278.15 | 0.09737 | 288.15 | 0.2
0.05856 | 278.15 | 0.09737 | 288.15 | 0.3
0.05856 | 278.15 | 0.09737 | 288.15 | 0.4
0.05856 | 278.15 | 0.09737 | 288.15 | 0.5
0.05856 | 278.15 | 0.09737 | 288.15 | 0.6
0.05856 | 278.15 | 0.09737 | 288.15 | 0.7
0.05856 | 278.15 | 0.09737 | 288.15 | 0.8
0.05856 | 278.15 | 0.09737 | 288.15 | 0.9
0.05856 | 278.15 | 0.09737 | 288.15 | 1
0.05856 | 278.15 | 0.09737 | 288.65 | 0.15
0.05856 | 278.15 | 0.09737 | 288.65 | 0.2
0.05856 | 278.15 | 0.09737 | 288.65 | 0.3
0.05856 | 278.15 | 0.09737 | 288.65 | 0.4
0.05856 | 278.15 | 0.09737 | 288.65 | 0.5
0.05856 | 278.15 | 0.09737 | 288.65 | 0.6
0.05856 | 278.15 | 0.09737 | 288.65 | 0.7
0.05856 | 278.15 | 0.09737 | 288.65 | 0.8
0.05856 | 278.15 | 0.09737 | 288.65 | 0.9
0.05856 | 278.15 | 0.09737 | 288.65 | 1
0.05856 | 278.15 | 0.09737 | 289.15 | 0.15
0.05856 | 278.15 | 0.09737 | 289.15 | 0.2
0.05856 | 278.15 | 0.09737 | 289.15 | 0.3
0.05856 | 278.15 | 0.09737 | 289.15 | 0.4
0.05856 | 278.15 | 0.09737 | 289.15 | 0.5
0.05856 | 278.15 | 0.09737 | 289.15 | 0.6
0.05856 | 278.15 | 0.09737 | 289.15 | 0.7
0.05856 | 278.15 | 0.09737 | 289.15 | 0.8
0.05856 | 278.15 | 0.09737 | 289.15 | 0.9
0.05856 | 278.15 | 0.09737 | 289.15 | 1
0.05856 | 278.15 | 0.09737 | 289.65 | 0.15
0.05856 | 278.15 | 0.09737 | 289.65 | 0.2
0.05856 | 278.15 | 0.09737 | 289.65 | 0.3
0.05856 | 278.15 | 0.09737 | 289.65 | 0.4
0.05856 | 278.15 | 0.09737 | 289.65 | 0.5
0.05856 | 278.15 | 0.09737 | 289.65 | 0.6
0.05856 | 278.15 | 0.09737 | 289.65 | 0.7
0.05856 | 278.15 | 0.09737 | 289.65 | 0.8
0.05856 | 278.15 | 0.09737 | 289.65 | 0.9
0.05856 | 278.15 | 0.09737 | 289.65 | 1
0.05856 | 278.15 | 0.09737 | 290.15 | 0.15
0.05856 | 278.15 | 0.09737 | 290.15 | 0.2
0.05856 | 278.15 | 0.09737 | 290.15 | 0.3
0.05856 | 278.15 | 0.09737 | 290.15 | 0.4
0.05856 | 278.15 | 0.09737 | 290.15 | 0.5
0.05856 | 278.15 | 0.09737 | 290.15 | 0.6
0.05856 | 278.15 | 0.09737 | 290.15 | 0.7
0.05856 | 278.15 | 0.09737 | 290.15 | 0.8
0.05856 | 278.15 | 0.09737 | 290.15 | 0.9
0.05856 | 278.15 | 0.09737 | 290.15 | 1
0.05856 | 278.15 | 0.09737 | 290.65 | 0.15
0.05856 | 278.15 | 0.09737 | 290.65 | 0.2
0.05856 | 278.15 | 0.09737 | 290.65 | 0.3
0.05856 | 278.15 | 0.09737 | 290.65 | 0.4
0.05856 | 278.15 | 0.09737 | 290.65 | 0.5
0.05856 | 278.15 | 0.09737 | 290.65 | 0.6
0.05856 | 278.15 | 0.09737 | 290.65 | 0.7
0.05856 | 278.15 | 0.09737 | 290.65 | 0.8
0.05856 | 278.15 | 0.09737 | 290.65 | 0.9
0.05856 | 278.15 | 0.09737 | 290.65 | 1
0.05856 | 278.15 | 0.09737 | 291.15 | 0.15
0.05856 | 278.15 | 0.09737 | 291.15 | 0.2
0.05856 | 278.15 | 0.09737 | 291.15 | 0.3
0.05856 | 278.15 | 0.09737 | 291.15 | 0.4
0.05856 | 278.15 | 0.09737 | 291.15 | 0.5
0.05856 | 278.15 | 0.09737 | 291.15 | 0.6
0.05856 | 278.15 | 0.09737 | 291.15 | 0.7
0.05856 | 278.15 | 0.09737 | 291.15 | 0.8
0.05856 | 278.15 | 0.09737 | 291.15 | 0.9
0.05856 | 278.15 | 0.09737 | 291.15 | 1
0.05856 | 278.15 | 0.09737 | 294.15 | 0.15
0.05856 | 278.15 | 0.09737 | 294.15 | 0.2
0.05856 | 278.15 | 0.09737 | 294.15 | 0.3
0.05856 | 278.15 | 0.09737 | 294.15 | 0.4
0.05856 | 278.15 | 0.09737 | 294.15 | 0.5
0.05856 | 278.15 | 0.09737 | 294.15 | 0.6
0.05856 | 278.15 | 0.09737 | 294.15 | 0.7
0.05856 | 278.15 | 0.09737 | 294.15 | 0.8
0.05856 | 278.15 | 0.09737 | 294.15 | 0.9
0.05856 | 278.15 | 0.09737 | 294.15 | 1
0.05856 | 278.15 | 0.09737 | 297.15 | 0.15
0.05856 | 278.15 | 0.09737 | 297.15 | 0.2
0.05856 | 278.15 | 0.09737 | 297.15 | 0.3
0.05856 | 278.15 | 0.09737 | 297.15 | 0.4
0.05856 | 278.15 | 0.09737 | 297.15 | 0.5
0.05856 | 278.15 | 0.09737 | 297.15 | 0.6
0.05856 | 278.15 | 0.09737 | 297.15 | 0.7
0.05856 | 278.15 | 0.09737 | 297.15 | 0.8
0.05856 | 278.15 | 0.09737 | 297.15 | 0.9
0.05856 | 278.15 | 0.09737 | 297.15 | 1
0.05856 | 278.15 | 0.09737 | 300.15 | 0.15
0.05856 | 278.15 | 0.09737 | 300.15 | 0.2
0.05856 | 278.15 | 0.09737 | 300.15 | 0.3
0.05856 | 278.15 | 0.09737 | 300.15 | 0.4
0.05856 | 278.15 | 0.09737 | 300.15 | 0.5
0.05856 | 278.15 | 0.09737 | 300.15 | 0.6
0.05856 | 278.15 | 0.09737 | 300.15 | 0.7
0.05856 | 278.15 | 0.09737 | 300.15 | 0.8
0.05856 | 278.15 | 0.09737 | 300.15 | 0.9
0.05856 | 278.15 | 0.09737 | 300.15 | 1
0.05856 | 278.15 | 0.09737 | 303.15 | 0.15
0.05856 | 278.15 | 0.09737 | 303.15 | 0.2
0.05856 | 278.15 | 0.09737 | 303.15 | 0.3
0.05856 | 278.15 | 0.09737 | 303.15 | 0.4
0.05856 | 278.15 | 0.09737 | 303.15 | 0.5
0.05856 | 278.15 | 0.09737 | 303.15 | 0.6
0.05856 | 278.15 | 0.09737 | 303.15 | 0.7
0.05856 | 278.15 | 0.09737 | 303.15 | 0.8
0.05856 | 278.15 | 0.09737 | 303.15 | 0.9
0.05856 | 278.15 | 0.09737 | 303.15 | 1
0.05856 | 278.15 | 0.115 | 283.65 | 0.15
0.05856 | 278.15 | 0.115 | 283.65 | 0.2
0.05856 | 278.15 | 0.115 | 283.65 | 0.3
0.05856 | 278.15 | 0.115 | 283.65 | 0.4
0.05856 | 278.15 | 0.115 | 283.65 | 0.5
0.05856 | 278.15 | 0.115 | 283.65 | 0.6
0.05856 | 278.15 | 0.115 | 283.65 | 0.7
0.05856 | 278.15 | 0.115 | 283.65 | 0.8
0.05856 | 278.15 | 0.115 | 283.65 | 0.9
0.05856 | 278.15 | 0.115 | 283.65 | 1
0.05856 | 278.15 | 0.115 | 284.15 | 0.15
0.05856 | 278.15 | 0.115 | 284.15 | 0.2
0.05856 | 278.15 | 0.115 | 284.15 | 0.3
0.05856 | 278.15 | 0.115 | 284.15 | 0.4
0.05856 | 278.15 | 0.115 | 284.15 | 0.5
0.05856 | 278.15 | 0.115 | 284.15 | 0.6
0.05856 | 278.15 | 0.115 | 284.15 | 0.7
0.05856 | 278.15 | 0.115 | 284.15 | 0.8
0.05856 | 278.15 | 0.115 | 284.15 | 0.9
0.05856 | 278.15 | 0.115 | 284.15 | 1
0.05856 | 278.15 | 0.115 | 284.65 | 0.15
0.05856 | 278.15 | 0.115 | 284.65 | 0.2
0.05856 | 278.15 | 0.115 | 284.65 | 0.3
0.05856 | 278.15 | 0.115 | 284.65 | 0.4
0.05856 | 278.15 | 0.115 | 284.65 | 0.5
0.05856 | 278.15 | 0.115 | 284.65 | 0.6
0.05856 | 278.15 | 0.115 | 284.65 | 0.7
0.05856 | 278.15 | 0.115 | 284.65 | 0.8
0.05856 | 278.15 | 0.115 | 284.65 | 0.9
0.05856 | 278.15 | 0.115 | 284.65 | 1
0.05856 | 278.15 | 0.115 | 285.15 | 0.15
0.05856 | 278.15 | 0.115 | 285.15 | 0.2
0.05856 | 278.15 | 0.115 | 285.15 | 0.3
0.05856 | 278.15 | 0.115 | 285.15 | 0.4
0.05856 | 278.15 | 0.115 | 285.15 | 0.5
0.05856 | 278.15 | 0.115 | 285.15 | 0.6
0.05856 | 278.15 | 0.115 | 285.15 | 0.7
0.05856 | 278.15 | 0.115 | 285.15 | 0.8
0.05856 | 278.15 | 0.115 | 285.15 | 0.9
0.05856 | 278.15 | 0.115 | 285.15 | 1
0.05856 | 278.15 | 0.115 | 285.65 | 0.15
0.05856 | 278.15 | 0.115 | 285.65 | 0.2
0.05856 | 278.15 | 0.115 | 285.65 | 0.3
0.05856 | 278.15 | 0.115 | 285.65 | 0.4
0.05856 | 278.15 | 0.115 | 285.65 | 0.5
0.05856 | 278.15 | 0.115 | 285.65 | 0.6
0.05856 | 278.15 | 0.115 | 285.65 | 0.7
0.05856 | 278.15 | 0.115 | 285.65 | 0.8
0.05856 | 278.15 | 0.115 | 285.65 | 0.9
0.05856 | 278.15 | 0.115 | 285.65 | 1
0.05856 | 278.15 | 0.115 | 286.15 | 0.15
0.05856 | 278.15 | 0.115 | 286.15 | 0.2
0.05856 | 278.15 | 0.115 | 286.15 | 0.3
0.05856 | 278.15 | 0.115 | 286.15 | 0.4
0.05856 | 278.15 | 0.115 | 286.15 | 0.5
0.05856 | 278.15 | 0.115 | 286.15 | 0.6
0.05856 | 278.15 | 0.115 | 286.15 | 0.7
0.05856 | 278.15 | 0.115 | 286.15 | 0.8
0.05856 | 278.15 | 0.115 | 286.15 | 0.9
0.05856 | 278.15 | 0.115 | 286.15 | 1
0.05856 | 278.15 | 0.115 | 286.65 | 0.15
0.05856 | 278.15 | 0.115 | 286.65 | 0.2
0.05856 | 278.15 | 0.115 | 286.65 | 0.3
0.05856 | 278.15 | 0.115 | 286.65 | 0.4
0.05856 | 278.15 | 0.115 | 286.65 | 0.5
0.05856 | 278.15 | 0.115 | 286.65 | 0.6
0.05856 | 278.15 | 0.115 | 286.65 | 0.7
0.05856 | 278.15 | 0.115 | 286.65 | 0.8
0.05856 | 278.15 | 0.115 | 286.65 | 0.9
0.05856 | 278.15 | 0.115 | 286.65 | 1
0.05856 | 278.15 | 0.115 | 287.15 | 0.15
0.05856 | 278.15 | 0.115 | 287.15 | 0.2
0.05856 | 278.15 | 0.115 | 287.15 | 0.3
0.05856 | 278.15 | 0.115 | 287.15 | 0.4
0.05856 | 278.15 | 0.115 | 287.15 | 0.5
0.05856 | 278.15 | 0.115 | 287.15 | 0.6
0.05856 | 278.15 | 0.115 | 287.15 | 0.7
0.05856 | 278.15 | 0.115 | 287.15 | 0.8
0.05856 | 278.15 | 0.115 | 287.15 | 0.9
0.05856 | 278.15 | 0.115 | 287.15 | 1
0.05856 | 278.15 | 0.115 | 287.65 | 0.15
0.05856 | 278.15 | 0.115 | 287.65 | 0.2
0.05856 | 278.15 | 0.115 | 287.65 | 0.3
0.05856 | 278.15 | 0.115 | 287.65 | 0.4
0.05856 | 278.15 | 0.115 | 287.65 | 0.5
0.05856 | 278.15 | 0.115 | 287.65 | 0.6
0.05856 | 278.15 | 0.115 | 287.65 | 0.7
0.05856 | 278.15 | 0.115 | 287.65 | 0.8
0.05856 | 278.15 | 0.115 | 287.65 | 0.9
0.05856 | 278.15 | 0.115 | 287.65 | 1
0.05856 | 278.15 | 0.115 | 288.15 | 0.15
0.05856 | 278.15 | 0.115 | 288.15 | 0.2
0.05856 | 278.15 | 0.115 | 288.15 | 0.3
0.05856 | 278.15 | 0.115 | 288.15 | 0.4
0.05856 | 278.15 | 0.115 | 288.15 | 0.5
0.05856 | 278.15 | 0.115 | 288.15 | 0.6
0.05856 | 278.15 | 0.115 | 288.15 | 0.7
0.05856 | 278.15 | 0.115 | 288.15 | 0.8
0.05856 | 278.15 | 0.115 | 288.15 | 0.9
0.05856 | 278.15 | 0.115 | 288.15 | 1
0.05856 | 278.15 | 0.115 | 288.65 | 0.15
0.05856 | 278.15 | 0.115 | 288.65 | 0.2
0.05856 | 278.15 | 0.115 | 288.65 | 0.3
0.05856 | 278.15 | 0.115 | 288.65 | 0.4
0.05856 | 278.15 | 0.115 | 288.65 | 0.5
0.05856 | 278.15 | 0.115 | 288.65 | 0.6
0.05856 | 278.15 | 0.115 | 288.65 | 0.7
0.05856 | 278.15 | 0.115 | 288.65 | 0.8
0.05856 | 278.15 | 0.115 | 288.65 | 0.9
0.05856 | 278.15 | 0.115 | 288.65 | 1
0.05856 | 278.15 | 0.115 | 289.15 | 0.15
0.05856 | 278.15 | 0.115 | 289.15 | 0.2
0.05856 | 278.15 | 0.115 | 289.15 | 0.3
0.05856 | 278.15 | 0.115 | 289.15 | 0.4
0.05856 | 278.15 | 0.115 | 289.15 | 0.5
0.05856 | 278.15 | 0.115 | 289.15 | 0.6
0.05856 | 278.15 | 0.115 | 289.15 | 0.7
0.05856 | 278.15 | 0.115 | 289.15 | 0.8
0.05856 | 278.15 | 0.115 | 289.15 | 0.9
0.05856 | 278.15 | 0.115 | 289.15 | 1
0.05856 | 278.15 | 0.115 | 289.65 | 0.15
0.05856 | 278.15 | 0.115 | 289.65 | 0.2
0.05856 | 278.15 | 0.115 | 289.65 | 0.3
0.05856 | 278.15 | 0.115 | 289.65 | 0.4
0.05856 | 278.15 | 0.115 | 289.65 | 0.5
0.05856 | 278.15 | 0.115 | 289.65 | 0.6
0.05856 | 278.15 | 0.115 | 289.65 | 0.7
0.05856 | 278.15 | 0.115 | 289.65 | 0.8
0.05856 | 278.15 | 0.115 | 289.65 | 0.9
0.05856 | 278.15 | 0.115 | 289.65 | 1
0.05856 | 278.15 | 0.115 | 290.15 | 0.15
0.05856 | 278.15 | 0.115 | 290.15 | 0.2
0.05856 | 278.15 | 0.115 | 290.15 | 0.3
0.05856 | 278.15 | 0.115 | 290.15 | 0.4
0.05856 | 278.15 | 0.115 | 290.15 | 0.5
0.05856 | 278.15 | 0.115 | 290.15 | 0.6
0.05856 | 278.15 | 0.115 | 290.15 | 0.7
0.05856 | 278.15 | 0.115 | 290.15 | 0.8
0.05856 | 278.15 | 0.115 | 290.15 | 0.9
0.05856 | 278.15 | 0.115 | 290.15 | 1
0.05856 | 278.15 | 0.115 | 290.65 | 0.15
0.05856 | 278.15 | 0.115 | 290.65 | 0.2
0.05856 | 278.15 | 0.115 | 290.65 | 0.3
0.05856 | 278.15 | 0.115 | 290.65 | 0.4
0.05856 | 278.15 | 0.115 | 290.65 | 0.5
0.05856 | 278.15 | 0.115 | 290.65 | 0.6
0.05856 | 278.15 | 0.115 | 290.65 | 0.7
0.05856 | 278.15 | 0.115 | 290.65 | 0.8
0.05856 | 278.15 | 0.115 | 290.65 | 0.9
0.05856 | 278.15 | 0.115 | 290.65 | 1
0.05856 | 278.15 | 0.115 | 291.15 | 0.15
0.05856 | 278.15 | 0.115 | 291.15 | 0.2
0.05856 | 278.15 | 0.115 | 291.15 | 0.3
0.05856 | 278.15 | 0.115 | 291.15 | 0.4
0.05856 | 278.15 | 0.115 | 291.15 | 0.5
0.05856 | 278.15 | 0.115 | 291.15 | 0.6
0.05856 | 278.15 | 0.115 | 291.15 | 0.7
0.05856 | 278.15 | 0.115 | 291.15 | 0.8
0.05856 | 278.15 | 0.115 | 291.15 | 0.9
0.05856 | 278.15 | 0.115 | 291.15 | 1
0.05856 | 278.15 | 0.115 | 294.15 | 0.15
0.05856 | 278.15 | 0.115 | 294.15 | 0.2
0.05856 | 278.15 | 0.115 | 294.15 | 0.3
0.05856 | 278.15 | 0.115 | 294.15 | 0.4
0.05856 | 278.15 | 0.115 | 294.15 | 0.5
0.05856 | 278.15 | 0.115 | 294.15 | 0.6
0.05856 | 278.15 | 0.115 | 294.15 | 0.7
0.05856 | 278.15 | 0.115 | 294.15 | 0.8
0.05856 | 278.15 | 0.115 | 294.15 | 0.9
0.05856 | 278.15 | 0.115 | 294.15 | 1
0.05856 | 278.15 | 0.115 | 297.15 | 0.15
0.05856 | 278.15 | 0.115 | 297.15 | 0.2
0.05856 | 278.15 | 0.115 | 297.15 | 0.3
0.05856 | 278.15 | 0.115 | 297.15 | 0.4
0.05856 | 278.15 | 0.115 | 297.15 | 0.5
0.05856 | 278.15 | 0.115 | 297.15 | 0.6
0.05856 | 278.15 | 0.115 | 297.15 | 0.7
0.05856 | 278.15 | 0.115 | 297.15 | 0.8
0.05856 | 278.15 | 0.115 | 297.15 | 0.9
0.05856 | 278.15 | 0.115 | 297.15 | 1
0.05856 | 278.15 | 0.115 | 300.15 | 0.15
0.05856 | 278.15 | 0.115 | 300.15 | 0.2
0.05856 | 278.15 | 0.115 | 300.15 | 0.3
0.05856 | 278.15 | 0.115 | 300.15 | 0.4
0.05856 | 278.15 | 0.115 | 300.15 | 0.5
0.05856 | 278.15 | 0.115 | 300.15 | 0.6
0.05856 | 278.15 | 0.115 | 300.15 | 0.7
0.05856 | 278.15 | 0.115 | 300.15 | 0.8
0.05856 | 278.15 | 0.115 | 300.15 | 0.9
0.05856 | 278.15 | 0.115 | 300.15 | 1
0.05856 | 278.15 | 0.115 | 303.15 | 0.15
0.05856 | 278.15 | 0.115 | 303.15 | 0.2
0.05856 | 278.15 | 0.115 | 303.15 | 0.3
0.05856 | 278.15 | 0.115 | 303.15 | 0.4
0.05856 | 278.15 | 0.115 | 303.15 | 0.5
0.05856 | 278.15 | 0.115 | 303.15 | 0.6
0.05856 | 278.15 | 0.115 | 303.15 | 0.7
0.05856 | 278.15 | 0.115 | 303.15 | 0.8
0.05856 | 278.15 | 0.115 | 303.15 | 0.9
0.05856 | 278.15 | 0.115 | 303.15 | 1
0.05856 | 280.15 | 0.00115 | 283.65 | 0.15
0.05856 | 280.15 | 0.00115 | 283.65 | 0.2
0.05856 | 280.15 | 0.00115 | 283.65 | 0.3
0.05856 | 280.15 | 0.00115 | 283.65 | 0.4
0.05856 | 280.15 | 0.00115 | 283.65 | 0.5
0.05856 | 280.15 | 0.00115 | 283.65 | 0.6
0.05856 | 280.15 | 0.00115 | 283.65 | 0.7
0.05856 | 280.15 | 0.00115 | 283.65 | 0.8
0.05856 | 280.15 | 0.00115 | 283.65 | 0.9
0.05856 | 280.15 | 0.00115 | 283.65 | 1
0.05856 | 280.15 | 0.00115 | 284.15 | 0.15
0.05856 | 280.15 | 0.00115 | 284.15 | 0.2
0.05856 | 280.15 | 0.00115 | 284.15 | 0.3
0.05856 | 280.15 | 0.00115 | 284.15 | 0.4
0.05856 | 280.15 | 0.00115 | 284.15 | 0.5
0.05856 | 280.15 | 0.00115 | 284.15 | 0.6
0.05856 | 280.15 | 0.00115 | 284.15 | 0.7
0.05856 | 280.15 | 0.00115 | 284.15 | 0.8
0.05856 | 280.15 | 0.00115 | 284.15 | 0.9
0.05856 | 280.15 | 0.00115 | 284.15 | 1
0.05856 | 280.15 | 0.00115 | 284.65 | 0.15
0.05856 | 280.15 | 0.00115 | 284.65 | 0.2
0.05856 | 280.15 | 0.00115 | 284.65 | 0.3
0.05856 | 280.15 | 0.00115 | 284.65 | 0.4
0.05856 | 280.15 | 0.00115 | 284.65 | 0.5
0.05856 | 280.15 | 0.00115 | 284.65 | 0.6
0.05856 | 280.15 | 0.00115 | 284.65 | 0.7
0.05856 | 280.15 | 0.00115 | 284.65 | 0.8
0.05856 | 280.15 | 0.00115 | 284.65 | 0.9
0.05856 | 280.15 | 0.00115 | 284.65 | 1
0.05856 | 280.15 | 0.00115 | 285.15 | 0.15
0.05856 | 280.15 | 0.00115 | 285.15 | 0.2
0.05856 | 280.15 | 0.00115 | 285.15 | 0.3
0.05856 | 280.15 | 0.00115 | 285.15 | 0.4
0.05856 | 280.15 | 0.00115 | 285.15 | 0.5
0.05856 | 280.15 | 0.00115 | 285.15 | 0.6
0.05856 | 280.15 | 0.00115 | 285.15 | 0.7
0.05856 | 280.15 | 0.00115 | 285.15 | 0.8
0.05856 | 280.15 | 0.00115 | 285.15 | 0.9
0.05856 | 280.15 | 0.00115 | 285.15 | 1
0.05856 | 280.15 | 0.00115 | 285.65 | 0.15
0.05856 | 280.15 | 0.00115 | 285.65 | 0.2
0.05856 | 280.15 | 0.00115 | 285.65 | 0.3
0.05856 | 280.15 | 0.00115 | 285.65 | 0.4
0.05856 | 280.15 | 0.00115 | 285.65 | 0.5
0.05856 | 280.15 | 0.00115 | 285.65 | 0.6
0.05856 | 280.15 | 0.00115 | 285.65 | 0.7
0.05856 | 280.15 | 0.00115 | 285.65 | 0.8
0.05856 | 280.15 | 0.00115 | 285.65 | 0.9
0.05856 | 280.15 | 0.00115 | 285.65 | 1
0.05856 | 280.15 | 0.00115 | 286.15 | 0.15
0.05856 | 280.15 | 0.00115 | 286.15 | 0.2
0.05856 | 280.15 | 0.00115 | 286.15 | 0.3
0.05856 | 280.15 | 0.00115 | 286.15 | 0.4
0.05856 | 280.15 | 0.00115 | 286.15 | 0.5
0.05856 | 280.15 | 0.00115 | 286.15 | 0.6
0.05856 | 280.15 | 0.00115 | 286.15 | 0.7
0.05856 | 280.15 | 0.00115 | 286.15 | 0.8
0.05856 | 280.15 | 0.00115 | 286.15 | 0.9
0.05856 | 280.15 | 0.00115 | 286.15 | 1
0.05856 | 280.15 | 0.00115 | 286.65 | 0.15
0.05856 | 280.15 | 0.00115 | 286.65 | 0.2
0.05856 | 280.15 | 0.00115 | 286.65 | 0.3
0.05856 | 280.15 | 0.00115 | 286.65 | 0.4
0.05856 | 280.15 | 0.00115 | 286.65 | 0.5
0.05856 | 280.15 | 0.00115 | 286.65 | 0.6
0.05856 | 280.15 | 0.00115 | 286.65 | 0.7
0.05856 | 280.15 | 0.00115 | 286.65 | 0.8
0.05856 | 280.15 | 0.00115 | 286.65 | 0.9
0.05856 | 280.15 | 0.00115 | 286.65 | 1
0.05856 | 280.15 | 0.00115 | 287.15 | 0.15
0.05856 | 280.15 | 0.00115 | 287.15 | 0.2
0.05856 | 280.15 | 0.00115 | 287.15 | 0.3
0.05856 | 280.15 | 0.00115 | 287.15 | 0.4
0.05856 | 280.15 | 0.00115 | 287.15 | 0.5
0.05856 | 280.15 | 0.00115 | 287.15 | 0.6
0.05856 | 280.15 | 0.00115 | 287.15 | 0.7
0.05856 | 280.15 | 0.00115 | 287.15 | 0.8
0.05856 | 280.15 | 0.00115 | 287.15 | 0.9
0.05856 | 280.15 | 0.00115 | 287.15 | 1
0.05856 | 280.15 | 0.00115 | 287.65 | 0.15
0.05856 | 280.15 | 0.00115 | 287.65 | 0.2
0.05856 | 280.15 | 0.00115 | 287.65 | 0.3
0.05856 | 280.15 | 0.00115 | 287.65 | 0.4
0.05856 | 280.15 | 0.00115 | 287.65 | 0.5
0.05856 | 280.15 | 0.00115 | 287.65 | 0.6
0.05856 | 280.15 | 0.00115 | 287.65 | 0.7
0.05856 | 280.15 | 0.00115 | 287.65 | 0.8
0.05856 | 280.15 | 0.00115 | 287.65 | 0.9
0.05856 | 280.15 | 0.00115 | 287.65 | 1
0.05856 | 280.15 | 0.00115 | 288.15 | 0.15
0.05856 | 280.15 | 0.00115 | 288.15 | 0.2
0.05856 | 280.15 | 0.00115 | 288.15 | 0.3
0.05856 | 280.15 | 0.00115 | 288.15 | 0.4
0.05856 | 280.15 | 0.00115 | 288.15 | 0.5
0.05856 | 280.15 | 0.00115 | 288.15 | 0.6
0.05856 | 280.15 | 0.00115 | 288.15 | 0.7
0.05856 | 280.15 | 0.00115 | 288.15 | 0.8
0.05856 | 280.15 | 0.00115 | 288.15 | 0.9
0.05856 | 280.15 | 0.00115 | 288.15 | 1
0.05856 | 280.15 | 0.00115 | 288.65 | 0.15
0.05856 | 280.15 | 0.00115 | 288.65 | 0.2
0.05856 | 280.15 | 0.00115 | 288.65 | 0.3
0.05856 | 280.15 | 0.00115 | 288.65 | 0.4
0.05856 | 280.15 | 0.00115 | 288.65 | 0.5
0.05856 | 280.15 | 0.00115 | 288.65 | 0.6
0.05856 | 280.15 | 0.00115 | 288.65 | 0.7
0.05856 | 280.15 | 0.00115 | 288.65 | 0.8
0.05856 | 280.15 | 0.00115 | 288.65 | 0.9
0.05856 | 280.15 | 0.00115 | 288.65 | 1
0.05856 | 280.15 | 0.00115 | 289.15 | 0.15
0.05856 | 280.15 | 0.00115 | 289.15 | 0.2
0.05856 | 280.15 | 0.00115 | 289.15 | 0.3
0.05856 | 280.15 | 0.00115 | 289.15 | 0.4
0.05856 | 280.15 | 0.00115 | 289.15 | 0.5
0.05856 | 280.15 | 0.00115 | 289.15 | 0.6
0.05856 | 280.15 | 0.00115 | 289.15 | 0.7
0.05856 | 280.15 | 0.00115 | 289.15 | 0.8
0.05856 | 280.15 | 0.00115 | 289.15 | 0.9
0.05856 | 280.15 | 0.00115 | 289.15 | 1
0.05856 | 280.15 | 0.00115 | 289.65 | 0.15
0.05856 | 280.15 | 0.00115 | 289.65 | 0.2
0.05856 | 280.15 | 0.00115 | 289.65 | 0.3
0.05856 | 280.15 | 0.00115 | 289.65 | 0.4
0.05856 | 280.15 | 0.00115 | 289.65 | 0.5
0.05856 | 280.15 | 0.00115 | 289.65 | 0.6
0.05856 | 280.15 | 0.00115 | 289.65 | 0.7
0.05856 | 280.15 | 0.00115 | 289.65 | 0.8
0.05856 | 280.15 | 0.00115 | 289.65 | 0.9
0.05856 | 280.15 | 0.00115 | 289.65 | 1
0.05856 | 280.15 | 0.00115 | 290.15 | 0.15
0.05856 | 280.15 | 0.00115 | 290.15 | 0.2
0.05856 | 280.15 | 0.00115 | 290.15 | 0.3
0.05856 | 280.15 | 0.00115 | 290.15 | 0.4
0.05856 | 280.15 | 0.00115 | 290.15 | 0.5
0.05856 | 280.15 | 0.00115 | 290.15 | 0.6
0.05856 | 280.15 | 0.00115 | 290.15 | 0.7
0.05856 | 280.15 | 0.00115 | 290.15 | 0.8
0.05856 | 280.15 | 0.00115 | 290.15 | 0.9
0.05856 | 280.15 | 0.00115 | 290.15 | 1
0.05856 | 280.15 | 0.00115 | 290.65 | 0.15
0.05856 | 280.15 | 0.00115 | 290.65 | 0.2
0.05856 | 280.15 | 0.00115 | 290.65 | 0.3
0.05856 | 280.15 | 0.00115 | 290.65 | 0.4
0.05856 | 280.15 | 0.00115 | 290.65 | 0.5
0.05856 | 280.15 | 0.00115 | 290.65 | 0.6
0.05856 | 280.15 | 0.00115 | 290.65 | 0.7
0.05856 | 280.15 | 0.00115 | 290.65 | 0.8
0.05856 | 280.15 | 0.00115 | 290.65 | 0.9
0.05856 | 280.15 | 0.00115 | 290.65 | 1
0.05856 | 280.15 | 0.00115 | 291.15 | 0.15
0.05856 | 280.15 | 0.00115 | 291.15 | 0.2
0.05856 | 280.15 | 0.00115 | 291.15 | 0.3
0.05856 | 280.15 | 0.00115 | 291.15 | 0.4
0.05856 | 280.15 | 0.00115 | 291.15 | 0.5
0.05856 | 280.15 | 0.00115 | 291.15 | 0.6
0.05856 | 280.15 | 0.00115 | 291.15 | 0.7
0.05856 | 280.15 | 0.00115 | 291.15 | 0.8
0.05856 | 280.15 | 0.00115 | 291.15 | 0.9
0.05856 | 280.15 | 0.00115 | 291.15 | 1
0.05856 | 280.15 | 0.00115 | 294.15 | 0.15
0.05856 | 280.15 | 0.00115 | 294.15 | 0.2
0.05856 | 280.15 | 0.00115 | 294.15 | 0.3
0.05856 | 280.15 | 0.00115 | 294.15 | 0.4
0.05856 | 280.15 | 0.00115 | 294.15 | 0.5
0.05856 | 280.15 | 0.00115 | 294.15 | 0.6
0.05856 | 280.15 | 0.00115 | 294.15 | 0.7
0.05856 | 280.15 | 0.00115 | 294.15 | 0.8
0.05856 | 280.15 | 0.00115 | 294.15 | 0.9
0.05856 | 280.15 | 0.00115 | 294.15 | 1
0.05856 | 280.15 | 0.00115 | 297.15 | 0.15
0.05856 | 280.15 | 0.00115 | 297.15 | 0.2
0.05856 | 280.15 | 0.00115 | 297.15 | 0.3
0.05856 | 280.15 | 0.00115 | 297.15 | 0.4
0.05856 | 280.15 | 0.00115 | 297.15 | 0.5
0.05856 | 280.15 | 0.00115 | 297.15 | 0.6
0.05856 | 280.15 | 0.00115 | 297.15 | 0.7
0.05856 | 280.15 | 0.00115 | 297.15 | 0.8
0.05856 | 280.15 | 0.00115 | 297.15 | 0.9
0.05856 | 280.15 | 0.00115 | 297.15 | 1
0.05856 | 280.15 | 0.00115 | 300.15 | 0.15
0.05856 | 280.15 | 0.00115 | 300.15 | 0.2
0.05856 | 280.15 | 0.00115 | 300.15 | 0.3
0.05856 | 280.15 | 0.00115 | 300.15 | 0.4
0.05856 | 280.15 | 0.00115 | 300.15 | 0.5
0.05856 | 280.15 | 0.00115 | 300.15 | 0.6
0.05856 | 280.15 | 0.00115 | 300.15 | 0.7
0.05856 | 280.15 | 0.00115 | 300.15 | 0.8
0.05856 | 280.15 | 0.00115 | 300.15 | 0.9
0.05856 | 280.15 | 0.00115 | 300.15 | 1
0.05856 | 280.15 | 0.00115 | 303.15 | 0.15
0.05856 | 280.15 | 0.00115 | 303.15 | 0.2
0.05856 | 280.15 | 0.00115 | 303.15 | 0.3
0.05856 | 280.15 | 0.00115 | 303.15 | 0.4
0.05856 | 280.15 | 0.00115 | 303.15 | 0.5
0.05856 | 280.15 | 0.00115 | 303.15 | 0.6
0.05856 | 280.15 | 0.00115 | 303.15 | 0.7
0.05856 | 280.15 | 0.00115 | 303.15 | 0.8
0.05856 | 280.15 | 0.00115 | 303.15 | 0.9
0.05856 | 280.15 | 0.00115 | 303.15 | 1
0.05856 | 280.15 | 0.077 | 283.65 | 0.15
0.05856 | 280.15 | 0.077 | 283.65 | 0.2
0.05856 | 280.15 | 0.077 | 283.65 | 0.3
0.05856 | 280.15 | 0.077 | 283.65 | 0.4
0.05856 | 280.15 | 0.077 | 283.65 | 0.5
0.05856 | 280.15 | 0.077 | 283.65 | 0.6
0.05856 | 280.15 | 0.077 | 283.65 | 0.7
0.05856 | 280.15 | 0.077 | 283.65 | 0.8
0.05856 | 280.15 | 0.077 | 283.65 | 0.9
0.05856 | 280.15 | 0.077 | 283.65 | 1
0.05856 | 280.15 | 0.077 | 284.15 | 0.15
0.05856 | 280.15 | 0.077 | 284.15 | 0.2
0.05856 | 280.15 | 0.077 | 284.15 | 0.3
0.05856 | 280.15 | 0.077 | 284.15 | 0.4
0.05856 | 280.15 | 0.077 | 284.15 | 0.5
0.05856 | 280.15 | 0.077 | 284.15 | 0.6
0.05856 | 280.15 | 0.077 | 284.15 | 0.7
0.05856 | 280.15 | 0.077 | 284.15 | 0.8
0.05856 | 280.15 | 0.077 | 284.15 | 0.9
0.05856 | 280.15 | 0.077 | 284.15 | 1
0.05856 | 280.15 | 0.077 | 284.65 | 0.15
0.05856 | 280.15 | 0.077 | 284.65 | 0.2
0.05856 | 280.15 | 0.077 | 284.65 | 0.3
0.05856 | 280.15 | 0.077 | 284.65 | 0.4
0.05856 | 280.15 | 0.077 | 284.65 | 0.5
0.05856 | 280.15 | 0.077 | 284.65 | 0.6
0.05856 | 280.15 | 0.077 | 284.65 | 0.7
0.05856 | 280.15 | 0.077 | 284.65 | 0.8
0.05856 | 280.15 | 0.077 | 284.65 | 0.9
0.05856 | 280.15 | 0.077 | 284.65 | 1
0.05856 | 280.15 | 0.077 | 285.15 | 0.15
0.05856 | 280.15 | 0.077 | 285.15 | 0.2
0.05856 | 280.15 | 0.077 | 285.15 | 0.3
0.05856 | 280.15 | 0.077 | 285.15 | 0.4
0.05856 | 280.15 | 0.077 | 285.15 | 0.5
0.05856 | 280.15 | 0.077 | 285.15 | 0.6
0.05856 | 280.15 | 0.077 | 285.15 | 0.7
0.05856 | 280.15 | 0.077 | 285.15 | 0.8
0.05856 | 280.15 | 0.077 | 285.15 | 0.9
0.05856 | 280.15 | 0.077 | 285.15 | 1
0.05856 | 280.15 | 0.077 | 285.65 | 0.15
0.05856 | 280.15 | 0.077 | 285.65 | 0.2
0.05856 | 280.15 | 0.077 | 285.65 | 0.3
0.05856 | 280.15 | 0.077 | 285.65 | 0.4
0.05856 | 280.15 | 0.077 | 285.65 | 0.5
0.05856 | 280.15 | 0.077 | 285.65 | 0.6
0.05856 | 280.15 | 0.077 | 285.65 | 0.7
0.05856 | 280.15 | 0.077 | 285.65 | 0.8
0.05856 | 280.15 | 0.077 | 285.65 | 0.9
0.05856 | 280.15 | 0.077 | 285.65 | 1
0.05856 | 280.15 | 0.077 | 286.15 | 0.15
0.05856 | 280.15 | 0.077 | 286.15 | 0.2
0.05856 | 280.15 | 0.077 | 286.15 | 0.3
0.05856 | 280.15 | 0.077 | 286.15 | 0.4
0.05856 | 280.15 | 0.077 | 286.15 | 0.5
0.05856 | 280.15 | 0.077 | 286.15 | 0.6
0.05856 | 280.15 | 0.077 | 286.15 | 0.7
0.05856 | 280.15 | 0.077 | 286.15 | 0.8
0.05856 | 280.15 | 0.077 | 286.15 | 0.9
0.05856 | 280.15 | 0.077 | 286.15 | 1
0.05856 | 280.15 | 0.077 | 286.65 | 0.15
0.05856 | 280.15 | 0.077 | 286.65 | 0.2
0.05856 | 280.15 | 0.077 | 286.65 | 0.3
0.05856 | 280.15 | 0.077 | 286.65 | 0.4
0.05856 | 280.15 | 0.077 | 286.65 | 0.5
0.05856 | 280.15 | 0.077 | 286.65 | 0.6
0.05856 | 280.15 | 0.077 | 286.65 | 0.7
0.05856 | 280.15 | 0.077 | 286.65 | 0.8
0.05856 | 280.15 | 0.077 | 286.65 | 0.9
0.05856 | 280.15 | 0.077 | 286.65 | 1
0.05856 | 280.15 | 0.077 | 287.15 | 0.15
0.05856 | 280.15 | 0.077 | 287.15 | 0.2
0.05856 | 280.15 | 0.077 | 287.15 | 0.3
0.05856 | 280.15 | 0.077 | 287.15 | 0.4
0.05856 | 280.15 | 0.077 | 287.15 | 0.5
0.05856 | 280.15 | 0.077 | 287.15 | 0.6
0.05856 | 280.15 | 0.077 | 287.15 | 0.7
0.05856 | 280.15 | 0.077 | 287.15 | 0.8
0.05856 | 280.15 | 0.077 | 287.15 | 0.9
0.05856 | 280.15 | 0.077 | 287.15 | 1
0.05856 | 280.15 | 0.077 | 287.65 | 0.15
0.05856 | 280.15 | 0.077 | 287.65 | 0.2
0.05856 | 280.15 | 0.077 | 287.65 | 0.3
0.05856 | 280.15 | 0.077 | 287.65 | 0.4
0.05856 | 280.15 | 0.077 | 287.65 | 0.5
0.05856 | 280.15 | 0.077 | 287.65 | 0.6
0.05856 | 280.15 | 0.077 | 287.65 | 0.7
0.05856 | 280.15 | 0.077 | 287.65 | 0.8
0.05856 | 280.15 | 0.077 | 287.65 | 0.9
0.05856 | 280.15 | 0.077 | 287.65 | 1
0.05856 | 280.15 | 0.077 | 288.15 | 0.15
0.05856 | 280.15 | 0.077 | 288.15 | 0.2
0.05856 | 280.15 | 0.077 | 288.15 | 0.3
0.05856 | 280.15 | 0.077 | 288.15 | 0.4
0.05856 | 280.15 | 0.077 | 288.15 | 0.5
0.05856 | 280.15 | 0.077 | 288.15 | 0.6
0.05856 | 280.15 | 0.077 | 288.15 | 0.7
0.05856 | 280.15 | 0.077 | 288.15 | 0.8
0.05856 | 280.15 | 0.077 | 288.15 | 0.9
0.05856 | 280.15 | 0.077 | 288.15 | 1
0.05856 | 280.15 | 0.077 | 288.65 | 0.15
0.05856 | 280.15 | 0.077 | 288.65 | 0.2
0.05856 | 280.15 | 0.077 | 288.65 | 0.3
0.05856 | 280.15 | 0.077 | 288.65 | 0.4
0.05856 | 280.15 | 0.077 | 288.65 | 0.5
0.05856 | 280.15 | 0.077 | 288.65 | 0.6
0.05856 | 280.15 | 0.077 | 288.65 | 0.7
0.05856 | 280.15 | 0.077 | 288.65 | 0.8
0.05856 | 280.15 | 0.077 | 288.65 | 0.9
0.05856 | 280.15 | 0.077 | 288.65 | 1
0.05856 | 280.15 | 0.077 | 289.15 | 0.15
0.05856 | 280.15 | 0.077 | 289.15 | 0.2
0.05856 | 280.15 | 0.077 | 289.15 | 0.3
0.05856 | 280.15 | 0.077 | 289.15 | 0.4
0.05856 | 280.15 | 0.077 | 289.15 | 0.5
0.05856 | 280.15 | 0.077 | 289.15 | 0.6
0.05856 | 280.15 | 0.077 | 289.15 | 0.7
0.05856 | 280.15 | 0.077 | 289.15 | 0.8
0.05856 | 280.15 | 0.077 | 289.15 | 0.9
0.05856 | 280.15 | 0.077 | 289.15 | 1
0.05856 | 280.15 | 0.077 | 289.65 | 0.15
0.05856 | 280.15 | 0.077 | 289.65 | 0.2
0.05856 | 280.15 | 0.077 | 289.65 | 0.3
0.05856 | 280.15 | 0.077 | 289.65 | 0.4
0.05856 | 280.15 | 0.077 | 289.65 | 0.5
0.05856 | 280.15 | 0.077 | 289.65 | 0.6
0.05856 | 280.15 | 0.077 | 289.65 | 0.7
0.05856 | 280.15 | 0.077 | 289.65 | 0.8
0.05856 | 280.15 | 0.077 | 289.65 | 0.9
0.05856 | 280.15 | 0.077 | 289.65 | 1
0.05856 | 280.15 | 0.077 | 290.15 | 0.15
0.05856 | 280.15 | 0.077 | 290.15 | 0.2
0.05856 | 280.15 | 0.077 | 290.15 | 0.3
0.05856 | 280.15 | 0.077 | 290.15 | 0.4
0.05856 | 280.15 | 0.077 | 290.15 | 0.5
0.05856 | 280.15 | 0.077 | 290.15 | 0.6
0.05856 | 280.15 | 0.077 | 290.15 | 0.7
0.05856 | 280.15 | 0.077 | 290.15 | 0.8
0.05856 | 280.15 | 0.077 | 290.15 | 0.9
0.05856 | 280.15 | 0.077 | 290.15 | 1
0.05856 | 280.15 | 0.077 | 290.65 | 0.15
0.05856 | 280.15 | 0.077 | 290.65 | 0.2
0.05856 | 280.15 | 0.077 | 290.65 | 0.3
0.05856 | 280.15 | 0.077 | 290.65 | 0.4
0.05856 | 280.15 | 0.077 | 290.65 | 0.5
0.05856 | 280.15 | 0.077 | 290.65 | 0.6
0.05856 | 280.15 | 0.077 | 290.65 | 0.7
0.05856 | 280.15 | 0.077 | 290.65 | 0.8
0.05856 | 280.15 | 0.077 | 290.65 | 0.9
0.05856 | 280.15 | 0.077 | 290.65 | 1
0.05856 | 280.15 | 0.077 | 291.15 | 0.15
0.05856 | 280.15 | 0.077 | 291.15 | 0.2
0.05856 | 280.15 | 0.077 | 291.15 | 0.3
0.05856 | 280.15 | 0.077 | 291.15 | 0.4
0.05856 | 280.15 | 0.077 | 291.15 | 0.5
0.05856 | 280.15 | 0.077 | 291.15 | 0.6
0.05856 | 280.15 | 0.077 | 291.15 | 0.7
0.05856 | 280.15 | 0.077 | 291.15 | 0.8
0.05856 | 280.15 | 0.077 | 291.15 | 0.9
0.05856 | 280.15 | 0.077 | 291.15 | 1
0.05856 | 280.15 | 0.077 | 294.15 | 0.15
0.05856 | 280.15 | 0.077 | 294.15 | 0.2
0.05856 | 280.15 | 0.077 | 294.15 | 0.3
0.05856 | 280.15 | 0.077 | 294.15 | 0.4
0.05856 | 280.15 | 0.077 | 294.15 | 0.5
0.05856 | 280.15 | 0.077 | 294.15 | 0.6
0.05856 | 280.15 | 0.077 | 294.15 | 0.7
0.05856 | 280.15 | 0.077 | 294.15 | 0.8
0.05856 | 280.15 | 0.077 | 294.15 | 0.9
0.05856 | 280.15 | 0.077 | 294.15 | 1
0.05856 | 280.15 | 0.077 | 297.15 | 0.15
0.05856 | 280.15 | 0.077 | 297.15 | 0.2
0.05856 | 280.15 | 0.077 | 297.15 | 0.3
0.05856 | 280.15 | 0.077 | 297.15 | 0.4
0.05856 | 280.15 | 0.077 | 297.15 | 0.5
0.05856 | 280.15 | 0.077 | 297.15 | 0.6
0.05856 | 280.15 | 0.077 | 297.15 | 0.7
0.05856 | 280.15 | 0.077 | 297.15 | 0.8
0.05856 | 280.15 | 0.077 | 297.15 | 0.9
0.05856 | 280.15 | 0.077 | 297.15 | 1
0.05856 | 280.15 | 0.077 | 300.15 | 0.15
0.05856 | 280.15 | 0.077 | 300.15 | 0.2
0.05856 | 280.15 | 0.077 | 300.15 | 0.3
0.05856 | 280.15 | 0.077 | 300.15 | 0.4
0.05856 | 280.15 | 0.077 | 300.15 | 0.5
0.05856 | 280.15 | 0.077 | 300.15 | 0.6
0.05856 | 280.15 | 0.077 | 300.15 | 0.7
0.05856 | 280.15 | 0.077 | 300.15 | 0.8
0.05856 | 280.15 | 0.077 | 300.15 | 0.9
0.05856 | 280.15 | 0.077 | 300.15 | 1
0.05856 | 280.15 | 0.077 | 303.15 | 0.15
0.05856 | 280.15 | 0.077 | 303.15 | 0.2
0.05856 | 280.15 | 0.077 | 303.15 | 0.3
0.05856 | 280.15 | 0.077 | 303.15 | 0.4
0.05856 | 280.15 | 0.077 | 303.15 | 0.5
0.05856 | 280.15 | 0.077 | 303.15 | 0.6
0.05856 | 280.15 | 0.077 | 303.15 | 0.7
0.05856 | 280.15 | 0.077 | 303.15 | 0.8
0.05856 | 280.15 | 0.077 | 303.15 | 0.9
0.05856 | 280.15 | 0.077 | 303.15 | 1
0.05856 | 280.15 | 0.09437 | 283.65 | 0.15
0.05856 | 280.15 | 0.09437 | 283.65 | 0.2
0.05856 | 280.15 | 0.09437 | 283.65 | 0.3
0.05856 | 280.15 | 0.09437 | 283.65 | 0.4
0.05856 | 280.15 | 0.09437 | 283.65 | 0.5
0.05856 | 280.15 | 0.09437 | 283.65 | 0.6
0.05856 | 280.15 | 0.09437 | 283.65 | 0.7
0.05856 | 280.15 | 0.09437 | 283.65 | 0.8
0.05856 | 280.15 | 0.09437 | 283.65 | 0.9
0.05856 | 280.15 | 0.09437 | 283.65 | 1
0.05856 | 280.15 | 0.09437 | 284.15 | 0.15
0.05856 | 280.15 | 0.09437 | 284.15 | 0.2
0.05856 | 280.15 | 0.09437 | 284.15 | 0.3
0.05856 | 280.15 | 0.09437 | 284.15 | 0.4
0.05856 | 280.15 | 0.09437 | 284.15 | 0.5
0.05856 | 280.15 | 0.09437 | 284.15 | 0.6
0.05856 | 280.15 | 0.09437 | 284.15 | 0.7
0.05856 | 280.15 | 0.09437 | 284.15 | 0.8
0.05856 | 280.15 | 0.09437 | 284.15 | 0.9
0.05856 | 280.15 | 0.09437 | 284.15 | 1
0.05856 | 280.15 | 0.09437 | 284.65 | 0.15
0.05856 | 280.15 | 0.09437 | 284.65 | 0.2
0.05856 | 280.15 | 0.09437 | 284.65 | 0.3
0.05856 | 280.15 | 0.09437 | 284.65 | 0.4
0.05856 | 280.15 | 0.09437 | 284.65 | 0.5
0.05856 | 280.15 | 0.09437 | 284.65 | 0.6
0.05856 | 280.15 | 0.09437 | 284.65 | 0.7
0.05856 | 280.15 | 0.09437 | 284.65 | 0.8
0.05856 | 280.15 | 0.09437 | 284.65 | 0.9
0.05856 | 280.15 | 0.09437 | 284.65 | 1
0.05856 | 280.15 | 0.09437 | 285.15 | 0.15
0.05856 | 280.15 | 0.09437 | 285.15 | 0.2
0.05856 | 280.15 | 0.09437 | 285.15 | 0.3
0.05856 | 280.15 | 0.09437 | 285.15 | 0.4
0.05856 | 280.15 | 0.09437 | 285.15 | 0.5
0.05856 | 280.15 | 0.09437 | 285.15 | 0.6
0.05856 | 280.15 | 0.09437 | 285.15 | 0.7
0.05856 | 280.15 | 0.09437 | 285.15 | 0.8
0.05856 | 280.15 | 0.09437 | 285.15 | 0.9
0.05856 | 280.15 | 0.09437 | 285.15 | 1
0.05856 | 280.15 | 0.09437 | 285.65 | 0.15
0.05856 | 280.15 | 0.09437 | 285.65 | 0.2
0.05856 | 280.15 | 0.09437 | 285.65 | 0.3
0.05856 | 280.15 | 0.09437 | 285.65 | 0.4
0.05856 | 280.15 | 0.09437 | 285.65 | 0.5
0.05856 | 280.15 | 0.09437 | 285.65 | 0.6
0.05856 | 280.15 | 0.09437 | 285.65 | 0.7
0.05856 | 280.15 | 0.09437 | 285.65 | 0.8
0.05856 | 280.15 | 0.09437 | 285.65 | 0.9
0.05856 | 280.15 | 0.09437 | 285.65 | 1
0.05856 | 280.15 | 0.09437 | 286.15 | 0.15
0.05856 | 280.15 | 0.09437 | 286.15 | 0.2
0.05856 | 280.15 | 0.09437 | 286.15 | 0.3
0.05856 | 280.15 | 0.09437 | 286.15 | 0.4
0.05856 | 280.15 | 0.09437 | 286.15 | 0.5
0.05856 | 280.15 | 0.09437 | 286.15 | 0.6
0.05856 | 280.15 | 0.09437 | 286.15 | 0.7
0.05856 | 280.15 | 0.09437 | 286.15 | 0.8
0.05856 | 280.15 | 0.09437 | 286.15 | 0.9
0.05856 | 280.15 | 0.09437 | 286.15 | 1
0.05856 | 280.15 | 0.09437 | 286.65 | 0.15
0.05856 | 280.15 | 0.09437 | 286.65 | 0.2
0.05856 | 280.15 | 0.09437 | 286.65 | 0.3
0.05856 | 280.15 | 0.09437 | 286.65 | 0.4
0.05856 | 280.15 | 0.09437 | 286.65 | 0.5
0.05856 | 280.15 | 0.09437 | 286.65 | 0.6
0.05856 | 280.15 | 0.09437 | 286.65 | 0.7
0.05856 | 280.15 | 0.09437 | 286.65 | 0.8
0.05856 | 280.15 | 0.09437 | 286.65 | 0.9
0.05856 | 280.15 | 0.09437 | 286.65 | 1
0.05856 | 280.15 | 0.09437 | 287.15 | 0.15
0.05856 | 280.15 | 0.09437 | 287.15 | 0.2
0.05856 | 280.15 | 0.09437 | 287.15 | 0.3
0.05856 | 280.15 | 0.09437 | 287.15 | 0.4
0.05856 | 280.15 | 0.09437 | 287.15 | 0.5
0.05856 | 280.15 | 0.09437 | 287.15 | 0.6
0.05856 | 280.15 | 0.09437 | 287.15 | 0.7
0.05856 | 280.15 | 0.09437 | 287.15 | 0.8
0.05856 | 280.15 | 0.09437 | 287.15 | 0.9
0.05856 | 280.15 | 0.09437 | 287.15 | 1
0.05856 | 280.15 | 0.09437 | 287.65 | 0.15
0.05856 | 280.15 | 0.09437 | 287.65 | 0.2
0.05856 | 280.15 | 0.09437 | 287.65 | 0.3
0.05856 | 280.15 | 0.09437 | 287.65 | 0.4
0.05856 | 280.15 | 0.09437 | 287.65 | 0.5
0.05856 | 280.15 | 0.09437 | 287.65 | 0.6
0.05856 | 280.15 | 0.09437 | 287.65 | 0.7
0.05856 | 280.15 | 0.09437 | 287.65 | 0.8
0.05856 | 280.15 | 0.09437 | 287.65 | 0.9
0.05856 | 280.15 | 0.09437 | 287.65 | 1
0.05856 | 280.15 | 0.09437 | 288.15 | 0.15
0.05856 | 280.15 | 0.09437 | 288.15 | 0.2
0.05856 | 280.15 | 0.09437 | 288.15 | 0.3
0.05856 | 280.15 | 0.09437 | 288.15 | 0.4
0.05856 | 280.15 | 0.09437 | 288.15 | 0.5
0.05856 | 280.15 | 0.09437 | 288.15 | 0.6
0.05856 | 280.15 | 0.09437 | 288.15 | 0.7
0.05856 | 280.15 | 0.09437 | 288.15 | 0.8
0.05856 | 280.15 | 0.09437 | 288.15 | 0.9
0.05856 | 280.15 | 0.09437 | 288.15 | 1
0.05856 | 280.15 | 0.09437 | 288.65 | 0.15
0.05856 | 280.15 | 0.09437 | 288.65 | 0.2
0.05856 | 280.15 | 0.09437 | 288.65 | 0.3
0.05856 | 280.15 | 0.09437 | 288.65 | 0.4
0.05856 | 280.15 | 0.09437 | 288.65 | 0.5
0.05856 | 280.15 | 0.09437 | 288.65 | 0.6
0.05856 | 280.15 | 0.09437 | 288.65 | 0.7
0.05856 | 280.15 | 0.09437 | 288.65 | 0.8
0.05856 | 280.15 | 0.09437 | 288.65 | 0.9
0.05856 | 280.15 | 0.09437 | 288.65 | 1
0.05856 | 280.15 | 0.09437 | 289.15 | 0.15
0.05856 | 280.15 | 0.09437 | 289.15 | 0.2
0.05856 | 280.15 | 0.09437 | 289.15 | 0.3
0.05856 | 280.15 | 0.09437 | 289.15 | 0.4
0.05856 | 280.15 | 0.09437 | 289.15 | 0.5
0.05856 | 280.15 | 0.09437 | 289.15 | 0.6
0.05856 | 280.15 | 0.09437 | 289.15 | 0.7
0.05856 | 280.15 | 0.09437 | 289.15 | 0.8
0.05856 | 280.15 | 0.09437 | 289.15 | 0.9
0.05856 | 280.15 | 0.09437 | 289.15 | 1
0.05856 | 280.15 | 0.09437 | 289.65 | 0.15
0.05856 | 280.15 | 0.09437 | 289.65 | 0.2
0.05856 | 280.15 | 0.09437 | 289.65 | 0.3
0.05856 | 280.15 | 0.09437 | 289.65 | 0.4
0.05856 | 280.15 | 0.09437 | 289.65 | 0.5
0.05856 | 280.15 | 0.09437 | 289.65 | 0.6
0.05856 | 280.15 | 0.09437 | 289.65 | 0.7
0.05856 | 280.15 | 0.09437 | 289.65 | 0.8
0.05856 | 280.15 | 0.09437 | 289.65 | 0.9
0.05856 | 280.15 | 0.09437 | 289.65 | 1
0.05856 | 280.15 | 0.09437 | 290.15 | 0.15
0.05856 | 280.15 | 0.09437 | 290.15 | 0.2
0.05856 | 280.15 | 0.09437 | 290.15 | 0.3
0.05856 | 280.15 | 0.09437 | 290.15 | 0.4
0.05856 | 280.15 | 0.09437 | 290.15 | 0.5
0.05856 | 280.15 | 0.09437 | 290.15 | 0.6
0.05856 | 280.15 | 0.09437 | 290.15 | 0.7
0.05856 | 280.15 | 0.09437 | 290.15 | 0.8
0.05856 | 280.15 | 0.09437 | 290.15 | 0.9
0.05856 | 280.15 | 0.09437 | 290.15 | 1
0.05856 | 280.15 | 0.09437 | 290.65 | 0.15
0.05856 | 280.15 | 0.09437 | 290.65 | 0.2
0.05856 | 280.15 | 0.09437 | 290.65 | 0.3
0.05856 | 280.15 | 0.09437 | 290.65 | 0.4
0.05856 | 280.15 | 0.09437 | 290.65 | 0.5
0.05856 | 280.15 | 0.09437 | 290.65 | 0.6
0.05856 | 280.15 | 0.09437 | 290.65 | 0.7
0.05856 | 280.15 | 0.09437 | 290.65 | 0.8
0.05856 | 280.15 | 0.09437 | 290.65 | 0.9
0.05856 | 280.15 | 0.09437 | 290.65 | 1
0.05856 | 280.15 | 0.09437 | 291.15 | 0.15
0.05856 | 280.15 | 0.09437 | 291.15 | 0.2
0.05856 | 280.15 | 0.09437 | 291.15 | 0.3
0.05856 | 280.15 | 0.09437 | 291.15 | 0.4
0.05856 | 280.15 | 0.09437 | 291.15 | 0.5
0.05856 | 280.15 | 0.09437 | 291.15 | 0.6
0.05856 | 280.15 | 0.09437 | 291.15 | 0.7
0.05856 | 280.15 | 0.09437 | 291.15 | 0.8
0.05856 | 280.15 | 0.09437 | 291.15 | 0.9
0.05856 | 280.15 | 0.09437 | 291.15 | 1
0.05856 | 280.15 | 0.09437 | 294.15 | 0.15
0.05856 | 280.15 | 0.09437 | 294.15 | 0.2
0.05856 | 280.15 | 0.09437 | 294.15 | 0.3
0.05856 | 280.15 | 0.09437 | 294.15 | 0.4
0.05856 | 280.15 | 0.09437 | 294.15 | 0.5
0.05856 | 280.15 | 0.09437 | 294.15 | 0.6
0.05856 | 280.15 | 0.09437 | 294.15 | 0.7
0.05856 | 280.15 | 0.09437 | 294.15 | 0.8
0.05856 | 280.15 | 0.09437 | 294.15 | 0.9
0.05856 | 280.15 | 0.09437 | 294.15 | 1
0.05856 | 280.15 | 0.09437 | 297.15 | 0.15
0.05856 | 280.15 | 0.09437 | 297.15 | 0.2
0.05856 | 280.15 | 0.09437 | 297.15 | 0.3
0.05856 | 280.15 | 0.09437 | 297.15 | 0.4
0.05856 | 280.15 | 0.09437 | 297.15 | 0.5
0.05856 | 280.15 | 0.09437 | 297.15 | 0.6
0.05856 | 280.15 | 0.09437 | 297.15 | 0.7
0.05856 | 280.15 | 0.09437 | 297.15 | 0.8
0.05856 | 280.15 | 0.09437 | 297.15 | 0.9
0.05856 | 280.15 | 0.09437 | 297.15 | 1
0.05856 | 280.15 | 0.09437 | 300.15 | 0.15
0.05856 | 280.15 | 0.09437 | 300.15 | 0.2
0.05856 | 280.15 | 0.09437 | 300.15 | 0.3
0.05856 | 280.15 | 0.09437 | 300.15 | 0.4
0.05856 | 280.15 | 0.09437 | 300.15 | 0.5
0.05856 | 280.15 | 0.09437 | 300.15 | 0.6
0.05856 | 280.15 | 0.09437 | 300.15 | 0.7
0.05856 | 280.15 | 0.09437 | 300.15 | 0.8
0.05856 | 280.15 | 0.09437 | 300.15 | 0.9
0.05856 | 280.15 | 0.09437 | 300.15 | 1
0.05856 | 280.15 | 0.09437 | 303.15 | 0.15
0.05856 | 280.15 | 0.09437 | 303.15 | 0.2
0.05856 | 280.15 | 0.09437 | 303.15 | 0.3
0.05856 | 280.15 | 0.09437 | 303.15 | 0.4
0.05856 | 280.15 | 0.09437 | 303.15 | 0.5
0.05856 | 280.15 | 0.09437 | 303.15 | 0.6
0.05856 | 280.15 | 0.09437 | 303.15 | 0.7
0.05856 | 280.15 | 0.09437 | 303.15 | 0.8
0.05856 | 280.15 | 0.09437 | 303.15 | 0.9
0.05856 | 280.15 | 0.09437 | 303.15 | 1
0.05856 | 280.15 | 0.09644 | 283.65 | 0.15
0.05856 | 280.15 | 0.09644 | 283.65 | 0.2
0.05856 | 280.15 | 0.09644 | 283.65 | 0.3
0.05856 | 280.15 | 0.09644 | 283.65 | 0.4
0.05856 | 280.15 | 0.09644 | 283.65 | 0.5
0.05856 | 280.15 | 0.09644 | 283.65 | 0.6
0.05856 | 280.15 | 0.09644 | 283.65 | 0.7
0.05856 | 280.15 | 0.09644 | 283.65 | 0.8
0.05856 | 280.15 | 0.09644 | 283.65 | 0.9
0.05856 | 280.15 | 0.09644 | 283.65 | 1
0.05856 | 280.15 | 0.09644 | 284.15 | 0.15
0.05856 | 280.15 | 0.09644 | 284.15 | 0.2
0.05856 | 280.15 | 0.09644 | 284.15 | 0.3
0.05856 | 280.15 | 0.09644 | 284.15 | 0.4
0.05856 | 280.15 | 0.09644 | 284.15 | 0.5
0.05856 | 280.15 | 0.09644 | 284.15 | 0.6
0.05856 | 280.15 | 0.09644 | 284.15 | 0.7
0.05856 | 280.15 | 0.09644 | 284.15 | 0.8
0.05856 | 280.15 | 0.09644 | 284.15 | 0.9
0.05856 | 280.15 | 0.09644 | 284.15 | 1
0.05856 | 280.15 | 0.09644 | 284.65 | 0.15
0.05856 | 280.15 | 0.09644 | 284.65 | 0.2
0.05856 | 280.15 | 0.09644 | 284.65 | 0.3
0.05856 | 280.15 | 0.09644 | 284.65 | 0.4
0.05856 | 280.15 | 0.09644 | 284.65 | 0.5
0.05856 | 280.15 | 0.09644 | 284.65 | 0.6
0.05856 | 280.15 | 0.09644 | 284.65 | 0.7
0.05856 | 280.15 | 0.09644 | 284.65 | 0.8
0.05856 | 280.15 | 0.09644 | 284.65 | 0.9
0.05856 | 280.15 | 0.09644 | 284.65 | 1
0.05856 | 280.15 | 0.09644 | 285.15 | 0.15
0.05856 | 280.15 | 0.09644 | 285.15 | 0.2
0.05856 | 280.15 | 0.09644 | 285.15 | 0.3
0.05856 | 280.15 | 0.09644 | 285.15 | 0.4
0.05856 | 280.15 | 0.09644 | 285.15 | 0.5
0.05856 | 280.15 | 0.09644 | 285.15 | 0.6
0.05856 | 280.15 | 0.09644 | 285.15 | 0.7
0.05856 | 280.15 | 0.09644 | 285.15 | 0.8
0.05856 | 280.15 | 0.09644 | 285.15 | 0.9
0.05856 | 280.15 | 0.09644 | 285.15 | 1
0.05856 | 280.15 | 0.09644 | 285.65 | 0.15
0.05856 | 280.15 | 0.09644 | 285.65 | 0.2
0.05856 | 280.15 | 0.09644 | 285.65 | 0.3
0.05856 | 280.15 | 0.09644 | 285.65 | 0.4
0.05856 | 280.15 | 0.09644 | 285.65 | 0.5
0.05856 | 280.15 | 0.09644 | 285.65 | 0.6
0.05856 | 280.15 | 0.09644 | 285.65 | 0.7
0.05856 | 280.15 | 0.09644 | 285.65 | 0.8
0.05856 | 280.15 | 0.09644 | 285.65 | 0.9
0.05856 | 280.15 | 0.09644 | 285.65 | 1
0.05856 | 280.15 | 0.09644 | 286.15 | 0.15
0.05856 | 280.15 | 0.09644 | 286.15 | 0.2
0.05856 | 280.15 | 0.09644 | 286.15 | 0.3
0.05856 | 280.15 | 0.09644 | 286.15 | 0.4
0.05856 | 280.15 | 0.09644 | 286.15 | 0.5
0.05856 | 280.15 | 0.09644 | 286.15 | 0.6
0.05856 | 280.15 | 0.09644 | 286.15 | 0.7
0.05856 | 280.15 | 0.09644 | 286.15 | 0.8
0.05856 | 280.15 | 0.09644 | 286.15 | 0.9
0.05856 | 280.15 | 0.09644 | 286.15 | 1
0.05856 | 280.15 | 0.09644 | 286.65 | 0.15
0.05856 | 280.15 | 0.09644 | 286.65 | 0.2
0.05856 | 280.15 | 0.09644 | 286.65 | 0.3
0.05856 | 280.15 | 0.09644 | 286.65 | 0.4
0.05856 | 280.15 | 0.09644 | 286.65 | 0.5
0.05856 | 280.15 | 0.09644 | 286.65 | 0.6
0.05856 | 280.15 | 0.09644 | 286.65 | 0.7
0.05856 | 280.15 | 0.09644 | 286.65 | 0.8
0.05856 | 280.15 | 0.09644 | 286.65 | 0.9
0.05856 | 280.15 | 0.09644 | 286.65 | 1
0.05856 | 280.15 | 0.09644 | 287.15 | 0.15
0.05856 | 280.15 | 0.09644 | 287.15 | 0.2
0.05856 | 280.15 | 0.09644 | 287.15 | 0.3
0.05856 | 280.15 | 0.09644 | 287.15 | 0.4
0.05856 | 280.15 | 0.09644 | 287.15 | 0.5
0.05856 | 280.15 | 0.09644 | 287.15 | 0.6
0.05856 | 280.15 | 0.09644 | 287.15 | 0.7
0.05856 | 280.15 | 0.09644 | 287.15 | 0.8
0.05856 | 280.15 | 0.09644 | 287.15 | 0.9
0.05856 | 280.15 | 0.09644 | 287.15 | 1
0.05856 | 280.15 | 0.09644 | 287.65 | 0.15
0.05856 | 280.15 | 0.09644 | 287.65 | 0.2
0.05856 | 280.15 | 0.09644 | 287.65 | 0.3
0.05856 | 280.15 | 0.09644 | 287.65 | 0.4
0.05856 | 280.15 | 0.09644 | 287.65 | 0.5
0.05856 | 280.15 | 0.09644 | 287.65 | 0.6
0.05856 | 280.15 | 0.09644 | 287.65 | 0.7
0.05856 | 280.15 | 0.09644 | 287.65 | 0.8
0.05856 | 280.15 | 0.09644 | 287.65 | 0.9
0.05856 | 280.15 | 0.09644 | 287.65 | 1
0.05856 | 280.15 | 0.09644 | 288.15 | 0.15
0.05856 | 280.15 | 0.09644 | 288.15 | 0.2
0.05856 | 280.15 | 0.09644 | 288.15 | 0.3
0.05856 | 280.15 | 0.09644 | 288.15 | 0.4
0.05856 | 280.15 | 0.09644 | 288.15 | 0.5
0.05856 | 280.15 | 0.09644 | 288.15 | 0.6
0.05856 | 280.15 | 0.09644 | 288.15 | 0.7
0.05856 | 280.15 | 0.09644 | 288.15 | 0.8
0.05856 | 280.15 | 0.09644 | 288.15 | 0.9
0.05856 | 280.15 | 0.09644 | 288.15 | 1
0.05856 | 280.15 | 0.09644 | 288.65 | 0.15
0.05856 | 280.15 | 0.09644 | 288.65 | 0.2
0.05856 | 280.15 | 0.09644 | 288.65 | 0.3
0.05856 | 280.15 | 0.09644 | 288.65 | 0.4
0.05856 | 280.15 | 0.09644 | 288.65 | 0.5
0.05856 | 280.15 | 0.09644 | 288.65 | 0.6
0.05856 | 280.15 | 0.09644 | 288.65 | 0.7
0.05856 | 280.15 | 0.09644 | 288.65 | 0.8
0.05856 | 280.15 | 0.09644 | 288.65 | 0.9
0.05856 | 280.15 | 0.09644 | 288.65 | 1
0.05856 | 280.15 | 0.09644 | 289.15 | 0.15
0.05856 | 280.15 | 0.09644 | 289.15 | 0.2
0.05856 | 280.15 | 0.09644 | 289.15 | 0.3
0.05856 | 280.15 | 0.09644 | 289.15 | 0.4
0.05856 | 280.15 | 0.09644 | 289.15 | 0.5
0.05856 | 280.15 | 0.09644 | 289.15 | 0.6
0.05856 | 280.15 | 0.09644 | 289.15 | 0.7
0.05856 | 280.15 | 0.09644 | 289.15 | 0.8
0.05856 | 280.15 | 0.09644 | 289.15 | 0.9
0.05856 | 280.15 | 0.09644 | 289.15 | 1
0.05856 | 280.15 | 0.09644 | 289.65 | 0.15
0.05856 | 280.15 | 0.09644 | 289.65 | 0.2
0.05856 | 280.15 | 0.09644 | 289.65 | 0.3
0.05856 | 280.15 | 0.09644 | 289.65 | 0.4
0.05856 | 280.15 | 0.09644 | 289.65 | 0.5
0.05856 | 280.15 | 0.09644 | 289.65 | 0.6
0.05856 | 280.15 | 0.09644 | 289.65 | 0.7
0.05856 | 280.15 | 0.09644 | 289.65 | 0.8
0.05856 | 280.15 | 0.09644 | 289.65 | 0.9
0.05856 | 280.15 | 0.09644 | 289.65 | 1
0.05856 | 280.15 | 0.09644 | 290.15 | 0.15
0.05856 | 280.15 | 0.09644 | 290.15 | 0.2
0.05856 | 280.15 | 0.09644 | 290.15 | 0.3
0.05856 | 280.15 | 0.09644 | 290.15 | 0.4
0.05856 | 280.15 | 0.09644 | 290.15 | 0.5
0.05856 | 280.15 | 0.09644 | 290.15 | 0.6
0.05856 | 280.15 | 0.09644 | 290.15 | 0.7
0.05856 | 280.15 | 0.09644 | 290.15 | 0.8
0.05856 | 280.15 | 0.09644 | 290.15 | 0.9
0.05856 | 280.15 | 0.09644 | 290.15 | 1
0.05856 | 280.15 | 0.09644 | 290.65 | 0.15
0.05856 | 280.15 | 0.09644 | 290.65 | 0.2
0.05856 | 280.15 | 0.09644 | 290.65 | 0.3
0.05856 | 280.15 | 0.09644 | 290.65 | 0.4
0.05856 | 280.15 | 0.09644 | 290.65 | 0.5
0.05856 | 280.15 | 0.09644 | 290.65 | 0.6
0.05856 | 280.15 | 0.09644 | 290.65 | 0.7
0.05856 | 280.15 | 0.09644 | 290.65 | 0.8
0.05856 | 280.15 | 0.09644 | 290.65 | 0.9
0.05856 | 280.15 | 0.09644 | 290.65 | 1
0.05856 | 280.15 | 0.09644 | 291.15 | 0.15
0.05856 | 280.15 | 0.09644 | 291.15 | 0.2
0.05856 | 280.15 | 0.09644 | 291.15 | 0.3
0.05856 | 280.15 | 0.09644 | 291.15 | 0.4
0.05856 | 280.15 | 0.09644 | 291.15 | 0.5
0.05856 | 280.15 | 0.09644 | 291.15 | 0.6
0.05856 | 280.15 | 0.09644 | 291.15 | 0.7
0.05856 | 280.15 | 0.09644 | 291.15 | 0.8
0.05856 | 280.15 | 0.09644 | 291.15 | 0.9
0.05856 | 280.15 | 0.09644 | 291.15 | 1
0.05856 | 280.15 | 0.09644 | 294.15 | 0.15
0.05856 | 280.15 | 0.09644 | 294.15 | 0.2
0.05856 | 280.15 | 0.09644 | 294.15 | 0.3
0.05856 | 280.15 | 0.09644 | 294.15 | 0.4
0.05856 | 280.15 | 0.09644 | 294.15 | 0.5
0.05856 | 280.15 | 0.09644 | 294.15 | 0.6
0.05856 | 280.15 | 0.09644 | 294.15 | 0.7
0.05856 | 280.15 | 0.09644 | 294.15 | 0.8
0.05856 | 280.15 | 0.09644 | 294.15 | 0.9
0.05856 | 280.15 | 0.09644 | 294.15 | 1
0.05856 | 280.15 | 0.09644 | 297.15 | 0.15
0.05856 | 280.15 | 0.09644 | 297.15 | 0.2
0.05856 | 280.15 | 0.09644 | 297.15 | 0.3
0.05856 | 280.15 | 0.09644 | 297.15 | 0.4
0.05856 | 280.15 | 0.09644 | 297.15 | 0.5
0.05856 | 280.15 | 0.09644 | 297.15 | 0.6
0.05856 | 280.15 | 0.09644 | 297.15 | 0.7
0.05856 | 280.15 | 0.09644 | 297.15 | 0.8
0.05856 | 280.15 | 0.09644 | 297.15 | 0.9
0.05856 | 280.15 | 0.09644 | 297.15 | 1
0.05856 | 280.15 | 0.09644 | 300.15 | 0.15
0.05856 | 280.15 | 0.09644 | 300.15 | 0.2
0.05856 | 280.15 | 0.09644 | 300.15 | 0.3
0.05856 | 280.15 | 0.09644 | 300.15 | 0.4
0.05856 | 280.15 | 0.09644 | 300.15 | 0.5
0.05856 | 280.15 | 0.09644 | 300.15 | 0.6
0.05856 | 280.15 | 0.09644 | 300.15 | 0.7
0.05856 | 280.15 | 0.09644 | 300.15 | 0.8
0.05856 | 280.15 | 0.09644 | 300.15 | 0.9
0.05856 | 280.15 | 0.09644 | 300.15 | 1
0.05856 | 280.15 | 0.09644 | 303.15 | 0.15
0.05856 | 280.15 | 0.09644 | 303.15 | 0.2
0.05856 | 280.15 | 0.09644 | 303.15 | 0.3
0.05856 | 280.15 | 0.09644 | 303.15 | 0.4
0.05856 | 280.15 | 0.09644 | 303.15 | 0.5
0.05856 | 280.15 | 0.09644 | 303.15 | 0.6
0.05856 | 280.15 | 0.09644 | 303.15 | 0.7
0.05856 | 280.15 | 0.09644 | 303.15 | 0.8
0.05856 | 280.15 | 0.09644 | 303.15 | 0.9
0.05856 | 280.15 | 0.09644 | 303.15 | 1
0.05856 | 280.15 | 0.09737 | 283.65 | 0.15
0.05856 | 280.15 | 0.09737 | 283.65 | 0.2
0.05856 | 280.15 | 0.09737 | 283.65 | 0.3
0.05856 | 280.15 | 0.09737 | 283.65 | 0.4
0.05856 | 280.15 | 0.09737 | 283.65 | 0.5
0.05856 | 280.15 | 0.09737 | 283.65 | 0.6
0.05856 | 280.15 | 0.09737 | 283.65 | 0.7
0.05856 | 280.15 | 0.09737 | 283.65 | 0.8
0.05856 | 280.15 | 0.09737 | 283.65 | 0.9
0.05856 | 280.15 | 0.09737 | 283.65 | 1
0.05856 | 280.15 | 0.09737 | 284.15 | 0.15
0.05856 | 280.15 | 0.09737 | 284.15 | 0.2
0.05856 | 280.15 | 0.09737 | 284.15 | 0.3
0.05856 | 280.15 | 0.09737 | 284.15 | 0.4
0.05856 | 280.15 | 0.09737 | 284.15 | 0.5
0.05856 | 280.15 | 0.09737 | 284.15 | 0.6
0.05856 | 280.15 | 0.09737 | 284.15 | 0.7
0.05856 | 280.15 | 0.09737 | 284.15 | 0.8
0.05856 | 280.15 | 0.09737 | 284.15 | 0.9
0.05856 | 280.15 | 0.09737 | 284.15 | 1
0.05856 | 280.15 | 0.09737 | 284.65 | 0.15
0.05856 | 280.15 | 0.09737 | 284.65 | 0.2
0.05856 | 280.15 | 0.09737 | 284.65 | 0.3
0.05856 | 280.15 | 0.09737 | 284.65 | 0.4
0.05856 | 280.15 | 0.09737 | 284.65 | 0.5
0.05856 | 280.15 | 0.09737 | 284.65 | 0.6
0.05856 | 280.15 | 0.09737 | 284.65 | 0.7
0.05856 | 280.15 | 0.09737 | 284.65 | 0.8
0.05856 | 280.15 | 0.09737 | 284.65 | 0.9
0.05856 | 280.15 | 0.09737 | 284.65 | 1
0.05856 | 280.15 | 0.09737 | 285.15 | 0.15
0.05856 | 280.15 | 0.09737 | 285.15 | 0.2
0.05856 | 280.15 | 0.09737 | 285.15 | 0.3
0.05856 | 280.15 | 0.09737 | 285.15 | 0.4
0.05856 | 280.15 | 0.09737 | 285.15 | 0.5
0.05856 | 280.15 | 0.09737 | 285.15 | 0.6
0.05856 | 280.15 | 0.09737 | 285.15 | 0.7
0.05856 | 280.15 | 0.09737 | 285.15 | 0.8
0.05856 | 280.15 | 0.09737 | 285.15 | 0.9
0.05856 | 280.15 | 0.09737 | 285.15 | 1
0.05856 | 280.15 | 0.09737 | 285.65 | 0.15
0.05856 | 280.15 | 0.09737 | 285.65 | 0.2
0.05856 | 280.15 | 0.09737 | 285.65 | 0.3
0.05856 | 280.15 | 0.09737 | 285.65 | 0.4
0.05856 | 280.15 | 0.09737 | 285.65 | 0.5
0.05856 | 280.15 | 0.09737 | 285.65 | 0.6
0.05856 | 280.15 | 0.09737 | 285.65 | 0.7
0.05856 | 280.15 | 0.09737 | 285.65 | 0.8
0.05856 | 280.15 | 0.09737 | 285.65 | 0.9
0.05856 | 280.15 | 0.09737 | 285.65 | 1
0.05856 | 280.15 | 0.09737 | 286.15 | 0.15
0.05856 | 280.15 | 0.09737 | 286.15 | 0.2
0.05856 | 280.15 | 0.09737 | 286.15 | 0.3
0.05856 | 280.15 | 0.09737 | 286.15 | 0.4
0.05856 | 280.15 | 0.09737 | 286.15 | 0.5
0.05856 | 280.15 | 0.09737 | 286.15 | 0.6
0.05856 | 280.15 | 0.09737 | 286.15 | 0.7
0.05856 | 280.15 | 0.09737 | 286.15 | 0.8
0.05856 | 280.15 | 0.09737 | 286.15 | 0.9
0.05856 | 280.15 | 0.09737 | 286.15 | 1
0.05856 | 280.15 | 0.09737 | 286.65 | 0.15
0.05856 | 280.15 | 0.09737 | 286.65 | 0.2
0.05856 | 280.15 | 0.09737 | 286.65 | 0.3
0.05856 | 280.15 | 0.09737 | 286.65 | 0.4
0.05856 | 280.15 | 0.09737 | 286.65 | 0.5
0.05856 | 280.15 | 0.09737 | 286.65 | 0.6
0.05856 | 280.15 | 0.09737 | 286.65 | 0.7
0.05856 | 280.15 | 0.09737 | 286.65 | 0.8
0.05856 | 280.15 | 0.09737 | 286.65 | 0.9
0.05856 | 280.15 | 0.09737 | 286.65 | 1
0.05856 | 280.15 | 0.09737 | 287.15 | 0.15
0.05856 | 280.15 | 0.09737 | 287.15 | 0.2
0.05856 | 280.15 | 0.09737 | 287.15 | 0.3
0.05856 | 280.15 | 0.09737 | 287.15 | 0.4
0.05856 | 280.15 | 0.09737 | 287.15 | 0.5
0.05856 | 280.15 | 0.09737 | 287.15 | 0.6
0.05856 | 280.15 | 0.09737 | 287.15 | 0.7
0.05856 | 280.15 | 0.09737 | 287.15 | 0.8
0.05856 | 280.15 | 0.09737 | 287.15 | 0.9
0.05856 | 280.15 | 0.09737 | 287.15 | 1
0.05856 | 280.15 | 0.09737 | 287.65 | 0.15
0.05856 | 280.15 | 0.09737 | 287.65 | 0.2
0.05856 | 280.15 | 0.09737 | 287.65 | 0.3
0.05856 | 280.15 | 0.09737 | 287.65 | 0.4
0.05856 | 280.15 | 0.09737 | 287.65 | 0.5
0.05856 | 280.15 | 0.09737 | 287.65 | 0.6
0.05856 | 280.15 | 0.09737 | 287.65 | 0.7
0.05856 | 280.15 | 0.09737 | 287.65 | 0.8
0.05856 | 280.15 | 0.09737 | 287.65 | 0.9
0.05856 | 280.15 | 0.09737 | 287.65 | 1
0.05856 | 280.15 | 0.09737 | 288.15 | 0.15
0.05856 | 280.15 | 0.09737 | 288.15 | 0.2
0.05856 | 280.15 | 0.09737 | 288.15 | 0.3
0.05856 | 280.15 | 0.09737 | 288.15 | 0.4
0.05856 | 280.15 | 0.09737 | 288.15 | 0.5
0.05856 | 280.15 | 0.09737 | 288.15 | 0.6
0.05856 | 280.15 | 0.09737 | 288.15 | 0.7
0.05856 | 280.15 | 0.09737 | 288.15 | 0.8
0.05856 | 280.15 | 0.09737 | 288.15 | 0.9
0.05856 | 280.15 | 0.09737 | 288.15 | 1
0.05856 | 280.15 | 0.09737 | 288.65 | 0.15
0.05856 | 280.15 | 0.09737 | 288.65 | 0.2
0.05856 | 280.15 | 0.09737 | 288.65 | 0.3
0.05856 | 280.15 | 0.09737 | 288.65 | 0.4
0.05856 | 280.15 | 0.09737 | 288.65 | 0.5
0.05856 | 280.15 | 0.09737 | 288.65 | 0.6
0.05856 | 280.15 | 0.09737 | 288.65 | 0.7
0.05856 | 280.15 | 0.09737 | 288.65 | 0.8
0.05856 | 280.15 | 0.09737 | 288.65 | 0.9
0.05856 | 280.15 | 0.09737 | 288.65 | 1
0.05856 | 280.15 | 0.09737 | 289.15 | 0.15
0.05856 | 280.15 | 0.09737 | 289.15 | 0.2
0.05856 | 280.15 | 0.09737 | 289.15 | 0.3
0.05856 | 280.15 | 0.09737 | 289.15 | 0.4
0.05856 | 280.15 | 0.09737 | 289.15 | 0.5
0.05856 | 280.15 | 0.09737 | 289.15 | 0.6
0.05856 | 280.15 | 0.09737 | 289.15 | 0.7
0.05856 | 280.15 | 0.09737 | 289.15 | 0.8
0.05856 | 280.15 | 0.09737 | 289.15 | 0.9
0.05856 | 280.15 | 0.09737 | 289.15 | 1
0.05856 | 280.15 | 0.09737 | 289.65 | 0.15
0.05856 | 280.15 | 0.09737 | 289.65 | 0.2
0.05856 | 280.15 | 0.09737 | 289.65 | 0.3
0.05856 | 280.15 | 0.09737 | 289.65 | 0.4
0.05856 | 280.15 | 0.09737 | 289.65 | 0.5
0.05856 | 280.15 | 0.09737 | 289.65 | 0.6
0.05856 | 280.15 | 0.09737 | 289.65 | 0.7
0.05856 | 280.15 | 0.09737 | 289.65 | 0.8
0.05856 | 280.15 | 0.09737 | 289.65 | 0.9
0.05856 | 280.15 | 0.09737 | 289.65 | 1
0.05856 | 280.15 | 0.09737 | 290.15 | 0.15
0.05856 | 280.15 | 0.09737 | 290.15 | 0.2
0.05856 | 280.15 | 0.09737 | 290.15 | 0.3
0.05856 | 280.15 | 0.09737 | 290.15 | 0.4
0.05856 | 280.15 | 0.09737 | 290.15 | 0.5
0.05856 | 280.15 | 0.09737 | 290.15 | 0.6
0.05856 | 280.15 | 0.09737 | 290.15 | 0.7
0.05856 | 280.15 | 0.09737 | 290.15 | 0.8
0.05856 | 280.15 | 0.09737 | 290.15 | 0.9
0.05856 | 280.15 | 0.09737 | 290.15 | 1
0.05856 | 280.15 | 0.09737 | 290.65 | 0.15
0.05856 | 280.15 | 0.09737 | 290.65 | 0.2
0.05856 | 280.15 | 0.09737 | 290.65 | 0.3
0.05856 | 280.15 | 0.09737 | 290.65 | 0.4
0.05856 | 280.15 | 0.09737 | 290.65 | 0.5
0.05856 | 280.15 | 0.09737 | 290.65 | 0.6
0.05856 | 280.15 | 0.09737 | 290.65 | 0.7
0.05856 | 280.15 | 0.09737 | 290.65 | 0.8
0.05856 | 280.15 | 0.09737 | 290.65 | 0.9
0.05856 | 280.15 | 0.09737 | 290.65 | 1
0.05856 | 280.15 | 0.09737 | 291.15 | 0.15
0.05856 | 280.15 | 0.09737 | 291.15 | 0.2
0.05856 | 280.15 | 0.09737 | 291.15 | 0.3
0.05856 | 280.15 | 0.09737 | 291.15 | 0.4
0.05856 | 280.15 | 0.09737 | 291.15 | 0.5
0.05856 | 280.15 | 0.09737 | 291.15 | 0.6
0.05856 | 280.15 | 0.09737 | 291.15 | 0.7
0.05856 | 280.15 | 0.09737 | 291.15 | 0.8
0.05856 | 280.15 | 0.09737 | 291.15 | 0.9
0.05856 | 280.15 | 0.09737 | 291.15 | 1
0.05856 | 280.15 | 0.09737 | 294.15 | 0.15
0.05856 | 280.15 | 0.09737 | 294.15 | 0.2
0.05856 | 280.15 | 0.09737 | 294.15 | 0.3
0.05856 | 280.15 | 0.09737 | 294.15 | 0.4
0.05856 | 280.15 | 0.09737 | 294.15 | 0.5
0.05856 | 280.15 | 0.09737 | 294.15 | 0.6
0.05856 | 280.15 | 0.09737 | 294.15 | 0.7
0.05856 | 280.15 | 0.09737 | 294.15 | 0.8
0.05856 | 280.15 | 0.09737 | 294.15 | 0.9
0.05856 | 280.15 | 0.09737 | 294.15 | 1
0.05856 | 280.15 | 0.09737 | 297.15 | 0.15
0.05856 | 280.15 | 0.09737 | 297.15 | 0.2
0.05856 | 280.15 | 0.09737 | 297.15 | 0.3
0.05856 | 280.15 | 0.09737 | 297.15 | 0.4
0.05856 | 280.15 | 0.09737 | 297.15 | 0.5
0.05856 | 280.15 | 0.09737 | 297.15 | 0.6
0.05856 | 280.15 | 0.09737 | 297.15 | 0.7
0.05856 | 280.15 | 0.09737 | 297.15 | 0.8
0.05856 | 280.15 | 0.09737 | 297.15 | 0.9
0.05856 | 280.15 | 0.09737 | 297.15 | 1
0.05856 | 280.15 | 0.09737 | 300.15 | 0.15
0.05856 | 280.15 | 0.09737 | 300.15 | 0.2
0.05856 | 280.15 | 0.09737 | 300.15 | 0.3
0.05856 | 280.15 | 0.09737 | 300.15 | 0.4
0.05856 | 280.15 | 0.09737 | 300.15 | 0.5
0.05856 | 280.15 | 0.09737 | 300.15 | 0.6
0.05856 | 280.15 | 0.09737 | 300.15 | 0.7
0.05856 | 280.15 | 0.09737 | 300.15 | 0.8
0.05856 | 280.15 | 0.09737 | 300.15 | 0.9
0.05856 | 280.15 | 0.09737 | 300.15 | 1
0.05856 | 280.15 | 0.09737 | 303.15 | 0.15
0.05856 | 280.15 | 0.09737 | 303.15 | 0.2
0.05856 | 280.15 | 0.09737 | 303.15 | 0.3
0.05856 | 280.15 | 0.09737 | 303.15 | 0.4
0.05856 | 280.15 | 0.09737 | 303.15 | 0.5
0.05856 | 280.15 | 0.09737 | 303.15 | 0.6
0.05856 | 280.15 | 0.09737 | 303.15 | 0.7
0.05856 | 280.15 | 0.09737 | 303.15 | 0.8
0.05856 | 280.15 | 0.09737 | 303.15 | 0.9
0.05856 | 280.15 | 0.09737 | 303.15 | 1
0.05856 | 280.15 | 0.115 | 283.65 | 0.15
0.05856 | 280.15 | 0.115 | 283.65 | 0.2
0.05856 | 280.15 | 0.115 | 283.65 | 0.3
0.05856 | 280.15 | 0.115 | 283.65 | 0.4
0.05856 | 280.15 | 0.115 | 283.65 | 0.5
0.05856 | 280.15 | 0.115 | 283.65 | 0.6
0.05856 | 280.15 | 0.115 | 283.65 | 0.7
0.05856 | 280.15 | 0.115 | 283.65 | 0.8
0.05856 | 280.15 | 0.115 | 283.65 | 0.9
0.05856 | 280.15 | 0.115 | 283.65 | 1
0.05856 | 280.15 | 0.115 | 284.15 | 0.15
0.05856 | 280.15 | 0.115 | 284.15 | 0.2
0.05856 | 280.15 | 0.115 | 284.15 | 0.3
0.05856 | 280.15 | 0.115 | 284.15 | 0.4
0.05856 | 280.15 | 0.115 | 284.15 | 0.5
0.05856 | 280.15 | 0.115 | 284.15 | 0.6
0.05856 | 280.15 | 0.115 | 284.15 | 0.7
0.05856 | 280.15 | 0.115 | 284.15 | 0.8
0.05856 | 280.15 | 0.115 | 284.15 | 0.9
0.05856 | 280.15 | 0.115 | 284.15 | 1
0.05856 | 280.15 | 0.115 | 284.65 | 0.15
0.05856 | 280.15 | 0.115 | 284.65 | 0.2
0.05856 | 280.15 | 0.115 | 284.65 | 0.3
0.05856 | 280.15 | 0.115 | 284.65 | 0.4
0.05856 | 280.15 | 0.115 | 284.65 | 0.5
0.05856 | 280.15 | 0.115 | 284.65 | 0.6
0.05856 | 280.15 | 0.115 | 284.65 | 0.7
0.05856 | 280.15 | 0.115 | 284.65 | 0.8
0.05856 | 280.15 | 0.115 | 284.65 | 0.9
0.05856 | 280.15 | 0.115 | 284.65 | 1
0.05856 | 280.15 | 0.115 | 285.15 | 0.15
0.05856 | 280.15 | 0.115 | 285.15 | 0.2
0.05856 | 280.15 | 0.115 | 285.15 | 0.3
0.05856 | 280.15 | 0.115 | 285.15 | 0.4
0.05856 | 280.15 | 0.115 | 285.15 | 0.5
0.05856 | 280.15 | 0.115 | 285.15 | 0.6
0.05856 | 280.15 | 0.115 | 285.15 | 0.7
0.05856 | 280.15 | 0.115 | 285.15 | 0.8
0.05856 | 280.15 | 0.115 | 285.15 | 0.9
0.05856 | 280.15 | 0.115 | 285.15 | 1
0.05856 | 280.15 | 0.115 | 285.65 | 0.15
0.05856 | 280.15 | 0.115 | 285.65 | 0.2
0.05856 | 280.15 | 0.115 | 285.65 | 0.3
0.05856 | 280.15 | 0.115 | 285.65 | 0.4
0.05856 | 280.15 | 0.115 | 285.65 | 0.5
0.05856 | 280.15 | 0.115 | 285.65 | 0.6
0.05856 | 280.15 | 0.115 | 285.65 | 0.7
0.05856 | 280.15 | 0.115 | 285.65 | 0.8
0.05856 | 280.15 | 0.115 | 285.65 | 0.9
0.05856 | 280.15 | 0.115 | 285.65 | 1
0.05856 | 280.15 | 0.115 | 286.15 | 0.15
0.05856 | 280.15 | 0.115 | 286.15 | 0.2
0.05856 | 280.15 | 0.115 | 286.15 | 0.3
0.05856 | 280.15 | 0.115 | 286.15 | 0.4
0.05856 | 280.15 | 0.115 | 286.15 | 0.5
0.05856 | 280.15 | 0.115 | 286.15 | 0.6
0.05856 | 280.15 | 0.115 | 286.15 | 0.7
0.05856 | 280.15 | 0.115 | 286.15 | 0.8
0.05856 | 280.15 | 0.115 | 286.15 | 0.9
0.05856 | 280.15 | 0.115 | 286.15 | 1
0.05856 | 280.15 | 0.115 | 286.65 | 0.15
0.05856 | 280.15 | 0.115 | 286.65 | 0.2
0.05856 | 280.15 | 0.115 | 286.65 | 0.3
0.05856 | 280.15 | 0.115 | 286.65 | 0.4
0.05856 | 280.15 | 0.115 | 286.65 | 0.5
0.05856 | 280.15 | 0.115 | 286.65 | 0.6
0.05856 | 280.15 | 0.115 | 286.65 | 0.7
0.05856 | 280.15 | 0.115 | 286.65 | 0.8
0.05856 | 280.15 | 0.115 | 286.65 | 0.9
0.05856 | 280.15 | 0.115 | 286.65 | 1
0.05856 | 280.15 | 0.115 | 287.15 | 0.15
0.05856 | 280.15 | 0.115 | 287.15 | 0.2
0.05856 | 280.15 | 0.115 | 287.15 | 0.3
0.05856 | 280.15 | 0.115 | 287.15 | 0.4
0.05856 | 280.15 | 0.115 | 287.15 | 0.5
0.05856 | 280.15 | 0.115 | 287.15 | 0.6
0.05856 | 280.15 | 0.115 | 287.15 | 0.7
0.05856 | 280.15 | 0.115 | 287.15 | 0.8
0.05856 | 280.15 | 0.115 | 287.15 | 0.9
0.05856 | 280.15 | 0.115 | 287.15 | 1
0.05856 | 280.15 | 0.115 | 287.65 | 0.15
0.05856 | 280.15 | 0.115 | 287.65 | 0.2
0.05856 | 280.15 | 0.115 | 287.65 | 0.3
0.05856 | 280.15 | 0.115 | 287.65 | 0.4
0.05856 | 280.15 | 0.115 | 287.65 | 0.5
0.05856 | 280.15 | 0.115 | 287.65 | 0.6
0.05856 | 280.15 | 0.115 | 287.65 | 0.7
0.05856 | 280.15 | 0.115 | 287.65 | 0.8
0.05856 | 280.15 | 0.115 | 287.65 | 0.9
0.05856 | 280.15 | 0.115 | 287.65 | 1
0.05856 | 280.15 | 0.115 | 288.15 | 0.15
0.05856 | 280.15 | 0.115 | 288.15 | 0.2
0.05856 | 280.15 | 0.115 | 288.15 | 0.3
0.05856 | 280.15 | 0.115 | 288.15 | 0.4
0.05856 | 280.15 | 0.115 | 288.15 | 0.5
0.05856 | 280.15 | 0.115 | 288.15 | 0.6
0.05856 | 280.15 | 0.115 | 288.15 | 0.7
0.05856 | 280.15 | 0.115 | 288.15 | 0.8
0.05856 | 280.15 | 0.115 | 288.15 | 0.9
0.05856 | 280.15 | 0.115 | 288.15 | 1
0.05856 | 280.15 | 0.115 | 288.65 | 0.15
0.05856 | 280.15 | 0.115 | 288.65 | 0.2
0.05856 | 280.15 | 0.115 | 288.65 | 0.3
0.05856 | 280.15 | 0.115 | 288.65 | 0.4
0.05856 | 280.15 | 0.115 | 288.65 | 0.5
0.05856 | 280.15 | 0.115 | 288.65 | 0.6
0.05856 | 280.15 | 0.115 | 288.65 | 0.7
0.05856 | 280.15 | 0.115 | 288.65 | 0.8
0.05856 | 280.15 | 0.115 | 288.65 | 0.9
0.05856 | 280.15 | 0.115 | 288.65 | 1
0.05856 | 280.15 | 0.115 | 289.15 | 0.15
0.05856 | 280.15 | 0.115 | 289.15 | 0.2
0.05856 | 280.15 | 0.115 | 289.15 | 0.3
0.05856 | 280.15 | 0.115 | 289.15 | 0.4
0.05856 | 280.15 | 0.115 | 289.15 | 0.5
0.05856 | 280.15 | 0.115 | 289.15 | 0.6
0.05856 | 280.15 | 0.115 | 289.15 | 0.7
0.05856 | 280.15 | 0.115 | 289.15 | 0.8
0.05856 | 280.15 | 0.115 | 289.15 | 0.9
0.05856 | 280.15 | 0.115 | 289.15 | 1
0.05856 | 280.15 | 0.115 | 289.65 | 0.15
0.05856 | 280.15 | 0.115 | 289.65 | 0.2
0.05856 | 280.15 | 0.115 | 289.65 | 0.3
0.05856 | 280.15 | 0.115 | 289.65 | 0.4
0.05856 | 280.15 | 0.115 | 289.65 | 0.5
0.05856 | 280.15 | 0.115 | 289.65 | 0.6
0.05856 | 280.15 | 0.115 | 289.65 | 0.7
0.05856 | 280.15 | 0.115 | 289.65 | 0.8
0.05856 | 280.15 | 0.115 | 289.65 | 0.9
0.05856 | 280.15 | 0.115 | 289.65 | 1
0.05856 | 280.15 | 0.115 | 290.15 | 0.15
0.05856 | 280.15 | 0.115 | 290.15 | 0.2
0.05856 | 280.15 | 0.115 | 290.15 | 0.3
0.05856 | 280.15 | 0.115 | 290.15 | 0.4
0.05856 | 280.15 | 0.115 | 290.15 | 0.5
0.05856 | 280.15 | 0.115 | 290.15 | 0.6
0.05856 | 280.15 | 0.115 | 290.15 | 0.7
0.05856 | 280.15 | 0.115 | 290.15 | 0.8
0.05856 | 280.15 | 0.115 | 290.15 | 0.9
0.05856 | 280.15 | 0.115 | 290.15 | 1
0.05856 | 280.15 | 0.115 | 290.65 | 0.15
0.05856 | 280.15 | 0.115 | 290.65 | 0.2
0.05856 | 280.15 | 0.115 | 290.65 | 0.3
0.05856 | 280.15 | 0.115 | 290.65 | 0.4
0.05856 | 280.15 | 0.115 | 290.65 | 0.5
0.05856 | 280.15 | 0.115 | 290.65 | 0.6
0.05856 | 280.15 | 0.115 | 290.65 | 0.7
0.05856 | 280.15 | 0.115 | 290.65 | 0.8
0.05856 | 280.15 | 0.115 | 290.65 | 0.9
0.05856 | 280.15 | 0.115 | 290.65 | 1
0.05856 | 280.15 | 0.115 | 291.15 | 0.15
0.05856 | 280.15 | 0.115 | 291.15 | 0.2
0.05856 | 280.15 | 0.115 | 291.15 | 0.3
0.05856 | 280.15 | 0.115 | 291.15 | 0.4
0.05856 | 280.15 | 0.115 | 291.15 | 0.5
0.05856 | 280.15 | 0.115 | 291.15 | 0.6
0.05856 | 280.15 | 0.115 | 291.15 | 0.7
0.05856 | 280.15 | 0.115 | 291.15 | 0.8
0.05856 | 280.15 | 0.115 | 291.15 | 0.9
0.05856 | 280.15 | 0.115 | 291.15 | 1
0.05856 | 280.15 | 0.115 | 294.15 | 0.15
0.05856 | 280.15 | 0.115 | 294.15 | 0.2
0.05856 | 280.15 | 0.115 | 294.15 | 0.3
0.05856 | 280.15 | 0.115 | 294.15 | 0.4
0.05856 | 280.15 | 0.115 | 294.15 | 0.5
0.05856 | 280.15 | 0.115 | 294.15 | 0.6
0.05856 | 280.15 | 0.115 | 294.15 | 0.7
0.05856 | 280.15 | 0.115 | 294.15 | 0.8
0.05856 | 280.15 | 0.115 | 294.15 | 0.9
0.05856 | 280.15 | 0.115 | 294.15 | 1
0.05856 | 280.15 | 0.115 | 297.15 | 0.15
0.05856 | 280.15 | 0.115 | 297.15 | 0.2
0.05856 | 280.15 | 0.115 | 297.15 | 0.3
0.05856 | 280.15 | 0.115 | 297.15 | 0.4
0.05856 | 280.15 | 0.115 | 297.15 | 0.5
0.05856 | 280.15 | 0.115 | 297.15 | 0.6
0.05856 | 280.15 | 0.115 | 297.15 | 0.7
0.05856 | 280.15 | 0.115 | 297.15 | 0.8
0.05856 | 280.15 | 0.115 | 297.15 | 0.9
0.05856 | 280.15 | 0.115 | 297.15 | 1
0.05856 | 280.15 | 0.115 | 300.15 | 0.15
0.05856 | 280.15 | 0.115 | 300.15 | 0.2
0.05856 | 280.15 | 0.115 | 300.15 | 0.3
0.05856 | 280.15 | 0.115 | 300.15 | 0.4
0.05856 | 280.15 | 0.115 | 300.15 | 0.5
0.05856 | 280.15 | 0.115 | 300.15 | 0.6
0.05856 | 280.15 | 0.115 | 300.15 | 0.7
0.05856 | 280.15 | 0.115 | 300.15 | 0.8
0.05856 | 280.15 | 0.115 | 300.15 | 0.9
0.05856 | 280.15 | 0.115 | 300.15 | 1
0.05856 | 280.15 | 0.115 | 303.15 | 0.15
0.05856 | 280.15 | 0.115 | 303.15 | 0.2
0.05856 | 280.15 | 0.115 | 303.15 | 0.3
0.05856 | 280.15 | 0.115 | 303.15 | 0.4
0.05856 | 280.15 | 0.115 | 303.15 | 0.5
0.05856 | 280.15 | 0.115 | 303.15 | 0.6
0.05856 | 280.15 | 0.115 | 303.15 | 0.7
0.05856 | 280.15 | 0.115 | 303.15 | 0.8
0.05856 | 280.15 | 0.115 | 303.15 | 0.9
0.05856 | 280.15 | 0.115 | 303.15 | 1
0.05856 | 282.15 | 0.00115 | 283.65 | 0.15
0.05856 | 282.15 | 0.00115 | 283.65 | 0.2
0.05856 | 282.15 | 0.00115 | 283.65 | 0.3
0.05856 | 282.15 | 0.00115 | 283.65 | 0.4
0.05856 | 282.15 | 0.00115 | 283.65 | 0.5
0.05856 | 282.15 | 0.00115 | 283.65 | 0.6
0.05856 | 282.15 | 0.00115 | 283.65 | 0.7
0.05856 | 282.15 | 0.00115 | 283.65 | 0.8
0.05856 | 282.15 | 0.00115 | 283.65 | 0.9
0.05856 | 282.15 | 0.00115 | 283.65 | 1
0.05856 | 282.15 | 0.00115 | 284.15 | 0.15
0.05856 | 282.15 | 0.00115 | 284.15 | 0.2
0.05856 | 282.15 | 0.00115 | 284.15 | 0.3
0.05856 | 282.15 | 0.00115 | 284.15 | 0.4
0.05856 | 282.15 | 0.00115 | 284.15 | 0.5
0.05856 | 282.15 | 0.00115 | 284.15 | 0.6
0.05856 | 282.15 | 0.00115 | 284.15 | 0.7
0.05856 | 282.15 | 0.00115 | 284.15 | 0.8
0.05856 | 282.15 | 0.00115 | 284.15 | 0.9
0.05856 | 282.15 | 0.00115 | 284.15 | 1
0.05856 | 282.15 | 0.00115 | 284.65 | 0.15
0.05856 | 282.15 | 0.00115 | 284.65 | 0.2
0.05856 | 282.15 | 0.00115 | 284.65 | 0.3
0.05856 | 282.15 | 0.00115 | 284.65 | 0.4
0.05856 | 282.15 | 0.00115 | 284.65 | 0.5
0.05856 | 282.15 | 0.00115 | 284.65 | 0.6
0.05856 | 282.15 | 0.00115 | 284.65 | 0.7
0.05856 | 282.15 | 0.00115 | 284.65 | 0.8
0.05856 | 282.15 | 0.00115 | 284.65 | 0.9
0.05856 | 282.15 | 0.00115 | 284.65 | 1
0.05856 | 282.15 | 0.00115 | 285.15 | 0.15
0.05856 | 282.15 | 0.00115 | 285.15 | 0.2
0.05856 | 282.15 | 0.00115 | 285.15 | 0.3
0.05856 | 282.15 | 0.00115 | 285.15 | 0.4
0.05856 | 282.15 | 0.00115 | 285.15 | 0.5
0.05856 | 282.15 | 0.00115 | 285.15 | 0.6
0.05856 | 282.15 | 0.00115 | 285.15 | 0.7
0.05856 | 282.15 | 0.00115 | 285.15 | 0.8
0.05856 | 282.15 | 0.00115 | 285.15 | 0.9
0.05856 | 282.15 | 0.00115 | 285.15 | 1
0.05856 | 282.15 | 0.00115 | 285.65 | 0.15
0.05856 | 282.15 | 0.00115 | 285.65 | 0.2
0.05856 | 282.15 | 0.00115 | 285.65 | 0.3
0.05856 | 282.15 | 0.00115 | 285.65 | 0.4
0.05856 | 282.15 | 0.00115 | 285.65 | 0.5
0.05856 | 282.15 | 0.00115 | 285.65 | 0.6
0.05856 | 282.15 | 0.00115 | 285.65 | 0.7
0.05856 | 282.15 | 0.00115 | 285.65 | 0.8
0.05856 | 282.15 | 0.00115 | 285.65 | 0.9
0.05856 | 282.15 | 0.00115 | 285.65 | 1
0.05856 | 282.15 | 0.00115 | 286.15 | 0.15
0.05856 | 282.15 | 0.00115 | 286.15 | 0.2
0.05856 | 282.15 | 0.00115 | 286.15 | 0.3
0.05856 | 282.15 | 0.00115 | 286.15 | 0.4
0.05856 | 282.15 | 0.00115 | 286.15 | 0.5
0.05856 | 282.15 | 0.00115 | 286.15 | 0.6
0.05856 | 282.15 | 0.00115 | 286.15 | 0.7
0.05856 | 282.15 | 0.00115 | 286.15 | 0.8
0.05856 | 282.15 | 0.00115 | 286.15 | 0.9
0.05856 | 282.15 | 0.00115 | 286.15 | 1
0.05856 | 282.15 | 0.00115 | 286.65 | 0.15
0.05856 | 282.15 | 0.00115 | 286.65 | 0.2
0.05856 | 282.15 | 0.00115 | 286.65 | 0.3
0.05856 | 282.15 | 0.00115 | 286.65 | 0.4
0.05856 | 282.15 | 0.00115 | 286.65 | 0.5
0.05856 | 282.15 | 0.00115 | 286.65 | 0.6
0.05856 | 282.15 | 0.00115 | 286.65 | 0.7
0.05856 | 282.15 | 0.00115 | 286.65 | 0.8
0.05856 | 282.15 | 0.00115 | 286.65 | 0.9
0.05856 | 282.15 | 0.00115 | 286.65 | 1
0.05856 | 282.15 | 0.00115 | 287.15 | 0.15
0.05856 | 282.15 | 0.00115 | 287.15 | 0.2
0.05856 | 282.15 | 0.00115 | 287.15 | 0.3
0.05856 | 282.15 | 0.00115 | 287.15 | 0.4
0.05856 | 282.15 | 0.00115 | 287.15 | 0.5
0.05856 | 282.15 | 0.00115 | 287.15 | 0.6
0.05856 | 282.15 | 0.00115 | 287.15 | 0.7
0.05856 | 282.15 | 0.00115 | 287.15 | 0.8
0.05856 | 282.15 | 0.00115 | 287.15 | 0.9
0.05856 | 282.15 | 0.00115 | 287.15 | 1
0.05856 | 282.15 | 0.00115 | 287.65 | 0.15
0.05856 | 282.15 | 0.00115 | 287.65 | 0.2
0.05856 | 282.15 | 0.00115 | 287.65 | 0.3
0.05856 | 282.15 | 0.00115 | 287.65 | 0.4
0.05856 | 282.15 | 0.00115 | 287.65 | 0.5
0.05856 | 282.15 | 0.00115 | 287.65 | 0.6
0.05856 | 282.15 | 0.00115 | 287.65 | 0.7
0.05856 | 282.15 | 0.00115 | 287.65 | 0.8
0.05856 | 282.15 | 0.00115 | 287.65 | 0.9
0.05856 | 282.15 | 0.00115 | 287.65 | 1
0.05856 | 282.15 | 0.00115 | 288.15 | 0.15
0.05856 | 282.15 | 0.00115 | 288.15 | 0.2
0.05856 | 282.15 | 0.00115 | 288.15 | 0.3
0.05856 | 282.15 | 0.00115 | 288.15 | 0.4
0.05856 | 282.15 | 0.00115 | 288.15 | 0.5
0.05856 | 282.15 | 0.00115 | 288.15 | 0.6
0.05856 | 282.15 | 0.00115 | 288.15 | 0.7
0.05856 | 282.15 | 0.00115 | 288.15 | 0.8
0.05856 | 282.15 | 0.00115 | 288.15 | 0.9
0.05856 | 282.15 | 0.00115 | 288.15 | 1
0.05856 | 282.15 | 0.00115 | 288.65 | 0.15
0.05856 | 282.15 | 0.00115 | 288.65 | 0.2
0.05856 | 282.15 | 0.00115 | 288.65 | 0.3
0.05856 | 282.15 | 0.00115 | 288.65 | 0.4
0.05856 | 282.15 | 0.00115 | 288.65 | 0.5
0.05856 | 282.15 | 0.00115 | 288.65 | 0.6
0.05856 | 282.15 | 0.00115 | 288.65 | 0.7
0.05856 | 282.15 | 0.00115 | 288.65 | 0.8
0.05856 | 282.15 | 0.00115 | 288.65 | 0.9
0.05856 | 282.15 | 0.00115 | 288.65 | 1
0.05856 | 282.15 | 0.00115 | 289.15 | 0.15
0.05856 | 282.15 | 0.00115 | 289.15 | 0.2
0.05856 | 282.15 | 0.00115 | 289.15 | 0.3
0.05856 | 282.15 | 0.00115 | 289.15 | 0.4
0.05856 | 282.15 | 0.00115 | 289.15 | 0.5
0.05856 | 282.15 | 0.00115 | 289.15 | 0.6
0.05856 | 282.15 | 0.00115 | 289.15 | 0.7
0.05856 | 282.15 | 0.00115 | 289.15 | 0.8
0.05856 | 282.15 | 0.00115 | 289.15 | 0.9
0.05856 | 282.15 | 0.00115 | 289.15 | 1
0.05856 | 282.15 | 0.00115 | 289.65 | 0.15
0.05856 | 282.15 | 0.00115 | 289.65 | 0.2
0.05856 | 282.15 | 0.00115 | 289.65 | 0.3
0.05856 | 282.15 | 0.00115 | 289.65 | 0.4
0.05856 | 282.15 | 0.00115 | 289.65 | 0.5
0.05856 | 282.15 | 0.00115 | 289.65 | 0.6
0.05856 | 282.15 | 0.00115 | 289.65 | 0.7
0.05856 | 282.15 | 0.00115 | 289.65 | 0.8
0.05856 | 282.15 | 0.00115 | 289.65 | 0.9
0.05856 | 282.15 | 0.00115 | 289.65 | 1
0.05856 | 282.15 | 0.00115 | 290.15 | 0.15
0.05856 | 282.15 | 0.00115 | 290.15 | 0.2
0.05856 | 282.15 | 0.00115 | 290.15 | 0.3
0.05856 | 282.15 | 0.00115 | 290.15 | 0.4
0.05856 | 282.15 | 0.00115 | 290.15 | 0.5
0.05856 | 282.15 | 0.00115 | 290.15 | 0.6
0.05856 | 282.15 | 0.00115 | 290.15 | 0.7
0.05856 | 282.15 | 0.00115 | 290.15 | 0.8
0.05856 | 282.15 | 0.00115 | 290.15 | 0.9
0.05856 | 282.15 | 0.00115 | 290.15 | 1
0.05856 | 282.15 | 0.00115 | 290.65 | 0.15
0.05856 | 282.15 | 0.00115 | 290.65 | 0.2
0.05856 | 282.15 | 0.00115 | 290.65 | 0.3
0.05856 | 282.15 | 0.00115 | 290.65 | 0.4
0.05856 | 282.15 | 0.00115 | 290.65 | 0.5
0.05856 | 282.15 | 0.00115 | 290.65 | 0.6
0.05856 | 282.15 | 0.00115 | 290.65 | 0.7
0.05856 | 282.15 | 0.00115 | 290.65 | 0.8
0.05856 | 282.15 | 0.00115 | 290.65 | 0.9
0.05856 | 282.15 | 0.00115 | 290.65 | 1
0.05856 | 282.15 | 0.00115 | 291.15 | 0.15
0.05856 | 282.15 | 0.00115 | 291.15 | 0.2
0.05856 | 282.15 | 0.00115 | 291.15 | 0.3
0.05856 | 282.15 | 0.00115 | 291.15 | 0.4
0.05856 | 282.15 | 0.00115 | 291.15 | 0.5
0.05856 | 282.15 | 0.00115 | 291.15 | 0.6
0.05856 | 282.15 | 0.00115 | 291.15 | 0.7
0.05856 | 282.15 | 0.00115 | 291.15 | 0.8
0.05856 | 282.15 | 0.00115 | 291.15 | 0.9
0.05856 | 282.15 | 0.00115 | 291.15 | 1
0.05856 | 282.15 | 0.00115 | 294.15 | 0.15
0.05856 | 282.15 | 0.00115 | 294.15 | 0.2
0.05856 | 282.15 | 0.00115 | 294.15 | 0.3
0.05856 | 282.15 | 0.00115 | 294.15 | 0.4
0.05856 | 282.15 | 0.00115 | 294.15 | 0.5
0.05856 | 282.15 | 0.00115 | 294.15 | 0.6
0.05856 | 282.15 | 0.00115 | 294.15 | 0.7
0.05856 | 282.15 | 0.00115 | 294.15 | 0.8
0.05856 | 282.15 | 0.00115 | 294.15 | 0.9
0.05856 | 282.15 | 0.00115 | 294.15 | 1
0.05856 | 282.15 | 0.00115 | 297.15 | 0.15
0.05856 | 282.15 | 0.00115 | 297.15 | 0.2
0.05856 | 282.15 | 0.00115 | 297.15 | 0.3
0.05856 | 282.15 | 0.00115 | 297.15 | 0.4
0.05856 | 282.15 | 0.00115 | 297.15 | 0.5
0.05856 | 282.15 | 0.00115 | 297.15 | 0.6
0.05856 | 282.15 | 0.00115 | 297.15 | 0.7
0.05856 | 282.15 | 0.00115 | 297.15 | 0.8
0.05856 | 282.15 | 0.00115 | 297.15 | 0.9
0.05856 | 282.15 | 0.00115 | 297.15 | 1
0.05856 | 282.15 | 0.00115 | 300.15 | 0.15
0.05856 | 282.15 | 0.00115 | 300.15 | 0.2
0.05856 | 282.15 | 0.00115 | 300.15 | 0.3
0.05856 | 282.15 | 0.00115 | 300.15 | 0.4
0.05856 | 282.15 | 0.00115 | 300.15 | 0.5
0.05856 | 282.15 | 0.00115 | 300.15 | 0.6
0.05856 | 282.15 | 0.00115 | 300.15 | 0.7
0.05856 | 282.15 | 0.00115 | 300.15 | 0.8
0.05856 | 282.15 | 0.00115 | 300.15 | 0.9
0.05856 | 282.15 | 0.00115 | 300.15 | 1
0.05856 | 282.15 | 0.00115 | 303.15 | 0.15
0.05856 | 282.15 | 0.00115 | 303.15 | 0.2
0.05856 | 282.15 | 0.00115 | 303.15 | 0.3
0.05856 | 282.15 | 0.00115 | 303.15 | 0.4
0.05856 | 282.15 | 0.00115 | 303.15 | 0.5
0.05856 | 282.15 | 0.00115 | 303.15 | 0.6
0.05856 | 282.15 | 0.00115 | 303.15 | 0.7
0.05856 | 282.15 | 0.00115 | 303.15 | 0.8
0.05856 | 282.15 | 0.00115 | 303.15 | 0.9
0.05856 | 282.15 | 0.00115 | 303.15 | 1
0.05856 | 282.15 | 0.077 | 283.65 | 0.15
0.05856 | 282.15 | 0.077 | 283.65 | 0.2
0.05856 | 282.15 | 0.077 | 283.65 | 0.3
0.05856 | 282.15 | 0.077 | 283.65 | 0.4
0.05856 | 282.15 | 0.077 | 283.65 | 0.5
0.05856 | 282.15 | 0.077 | 283.65 | 0.6
0.05856 | 282.15 | 0.077 | 283.65 | 0.7
0.05856 | 282.15 | 0.077 | 283.65 | 0.8
0.05856 | 282.15 | 0.077 | 283.65 | 0.9
0.05856 | 282.15 | 0.077 | 283.65 | 1
0.05856 | 282.15 | 0.077 | 284.15 | 0.15
0.05856 | 282.15 | 0.077 | 284.15 | 0.2
0.05856 | 282.15 | 0.077 | 284.15 | 0.3
0.05856 | 282.15 | 0.077 | 284.15 | 0.4
0.05856 | 282.15 | 0.077 | 284.15 | 0.5
0.05856 | 282.15 | 0.077 | 284.15 | 0.6
0.05856 | 282.15 | 0.077 | 284.15 | 0.7
0.05856 | 282.15 | 0.077 | 284.15 | 0.8
0.05856 | 282.15 | 0.077 | 284.15 | 0.9
0.05856 | 282.15 | 0.077 | 284.15 | 1
0.05856 | 282.15 | 0.077 | 284.65 | 0.15
0.05856 | 282.15 | 0.077 | 284.65 | 0.2
0.05856 | 282.15 | 0.077 | 284.65 | 0.3
0.05856 | 282.15 | 0.077 | 284.65 | 0.4
0.05856 | 282.15 | 0.077 | 284.65 | 0.5
0.05856 | 282.15 | 0.077 | 284.65 | 0.6
0.05856 | 282.15 | 0.077 | 284.65 | 0.7
0.05856 | 282.15 | 0.077 | 284.65 | 0.8
0.05856 | 282.15 | 0.077 | 284.65 | 0.9
0.05856 | 282.15 | 0.077 | 284.65 | 1
0.05856 | 282.15 | 0.077 | 285.15 | 0.15
0.05856 | 282.15 | 0.077 | 285.15 | 0.2
0.05856 | 282.15 | 0.077 | 285.15 | 0.3
0.05856 | 282.15 | 0.077 | 285.15 | 0.4
0.05856 | 282.15 | 0.077 | 285.15 | 0.5
0.05856 | 282.15 | 0.077 | 285.15 | 0.6
0.05856 | 282.15 | 0.077 | 285.15 | 0.7
0.05856 | 282.15 | 0.077 | 285.15 | 0.8
0.05856 | 282.15 | 0.077 | 285.15 | 0.9
0.05856 | 282.15 | 0.077 | 285.15 | 1
0.05856 | 282.15 | 0.077 | 285.65 | 0.15
0.05856 | 282.15 | 0.077 | 285.65 | 0.2
0.05856 | 282.15 | 0.077 | 285.65 | 0.3
0.05856 | 282.15 | 0.077 | 285.65 | 0.4
0.05856 | 282.15 | 0.077 | 285.65 | 0.5
0.05856 | 282.15 | 0.077 | 285.65 | 0.6
0.05856 | 282.15 | 0.077 | 285.65 | 0.7
0.05856 | 282.15 | 0.077 | 285.65 | 0.8
0.05856 | 282.15 | 0.077 | 285.65 | 0.9
0.05856 | 282.15 | 0.077 | 285.65 | 1
0.05856 | 282.15 | 0.077 | 286.15 | 0.15
0.05856 | 282.15 | 0.077 | 286.15 | 0.2
0.05856 | 282.15 | 0.077 | 286.15 | 0.3
0.05856 | 282.15 | 0.077 | 286.15 | 0.4
0.05856 | 282.15 | 0.077 | 286.15 | 0.5
0.05856 | 282.15 | 0.077 | 286.15 | 0.6
0.05856 | 282.15 | 0.077 | 286.15 | 0.7
0.05856 | 282.15 | 0.077 | 286.15 | 0.8
0.05856 | 282.15 | 0.077 | 286.15 | 0.9
0.05856 | 282.15 | 0.077 | 286.15 | 1
0.05856 | 282.15 | 0.077 | 286.65 | 0.15
0.05856 | 282.15 | 0.077 | 286.65 | 0.2
0.05856 | 282.15 | 0.077 | 286.65 | 0.3
0.05856 | 282.15 | 0.077 | 286.65 | 0.4
0.05856 | 282.15 | 0.077 | 286.65 | 0.5
0.05856 | 282.15 | 0.077 | 286.65 | 0.6
0.05856 | 282.15 | 0.077 | 286.65 | 0.7
0.05856 | 282.15 | 0.077 | 286.65 | 0.8
0.05856 | 282.15 | 0.077 | 286.65 | 0.9
0.05856 | 282.15 | 0.077 | 286.65 | 1
0.05856 | 282.15 | 0.077 | 287.15 | 0.15
0.05856 | 282.15 | 0.077 | 287.15 | 0.2
0.05856 | 282.15 | 0.077 | 287.15 | 0.3
0.05856 | 282.15 | 0.077 | 287.15 | 0.4
0.05856 | 282.15 | 0.077 | 287.15 | 0.5
0.05856 | 282.15 | 0.077 | 287.15 | 0.6
0.05856 | 282.15 | 0.077 | 287.15 | 0.7
0.05856 | 282.15 | 0.077 | 287.15 | 0.8
0.05856 | 282.15 | 0.077 | 287.15 | 0.9
0.05856 | 282.15 | 0.077 | 287.15 | 1
0.05856 | 282.15 | 0.077 | 287.65 | 0.15
0.05856 | 282.15 | 0.077 | 287.65 | 0.2
0.05856 | 282.15 | 0.077 | 287.65 | 0.3
0.05856 | 282.15 | 0.077 | 287.65 | 0.4
0.05856 | 282.15 | 0.077 | 287.65 | 0.5
0.05856 | 282.15 | 0.077 | 287.65 | 0.6
0.05856 | 282.15 | 0.077 | 287.65 | 0.7
0.05856 | 282.15 | 0.077 | 287.65 | 0.8
0.05856 | 282.15 | 0.077 | 287.65 | 0.9
0.05856 | 282.15 | 0.077 | 287.65 | 1
0.05856 | 282.15 | 0.077 | 288.15 | 0.15
0.05856 | 282.15 | 0.077 | 288.15 | 0.2
0.05856 | 282.15 | 0.077 | 288.15 | 0.3
0.05856 | 282.15 | 0.077 | 288.15 | 0.4
0.05856 | 282.15 | 0.077 | 288.15 | 0.5
0.05856 | 282.15 | 0.077 | 288.15 | 0.6
0.05856 | 282.15 | 0.077 | 288.15 | 0.7
0.05856 | 282.15 | 0.077 | 288.15 | 0.8
0.05856 | 282.15 | 0.077 | 288.15 | 0.9
0.05856 | 282.15 | 0.077 | 288.15 | 1
0.05856 | 282.15 | 0.077 | 288.65 | 0.15
0.05856 | 282.15 | 0.077 | 288.65 | 0.2
0.05856 | 282.15 | 0.077 | 288.65 | 0.3
0.05856 | 282.15 | 0.077 | 288.65 | 0.4
0.05856 | 282.15 | 0.077 | 288.65 | 0.5
0.05856 | 282.15 | 0.077 | 288.65 | 0.6
0.05856 | 282.15 | 0.077 | 288.65 | 0.7
0.05856 | 282.15 | 0.077 | 288.65 | 0.8
0.05856 | 282.15 | 0.077 | 288.65 | 0.9
0.05856 | 282.15 | 0.077 | 288.65 | 1
0.05856 | 282.15 | 0.077 | 289.15 | 0.15
0.05856 | 282.15 | 0.077 | 289.15 | 0.2
0.05856 | 282.15 | 0.077 | 289.15 | 0.3
0.05856 | 282.15 | 0.077 | 289.15 | 0.4
0.05856 | 282.15 | 0.077 | 289.15 | 0.5
0.05856 | 282.15 | 0.077 | 289.15 | 0.6
0.05856 | 282.15 | 0.077 | 289.15 | 0.7
0.05856 | 282.15 | 0.077 | 289.15 | 0.8
0.05856 | 282.15 | 0.077 | 289.15 | 0.9
0.05856 | 282.15 | 0.077 | 289.15 | 1
0.05856 | 282.15 | 0.077 | 289.65 | 0.15
0.05856 | 282.15 | 0.077 | 289.65 | 0.2
0.05856 | 282.15 | 0.077 | 289.65 | 0.3
0.05856 | 282.15 | 0.077 | 289.65 | 0.4
0.05856 | 282.15 | 0.077 | 289.65 | 0.5
0.05856 | 282.15 | 0.077 | 289.65 | 0.6
0.05856 | 282.15 | 0.077 | 289.65 | 0.7
0.05856 | 282.15 | 0.077 | 289.65 | 0.8
0.05856 | 282.15 | 0.077 | 289.65 | 0.9
0.05856 | 282.15 | 0.077 | 289.65 | 1
0.05856 | 282.15 | 0.077 | 290.15 | 0.15
0.05856 | 282.15 | 0.077 | 290.15 | 0.2
0.05856 | 282.15 | 0.077 | 290.15 | 0.3
0.05856 | 282.15 | 0.077 | 290.15 | 0.4
0.05856 | 282.15 | 0.077 | 290.15 | 0.5
0.05856 | 282.15 | 0.077 | 290.15 | 0.6
0.05856 | 282.15 | 0.077 | 290.15 | 0.7
0.05856 | 282.15 | 0.077 | 290.15 | 0.8
0.05856 | 282.15 | 0.077 | 290.15 | 0.9
0.05856 | 282.15 | 0.077 | 290.15 | 1
0.05856 | 282.15 | 0.077 | 290.65 | 0.15
0.05856 | 282.15 | 0.077 | 290.65 | 0.2
0.05856 | 282.15 | 0.077 | 290.65 | 0.3
0.05856 | 282.15 | 0.077 | 290.65 | 0.4
0.05856 | 282.15 | 0.077 | 290.65 | 0.5
0.05856 | 282.15 | 0.077 | 290.65 | 0.6
0.05856 | 282.15 | 0.077 | 290.65 | 0.7
0.05856 | 282.15 | 0.077 | 290.65 | 0.8
0.05856 | 282.15 | 0.077 | 290.65 | 0.9
0.05856 | 282.15 | 0.077 | 290.65 | 1
0.05856 | 282.15 | 0.077 | 291.15 | 0.15
0.05856 | 282.15 | 0.077 | 291.15 | 0.2
0.05856 | 282.15 | 0.077 | 291.15 | 0.3
0.05856 | 282.15 | 0.077 | 291.15 | 0.4
0.05856 | 282.15 | 0.077 | 291.15 | 0.5
0.05856 | 282.15 | 0.077 | 291.15 | 0.6
0.05856 | 282.15 | 0.077 | 291.15 | 0.7
0.05856 | 282.15 | 0.077 | 291.15 | 0.8
0.05856 | 282.15 | 0.077 | 291.15 | 0.9
0.05856 | 282.15 | 0.077 | 291.15 | 1
0.05856 | 282.15 | 0.077 | 294.15 | 0.15
0.05856 | 282.15 | 0.077 | 294.15 | 0.2
0.05856 | 282.15 | 0.077 | 294.15 | 0.3
0.05856 | 282.15 | 0.077 | 294.15 | 0.4
0.05856 | 282.15 | 0.077 | 294.15 | 0.5
0.05856 | 282.15 | 0.077 | 294.15 | 0.6
0.05856 | 282.15 | 0.077 | 294.15 | 0.7
0.05856 | 282.15 | 0.077 | 294.15 | 0.8
0.05856 | 282.15 | 0.077 | 294.15 | 0.9
0.05856 | 282.15 | 0.077 | 294.15 | 1
0.05856 | 282.15 | 0.077 | 297.15 | 0.15
0.05856 | 282.15 | 0.077 | 297.15 | 0.2
0.05856 | 282.15 | 0.077 | 297.15 | 0.3
0.05856 | 282.15 | 0.077 | 297.15 | 0.4
0.05856 | 282.15 | 0.077 | 297.15 | 0.5
0.05856 | 282.15 | 0.077 | 297.15 | 0.6
0.05856 | 282.15 | 0.077 | 297.15 | 0.7
0.05856 | 282.15 | 0.077 | 297.15 | 0.8
0.05856 | 282.15 | 0.077 | 297.15 | 0.9
0.05856 | 282.15 | 0.077 | 297.15 | 1
0.05856 | 282.15 | 0.077 | 300.15 | 0.15
0.05856 | 282.15 | 0.077 | 300.15 | 0.2
0.05856 | 282.15 | 0.077 | 300.15 | 0.3
0.05856 | 282.15 | 0.077 | 300.15 | 0.4
0.05856 | 282.15 | 0.077 | 300.15 | 0.5
0.05856 | 282.15 | 0.077 | 300.15 | 0.6
0.05856 | 282.15 | 0.077 | 300.15 | 0.7
0.05856 | 282.15 | 0.077 | 300.15 | 0.8
0.05856 | 282.15 | 0.077 | 300.15 | 0.9
0.05856 | 282.15 | 0.077 | 300.15 | 1
0.05856 | 282.15 | 0.077 | 303.15 | 0.15
0.05856 | 282.15 | 0.077 | 303.15 | 0.2
0.05856 | 282.15 | 0.077 | 303.15 | 0.3
0.05856 | 282.15 | 0.077 | 303.15 | 0.4
0.05856 | 282.15 | 0.077 | 303.15 | 0.5
0.05856 | 282.15 | 0.077 | 303.15 | 0.6
0.05856 | 282.15 | 0.077 | 303.15 | 0.7
0.05856 | 282.15 | 0.077 | 303.15 | 0.8
0.05856 | 282.15 | 0.077 | 303.15 | 0.9
0.05856 | 282.15 | 0.077 | 303.15 | 1
0.05856 | 282.15 | 0.09437 | 283.65 | 0.15
0.05856 | 282.15 | 0.09437 | 283.65 | 0.2
0.05856 | 282.15 | 0.09437 | 283.65 | 0.3
0.05856 | 282.15 | 0.09437 | 283.65 | 0.4
0.05856 | 282.15 | 0.09437 | 283.65 | 0.5
0.05856 | 282.15 | 0.09437 | 283.65 | 0.6
0.05856 | 282.15 | 0.09437 | 283.65 | 0.7
0.05856 | 282.15 | 0.09437 | 283.65 | 0.8
0.05856 | 282.15 | 0.09437 | 283.65 | 0.9
0.05856 | 282.15 | 0.09437 | 283.65 | 1
0.05856 | 282.15 | 0.09437 | 284.15 | 0.15
0.05856 | 282.15 | 0.09437 | 284.15 | 0.2
0.05856 | 282.15 | 0.09437 | 284.15 | 0.3
0.05856 | 282.15 | 0.09437 | 284.15 | 0.4
0.05856 | 282.15 | 0.09437 | 284.15 | 0.5
0.05856 | 282.15 | 0.09437 | 284.15 | 0.6
0.05856 | 282.15 | 0.09437 | 284.15 | 0.7
0.05856 | 282.15 | 0.09437 | 284.15 | 0.8
0.05856 | 282.15 | 0.09437 | 284.15 | 0.9
0.05856 | 282.15 | 0.09437 | 284.15 | 1
0.05856 | 282.15 | 0.09437 | 284.65 | 0.15
0.05856 | 282.15 | 0.09437 | 284.65 | 0.2
0.05856 | 282.15 | 0.09437 | 284.65 | 0.3
0.05856 | 282.15 | 0.09437 | 284.65 | 0.4
0.05856 | 282.15 | 0.09437 | 284.65 | 0.5
0.05856 | 282.15 | 0.09437 | 284.65 | 0.6
0.05856 | 282.15 | 0.09437 | 284.65 | 0.7
0.05856 | 282.15 | 0.09437 | 284.65 | 0.8
0.05856 | 282.15 | 0.09437 | 284.65 | 0.9
0.05856 | 282.15 | 0.09437 | 284.65 | 1
0.05856 | 282.15 | 0.09437 | 285.15 | 0.15
0.05856 | 282.15 | 0.09437 | 285.15 | 0.2
0.05856 | 282.15 | 0.09437 | 285.15 | 0.3
0.05856 | 282.15 | 0.09437 | 285.15 | 0.4
0.05856 | 282.15 | 0.09437 | 285.15 | 0.5
0.05856 | 282.15 | 0.09437 | 285.15 | 0.6
0.05856 | 282.15 | 0.09437 | 285.15 | 0.7
0.05856 | 282.15 | 0.09437 | 285.15 | 0.8
0.05856 | 282.15 | 0.09437 | 285.15 | 0.9
0.05856 | 282.15 | 0.09437 | 285.15 | 1
0.05856 | 282.15 | 0.09437 | 285.65 | 0.15
0.05856 | 282.15 | 0.09437 | 285.65 | 0.2
0.05856 | 282.15 | 0.09437 | 285.65 | 0.3
0.05856 | 282.15 | 0.09437 | 285.65 | 0.4
0.05856 | 282.15 | 0.09437 | 285.65 | 0.5
0.05856 | 282.15 | 0.09437 | 285.65 | 0.6
0.05856 | 282.15 | 0.09437 | 285.65 | 0.7
0.05856 | 282.15 | 0.09437 | 285.65 | 0.8
0.05856 | 282.15 | 0.09437 | 285.65 | 0.9
0.05856 | 282.15 | 0.09437 | 285.65 | 1
0.05856 | 282.15 | 0.09437 | 286.15 | 0.15
0.05856 | 282.15 | 0.09437 | 286.15 | 0.2
0.05856 | 282.15 | 0.09437 | 286.15 | 0.3
0.05856 | 282.15 | 0.09437 | 286.15 | 0.4
0.05856 | 282.15 | 0.09437 | 286.15 | 0.5
0.05856 | 282.15 | 0.09437 | 286.15 | 0.6
0.05856 | 282.15 | 0.09437 | 286.15 | 0.7
0.05856 | 282.15 | 0.09437 | 286.15 | 0.8
0.05856 | 282.15 | 0.09437 | 286.15 | 0.9
0.05856 | 282.15 | 0.09437 | 286.15 | 1
0.05856 | 282.15 | 0.09437 | 286.65 | 0.15
0.05856 | 282.15 | 0.09437 | 286.65 | 0.2
0.05856 | 282.15 | 0.09437 | 286.65 | 0.3
0.05856 | 282.15 | 0.09437 | 286.65 | 0.4
0.05856 | 282.15 | 0.09437 | 286.65 | 0.5
0.05856 | 282.15 | 0.09437 | 286.65 | 0.6
0.05856 | 282.15 | 0.09437 | 286.65 | 0.7
0.05856 | 282.15 | 0.09437 | 286.65 | 0.8
0.05856 | 282.15 | 0.09437 | 286.65 | 0.9
0.05856 | 282.15 | 0.09437 | 286.65 | 1
0.05856 | 282.15 | 0.09437 | 287.15 | 0.15
0.05856 | 282.15 | 0.09437 | 287.15 | 0.2
0.05856 | 282.15 | 0.09437 | 287.15 | 0.3
0.05856 | 282.15 | 0.09437 | 287.15 | 0.4
0.05856 | 282.15 | 0.09437 | 287.15 | 0.5
0.05856 | 282.15 | 0.09437 | 287.15 | 0.6
0.05856 | 282.15 | 0.09437 | 287.15 | 0.7
0.05856 | 282.15 | 0.09437 | 287.15 | 0.8
0.05856 | 282.15 | 0.09437 | 287.15 | 0.9
0.05856 | 282.15 | 0.09437 | 287.15 | 1
0.05856 | 282.15 | 0.09437 | 287.65 | 0.15
0.05856 | 282.15 | 0.09437 | 287.65 | 0.2
0.05856 | 282.15 | 0.09437 | 287.65 | 0.3
0.05856 | 282.15 | 0.09437 | 287.65 | 0.4
0.05856 | 282.15 | 0.09437 | 287.65 | 0.5
0.05856 | 282.15 | 0.09437 | 287.65 | 0.6
0.05856 | 282.15 | 0.09437 | 287.65 | 0.7
0.05856 | 282.15 | 0.09437 | 287.65 | 0.8
0.05856 | 282.15 | 0.09437 | 287.65 | 0.9
0.05856 | 282.15 | 0.09437 | 287.65 | 1
0.05856 | 282.15 | 0.09437 | 288.15 | 0.15
0.05856 | 282.15 | 0.09437 | 288.15 | 0.2
0.05856 | 282.15 | 0.09437 | 288.15 | 0.3
0.05856 | 282.15 | 0.09437 | 288.15 | 0.4
0.05856 | 282.15 | 0.09437 | 288.15 | 0.5
0.05856 | 282.15 | 0.09437 | 288.15 | 0.6
0.05856 | 282.15 | 0.09437 | 288.15 | 0.7
0.05856 | 282.15 | 0.09437 | 288.15 | 0.8
0.05856 | 282.15 | 0.09437 | 288.15 | 0.9
0.05856 | 282.15 | 0.09437 | 288.15 | 1
0.05856 | 282.15 | 0.09437 | 288.65 | 0.15
0.05856 | 282.15 | 0.09437 | 288.65 | 0.2
0.05856 | 282.15 | 0.09437 | 288.65 | 0.3
0.05856 | 282.15 | 0.09437 | 288.65 | 0.4
0.05856 | 282.15 | 0.09437 | 288.65 | 0.5
0.05856 | 282.15 | 0.09437 | 288.65 | 0.6
0.05856 | 282.15 | 0.09437 | 288.65 | 0.7
0.05856 | 282.15 | 0.09437 | 288.65 | 0.8
0.05856 | 282.15 | 0.09437 | 288.65 | 0.9
0.05856 | 282.15 | 0.09437 | 288.65 | 1
0.05856 | 282.15 | 0.09437 | 289.15 | 0.15
0.05856 | 282.15 | 0.09437 | 289.15 | 0.2
0.05856 | 282.15 | 0.09437 | 289.15 | 0.3
0.05856 | 282.15 | 0.09437 | 289.15 | 0.4
0.05856 | 282.15 | 0.09437 | 289.15 | 0.5
0.05856 | 282.15 | 0.09437 | 289.15 | 0.6
0.05856 | 282.15 | 0.09437 | 289.15 | 0.7
0.05856 | 282.15 | 0.09437 | 289.15 | 0.8
0.05856 | 282.15 | 0.09437 | 289.15 | 0.9
0.05856 | 282.15 | 0.09437 | 289.15 | 1
0.05856 | 282.15 | 0.09437 | 289.65 | 0.15
0.05856 | 282.15 | 0.09437 | 289.65 | 0.2
0.05856 | 282.15 | 0.09437 | 289.65 | 0.3
0.05856 | 282.15 | 0.09437 | 289.65 | 0.4
0.05856 | 282.15 | 0.09437 | 289.65 | 0.5
0.05856 | 282.15 | 0.09437 | 289.65 | 0.6
0.05856 | 282.15 | 0.09437 | 289.65 | 0.7
0.05856 | 282.15 | 0.09437 | 289.65 | 0.8
0.05856 | 282.15 | 0.09437 | 289.65 | 0.9
0.05856 | 282.15 | 0.09437 | 289.65 | 1
0.05856 | 282.15 | 0.09437 | 290.15 | 0.15
0.05856 | 282.15 | 0.09437 | 290.15 | 0.2
0.05856 | 282.15 | 0.09437 | 290.15 | 0.3
0.05856 | 282.15 | 0.09437 | 290.15 | 0.4
0.05856 | 282.15 | 0.09437 | 290.15 | 0.5
0.05856 | 282.15 | 0.09437 | 290.15 | 0.6
0.05856 | 282.15 | 0.09437 | 290.15 | 0.7
0.05856 | 282.15 | 0.09437 | 290.15 | 0.8
0.05856 | 282.15 | 0.09437 | 290.15 | 0.9
0.05856 | 282.15 | 0.09437 | 290.15 | 1
0.05856 | 282.15 | 0.09437 | 290.65 | 0.15
0.05856 | 282.15 | 0.09437 | 290.65 | 0.2
0.05856 | 282.15 | 0.09437 | 290.65 | 0.3
0.05856 | 282.15 | 0.09437 | 290.65 | 0.4
0.05856 | 282.15 | 0.09437 | 290.65 | 0.5
0.05856 | 282.15 | 0.09437 | 290.65 | 0.6
0.05856 | 282.15 | 0.09437 | 290.65 | 0.7
0.05856 | 282.15 | 0.09437 | 290.65 | 0.8
0.05856 | 282.15 | 0.09437 | 290.65 | 0.9
0.05856 | 282.15 | 0.09437 | 290.65 | 1
0.05856 | 282.15 | 0.09437 | 291.15 | 0.15
0.05856 | 282.15 | 0.09437 | 291.15 | 0.2
0.05856 | 282.15 | 0.09437 | 291.15 | 0.3
0.05856 | 282.15 | 0.09437 | 291.15 | 0.4
0.05856 | 282.15 | 0.09437 | 291.15 | 0.5
0.05856 | 282.15 | 0.09437 | 291.15 | 0.6
0.05856 | 282.15 | 0.09437 | 291.15 | 0.7
0.05856 | 282.15 | 0.09437 | 291.15 | 0.8
0.05856 | 282.15 | 0.09437 | 291.15 | 0.9
0.05856 | 282.15 | 0.09437 | 291.15 | 1
0.05856 | 282.15 | 0.09437 | 294.15 | 0.15
0.05856 | 282.15 | 0.09437 | 294.15 | 0.2
0.05856 | 282.15 | 0.09437 | 294.15 | 0.3
0.05856 | 282.15 | 0.09437 | 294.15 | 0.4
0.05856 | 282.15 | 0.09437 | 294.15 | 0.5
0.05856 | 282.15 | 0.09437 | 294.15 | 0.6
0.05856 | 282.15 | 0.09437 | 294.15 | 0.7
0.05856 | 282.15 | 0.09437 | 294.15 | 0.8
0.05856 | 282.15 | 0.09437 | 294.15 | 0.9
0.05856 | 282.15 | 0.09437 | 294.15 | 1
0.05856 | 282.15 | 0.09437 | 297.15 | 0.15
0.05856 | 282.15 | 0.09437 | 297.15 | 0.2
0.05856 | 282.15 | 0.09437 | 297.15 | 0.3
0.05856 | 282.15 | 0.09437 | 297.15 | 0.4
0.05856 | 282.15 | 0.09437 | 297.15 | 0.5
0.05856 | 282.15 | 0.09437 | 297.15 | 0.6
0.05856 | 282.15 | 0.09437 | 297.15 | 0.7
0.05856 | 282.15 | 0.09437 | 297.15 | 0.8
0.05856 | 282.15 | 0.09437 | 297.15 | 0.9
0.05856 | 282.15 | 0.09437 | 297.15 | 1
0.05856 | 282.15 | 0.09437 | 300.15 | 0.15
0.05856 | 282.15 | 0.09437 | 300.15 | 0.2
0.05856 | 282.15 | 0.09437 | 300.15 | 0.3
0.05856 | 282.15 | 0.09437 | 300.15 | 0.4
0.05856 | 282.15 | 0.09437 | 300.15 | 0.5
0.05856 | 282.15 | 0.09437 | 300.15 | 0.6
0.05856 | 282.15 | 0.09437 | 300.15 | 0.7
0.05856 | 282.15 | 0.09437 | 300.15 | 0.8
0.05856 | 282.15 | 0.09437 | 300.15 | 0.9
0.05856 | 282.15 | 0.09437 | 300.15 | 1
0.05856 | 282.15 | 0.09437 | 303.15 | 0.15
0.05856 | 282.15 | 0.09437 | 303.15 | 0.2
0.05856 | 282.15 | 0.09437 | 303.15 | 0.3
0.05856 | 282.15 | 0.09437 | 303.15 | 0.4
0.05856 | 282.15 | 0.09437 | 303.15 | 0.5
0.05856 | 282.15 | 0.09437 | 303.15 | 0.6
0.05856 | 282.15 | 0.09437 | 303.15 | 0.7
0.05856 | 282.15 | 0.09437 | 303.15 | 0.8
0.05856 | 282.15 | 0.09437 | 303.15 | 0.9
0.05856 | 282.15 | 0.09437 | 303.15 | 1
0.05856 | 282.15 | 0.09644 | 283.65 | 0.15
0.05856 | 282.15 | 0.09644 | 283.65 | 0.2
0.05856 | 282.15 | 0.09644 | 283.65 | 0.3
0.05856 | 282.15 | 0.09644 | 283.65 | 0.4
0.05856 | 282.15 | 0.09644 | 283.65 | 0.5
0.05856 | 282.15 | 0.09644 | 283.65 | 0.6
0.05856 | 282.15 | 0.09644 | 283.65 | 0.7
0.05856 | 282.15 | 0.09644 | 283.65 | 0.8
0.05856 | 282.15 | 0.09644 | 283.65 | 0.9
0.05856 | 282.15 | 0.09644 | 283.65 | 1
0.05856 | 282.15 | 0.09644 | 284.15 | 0.15
0.05856 | 282.15 | 0.09644 | 284.15 | 0.2
0.05856 | 282.15 | 0.09644 | 284.15 | 0.3
0.05856 | 282.15 | 0.09644 | 284.15 | 0.4
0.05856 | 282.15 | 0.09644 | 284.15 | 0.5
0.05856 | 282.15 | 0.09644 | 284.15 | 0.6
0.05856 | 282.15 | 0.09644 | 284.15 | 0.7
0.05856 | 282.15 | 0.09644 | 284.15 | 0.8
0.05856 | 282.15 | 0.09644 | 284.15 | 0.9
0.05856 | 282.15 | 0.09644 | 284.15 | 1
0.05856 | 282.15 | 0.09644 | 284.65 | 0.15
0.05856 | 282.15 | 0.09644 | 284.65 | 0.2
0.05856 | 282.15 | 0.09644 | 284.65 | 0.3
0.05856 | 282.15 | 0.09644 | 284.65 | 0.4
0.05856 | 282.15 | 0.09644 | 284.65 | 0.5
0.05856 | 282.15 | 0.09644 | 284.65 | 0.6
0.05856 | 282.15 | 0.09644 | 284.65 | 0.7
0.05856 | 282.15 | 0.09644 | 284.65 | 0.8
0.05856 | 282.15 | 0.09644 | 284.65 | 0.9
0.05856 | 282.15 | 0.09644 | 284.65 | 1
0.05856 | 282.15 | 0.09644 | 285.15 | 0.15
0.05856 | 282.15 | 0.09644 | 285.15 | 0.2
0.05856 | 282.15 | 0.09644 | 285.15 | 0.3
0.05856 | 282.15 | 0.09644 | 285.15 | 0.4
0.05856 | 282.15 | 0.09644 | 285.15 | 0.5
0.05856 | 282.15 | 0.09644 | 285.15 | 0.6
0.05856 | 282.15 | 0.09644 | 285.15 | 0.7
0.05856 | 282.15 | 0.09644 | 285.15 | 0.8
0.05856 | 282.15 | 0.09644 | 285.15 | 0.9
0.05856 | 282.15 | 0.09644 | 285.15 | 1
0.05856 | 282.15 | 0.09644 | 285.65 | 0.15
0.05856 | 282.15 | 0.09644 | 285.65 | 0.2
0.05856 | 282.15 | 0.09644 | 285.65 | 0.3
0.05856 | 282.15 | 0.09644 | 285.65 | 0.4
0.05856 | 282.15 | 0.09644 | 285.65 | 0.5
0.05856 | 282.15 | 0.09644 | 285.65 | 0.6
0.05856 | 282.15 | 0.09644 | 285.65 | 0.7
0.05856 | 282.15 | 0.09644 | 285.65 | 0.8
0.05856 | 282.15 | 0.09644 | 285.65 | 0.9
0.05856 | 282.15 | 0.09644 | 285.65 | 1
0.05856 | 282.15 | 0.09644 | 286.15 | 0.15
0.05856 | 282.15 | 0.09644 | 286.15 | 0.2
0.05856 | 282.15 | 0.09644 | 286.15 | 0.3
0.05856 | 282.15 | 0.09644 | 286.15 | 0.4
0.05856 | 282.15 | 0.09644 | 286.15 | 0.5
0.05856 | 282.15 | 0.09644 | 286.15 | 0.6
0.05856 | 282.15 | 0.09644 | 286.15 | 0.7
0.05856 | 282.15 | 0.09644 | 286.15 | 0.8
0.05856 | 282.15 | 0.09644 | 286.15 | 0.9
0.05856 | 282.15 | 0.09644 | 286.15 | 1
0.05856 | 282.15 | 0.09644 | 286.65 | 0.15
0.05856 | 282.15 | 0.09644 | 286.65 | 0.2
0.05856 | 282.15 | 0.09644 | 286.65 | 0.3
0.05856 | 282.15 | 0.09644 | 286.65 | 0.4
0.05856 | 282.15 | 0.09644 | 286.65 | 0.5
0.05856 | 282.15 | 0.09644 | 286.65 | 0.6
0.05856 | 282.15 | 0.09644 | 286.65 | 0.7
0.05856 | 282.15 | 0.09644 | 286.65 | 0.8
0.05856 | 282.15 | 0.09644 | 286.65 | 0.9
0.05856 | 282.15 | 0.09644 | 286.65 | 1
0.05856 | 282.15 | 0.09644 | 287.15 | 0.15
0.05856 | 282.15 | 0.09644 | 287.15 | 0.2
0.05856 | 282.15 | 0.09644 | 287.15 | 0.3
0.05856 | 282.15 | 0.09644 | 287.15 | 0.4
0.05856 | 282.15 | 0.09644 | 287.15 | 0.5
0.05856 | 282.15 | 0.09644 | 287.15 | 0.6
0.05856 | 282.15 | 0.09644 | 287.15 | 0.7
0.05856 | 282.15 | 0.09644 | 287.15 | 0.8
0.05856 | 282.15 | 0.09644 | 287.15 | 0.9
0.05856 | 282.15 | 0.09644 | 287.15 | 1
0.05856 | 282.15 | 0.09644 | 287.65 | 0.15
0.05856 | 282.15 | 0.09644 | 287.65 | 0.2
0.05856 | 282.15 | 0.09644 | 287.65 | 0.3
0.05856 | 282.15 | 0.09644 | 287.65 | 0.4
0.05856 | 282.15 | 0.09644 | 287.65 | 0.5
0.05856 | 282.15 | 0.09644 | 287.65 | 0.6
0.05856 | 282.15 | 0.09644 | 287.65 | 0.7
0.05856 | 282.15 | 0.09644 | 287.65 | 0.8
0.05856 | 282.15 | 0.09644 | 287.65 | 0.9
0.05856 | 282.15 | 0.09644 | 287.65 | 1
0.05856 | 282.15 | 0.09644 | 288.15 | 0.15
0.05856 | 282.15 | 0.09644 | 288.15 | 0.2
0.05856 | 282.15 | 0.09644 | 288.15 | 0.3
0.05856 | 282.15 | 0.09644 | 288.15 | 0.4
0.05856 | 282.15 | 0.09644 | 288.15 | 0.5
0.05856 | 282.15 | 0.09644 | 288.15 | 0.6
0.05856 | 282.15 | 0.09644 | 288.15 | 0.7
0.05856 | 282.15 | 0.09644 | 288.15 | 0.8
0.05856 | 282.15 | 0.09644 | 288.15 | 0.9
0.05856 | 282.15 | 0.09644 | 288.15 | 1
0.05856 | 282.15 | 0.09644 | 288.65 | 0.15
0.05856 | 282.15 | 0.09644 | 288.65 | 0.2
0.05856 | 282.15 | 0.09644 | 288.65 | 0.3
0.05856 | 282.15 | 0.09644 | 288.65 | 0.4
0.05856 | 282.15 | 0.09644 | 288.65 | 0.5
0.05856 | 282.15 | 0.09644 | 288.65 | 0.6
0.05856 | 282.15 | 0.09644 | 288.65 | 0.7
0.05856 | 282.15 | 0.09644 | 288.65 | 0.8
0.05856 | 282.15 | 0.09644 | 288.65 | 0.9
0.05856 | 282.15 | 0.09644 | 288.65 | 1
0.05856 | 282.15 | 0.09644 | 289.15 | 0.15
0.05856 | 282.15 | 0.09644 | 289.15 | 0.2
0.05856 | 282.15 | 0.09644 | 289.15 | 0.3
0.05856 | 282.15 | 0.09644 | 289.15 | 0.4
0.05856 | 282.15 | 0.09644 | 289.15 | 0.5
0.05856 | 282.15 | 0.09644 | 289.15 | 0.6
0.05856 | 282.15 | 0.09644 | 289.15 | 0.7
0.05856 | 282.15 | 0.09644 | 289.15 | 0.8
0.05856 | 282.15 | 0.09644 | 289.15 | 0.9
0.05856 | 282.15 | 0.09644 | 289.15 | 1
0.05856 | 282.15 | 0.09644 | 289.65 | 0.15
0.05856 | 282.15 | 0.09644 | 289.65 | 0.2
0.05856 | 282.15 | 0.09644 | 289.65 | 0.3
0.05856 | 282.15 | 0.09644 | 289.65 | 0.4
0.05856 | 282.15 | 0.09644 | 289.65 | 0.5
0.05856 | 282.15 | 0.09644 | 289.65 | 0.6
0.05856 | 282.15 | 0.09644 | 289.65 | 0.7
0.05856 | 282.15 | 0.09644 | 289.65 | 0.8
0.05856 | 282.15 | 0.09644 | 289.65 | 0.9
0.05856 | 282.15 | 0.09644 | 289.65 | 1
0.05856 | 282.15 | 0.09644 | 290.15 | 0.15
0.05856 | 282.15 | 0.09644 | 290.15 | 0.2
0.05856 | 282.15 | 0.09644 | 290.15 | 0.3
0.05856 | 282.15 | 0.09644 | 290.15 | 0.4
0.05856 | 282.15 | 0.09644 | 290.15 | 0.5
0.05856 | 282.15 | 0.09644 | 290.15 | 0.6
0.05856 | 282.15 | 0.09644 | 290.15 | 0.7
0.05856 | 282.15 | 0.09644 | 290.15 | 0.8
0.05856 | 282.15 | 0.09644 | 290.15 | 0.9
0.05856 | 282.15 | 0.09644 | 290.15 | 1
0.05856 | 282.15 | 0.09644 | 290.65 | 0.15
0.05856 | 282.15 | 0.09644 | 290.65 | 0.2
0.05856 | 282.15 | 0.09644 | 290.65 | 0.3
0.05856 | 282.15 | 0.09644 | 290.65 | 0.4
0.05856 | 282.15 | 0.09644 | 290.65 | 0.5
0.05856 | 282.15 | 0.09644 | 290.65 | 0.6
0.05856 | 282.15 | 0.09644 | 290.65 | 0.7
0.05856 | 282.15 | 0.09644 | 290.65 | 0.8
0.05856 | 282.15 | 0.09644 | 290.65 | 0.9
0.05856 | 282.15 | 0.09644 | 290.65 | 1
0.05856 | 282.15 | 0.09644 | 291.15 | 0.15
0.05856 | 282.15 | 0.09644 | 291.15 | 0.2
0.05856 | 282.15 | 0.09644 | 291.15 | 0.3
0.05856 | 282.15 | 0.09644 | 291.15 | 0.4
0.05856 | 282.15 | 0.09644 | 291.15 | 0.5
0.05856 | 282.15 | 0.09644 | 291.15 | 0.6
0.05856 | 282.15 | 0.09644 | 291.15 | 0.7
0.05856 | 282.15 | 0.09644 | 291.15 | 0.8
0.05856 | 282.15 | 0.09644 | 291.15 | 0.9
0.05856 | 282.15 | 0.09644 | 291.15 | 1
0.05856 | 282.15 | 0.09644 | 294.15 | 0.15
0.05856 | 282.15 | 0.09644 | 294.15 | 0.2
0.05856 | 282.15 | 0.09644 | 294.15 | 0.3
0.05856 | 282.15 | 0.09644 | 294.15 | 0.4
0.05856 | 282.15 | 0.09644 | 294.15 | 0.5
0.05856 | 282.15 | 0.09644 | 294.15 | 0.6
0.05856 | 282.15 | 0.09644 | 294.15 | 0.7
0.05856 | 282.15 | 0.09644 | 294.15 | 0.8
0.05856 | 282.15 | 0.09644 | 294.15 | 0.9
0.05856 | 282.15 | 0.09644 | 294.15 | 1
0.05856 | 282.15 | 0.09644 | 297.15 | 0.15
0.05856 | 282.15 | 0.09644 | 297.15 | 0.2
0.05856 | 282.15 | 0.09644 | 297.15 | 0.3
0.05856 | 282.15 | 0.09644 | 297.15 | 0.4
0.05856 | 282.15 | 0.09644 | 297.15 | 0.5
0.05856 | 282.15 | 0.09644 | 297.15 | 0.6
0.05856 | 282.15 | 0.09644 | 297.15 | 0.7
0.05856 | 282.15 | 0.09644 | 297.15 | 0.8
0.05856 | 282.15 | 0.09644 | 297.15 | 0.9
0.05856 | 282.15 | 0.09644 | 297.15 | 1
0.05856 | 282.15 | 0.09644 | 300.15 | 0.15
0.05856 | 282.15 | 0.09644 | 300.15 | 0.2
0.05856 | 282.15 | 0.09644 | 300.15 | 0.3
0.05856 | 282.15 | 0.09644 | 300.15 | 0.4
0.05856 | 282.15 | 0.09644 | 300.15 | 0.5
0.05856 | 282.15 | 0.09644 | 300.15 | 0.6
0.05856 | 282.15 | 0.09644 | 300.15 | 0.7
0.05856 | 282.15 | 0.09644 | 300.15 | 0.8
0.05856 | 282.15 | 0.09644 | 300.15 | 0.9
0.05856 | 282.15 | 0.09644 | 300.15 | 1
0.05856 | 282.15 | 0.09644 | 303.15 | 0.15
0.05856 | 282.15 | 0.09644 | 303.15 | 0.2
0.05856 | 282.15 | 0.09644 | 303.15 | 0.3
0.05856 | 282.15 | 0.09644 | 303.15 | 0.4
0.05856 | 282.15 | 0.09644 | 303.15 | 0.5
0.05856 | 282.15 | 0.09644 | 303.15 | 0.6
0.05856 | 282.15 | 0.09644 | 303.15 | 0.7
0.05856 | 282.15 | 0.09644 | 303.15 | 0.8
0.05856 | 282.15 | 0.09644 | 303.15 | 0.9
0.05856 | 282.15 | 0.09644 | 303.15 | 1
0.05856 | 282.15 | 0.09737 | 283.65 | 0.15
0.05856 | 282.15 | 0.09737 | 283.65 | 0.2
0.05856 | 282.15 | 0.09737 | 283.65 | 0.3
0.05856 | 282.15 | 0.09737 | 283.65 | 0.4
0.05856 | 282.15 | 0.09737 | 283.65 | 0.5
0.05856 | 282.15 | 0.09737 | 283.65 | 0.6
0.05856 | 282.15 | 0.09737 | 283.65 | 0.7
0.05856 | 282.15 | 0.09737 | 283.65 | 0.8
0.05856 | 282.15 | 0.09737 | 283.65 | 0.9
0.05856 | 282.15 | 0.09737 | 283.65 | 1
0.05856 | 282.15 | 0.09737 | 284.15 | 0.15
0.05856 | 282.15 | 0.09737 | 284.15 | 0.2
0.05856 | 282.15 | 0.09737 | 284.15 | 0.3
0.05856 | 282.15 | 0.09737 | 284.15 | 0.4
0.05856 | 282.15 | 0.09737 | 284.15 | 0.5
0.05856 | 282.15 | 0.09737 | 284.15 | 0.6
0.05856 | 282.15 | 0.09737 | 284.15 | 0.7
0.05856 | 282.15 | 0.09737 | 284.15 | 0.8
0.05856 | 282.15 | 0.09737 | 284.15 | 0.9
0.05856 | 282.15 | 0.09737 | 284.15 | 1
0.05856 | 282.15 | 0.09737 | 284.65 | 0.15
0.05856 | 282.15 | 0.09737 | 284.65 | 0.2
0.05856 | 282.15 | 0.09737 | 284.65 | 0.3
0.05856 | 282.15 | 0.09737 | 284.65 | 0.4
0.05856 | 282.15 | 0.09737 | 284.65 | 0.5
0.05856 | 282.15 | 0.09737 | 284.65 | 0.6
0.05856 | 282.15 | 0.09737 | 284.65 | 0.7
0.05856 | 282.15 | 0.09737 | 284.65 | 0.8
0.05856 | 282.15 | 0.09737 | 284.65 | 0.9
0.05856 | 282.15 | 0.09737 | 284.65 | 1
0.05856 | 282.15 | 0.09737 | 285.15 | 0.15
0.05856 | 282.15 | 0.09737 | 285.15 | 0.2
0.05856 | 282.15 | 0.09737 | 285.15 | 0.3
0.05856 | 282.15 | 0.09737 | 285.15 | 0.4
0.05856 | 282.15 | 0.09737 | 285.15 | 0.5
0.05856 | 282.15 | 0.09737 | 285.15 | 0.6
0.05856 | 282.15 | 0.09737 | 285.15 | 0.7
0.05856 | 282.15 | 0.09737 | 285.15 | 0.8
0.05856 | 282.15 | 0.09737 | 285.15 | 0.9
0.05856 | 282.15 | 0.09737 | 285.15 | 1
0.05856 | 282.15 | 0.09737 | 285.65 | 0.15
0.05856 | 282.15 | 0.09737 | 285.65 | 0.2
0.05856 | 282.15 | 0.09737 | 285.65 | 0.3
0.05856 | 282.15 | 0.09737 | 285.65 | 0.4
0.05856 | 282.15 | 0.09737 | 285.65 | 0.5
0.05856 | 282.15 | 0.09737 | 285.65 | 0.6
0.05856 | 282.15 | 0.09737 | 285.65 | 0.7
0.05856 | 282.15 | 0.09737 | 285.65 | 0.8
0.05856 | 282.15 | 0.09737 | 285.65 | 0.9
0.05856 | 282.15 | 0.09737 | 285.65 | 1
0.05856 | 282.15 | 0.09737 | 286.15 | 0.15
0.05856 | 282.15 | 0.09737 | 286.15 | 0.2
0.05856 | 282.15 | 0.09737 | 286.15 | 0.3
0.05856 | 282.15 | 0.09737 | 286.15 | 0.4
0.05856 | 282.15 | 0.09737 | 286.15 | 0.5
0.05856 | 282.15 | 0.09737 | 286.15 | 0.6
0.05856 | 282.15 | 0.09737 | 286.15 | 0.7
0.05856 | 282.15 | 0.09737 | 286.15 | 0.8
0.05856 | 282.15 | 0.09737 | 286.15 | 0.9
0.05856 | 282.15 | 0.09737 | 286.15 | 1
0.05856 | 282.15 | 0.09737 | 286.65 | 0.15
0.05856 | 282.15 | 0.09737 | 286.65 | 0.2
0.05856 | 282.15 | 0.09737 | 286.65 | 0.3
0.05856 | 282.15 | 0.09737 | 286.65 | 0.4
0.05856 | 282.15 | 0.09737 | 286.65 | 0.5
0.05856 | 282.15 | 0.09737 | 286.65 | 0.6
0.05856 | 282.15 | 0.09737 | 286.65 | 0.7
0.05856 | 282.15 | 0.09737 | 286.65 | 0.8
0.05856 | 282.15 | 0.09737 | 286.65 | 0.9
0.05856 | 282.15 | 0.09737 | 286.65 | 1
0.05856 | 282.15 | 0.09737 | 287.15 | 0.15
0.05856 | 282.15 | 0.09737 | 287.15 | 0.2
0.05856 | 282.15 | 0.09737 | 287.15 | 0.3
0.05856 | 282.15 | 0.09737 | 287.15 | 0.4
0.05856 | 282.15 | 0.09737 | 287.15 | 0.5
0.05856 | 282.15 | 0.09737 | 287.15 | 0.6
0.05856 | 282.15 | 0.09737 | 287.15 | 0.7
0.05856 | 282.15 | 0.09737 | 287.15 | 0.8
0.05856 | 282.15 | 0.09737 | 287.15 | 0.9
0.05856 | 282.15 | 0.09737 | 287.15 | 1
0.05856 | 282.15 | 0.09737 | 287.65 | 0.15
0.05856 | 282.15 | 0.09737 | 287.65 | 0.2
0.05856 | 282.15 | 0.09737 | 287.65 | 0.3
0.05856 | 282.15 | 0.09737 | 287.65 | 0.4
0.05856 | 282.15 | 0.09737 | 287.65 | 0.5
0.05856 | 282.15 | 0.09737 | 287.65 | 0.6
0.05856 | 282.15 | 0.09737 | 287.65 | 0.7
0.05856 | 282.15 | 0.09737 | 287.65 | 0.8
0.05856 | 282.15 | 0.09737 | 287.65 | 0.9
0.05856 | 282.15 | 0.09737 | 287.65 | 1
0.05856 | 282.15 | 0.09737 | 288.15 | 0.15
0.05856 | 282.15 | 0.09737 | 288.15 | 0.2
0.05856 | 282.15 | 0.09737 | 288.15 | 0.3
0.05856 | 282.15 | 0.09737 | 288.15 | 0.4
0.05856 | 282.15 | 0.09737 | 288.15 | 0.5
0.05856 | 282.15 | 0.09737 | 288.15 | 0.6
0.05856 | 282.15 | 0.09737 | 288.15 | 0.7
0.05856 | 282.15 | 0.09737 | 288.15 | 0.8
0.05856 | 282.15 | 0.09737 | 288.15 | 0.9
0.05856 | 282.15 | 0.09737 | 288.15 | 1
0.05856 | 282.15 | 0.09737 | 288.65 | 0.15
0.05856 | 282.15 | 0.09737 | 288.65 | 0.2
0.05856 | 282.15 | 0.09737 | 288.65 | 0.3
0.05856 | 282.15 | 0.09737 | 288.65 | 0.4
0.05856 | 282.15 | 0.09737 | 288.65 | 0.5
0.05856 | 282.15 | 0.09737 | 288.65 | 0.6
0.05856 | 282.15 | 0.09737 | 288.65 | 0.7
0.05856 | 282.15 | 0.09737 | 288.65 | 0.8
0.05856 | 282.15 | 0.09737 | 288.65 | 0.9
0.05856 | 282.15 | 0.09737 | 288.65 | 1
0.05856 | 282.15 | 0.09737 | 289.15 | 0.15
0.05856 | 282.15 | 0.09737 | 289.15 | 0.2
0.05856 | 282.15 | 0.09737 | 289.15 | 0.3
0.05856 | 282.15 | 0.09737 | 289.15 | 0.4
0.05856 | 282.15 | 0.09737 | 289.15 | 0.5
0.05856 | 282.15 | 0.09737 | 289.15 | 0.6
0.05856 | 282.15 | 0.09737 | 289.15 | 0.7
0.05856 | 282.15 | 0.09737 | 289.15 | 0.8
0.05856 | 282.15 | 0.09737 | 289.15 | 0.9
0.05856 | 282.15 | 0.09737 | 289.15 | 1
0.05856 | 282.15 | 0.09737 | 289.65 | 0.15
0.05856 | 282.15 | 0.09737 | 289.65 | 0.2
0.05856 | 282.15 | 0.09737 | 289.65 | 0.3
0.05856 | 282.15 | 0.09737 | 289.65 | 0.4
0.05856 | 282.15 | 0.09737 | 289.65 | 0.5
0.05856 | 282.15 | 0.09737 | 289.65 | 0.6
0.05856 | 282.15 | 0.09737 | 289.65 | 0.7
0.05856 | 282.15 | 0.09737 | 289.65 | 0.8
0.05856 | 282.15 | 0.09737 | 289.65 | 0.9
0.05856 | 282.15 | 0.09737 | 289.65 | 1
0.05856 | 282.15 | 0.09737 | 290.15 | 0.15
0.05856 | 282.15 | 0.09737 | 290.15 | 0.2
0.05856 | 282.15 | 0.09737 | 290.15 | 0.3
0.05856 | 282.15 | 0.09737 | 290.15 | 0.4
0.05856 | 282.15 | 0.09737 | 290.15 | 0.5
0.05856 | 282.15 | 0.09737 | 290.15 | 0.6
0.05856 | 282.15 | 0.09737 | 290.15 | 0.7
0.05856 | 282.15 | 0.09737 | 290.15 | 0.8
0.05856 | 282.15 | 0.09737 | 290.15 | 0.9
0.05856 | 282.15 | 0.09737 | 290.15 | 1
0.05856 | 282.15 | 0.09737 | 290.65 | 0.15
0.05856 | 282.15 | 0.09737 | 290.65 | 0.2
0.05856 | 282.15 | 0.09737 | 290.65 | 0.3
0.05856 | 282.15 | 0.09737 | 290.65 | 0.4
0.05856 | 282.15 | 0.09737 | 290.65 | 0.5
0.05856 | 282.15 | 0.09737 | 290.65 | 0.6
0.05856 | 282.15 | 0.09737 | 290.65 | 0.7
0.05856 | 282.15 | 0.09737 | 290.65 | 0.8
0.05856 | 282.15 | 0.09737 | 290.65 | 0.9
0.05856 | 282.15 | 0.09737 | 290.65 | 1
0.05856 | 282.15 | 0.09737 | 291.15 | 0.15
0.05856 | 282.15 | 0.09737 | 291.15 | 0.2
0.05856 | 282.15 | 0.09737 | 291.15 | 0.3
0.05856 | 282.15 | 0.09737 | 291.15 | 0.4
0.05856 | 282.15 | 0.09737 | 291.15 | 0.5
0.05856 | 282.15 | 0.09737 | 291.15 | 0.6
0.05856 | 282.15 | 0.09737 | 291.15 | 0.7
0.05856 | 282.15 | 0.09737 | 291.15 | 0.8
0.05856 | 282.15 | 0.09737 | 291.15 | 0.9
0.05856 | 282.15 | 0.09737 | 291.15 | 1
0.05856 | 282.15 | 0.09737 | 294.15 | 0.15
0.05856 | 282.15 | 0.09737 | 294.15 | 0.2
0.05856 | 282.15 | 0.09737 | 294.15 | 0.3
0.05856 | 282.15 | 0.09737 | 294.15 | 0.4
0.05856 | 282.15 | 0.09737 | 294.15 | 0.5
0.05856 | 282.15 | 0.09737 | 294.15 | 0.6
0.05856 | 282.15 | 0.09737 | 294.15 | 0.7
0.05856 | 282.15 | 0.09737 | 294.15 | 0.8
0.05856 | 282.15 | 0.09737 | 294.15 | 0.9
0.05856 | 282.15 | 0.09737 | 294.15 | 1
0.05856 | 282.15 | 0.09737 | 297.15 | 0.15
0.05856 | 282.15 | 0.09737 | 297.15 | 0.2
0.05856 | 282.15 | 0.09737 | 297.15 | 0.3
0.05856 | 282.15 | 0.09737 | 297.15 | 0.4
0.05856 | 282.15 | 0.09737 | 297.15 | 0.5
0.05856 | 282.15 | 0.09737 | 297.15 | 0.6
0.05856 | 282.15 | 0.09737 | 297.15 | 0.7
0.05856 | 282.15 | 0.09737 | 297.15 | 0.8
0.05856 | 282.15 | 0.09737 | 297.15 | 0.9
0.05856 | 282.15 | 0.09737 | 297.15 | 1
0.05856 | 282.15 | 0.09737 | 300.15 | 0.15
0.05856 | 282.15 | 0.09737 | 300.15 | 0.2
0.05856 | 282.15 | 0.09737 | 300.15 | 0.3
0.05856 | 282.15 | 0.09737 | 300.15 | 0.4
0.05856 | 282.15 | 0.09737 | 300.15 | 0.5
0.05856 | 282.15 | 0.09737 | 300.15 | 0.6
0.05856 | 282.15 | 0.09737 | 300.15 | 0.7
0.05856 | 282.15 | 0.09737 | 300.15 | 0.8
0.05856 | 282.15 | 0.09737 | 300.15 | 0.9
0.05856 | 282.15 | 0.09737 | 300.15 | 1
0.05856 | 282.15 | 0.09737 | 303.15 | 0.15
0.05856 | 282.15 | 0.09737 | 303.15 | 0.2
0.05856 | 282.15 | 0.09737 | 303.15 | 0.3
0.05856 | 282.15 | 0.09737 | 303.15 | 0.4
0.05856 | 282.15 | 0.09737 | 303.15 | 0.5
0.05856 | 282.15 | 0.09737 | 303.15 | 0.6
0.05856 | 282.15 | 0.09737 | 303.15 | 0.7
0.05856 | 282.15 | 0.09737 | 303.15 | 0.8
0.05856 | 282.15 | 0.09737 | 303.15 | 0.9
0.05856 | 282.15 | 0.09737 | 303.15 | 1
0.05856 | 282.15 | 0.115 | 283.65 | 0.15
0.05856 | 282.15 | 0.115 | 283.65 | 0.2
0.05856 | 282.15 | 0.115 | 283.65 | 0.3
0.05856 | 282.15 | 0.115 | 283.65 | 0.4
0.05856 | 282.15 | 0.115 | 283.65 | 0.5
0.05856 | 282.15 | 0.115 | 283.65 | 0.6
0.05856 | 282.15 | 0.115 | 283.65 | 0.7
0.05856 | 282.15 | 0.115 | 283.65 | 0.8
0.05856 | 282.15 | 0.115 | 283.65 | 0.9
0.05856 | 282.15 | 0.115 | 283.65 | 1
0.05856 | 282.15 | 0.115 | 284.15 | 0.15
0.05856 | 282.15 | 0.115 | 284.15 | 0.2
0.05856 | 282.15 | 0.115 | 284.15 | 0.3
0.05856 | 282.15 | 0.115 | 284.15 | 0.4
0.05856 | 282.15 | 0.115 | 284.15 | 0.5
0.05856 | 282.15 | 0.115 | 284.15 | 0.6
0.05856 | 282.15 | 0.115 | 284.15 | 0.7
0.05856 | 282.15 | 0.115 | 284.15 | 0.8
0.05856 | 282.15 | 0.115 | 284.15 | 0.9
0.05856 | 282.15 | 0.115 | 284.15 | 1
0.05856 | 282.15 | 0.115 | 284.65 | 0.15
0.05856 | 282.15 | 0.115 | 284.65 | 0.2
0.05856 | 282.15 | 0.115 | 284.65 | 0.3
0.05856 | 282.15 | 0.115 | 284.65 | 0.4
0.05856 | 282.15 | 0.115 | 284.65 | 0.5
0.05856 | 282.15 | 0.115 | 284.65 | 0.6
0.05856 | 282.15 | 0.115 | 284.65 | 0.7
0.05856 | 282.15 | 0.115 | 284.65 | 0.8
0.05856 | 282.15 | 0.115 | 284.65 | 0.9
0.05856 | 282.15 | 0.115 | 284.65 | 1
0.05856 | 282.15 | 0.115 | 285.15 | 0.15
0.05856 | 282.15 | 0.115 | 285.15 | 0.2
0.05856 | 282.15 | 0.115 | 285.15 | 0.3
0.05856 | 282.15 | 0.115 | 285.15 | 0.4
0.05856 | 282.15 | 0.115 | 285.15 | 0.5
0.05856 | 282.15 | 0.115 | 285.15 | 0.6
0.05856 | 282.15 | 0.115 | 285.15 | 0.7
0.05856 | 282.15 | 0.115 | 285.15 | 0.8
0.05856 | 282.15 | 0.115 | 285.15 | 0.9
0.05856 | 282.15 | 0.115 | 285.15 | 1
0.05856 | 282.15 | 0.115 | 285.65 | 0.15
0.05856 | 282.15 | 0.115 | 285.65 | 0.2
0.05856 | 282.15 | 0.115 | 285.65 | 0.3
0.05856 | 282.15 | 0.115 | 285.65 | 0.4
0.05856 | 282.15 | 0.115 | 285.65 | 0.5
0.05856 | 282.15 | 0.115 | 285.65 | 0.6
0.05856 | 282.15 | 0.115 | 285.65 | 0.7
0.05856 | 282.15 | 0.115 | 285.65 | 0.8
0.05856 | 282.15 | 0.115 | 285.65 | 0.9
0.05856 | 282.15 | 0.115 | 285.65 | 1
0.05856 | 282.15 | 0.115 | 286.15 | 0.15
0.05856 | 282.15 | 0.115 | 286.15 | 0.2
0.05856 | 282.15 | 0.115 | 286.15 | 0.3
0.05856 | 282.15 | 0.115 | 286.15 | 0.4
0.05856 | 282.15 | 0.115 | 286.15 | 0.5
0.05856 | 282.15 | 0.115 | 286.15 | 0.6
0.05856 | 282.15 | 0.115 | 286.15 | 0.7
0.05856 | 282.15 | 0.115 | 286.15 | 0.8
0.05856 | 282.15 | 0.115 | 286.15 | 0.9
0.05856 | 282.15 | 0.115 | 286.15 | 1
0.05856 | 282.15 | 0.115 | 286.65 | 0.15
0.05856 | 282.15 | 0.115 | 286.65 | 0.2
0.05856 | 282.15 | 0.115 | 286.65 | 0.3
0.05856 | 282.15 | 0.115 | 286.65 | 0.4
0.05856 | 282.15 | 0.115 | 286.65 | 0.5
0.05856 | 282.15 | 0.115 | 286.65 | 0.6
0.05856 | 282.15 | 0.115 | 286.65 | 0.7
0.05856 | 282.15 | 0.115 | 286.65 | 0.8
0.05856 | 282.15 | 0.115 | 286.65 | 0.9
0.05856 | 282.15 | 0.115 | 286.65 | 1
0.05856 | 282.15 | 0.115 | 287.15 | 0.15
0.05856 | 282.15 | 0.115 | 287.15 | 0.2
0.05856 | 282.15 | 0.115 | 287.15 | 0.3
0.05856 | 282.15 | 0.115 | 287.15 | 0.4
0.05856 | 282.15 | 0.115 | 287.15 | 0.5
0.05856 | 282.15 | 0.115 | 287.15 | 0.6
0.05856 | 282.15 | 0.115 | 287.15 | 0.7
0.05856 | 282.15 | 0.115 | 287.15 | 0.8
0.05856 | 282.15 | 0.115 | 287.15 | 0.9
0.05856 | 282.15 | 0.115 | 287.15 | 1
0.05856 | 282.15 | 0.115 | 287.65 | 0.15
0.05856 | 282.15 | 0.115 | 287.65 | 0.2
0.05856 | 282.15 | 0.115 | 287.65 | 0.3
0.05856 | 282.15 | 0.115 | 287.65 | 0.4
0.05856 | 282.15 | 0.115 | 287.65 | 0.5
0.05856 | 282.15 | 0.115 | 287.65 | 0.6
0.05856 | 282.15 | 0.115 | 287.65 | 0.7
0.05856 | 282.15 | 0.115 | 287.65 | 0.8
0.05856 | 282.15 | 0.115 | 287.65 | 0.9
0.05856 | 282.15 | 0.115 | 287.65 | 1
0.05856 | 282.15 | 0.115 | 288.15 | 0.15
0.05856 | 282.15 | 0.115 | 288.15 | 0.2
0.05856 | 282.15 | 0.115 | 288.15 | 0.3
0.05856 | 282.15 | 0.115 | 288.15 | 0.4
0.05856 | 282.15 | 0.115 | 288.15 | 0.5
0.05856 | 282.15 | 0.115 | 288.15 | 0.6
0.05856 | 282.15 | 0.115 | 288.15 | 0.7
0.05856 | 282.15 | 0.115 | 288.15 | 0.8
0.05856 | 282.15 | 0.115 | 288.15 | 0.9
0.05856 | 282.15 | 0.115 | 288.15 | 1
0.05856 | 282.15 | 0.115 | 288.65 | 0.15
0.05856 | 282.15 | 0.115 | 288.65 | 0.2
0.05856 | 282.15 | 0.115 | 288.65 | 0.3
0.05856 | 282.15 | 0.115 | 288.65 | 0.4
0.05856 | 282.15 | 0.115 | 288.65 | 0.5
0.05856 | 282.15 | 0.115 | 288.65 | 0.6
0.05856 | 282.15 | 0.115 | 288.65 | 0.7
0.05856 | 282.15 | 0.115 | 288.65 | 0.8
0.05856 | 282.15 | 0.115 | 288.65 | 0.9
0.05856 | 282.15 | 0.115 | 288.65 | 1
0.05856 | 282.15 | 0.115 | 289.15 | 0.15
0.05856 | 282.15 | 0.115 | 289.15 | 0.2
0.05856 | 282.15 | 0.115 | 289.15 | 0.3
0.05856 | 282.15 | 0.115 | 289.15 | 0.4
0.05856 | 282.15 | 0.115 | 289.15 | 0.5
0.05856 | 282.15 | 0.115 | 289.15 | 0.6
0.05856 | 282.15 | 0.115 | 289.15 | 0.7
0.05856 | 282.15 | 0.115 | 289.15 | 0.8
0.05856 | 282.15 | 0.115 | 289.15 | 0.9
0.05856 | 282.15 | 0.115 | 289.15 | 1
0.05856 | 282.15 | 0.115 | 289.65 | 0.15
0.05856 | 282.15 | 0.115 | 289.65 | 0.2
0.05856 | 282.15 | 0.115 | 289.65 | 0.3
0.05856 | 282.15 | 0.115 | 289.65 | 0.4
0.05856 | 282.15 | 0.115 | 289.65 | 0.5
0.05856 | 282.15 | 0.115 | 289.65 | 0.6
0.05856 | 282.15 | 0.115 | 289.65 | 0.7
0.05856 | 282.15 | 0.115 | 289.65 | 0.8
0.05856 | 282.15 | 0.115 | 289.65 | 0.9
0.05856 | 282.15 | 0.115 | 289.65 | 1
0.05856 | 282.15 | 0.115 | 290.15 | 0.15
0.05856 | 282.15 | 0.115 | 290.15 | 0.2
0.05856 | 282.15 | 0.115 | 290.15 | 0.3
0.05856 | 282.15 | 0.115 | 290.15 | 0.4
0.05856 | 282.15 | 0.115 | 290.15 | 0.5
0.05856 | 282.15 | 0.115 | 290.15 | 0.6
0.05856 | 282.15 | 0.115 | 290.15 | 0.7
0.05856 | 282.15 | 0.115 | 290.15 | 0.8
0.05856 | 282.15 | 0.115 | 290.15 | 0.9
0.05856 | 282.15 | 0.115 | 290.15 | 1
0.05856 | 282.15 | 0.115 | 290.65 | 0.15
0.05856 | 282.15 | 0.115 | 290.65 | 0.2
0.05856 | 282.15 | 0.115 | 290.65 | 0.3
0.05856 | 282.15 | 0.115 | 290.65 | 0.4
0.05856 | 282.15 | 0.115 | 290.65 | 0.5
0.05856 | 282.15 | 0.115 | 290.65 | 0.6
0.05856 | 282.15 | 0.115 | 290.65 | 0.7
0.05856 | 282.15 | 0.115 | 290.65 | 0.8
0.05856 | 282.15 | 0.115 | 290.65 | 0.9
0.05856 | 282.15 | 0.115 | 290.65 | 1
0.05856 | 282.15 | 0.115 | 291.15 | 0.15
0.05856 | 282.15 | 0.115 | 291.15 | 0.2
0.05856 | 282.15 | 0.115 | 291.15 | 0.3
0.05856 | 282.15 | 0.115 | 291.15 | 0.4
0.05856 | 282.15 | 0.115 | 291.15 | 0.5
0.05856 | 282.15 | 0.115 | 291.15 | 0.6
0.05856 | 282.15 | 0.115 | 291.15 | 0.7
0.05856 | 282.15 | 0.115 | 291.15 | 0.8
0.05856 | 282.15 | 0.115 | 291.15 | 0.9
0.05856 | 282.15 | 0.115 | 291.15 | 1
0.05856 | 282.15 | 0.115 | 294.15 | 0.15
0.05856 | 282.15 | 0.115 | 294.15 | 0.2
0.05856 | 282.15 | 0.115 | 294.15 | 0.3
0.05856 | 282.15 | 0.115 | 294.15 | 0.4
0.05856 | 282.15 | 0.115 | 294.15 | 0.5
0.05856 | 282.15 | 0.115 | 294.15 | 0.6
0.05856 | 282.15 | 0.115 | 294.15 | 0.7
0.05856 | 282.15 | 0.115 | 294.15 | 0.8
0.05856 | 282.15 | 0.115 | 294.15 | 0.9
0.05856 | 282.15 | 0.115 | 294.15 | 1
0.05856 | 282.15 | 0.115 | 297.15 | 0.15
0.05856 | 282.15 | 0.115 | 297.15 | 0.2
0.05856 | 282.15 | 0.115 | 297.15 | 0.3
0.05856 | 282.15 | 0.115 | 297.15 | 0.4
0.05856 | 282.15 | 0.115 | 297.15 | 0.5
0.05856 | 282.15 | 0.115 | 297.15 | 0.6
0.05856 | 282.15 | 0.115 | 297.15 | 0.7
0.05856 | 282.15 | 0.115 | 297.15 | 0.8
0.05856 | 282.15 | 0.115 | 297.15 | 0.9
0.05856 | 282.15 | 0.115 | 297.15 | 1
0.05856 | 282.15 | 0.115 | 300.15 | 0.15
0.05856 | 282.15 | 0.115 | 300.15 | 0.2
0.05856 | 282.15 | 0.115 | 300.15 | 0.3
0.05856 | 282.15 | 0.115 | 300.15 | 0.4
0.05856 | 282.15 | 0.115 | 300.15 | 0.5
0.05856 | 282.15 | 0.115 | 300.15 | 0.6
0.05856 | 282.15 | 0.115 | 300.15 | 0.7
0.05856 | 282.15 | 0.115 | 300.15 | 0.8
0.05856 | 282.15 | 0.115 | 300.15 | 0.9
0.05856 | 282.15 | 0.115 | 300.15 | 1
0.05856 | 282.15 | 0.115 | 303.15 | 0.15
0.05856 | 282.15 | 0.115 | 303.15 | 0.2
0.05856 | 282.15 | 0.115 | 303.15 | 0.3
0.05856 | 282.15 | 0.115 | 303.15 | 0.4
0.05856 | 282.15 | 0.115 | 303.15 | 0.5
0.05856 | 282.15 | 0.115 | 303.15 | 0.6
0.05856 | 282.15 | 0.115 | 303.15 | 0.7
0.05856 | 282.15 | 0.115 | 303.15 | 0.8
0.05856 | 282.15 | 0.115 | 303.15 | 0.9
0.05856 | 282.15 | 0.115 | 303.15 | 1
0.08385 | 278.15 | 0.00115 | 283.65 | 0.15
0.08385 | 278.15 | 0.00115 | 283.65 | 0.2
0.08385 | 278.15 | 0.00115 | 283.65 | 0.3
0.08385 | 278.15 | 0.00115 | 283.65 | 0.4
0.08385 | 278.15 | 0.00115 | 283.65 | 0.5
0.08385 | 278.15 | 0.00115 | 283.65 | 0.6
0.08385 | 278.15 | 0.00115 | 283.65 | 0.7
0.08385 | 278.15 | 0.00115 | 283.65 | 0.8
0.08385 | 278.15 | 0.00115 | 283.65 | 0.9
0.08385 | 278.15 | 0.00115 | 283.65 | 1
0.08385 | 278.15 | 0.00115 | 284.15 | 0.15
0.08385 | 278.15 | 0.00115 | 284.15 | 0.2
0.08385 | 278.15 | 0.00115 | 284.15 | 0.3
0.08385 | 278.15 | 0.00115 | 284.15 | 0.4
0.08385 | 278.15 | 0.00115 | 284.15 | 0.5
0.08385 | 278.15 | 0.00115 | 284.15 | 0.6
0.08385 | 278.15 | 0.00115 | 284.15 | 0.7
0.08385 | 278.15 | 0.00115 | 284.15 | 0.8
0.08385 | 278.15 | 0.00115 | 284.15 | 0.9
0.08385 | 278.15 | 0.00115 | 284.15 | 1
0.08385 | 278.15 | 0.00115 | 284.65 | 0.15
0.08385 | 278.15 | 0.00115 | 284.65 | 0.2
0.08385 | 278.15 | 0.00115 | 284.65 | 0.3
0.08385 | 278.15 | 0.00115 | 284.65 | 0.4
0.08385 | 278.15 | 0.00115 | 284.65 | 0.5
0.08385 | 278.15 | 0.00115 | 284.65 | 0.6
0.08385 | 278.15 | 0.00115 | 284.65 | 0.7
0.08385 | 278.15 | 0.00115 | 284.65 | 0.8
0.08385 | 278.15 | 0.00115 | 284.65 | 0.9
0.08385 | 278.15 | 0.00115 | 284.65 | 1
0.08385 | 278.15 | 0.00115 | 285.15 | 0.15
0.08385 | 278.15 | 0.00115 | 285.15 | 0.2
0.08385 | 278.15 | 0.00115 | 285.15 | 0.3
0.08385 | 278.15 | 0.00115 | 285.15 | 0.4
0.08385 | 278.15 | 0.00115 | 285.15 | 0.5
0.08385 | 278.15 | 0.00115 | 285.15 | 0.6
0.08385 | 278.15 | 0.00115 | 285.15 | 0.7
0.08385 | 278.15 | 0.00115 | 285.15 | 0.8
0.08385 | 278.15 | 0.00115 | 285.15 | 0.9
0.08385 | 278.15 | 0.00115 | 285.15 | 1
0.08385 | 278.15 | 0.00115 | 285.65 | 0.15
0.08385 | 278.15 | 0.00115 | 285.65 | 0.2
0.08385 | 278.15 | 0.00115 | 285.65 | 0.3
0.08385 | 278.15 | 0.00115 | 285.65 | 0.4
0.08385 | 278.15 | 0.00115 | 285.65 | 0.5
0.08385 | 278.15 | 0.00115 | 285.65 | 0.6
0.08385 | 278.15 | 0.00115 | 285.65 | 0.7
0.08385 | 278.15 | 0.00115 | 285.65 | 0.8
0.08385 | 278.15 | 0.00115 | 285.65 | 0.9
0.08385 | 278.15 | 0.00115 | 285.65 | 1
0.08385 | 278.15 | 0.00115 | 286.15 | 0.15
0.08385 | 278.15 | 0.00115 | 286.15 | 0.2
0.08385 | 278.15 | 0.00115 | 286.15 | 0.3
0.08385 | 278.15 | 0.00115 | 286.15 | 0.4
0.08385 | 278.15 | 0.00115 | 286.15 | 0.5
0.08385 | 278.15 | 0.00115 | 286.15 | 0.6
0.08385 | 278.15 | 0.00115 | 286.15 | 0.7
0.08385 | 278.15 | 0.00115 | 286.15 | 0.8
0.08385 | 278.15 | 0.00115 | 286.15 | 0.9
0.08385 | 278.15 | 0.00115 | 286.15 | 1
0.08385 | 278.15 | 0.00115 | 286.65 | 0.15
0.08385 | 278.15 | 0.00115 | 286.65 | 0.2
0.08385 | 278.15 | 0.00115 | 286.65 | 0.3
0.08385 | 278.15 | 0.00115 | 286.65 | 0.4
0.08385 | 278.15 | 0.00115 | 286.65 | 0.5
0.08385 | 278.15 | 0.00115 | 286.65 | 0.6
0.08385 | 278.15 | 0.00115 | 286.65 | 0.7
0.08385 | 278.15 | 0.00115 | 286.65 | 0.8
0.08385 | 278.15 | 0.00115 | 286.65 | 0.9
0.08385 | 278.15 | 0.00115 | 286.65 | 1
0.08385 | 278.15 | 0.00115 | 287.15 | 0.15
0.08385 | 278.15 | 0.00115 | 287.15 | 0.2
0.08385 | 278.15 | 0.00115 | 287.15 | 0.3
0.08385 | 278.15 | 0.00115 | 287.15 | 0.4
0.08385 | 278.15 | 0.00115 | 287.15 | 0.5
0.08385 | 278.15 | 0.00115 | 287.15 | 0.6
0.08385 | 278.15 | 0.00115 | 287.15 | 0.7
0.08385 | 278.15 | 0.00115 | 287.15 | 0.8
0.08385 | 278.15 | 0.00115 | 287.15 | 0.9
0.08385 | 278.15 | 0.00115 | 287.15 | 1
0.08385 | 278.15 | 0.00115 | 287.65 | 0.15
0.08385 | 278.15 | 0.00115 | 287.65 | 0.2
0.08385 | 278.15 | 0.00115 | 287.65 | 0.3
0.08385 | 278.15 | 0.00115 | 287.65 | 0.4
0.08385 | 278.15 | 0.00115 | 287.65 | 0.5
0.08385 | 278.15 | 0.00115 | 287.65 | 0.6
0.08385 | 278.15 | 0.00115 | 287.65 | 0.7
0.08385 | 278.15 | 0.00115 | 287.65 | 0.8
0.08385 | 278.15 | 0.00115 | 287.65 | 0.9
0.08385 | 278.15 | 0.00115 | 287.65 | 1
0.08385 | 278.15 | 0.00115 | 288.15 | 0.15
0.08385 | 278.15 | 0.00115 | 288.15 | 0.2
0.08385 | 278.15 | 0.00115 | 288.15 | 0.3
0.08385 | 278.15 | 0.00115 | 288.15 | 0.4
0.08385 | 278.15 | 0.00115 | 288.15 | 0.5
0.08385 | 278.15 | 0.00115 | 288.15 | 0.6
0.08385 | 278.15 | 0.00115 | 288.15 | 0.7
0.08385 | 278.15 | 0.00115 | 288.15 | 0.8
0.08385 | 278.15 | 0.00115 | 288.15 | 0.9
0.08385 | 278.15 | 0.00115 | 288.15 | 1
0.08385 | 278.15 | 0.00115 | 288.65 | 0.15
0.08385 | 278.15 | 0.00115 | 288.65 | 0.2
0.08385 | 278.15 | 0.00115 | 288.65 | 0.3
0.08385 | 278.15 | 0.00115 | 288.65 | 0.4
0.08385 | 278.15 | 0.00115 | 288.65 | 0.5
0.08385 | 278.15 | 0.00115 | 288.65 | 0.6
0.08385 | 278.15 | 0.00115 | 288.65 | 0.7
0.08385 | 278.15 | 0.00115 | 288.65 | 0.8
0.08385 | 278.15 | 0.00115 | 288.65 | 0.9
0.08385 | 278.15 | 0.00115 | 288.65 | 1
0.08385 | 278.15 | 0.00115 | 289.15 | 0.15
0.08385 | 278.15 | 0.00115 | 289.15 | 0.2
0.08385 | 278.15 | 0.00115 | 289.15 | 0.3
0.08385 | 278.15 | 0.00115 | 289.15 | 0.4
0.08385 | 278.15 | 0.00115 | 289.15 | 0.5
0.08385 | 278.15 | 0.00115 | 289.15 | 0.6
0.08385 | 278.15 | 0.00115 | 289.15 | 0.7
0.08385 | 278.15 | 0.00115 | 289.15 | 0.8
0.08385 | 278.15 | 0.00115 | 289.15 | 0.9
0.08385 | 278.15 | 0.00115 | 289.15 | 1
0.08385 | 278.15 | 0.00115 | 289.65 | 0.15
0.08385 | 278.15 | 0.00115 | 289.65 | 0.2
0.08385 | 278.15 | 0.00115 | 289.65 | 0.3
0.08385 | 278.15 | 0.00115 | 289.65 | 0.4
0.08385 | 278.15 | 0.00115 | 289.65 | 0.5
0.08385 | 278.15 | 0.00115 | 289.65 | 0.6
0.08385 | 278.15 | 0.00115 | 289.65 | 0.7
0.08385 | 278.15 | 0.00115 | 289.65 | 0.8
0.08385 | 278.15 | 0.00115 | 289.65 | 0.9
0.08385 | 278.15 | 0.00115 | 289.65 | 1
0.08385 | 278.15 | 0.00115 | 290.15 | 0.15
0.08385 | 278.15 | 0.00115 | 290.15 | 0.2
0.08385 | 278.15 | 0.00115 | 290.15 | 0.3
0.08385 | 278.15 | 0.00115 | 290.15 | 0.4
0.08385 | 278.15 | 0.00115 | 290.15 | 0.5
0.08385 | 278.15 | 0.00115 | 290.15 | 0.6
0.08385 | 278.15 | 0.00115 | 290.15 | 0.7
0.08385 | 278.15 | 0.00115 | 290.15 | 0.8
0.08385 | 278.15 | 0.00115 | 290.15 | 0.9
0.08385 | 278.15 | 0.00115 | 290.15 | 1
0.08385 | 278.15 | 0.00115 | 290.65 | 0.15
0.08385 | 278.15 | 0.00115 | 290.65 | 0.2
0.08385 | 278.15 | 0.00115 | 290.65 | 0.3
0.08385 | 278.15 | 0.00115 | 290.65 | 0.4
0.08385 | 278.15 | 0.00115 | 290.65 | 0.5
0.08385 | 278.15 | 0.00115 | 290.65 | 0.6
0.08385 | 278.15 | 0.00115 | 290.65 | 0.7
0.08385 | 278.15 | 0.00115 | 290.65 | 0.8
0.08385 | 278.15 | 0.00115 | 290.65 | 0.9
0.08385 | 278.15 | 0.00115 | 290.65 | 1
0.08385 | 278.15 | 0.00115 | 291.15 | 0.15
0.08385 | 278.15 | 0.00115 | 291.15 | 0.2
0.08385 | 278.15 | 0.00115 | 291.15 | 0.3
0.08385 | 278.15 | 0.00115 | 291.15 | 0.4
0.08385 | 278.15 | 0.00115 | 291.15 | 0.5
0.08385 | 278.15 | 0.00115 | 291.15 | 0.6
0.08385 | 278.15 | 0.00115 | 291.15 | 0.7
0.08385 | 278.15 | 0.00115 | 291.15 | 0.8
0.08385 | 278.15 | 0.00115 | 291.15 | 0.9
0.08385 | 278.15 | 0.00115 | 291.15 | 1
0.08385 | 278.15 | 0.00115 | 294.15 | 0.15
0.08385 | 278.15 | 0.00115 | 294.15 | 0.2
0.08385 | 278.15 | 0.00115 | 294.15 | 0.3
0.08385 | 278.15 | 0.00115 | 294.15 | 0.4
0.08385 | 278.15 | 0.00115 | 294.15 | 0.5
0.08385 | 278.15 | 0.00115 | 294.15 | 0.6
0.08385 | 278.15 | 0.00115 | 294.15 | 0.7
0.08385 | 278.15 | 0.00115 | 294.15 | 0.8
0.08385 | 278.15 | 0.00115 | 294.15 | 0.9
0.08385 | 278.15 | 0.00115 | 294.15 | 1
0.08385 | 278.15 | 0.00115 | 297.15 | 0.15
0.08385 | 278.15 | 0.00115 | 297.15 | 0.2
0.08385 | 278.15 | 0.00115 | 297.15 | 0.3
0.08385 | 278.15 | 0.00115 | 297.15 | 0.4
0.08385 | 278.15 | 0.00115 | 297.15 | 0.5
0.08385 | 278.15 | 0.00115 | 297.15 | 0.6
0.08385 | 278.15 | 0.00115 | 297.15 | 0.7
0.08385 | 278.15 | 0.00115 | 297.15 | 0.8
0.08385 | 278.15 | 0.00115 | 297.15 | 0.9
0.08385 | 278.15 | 0.00115 | 297.15 | 1
0.08385 | 278.15 | 0.00115 | 300.15 | 0.15
0.08385 | 278.15 | 0.00115 | 300.15 | 0.2
0.08385 | 278.15 | 0.00115 | 300.15 | 0.3
0.08385 | 278.15 | 0.00115 | 300.15 | 0.4
0.08385 | 278.15 | 0.00115 | 300.15 | 0.5
0.08385 | 278.15 | 0.00115 | 300.15 | 0.6
0.08385 | 278.15 | 0.00115 | 300.15 | 0.7
0.08385 | 278.15 | 0.00115 | 300.15 | 0.8
0.08385 | 278.15 | 0.00115 | 300.15 | 0.9
0.08385 | 278.15 | 0.00115 | 300.15 | 1
0.08385 | 278.15 | 0.00115 | 303.15 | 0.15
0.08385 | 278.15 | 0.00115 | 303.15 | 0.2
0.08385 | 278.15 | 0.00115 | 303.15 | 0.3
0.08385 | 278.15 | 0.00115 | 303.15 | 0.4
0.08385 | 278.15 | 0.00115 | 303.15 | 0.5
0.08385 | 278.15 | 0.00115 | 303.15 | 0.6
0.08385 | 278.15 | 0.00115 | 303.15 | 0.7
0.08385 | 278.15 | 0.00115 | 303.15 | 0.8
0.08385 | 278.15 | 0.00115 | 303.15 | 0.9
0.08385 | 278.15 | 0.00115 | 303.15 | 1
0.08385 | 278.15 | 0.077 | 283.65 | 0.15
0.08385 | 278.15 | 0.077 | 283.65 | 0.2
0.08385 | 278.15 | 0.077 | 283.65 | 0.3
0.08385 | 278.15 | 0.077 | 283.65 | 0.4
0.08385 | 278.15 | 0.077 | 283.65 | 0.5
0.08385 | 278.15 | 0.077 | 283.65 | 0.6
0.08385 | 278.15 | 0.077 | 283.65 | 0.7
0.08385 | 278.15 | 0.077 | 283.65 | 0.8
0.08385 | 278.15 | 0.077 | 283.65 | 0.9
0.08385 | 278.15 | 0.077 | 283.65 | 1
0.08385 | 278.15 | 0.077 | 284.15 | 0.15
0.08385 | 278.15 | 0.077 | 284.15 | 0.2
0.08385 | 278.15 | 0.077 | 284.15 | 0.3
0.08385 | 278.15 | 0.077 | 284.15 | 0.4
0.08385 | 278.15 | 0.077 | 284.15 | 0.5
0.08385 | 278.15 | 0.077 | 284.15 | 0.6
0.08385 | 278.15 | 0.077 | 284.15 | 0.7
0.08385 | 278.15 | 0.077 | 284.15 | 0.8
0.08385 | 278.15 | 0.077 | 284.15 | 0.9
0.08385 | 278.15 | 0.077 | 284.15 | 1
0.08385 | 278.15 | 0.077 | 284.65 | 0.15
0.08385 | 278.15 | 0.077 | 284.65 | 0.2
0.08385 | 278.15 | 0.077 | 284.65 | 0.3
0.08385 | 278.15 | 0.077 | 284.65 | 0.4
0.08385 | 278.15 | 0.077 | 284.65 | 0.5
0.08385 | 278.15 | 0.077 | 284.65 | 0.6
0.08385 | 278.15 | 0.077 | 284.65 | 0.7
0.08385 | 278.15 | 0.077 | 284.65 | 0.8
0.08385 | 278.15 | 0.077 | 284.65 | 0.9
0.08385 | 278.15 | 0.077 | 284.65 | 1
0.08385 | 278.15 | 0.077 | 285.15 | 0.15
0.08385 | 278.15 | 0.077 | 285.15 | 0.2
0.08385 | 278.15 | 0.077 | 285.15 | 0.3
0.08385 | 278.15 | 0.077 | 285.15 | 0.4
0.08385 | 278.15 | 0.077 | 285.15 | 0.5
0.08385 | 278.15 | 0.077 | 285.15 | 0.6
0.08385 | 278.15 | 0.077 | 285.15 | 0.7
0.08385 | 278.15 | 0.077 | 285.15 | 0.8
0.08385 | 278.15 | 0.077 | 285.15 | 0.9
0.08385 | 278.15 | 0.077 | 285.15 | 1
0.08385 | 278.15 | 0.077 | 285.65 | 0.15
0.08385 | 278.15 | 0.077 | 285.65 | 0.2
0.08385 | 278.15 | 0.077 | 285.65 | 0.3
0.08385 | 278.15 | 0.077 | 285.65 | 0.4
0.08385 | 278.15 | 0.077 | 285.65 | 0.5
0.08385 | 278.15 | 0.077 | 285.65 | 0.6
0.08385 | 278.15 | 0.077 | 285.65 | 0.7
0.08385 | 278.15 | 0.077 | 285.65 | 0.8
0.08385 | 278.15 | 0.077 | 285.65 | 0.9
0.08385 | 278.15 | 0.077 | 285.65 | 1
0.08385 | 278.15 | 0.077 | 286.15 | 0.15
0.08385 | 278.15 | 0.077 | 286.15 | 0.2
0.08385 | 278.15 | 0.077 | 286.15 | 0.3
0.08385 | 278.15 | 0.077 | 286.15 | 0.4
0.08385 | 278.15 | 0.077 | 286.15 | 0.5
0.08385 | 278.15 | 0.077 | 286.15 | 0.6
0.08385 | 278.15 | 0.077 | 286.15 | 0.7
0.08385 | 278.15 | 0.077 | 286.15 | 0.8
0.08385 | 278.15 | 0.077 | 286.15 | 0.9
0.08385 | 278.15 | 0.077 | 286.15 | 1
0.08385 | 278.15 | 0.077 | 286.65 | 0.15
0.08385 | 278.15 | 0.077 | 286.65 | 0.2
0.08385 | 278.15 | 0.077 | 286.65 | 0.3
0.08385 | 278.15 | 0.077 | 286.65 | 0.4
0.08385 | 278.15 | 0.077 | 286.65 | 0.5
0.08385 | 278.15 | 0.077 | 286.65 | 0.6
0.08385 | 278.15 | 0.077 | 286.65 | 0.7
0.08385 | 278.15 | 0.077 | 286.65 | 0.8
0.08385 | 278.15 | 0.077 | 286.65 | 0.9
0.08385 | 278.15 | 0.077 | 286.65 | 1
0.08385 | 278.15 | 0.077 | 287.15 | 0.15
0.08385 | 278.15 | 0.077 | 287.15 | 0.2
0.08385 | 278.15 | 0.077 | 287.15 | 0.3
0.08385 | 278.15 | 0.077 | 287.15 | 0.4
0.08385 | 278.15 | 0.077 | 287.15 | 0.5
0.08385 | 278.15 | 0.077 | 287.15 | 0.6
0.08385 | 278.15 | 0.077 | 287.15 | 0.7
0.08385 | 278.15 | 0.077 | 287.15 | 0.8
0.08385 | 278.15 | 0.077 | 287.15 | 0.9
0.08385 | 278.15 | 0.077 | 287.15 | 1
0.08385 | 278.15 | 0.077 | 287.65 | 0.15
0.08385 | 278.15 | 0.077 | 287.65 | 0.2
0.08385 | 278.15 | 0.077 | 287.65 | 0.3
0.08385 | 278.15 | 0.077 | 287.65 | 0.4
0.08385 | 278.15 | 0.077 | 287.65 | 0.5
0.08385 | 278.15 | 0.077 | 287.65 | 0.6
0.08385 | 278.15 | 0.077 | 287.65 | 0.7
0.08385 | 278.15 | 0.077 | 287.65 | 0.8
0.08385 | 278.15 | 0.077 | 287.65 | 0.9
0.08385 | 278.15 | 0.077 | 287.65 | 1
0.08385 | 278.15 | 0.077 | 288.15 | 0.15
0.08385 | 278.15 | 0.077 | 288.15 | 0.2
0.08385 | 278.15 | 0.077 | 288.15 | 0.3
0.08385 | 278.15 | 0.077 | 288.15 | 0.4
0.08385 | 278.15 | 0.077 | 288.15 | 0.5
0.08385 | 278.15 | 0.077 | 288.15 | 0.6
0.08385 | 278.15 | 0.077 | 288.15 | 0.7
0.08385 | 278.15 | 0.077 | 288.15 | 0.8
0.08385 | 278.15 | 0.077 | 288.15 | 0.9
0.08385 | 278.15 | 0.077 | 288.15 | 1
0.08385 | 278.15 | 0.077 | 288.65 | 0.15
0.08385 | 278.15 | 0.077 | 288.65 | 0.2
0.08385 | 278.15 | 0.077 | 288.65 | 0.3
0.08385 | 278.15 | 0.077 | 288.65 | 0.4
0.08385 | 278.15 | 0.077 | 288.65 | 0.5
0.08385 | 278.15 | 0.077 | 288.65 | 0.6
0.08385 | 278.15 | 0.077 | 288.65 | 0.7
0.08385 | 278.15 | 0.077 | 288.65 | 0.8
0.08385 | 278.15 | 0.077 | 288.65 | 0.9
0.08385 | 278.15 | 0.077 | 288.65 | 1
0.08385 | 278.15 | 0.077 | 289.15 | 0.15
0.08385 | 278.15 | 0.077 | 289.15 | 0.2
0.08385 | 278.15 | 0.077 | 289.15 | 0.3
0.08385 | 278.15 | 0.077 | 289.15 | 0.4
0.08385 | 278.15 | 0.077 | 289.15 | 0.5
0.08385 | 278.15 | 0.077 | 289.15 | 0.6
0.08385 | 278.15 | 0.077 | 289.15 | 0.7
0.08385 | 278.15 | 0.077 | 289.15 | 0.8
0.08385 | 278.15 | 0.077 | 289.15 | 0.9
0.08385 | 278.15 | 0.077 | 289.15 | 1
0.08385 | 278.15 | 0.077 | 289.65 | 0.15
0.08385 | 278.15 | 0.077 | 289.65 | 0.2
0.08385 | 278.15 | 0.077 | 289.65 | 0.3
0.08385 | 278.15 | 0.077 | 289.65 | 0.4
0.08385 | 278.15 | 0.077 | 289.65 | 0.5
0.08385 | 278.15 | 0.077 | 289.65 | 0.6
0.08385 | 278.15 | 0.077 | 289.65 | 0.7
0.08385 | 278.15 | 0.077 | 289.65 | 0.8
0.08385 | 278.15 | 0.077 | 289.65 | 0.9
0.08385 | 278.15 | 0.077 | 289.65 | 1
0.08385 | 278.15 | 0.077 | 290.15 | 0.15
0.08385 | 278.15 | 0.077 | 290.15 | 0.2
0.08385 | 278.15 | 0.077 | 290.15 | 0.3
0.08385 | 278.15 | 0.077 | 290.15 | 0.4
0.08385 | 278.15 | 0.077 | 290.15 | 0.5
0.08385 | 278.15 | 0.077 | 290.15 | 0.6
0.08385 | 278.15 | 0.077 | 290.15 | 0.7
0.08385 | 278.15 | 0.077 | 290.15 | 0.8
0.08385 | 278.15 | 0.077 | 290.15 | 0.9
0.08385 | 278.15 | 0.077 | 290.15 | 1
0.08385 | 278.15 | 0.077 | 290.65 | 0.15
0.08385 | 278.15 | 0.077 | 290.65 | 0.2
0.08385 | 278.15 | 0.077 | 290.65 | 0.3
0.08385 | 278.15 | 0.077 | 290.65 | 0.4
0.08385 | 278.15 | 0.077 | 290.65 | 0.5
0.08385 | 278.15 | 0.077 | 290.65 | 0.6
0.08385 | 278.15 | 0.077 | 290.65 | 0.7
0.08385 | 278.15 | 0.077 | 290.65 | 0.8
0.08385 | 278.15 | 0.077 | 290.65 | 0.9
0.08385 | 278.15 | 0.077 | 290.65 | 1
0.08385 | 278.15 | 0.077 | 291.15 | 0.15
0.08385 | 278.15 | 0.077 | 291.15 | 0.2
0.08385 | 278.15 | 0.077 | 291.15 | 0.3
0.08385 | 278.15 | 0.077 | 291.15 | 0.4
0.08385 | 278.15 | 0.077 | 291.15 | 0.5
0.08385 | 278.15 | 0.077 | 291.15 | 0.6
0.08385 | 278.15 | 0.077 | 291.15 | 0.7
0.08385 | 278.15 | 0.077 | 291.15 | 0.8
0.08385 | 278.15 | 0.077 | 291.15 | 0.9
0.08385 | 278.15 | 0.077 | 291.15 | 1
0.08385 | 278.15 | 0.077 | 294.15 | 0.15
0.08385 | 278.15 | 0.077 | 294.15 | 0.2
0.08385 | 278.15 | 0.077 | 294.15 | 0.3
0.08385 | 278.15 | 0.077 | 294.15 | 0.4
0.08385 | 278.15 | 0.077 | 294.15 | 0.5
0.08385 | 278.15 | 0.077 | 294.15 | 0.6
0.08385 | 278.15 | 0.077 | 294.15 | 0.7
0.08385 | 278.15 | 0.077 | 294.15 | 0.8
0.08385 | 278.15 | 0.077 | 294.15 | 0.9
0.08385 | 278.15 | 0.077 | 294.15 | 1
0.08385 | 278.15 | 0.077 | 297.15 | 0.15
0.08385 | 278.15 | 0.077 | 297.15 | 0.2
0.08385 | 278.15 | 0.077 | 297.15 | 0.3
0.08385 | 278.15 | 0.077 | 297.15 | 0.4
0.08385 | 278.15 | 0.077 | 297.15 | 0.5
0.08385 | 278.15 | 0.077 | 297.15 | 0.6
0.08385 | 278.15 | 0.077 | 297.15 | 0.7
0.08385 | 278.15 | 0.077 | 297.15 | 0.8
0.08385 | 278.15 | 0.077 | 297.15 | 0.9
0.08385 | 278.15 | 0.077 | 297.15 | 1
0.08385 | 278.15 | 0.077 | 300.15 | 0.15
0.08385 | 278.15 | 0.077 | 300.15 | 0.2
0.08385 | 278.15 | 0.077 | 300.15 | 0.3
0.08385 | 278.15 | 0.077 | 300.15 | 0.4
0.08385 | 278.15 | 0.077 | 300.15 | 0.5
0.08385 | 278.15 | 0.077 | 300.15 | 0.6
0.08385 | 278.15 | 0.077 | 300.15 | 0.7
0.08385 | 278.15 | 0.077 | 300.15 | 0.8
0.08385 | 278.15 | 0.077 | 300.15 | 0.9
0.08385 | 278.15 | 0.077 | 300.15 | 1
0.08385 | 278.15 | 0.077 | 303.15 | 0.15
0.08385 | 278.15 | 0.077 | 303.15 | 0.2
0.08385 | 278.15 | 0.077 | 303.15 | 0.3
0.08385 | 278.15 | 0.077 | 303.15 | 0.4
0.08385 | 278.15 | 0.077 | 303.15 | 0.5
0.08385 | 278.15 | 0.077 | 303.15 | 0.6
0.08385 | 278.15 | 0.077 | 303.15 | 0.7
0.08385 | 278.15 | 0.077 | 303.15 | 0.8
0.08385 | 278.15 | 0.077 | 303.15 | 0.9
0.08385 | 278.15 | 0.077 | 303.15 | 1
0.08385 | 278.15 | 0.09437 | 283.65 | 0.15
0.08385 | 278.15 | 0.09437 | 283.65 | 0.2
0.08385 | 278.15 | 0.09437 | 283.65 | 0.3
0.08385 | 278.15 | 0.09437 | 283.65 | 0.4
0.08385 | 278.15 | 0.09437 | 283.65 | 0.5
0.08385 | 278.15 | 0.09437 | 283.65 | 0.6
0.08385 | 278.15 | 0.09437 | 283.65 | 0.7
0.08385 | 278.15 | 0.09437 | 283.65 | 0.8
0.08385 | 278.15 | 0.09437 | 283.65 | 0.9
0.08385 | 278.15 | 0.09437 | 283.65 | 1
0.08385 | 278.15 | 0.09437 | 284.15 | 0.15
0.08385 | 278.15 | 0.09437 | 284.15 | 0.2
0.08385 | 278.15 | 0.09437 | 284.15 | 0.3
0.08385 | 278.15 | 0.09437 | 284.15 | 0.4
0.08385 | 278.15 | 0.09437 | 284.15 | 0.5
0.08385 | 278.15 | 0.09437 | 284.15 | 0.6
0.08385 | 278.15 | 0.09437 | 284.15 | 0.7
0.08385 | 278.15 | 0.09437 | 284.15 | 0.8
0.08385 | 278.15 | 0.09437 | 284.15 | 0.9
0.08385 | 278.15 | 0.09437 | 284.15 | 1
0.08385 | 278.15 | 0.09437 | 284.65 | 0.15
0.08385 | 278.15 | 0.09437 | 284.65 | 0.2
0.08385 | 278.15 | 0.09437 | 284.65 | 0.3
0.08385 | 278.15 | 0.09437 | 284.65 | 0.4
0.08385 | 278.15 | 0.09437 | 284.65 | 0.5
0.08385 | 278.15 | 0.09437 | 284.65 | 0.6
0.08385 | 278.15 | 0.09437 | 284.65 | 0.7
0.08385 | 278.15 | 0.09437 | 284.65 | 0.8
0.08385 | 278.15 | 0.09437 | 284.65 | 0.9
0.08385 | 278.15 | 0.09437 | 284.65 | 1
0.08385 | 278.15 | 0.09437 | 285.15 | 0.15
0.08385 | 278.15 | 0.09437 | 285.15 | 0.2
0.08385 | 278.15 | 0.09437 | 285.15 | 0.3
0.08385 | 278.15 | 0.09437 | 285.15 | 0.4
0.08385 | 278.15 | 0.09437 | 285.15 | 0.5
0.08385 | 278.15 | 0.09437 | 285.15 | 0.6
0.08385 | 278.15 | 0.09437 | 285.15 | 0.7
0.08385 | 278.15 | 0.09437 | 285.15 | 0.8
0.08385 | 278.15 | 0.09437 | 285.15 | 0.9
0.08385 | 278.15 | 0.09437 | 285.15 | 1
0.08385 | 278.15 | 0.09437 | 285.65 | 0.15
0.08385 | 278.15 | 0.09437 | 285.65 | 0.2
0.08385 | 278.15 | 0.09437 | 285.65 | 0.3
0.08385 | 278.15 | 0.09437 | 285.65 | 0.4
0.08385 | 278.15 | 0.09437 | 285.65 | 0.5
0.08385 | 278.15 | 0.09437 | 285.65 | 0.6
0.08385 | 278.15 | 0.09437 | 285.65 | 0.7
0.08385 | 278.15 | 0.09437 | 285.65 | 0.8
0.08385 | 278.15 | 0.09437 | 285.65 | 0.9
0.08385 | 278.15 | 0.09437 | 285.65 | 1
0.08385 | 278.15 | 0.09437 | 286.15 | 0.15
0.08385 | 278.15 | 0.09437 | 286.15 | 0.2
0.08385 | 278.15 | 0.09437 | 286.15 | 0.3
0.08385 | 278.15 | 0.09437 | 286.15 | 0.4
0.08385 | 278.15 | 0.09437 | 286.15 | 0.5
0.08385 | 278.15 | 0.09437 | 286.15 | 0.6
0.08385 | 278.15 | 0.09437 | 286.15 | 0.7
0.08385 | 278.15 | 0.09437 | 286.15 | 0.8
0.08385 | 278.15 | 0.09437 | 286.15 | 0.9
0.08385 | 278.15 | 0.09437 | 286.15 | 1
0.08385 | 278.15 | 0.09437 | 286.65 | 0.15
0.08385 | 278.15 | 0.09437 | 286.65 | 0.2
0.08385 | 278.15 | 0.09437 | 286.65 | 0.3
0.08385 | 278.15 | 0.09437 | 286.65 | 0.4
0.08385 | 278.15 | 0.09437 | 286.65 | 0.5
0.08385 | 278.15 | 0.09437 | 286.65 | 0.6
0.08385 | 278.15 | 0.09437 | 286.65 | 0.7
0.08385 | 278.15 | 0.09437 | 286.65 | 0.8
0.08385 | 278.15 | 0.09437 | 286.65 | 0.9
0.08385 | 278.15 | 0.09437 | 286.65 | 1
0.08385 | 278.15 | 0.09437 | 287.15 | 0.15
0.08385 | 278.15 | 0.09437 | 287.15 | 0.2
0.08385 | 278.15 | 0.09437 | 287.15 | 0.3
0.08385 | 278.15 | 0.09437 | 287.15 | 0.4
0.08385 | 278.15 | 0.09437 | 287.15 | 0.5
0.08385 | 278.15 | 0.09437 | 287.15 | 0.6
0.08385 | 278.15 | 0.09437 | 287.15 | 0.7
0.08385 | 278.15 | 0.09437 | 287.15 | 0.8
0.08385 | 278.15 | 0.09437 | 287.15 | 0.9
0.08385 | 278.15 | 0.09437 | 287.15 | 1
0.08385 | 278.15 | 0.09437 | 287.65 | 0.15
0.08385 | 278.15 | 0.09437 | 287.65 | 0.2
0.08385 | 278.15 | 0.09437 | 287.65 | 0.3
0.08385 | 278.15 | 0.09437 | 287.65 | 0.4
0.08385 | 278.15 | 0.09437 | 287.65 | 0.5
0.08385 | 278.15 | 0.09437 | 287.65 | 0.6
0.08385 | 278.15 | 0.09437 | 287.65 | 0.7
0.08385 | 278.15 | 0.09437 | 287.65 | 0.8
0.08385 | 278.15 | 0.09437 | 287.65 | 0.9
0.08385 | 278.15 | 0.09437 | 287.65 | 1
0.08385 | 278.15 | 0.09437 | 288.15 | 0.15
0.08385 | 278.15 | 0.09437 | 288.15 | 0.2
0.08385 | 278.15 | 0.09437 | 288.15 | 0.3
0.08385 | 278.15 | 0.09437 | 288.15 | 0.4
0.08385 | 278.15 | 0.09437 | 288.15 | 0.5
0.08385 | 278.15 | 0.09437 | 288.15 | 0.6
0.08385 | 278.15 | 0.09437 | 288.15 | 0.7
0.08385 | 278.15 | 0.09437 | 288.15 | 0.8
0.08385 | 278.15 | 0.09437 | 288.15 | 0.9
0.08385 | 278.15 | 0.09437 | 288.15 | 1
0.08385 | 278.15 | 0.09437 | 288.65 | 0.15
0.08385 | 278.15 | 0.09437 | 288.65 | 0.2
0.08385 | 278.15 | 0.09437 | 288.65 | 0.3
0.08385 | 278.15 | 0.09437 | 288.65 | 0.4
0.08385 | 278.15 | 0.09437 | 288.65 | 0.5
0.08385 | 278.15 | 0.09437 | 288.65 | 0.6
0.08385 | 278.15 | 0.09437 | 288.65 | 0.7
0.08385 | 278.15 | 0.09437 | 288.65 | 0.8
0.08385 | 278.15 | 0.09437 | 288.65 | 0.9
0.08385 | 278.15 | 0.09437 | 288.65 | 1
0.08385 | 278.15 | 0.09437 | 289.15 | 0.15
0.08385 | 278.15 | 0.09437 | 289.15 | 0.2
0.08385 | 278.15 | 0.09437 | 289.15 | 0.3
0.08385 | 278.15 | 0.09437 | 289.15 | 0.4
0.08385 | 278.15 | 0.09437 | 289.15 | 0.5
0.08385 | 278.15 | 0.09437 | 289.15 | 0.6
0.08385 | 278.15 | 0.09437 | 289.15 | 0.7
0.08385 | 278.15 | 0.09437 | 289.15 | 0.8
0.08385 | 278.15 | 0.09437 | 289.15 | 0.9
0.08385 | 278.15 | 0.09437 | 289.15 | 1
0.08385 | 278.15 | 0.09437 | 289.65 | 0.15
0.08385 | 278.15 | 0.09437 | 289.65 | 0.2
0.08385 | 278.15 | 0.09437 | 289.65 | 0.3
0.08385 | 278.15 | 0.09437 | 289.65 | 0.4
0.08385 | 278.15 | 0.09437 | 289.65 | 0.5
0.08385 | 278.15 | 0.09437 | 289.65 | 0.6
0.08385 | 278.15 | 0.09437 | 289.65 | 0.7
0.08385 | 278.15 | 0.09437 | 289.65 | 0.8
0.08385 | 278.15 | 0.09437 | 289.65 | 0.9
0.08385 | 278.15 | 0.09437 | 289.65 | 1
0.08385 | 278.15 | 0.09437 | 290.15 | 0.15
0.08385 | 278.15 | 0.09437 | 290.15 | 0.2
0.08385 | 278.15 | 0.09437 | 290.15 | 0.3
0.08385 | 278.15 | 0.09437 | 290.15 | 0.4
0.08385 | 278.15 | 0.09437 | 290.15 | 0.5
0.08385 | 278.15 | 0.09437 | 290.15 | 0.6
0.08385 | 278.15 | 0.09437 | 290.15 | 0.7
0.08385 | 278.15 | 0.09437 | 290.15 | 0.8
0.08385 | 278.15 | 0.09437 | 290.15 | 0.9
0.08385 | 278.15 | 0.09437 | 290.15 | 1
0.08385 | 278.15 | 0.09437 | 290.65 | 0.15
0.08385 | 278.15 | 0.09437 | 290.65 | 0.2
0.08385 | 278.15 | 0.09437 | 290.65 | 0.3
0.08385 | 278.15 | 0.09437 | 290.65 | 0.4
0.08385 | 278.15 | 0.09437 | 290.65 | 0.5
0.08385 | 278.15 | 0.09437 | 290.65 | 0.6
0.08385 | 278.15 | 0.09437 | 290.65 | 0.7
0.08385 | 278.15 | 0.09437 | 290.65 | 0.8
0.08385 | 278.15 | 0.09437 | 290.65 | 0.9
0.08385 | 278.15 | 0.09437 | 290.65 | 1
0.08385 | 278.15 | 0.09437 | 291.15 | 0.15
0.08385 | 278.15 | 0.09437 | 291.15 | 0.2
0.08385 | 278.15 | 0.09437 | 291.15 | 0.3
0.08385 | 278.15 | 0.09437 | 291.15 | 0.4
0.08385 | 278.15 | 0.09437 | 291.15 | 0.5
0.08385 | 278.15 | 0.09437 | 291.15 | 0.6
0.08385 | 278.15 | 0.09437 | 291.15 | 0.7
0.08385 | 278.15 | 0.09437 | 291.15 | 0.8
0.08385 | 278.15 | 0.09437 | 291.15 | 0.9
0.08385 | 278.15 | 0.09437 | 291.15 | 1
0.08385 | 278.15 | 0.09437 | 294.15 | 0.15
0.08385 | 278.15 | 0.09437 | 294.15 | 0.2
0.08385 | 278.15 | 0.09437 | 294.15 | 0.3
0.08385 | 278.15 | 0.09437 | 294.15 | 0.4
0.08385 | 278.15 | 0.09437 | 294.15 | 0.5
0.08385 | 278.15 | 0.09437 | 294.15 | 0.6
0.08385 | 278.15 | 0.09437 | 294.15 | 0.7
0.08385 | 278.15 | 0.09437 | 294.15 | 0.8
0.08385 | 278.15 | 0.09437 | 294.15 | 0.9
0.08385 | 278.15 | 0.09437 | 294.15 | 1
0.08385 | 278.15 | 0.09437 | 297.15 | 0.15
0.08385 | 278.15 | 0.09437 | 297.15 | 0.2
0.08385 | 278.15 | 0.09437 | 297.15 | 0.3
0.08385 | 278.15 | 0.09437 | 297.15 | 0.4
0.08385 | 278.15 | 0.09437 | 297.15 | 0.5
0.08385 | 278.15 | 0.09437 | 297.15 | 0.6
0.08385 | 278.15 | 0.09437 | 297.15 | 0.7
0.08385 | 278.15 | 0.09437 | 297.15 | 0.8
0.08385 | 278.15 | 0.09437 | 297.15 | 0.9
0.08385 | 278.15 | 0.09437 | 297.15 | 1
0.08385 | 278.15 | 0.09437 | 300.15 | 0.15
0.08385 | 278.15 | 0.09437 | 300.15 | 0.2
0.08385 | 278.15 | 0.09437 | 300.15 | 0.3
0.08385 | 278.15 | 0.09437 | 300.15 | 0.4
0.08385 | 278.15 | 0.09437 | 300.15 | 0.5
0.08385 | 278.15 | 0.09437 | 300.15 | 0.6
0.08385 | 278.15 | 0.09437 | 300.15 | 0.7
0.08385 | 278.15 | 0.09437 | 300.15 | 0.8
0.08385 | 278.15 | 0.09437 | 300.15 | 0.9
0.08385 | 278.15 | 0.09437 | 300.15 | 1
0.08385 | 278.15 | 0.09437 | 303.15 | 0.15
0.08385 | 278.15 | 0.09437 | 303.15 | 0.2
0.08385 | 278.15 | 0.09437 | 303.15 | 0.3
0.08385 | 278.15 | 0.09437 | 303.15 | 0.4
0.08385 | 278.15 | 0.09437 | 303.15 | 0.5
0.08385 | 278.15 | 0.09437 | 303.15 | 0.6
0.08385 | 278.15 | 0.09437 | 303.15 | 0.7
0.08385 | 278.15 | 0.09437 | 303.15 | 0.8
0.08385 | 278.15 | 0.09437 | 303.15 | 0.9
0.08385 | 278.15 | 0.09437 | 303.15 | 1
0.08385 | 278.15 | 0.09644 | 283.65 | 0.15
0.08385 | 278.15 | 0.09644 | 283.65 | 0.2
0.08385 | 278.15 | 0.09644 | 283.65 | 0.3
0.08385 | 278.15 | 0.09644 | 283.65 | 0.4
0.08385 | 278.15 | 0.09644 | 283.65 | 0.5
0.08385 | 278.15 | 0.09644 | 283.65 | 0.6
0.08385 | 278.15 | 0.09644 | 283.65 | 0.7
0.08385 | 278.15 | 0.09644 | 283.65 | 0.8
0.08385 | 278.15 | 0.09644 | 283.65 | 0.9
0.08385 | 278.15 | 0.09644 | 283.65 | 1
0.08385 | 278.15 | 0.09644 | 284.15 | 0.15
0.08385 | 278.15 | 0.09644 | 284.15 | 0.2
0.08385 | 278.15 | 0.09644 | 284.15 | 0.3
0.08385 | 278.15 | 0.09644 | 284.15 | 0.4
0.08385 | 278.15 | 0.09644 | 284.15 | 0.5
0.08385 | 278.15 | 0.09644 | 284.15 | 0.6
0.08385 | 278.15 | 0.09644 | 284.15 | 0.7
0.08385 | 278.15 | 0.09644 | 284.15 | 0.8
0.08385 | 278.15 | 0.09644 | 284.15 | 0.9
0.08385 | 278.15 | 0.09644 | 284.15 | 1
0.08385 | 278.15 | 0.09644 | 284.65 | 0.15
0.08385 | 278.15 | 0.09644 | 284.65 | 0.2
0.08385 | 278.15 | 0.09644 | 284.65 | 0.3
0.08385 | 278.15 | 0.09644 | 284.65 | 0.4
0.08385 | 278.15 | 0.09644 | 284.65 | 0.5
0.08385 | 278.15 | 0.09644 | 284.65 | 0.6
0.08385 | 278.15 | 0.09644 | 284.65 | 0.7
0.08385 | 278.15 | 0.09644 | 284.65 | 0.8
0.08385 | 278.15 | 0.09644 | 284.65 | 0.9
0.08385 | 278.15 | 0.09644 | 284.65 | 1
0.08385 | 278.15 | 0.09644 | 285.15 | 0.15
0.08385 | 278.15 | 0.09644 | 285.15 | 0.2
0.08385 | 278.15 | 0.09644 | 285.15 | 0.3
0.08385 | 278.15 | 0.09644 | 285.15 | 0.4
0.08385 | 278.15 | 0.09644 | 285.15 | 0.5
0.08385 | 278.15 | 0.09644 | 285.15 | 0.6
0.08385 | 278.15 | 0.09644 | 285.15 | 0.7
0.08385 | 278.15 | 0.09644 | 285.15 | 0.8
0.08385 | 278.15 | 0.09644 | 285.15 | 0.9
0.08385 | 278.15 | 0.09644 | 285.15 | 1
0.08385 | 278.15 | 0.09644 | 285.65 | 0.15
0.08385 | 278.15 | 0.09644 | 285.65 | 0.2
0.08385 | 278.15 | 0.09644 | 285.65 | 0.3
0.08385 | 278.15 | 0.09644 | 285.65 | 0.4
0.08385 | 278.15 | 0.09644 | 285.65 | 0.5
0.08385 | 278.15 | 0.09644 | 285.65 | 0.6
0.08385 | 278.15 | 0.09644 | 285.65 | 0.7
0.08385 | 278.15 | 0.09644 | 285.65 | 0.8
0.08385 | 278.15 | 0.09644 | 285.65 | 0.9
0.08385 | 278.15 | 0.09644 | 285.65 | 1
0.08385 | 278.15 | 0.09644 | 286.15 | 0.15
0.08385 | 278.15 | 0.09644 | 286.15 | 0.2
0.08385 | 278.15 | 0.09644 | 286.15 | 0.3
0.08385 | 278.15 | 0.09644 | 286.15 | 0.4
0.08385 | 278.15 | 0.09644 | 286.15 | 0.5
0.08385 | 278.15 | 0.09644 | 286.15 | 0.6
0.08385 | 278.15 | 0.09644 | 286.15 | 0.7
0.08385 | 278.15 | 0.09644 | 286.15 | 0.8
0.08385 | 278.15 | 0.09644 | 286.15 | 0.9
0.08385 | 278.15 | 0.09644 | 286.15 | 1
0.08385 | 278.15 | 0.09644 | 286.65 | 0.15
0.08385 | 278.15 | 0.09644 | 286.65 | 0.2
0.08385 | 278.15 | 0.09644 | 286.65 | 0.3
0.08385 | 278.15 | 0.09644 | 286.65 | 0.4
0.08385 | 278.15 | 0.09644 | 286.65 | 0.5
0.08385 | 278.15 | 0.09644 | 286.65 | 0.6
0.08385 | 278.15 | 0.09644 | 286.65 | 0.7
0.08385 | 278.15 | 0.09644 | 286.65 | 0.8
0.08385 | 278.15 | 0.09644 | 286.65 | 0.9
0.08385 | 278.15 | 0.09644 | 286.65 | 1
0.08385 | 278.15 | 0.09644 | 287.15 | 0.15
0.08385 | 278.15 | 0.09644 | 287.15 | 0.2
0.08385 | 278.15 | 0.09644 | 287.15 | 0.3
0.08385 | 278.15 | 0.09644 | 287.15 | 0.4
0.08385 | 278.15 | 0.09644 | 287.15 | 0.5
0.08385 | 278.15 | 0.09644 | 287.15 | 0.6
0.08385 | 278.15 | 0.09644 | 287.15 | 0.7
0.08385 | 278.15 | 0.09644 | 287.15 | 0.8
0.08385 | 278.15 | 0.09644 | 287.15 | 0.9
0.08385 | 278.15 | 0.09644 | 287.15 | 1
0.08385 | 278.15 | 0.09644 | 287.65 | 0.15
0.08385 | 278.15 | 0.09644 | 287.65 | 0.2
0.08385 | 278.15 | 0.09644 | 287.65 | 0.3
0.08385 | 278.15 | 0.09644 | 287.65 | 0.4
0.08385 | 278.15 | 0.09644 | 287.65 | 0.5
0.08385 | 278.15 | 0.09644 | 287.65 | 0.6
0.08385 | 278.15 | 0.09644 | 287.65 | 0.7
0.08385 | 278.15 | 0.09644 | 287.65 | 0.8
0.08385 | 278.15 | 0.09644 | 287.65 | 0.9
0.08385 | 278.15 | 0.09644 | 287.65 | 1
0.08385 | 278.15 | 0.09644 | 288.15 | 0.15
0.08385 | 278.15 | 0.09644 | 288.15 | 0.2
0.08385 | 278.15 | 0.09644 | 288.15 | 0.3
0.08385 | 278.15 | 0.09644 | 288.15 | 0.4
0.08385 | 278.15 | 0.09644 | 288.15 | 0.5
0.08385 | 278.15 | 0.09644 | 288.15 | 0.6
0.08385 | 278.15 | 0.09644 | 288.15 | 0.7
0.08385 | 278.15 | 0.09644 | 288.15 | 0.8
0.08385 | 278.15 | 0.09644 | 288.15 | 0.9
0.08385 | 278.15 | 0.09644 | 288.15 | 1
0.08385 | 278.15 | 0.09644 | 288.65 | 0.15
0.08385 | 278.15 | 0.09644 | 288.65 | 0.2
0.08385 | 278.15 | 0.09644 | 288.65 | 0.3
0.08385 | 278.15 | 0.09644 | 288.65 | 0.4
0.08385 | 278.15 | 0.09644 | 288.65 | 0.5
0.08385 | 278.15 | 0.09644 | 288.65 | 0.6
0.08385 | 278.15 | 0.09644 | 288.65 | 0.7
0.08385 | 278.15 | 0.09644 | 288.65 | 0.8
0.08385 | 278.15 | 0.09644 | 288.65 | 0.9
0.08385 | 278.15 | 0.09644 | 288.65 | 1
0.08385 | 278.15 | 0.09644 | 289.15 | 0.15
0.08385 | 278.15 | 0.09644 | 289.15 | 0.2
0.08385 | 278.15 | 0.09644 | 289.15 | 0.3
0.08385 | 278.15 | 0.09644 | 289.15 | 0.4
0.08385 | 278.15 | 0.09644 | 289.15 | 0.5
0.08385 | 278.15 | 0.09644 | 289.15 | 0.6
0.08385 | 278.15 | 0.09644 | 289.15 | 0.7
0.08385 | 278.15 | 0.09644 | 289.15 | 0.8
0.08385 | 278.15 | 0.09644 | 289.15 | 0.9
0.08385 | 278.15 | 0.09644 | 289.15 | 1
0.08385 | 278.15 | 0.09644 | 289.65 | 0.15
0.08385 | 278.15 | 0.09644 | 289.65 | 0.2
0.08385 | 278.15 | 0.09644 | 289.65 | 0.3
0.08385 | 278.15 | 0.09644 | 289.65 | 0.4
0.08385 | 278.15 | 0.09644 | 289.65 | 0.5
0.08385 | 278.15 | 0.09644 | 289.65 | 0.6
0.08385 | 278.15 | 0.09644 | 289.65 | 0.7
0.08385 | 278.15 | 0.09644 | 289.65 | 0.8
0.08385 | 278.15 | 0.09644 | 289.65 | 0.9
0.08385 | 278.15 | 0.09644 | 289.65 | 1
0.08385 | 278.15 | 0.09644 | 290.15 | 0.15
0.08385 | 278.15 | 0.09644 | 290.15 | 0.2
0.08385 | 278.15 | 0.09644 | 290.15 | 0.3
0.08385 | 278.15 | 0.09644 | 290.15 | 0.4
0.08385 | 278.15 | 0.09644 | 290.15 | 0.5
0.08385 | 278.15 | 0.09644 | 290.15 | 0.6
0.08385 | 278.15 | 0.09644 | 290.15 | 0.7
0.08385 | 278.15 | 0.09644 | 290.15 | 0.8
0.08385 | 278.15 | 0.09644 | 290.15 | 0.9
0.08385 | 278.15 | 0.09644 | 290.15 | 1
0.08385 | 278.15 | 0.09644 | 290.65 | 0.15
0.08385 | 278.15 | 0.09644 | 290.65 | 0.2
0.08385 | 278.15 | 0.09644 | 290.65 | 0.3
0.08385 | 278.15 | 0.09644 | 290.65 | 0.4
0.08385 | 278.15 | 0.09644 | 290.65 | 0.5
0.08385 | 278.15 | 0.09644 | 290.65 | 0.6
0.08385 | 278.15 | 0.09644 | 290.65 | 0.7
0.08385 | 278.15 | 0.09644 | 290.65 | 0.8
0.08385 | 278.15 | 0.09644 | 290.65 | 0.9
0.08385 | 278.15 | 0.09644 | 290.65 | 1
0.08385 | 278.15 | 0.09644 | 291.15 | 0.15
0.08385 | 278.15 | 0.09644 | 291.15 | 0.2
0.08385 | 278.15 | 0.09644 | 291.15 | 0.3
0.08385 | 278.15 | 0.09644 | 291.15 | 0.4
0.08385 | 278.15 | 0.09644 | 291.15 | 0.5
0.08385 | 278.15 | 0.09644 | 291.15 | 0.6
0.08385 | 278.15 | 0.09644 | 291.15 | 0.7
0.08385 | 278.15 | 0.09644 | 291.15 | 0.8
0.08385 | 278.15 | 0.09644 | 291.15 | 0.9
0.08385 | 278.15 | 0.09644 | 291.15 | 1
0.08385 | 278.15 | 0.09644 | 294.15 | 0.15
0.08385 | 278.15 | 0.09644 | 294.15 | 0.2
0.08385 | 278.15 | 0.09644 | 294.15 | 0.3
0.08385 | 278.15 | 0.09644 | 294.15 | 0.4
0.08385 | 278.15 | 0.09644 | 294.15 | 0.5
0.08385 | 278.15 | 0.09644 | 294.15 | 0.6
0.08385 | 278.15 | 0.09644 | 294.15 | 0.7
0.08385 | 278.15 | 0.09644 | 294.15 | 0.8
0.08385 | 278.15 | 0.09644 | 294.15 | 0.9
0.08385 | 278.15 | 0.09644 | 294.15 | 1
0.08385 | 278.15 | 0.09644 | 297.15 | 0.15
0.08385 | 278.15 | 0.09644 | 297.15 | 0.2
0.08385 | 278.15 | 0.09644 | 297.15 | 0.3
0.08385 | 278.15 | 0.09644 | 297.15 | 0.4
0.08385 | 278.15 | 0.09644 | 297.15 | 0.5
0.08385 | 278.15 | 0.09644 | 297.15 | 0.6
0.08385 | 278.15 | 0.09644 | 297.15 | 0.7
0.08385 | 278.15 | 0.09644 | 297.15 | 0.8
0.08385 | 278.15 | 0.09644 | 297.15 | 0.9
0.08385 | 278.15 | 0.09644 | 297.15 | 1
0.08385 | 278.15 | 0.09644 | 300.15 | 0.15
0.08385 | 278.15 | 0.09644 | 300.15 | 0.2
0.08385 | 278.15 | 0.09644 | 300.15 | 0.3
0.08385 | 278.15 | 0.09644 | 300.15 | 0.4
0.08385 | 278.15 | 0.09644 | 300.15 | 0.5
0.08385 | 278.15 | 0.09644 | 300.15 | 0.6
0.08385 | 278.15 | 0.09644 | 300.15 | 0.7
0.08385 | 278.15 | 0.09644 | 300.15 | 0.8
0.08385 | 278.15 | 0.09644 | 300.15 | 0.9
0.08385 | 278.15 | 0.09644 | 300.15 | 1
0.08385 | 278.15 | 0.09644 | 303.15 | 0.15
0.08385 | 278.15 | 0.09644 | 303.15 | 0.2
0.08385 | 278.15 | 0.09644 | 303.15 | 0.3
0.08385 | 278.15 | 0.09644 | 303.15 | 0.4
0.08385 | 278.15 | 0.09644 | 303.15 | 0.5
0.08385 | 278.15 | 0.09644 | 303.15 | 0.6
0.08385 | 278.15 | 0.09644 | 303.15 | 0.7
0.08385 | 278.15 | 0.09644 | 303.15 | 0.8
0.08385 | 278.15 | 0.09644 | 303.15 | 0.9
0.08385 | 278.15 | 0.09644 | 303.15 | 1
0.08385 | 278.15 | 0.09737 | 283.65 | 0.15
0.08385 | 278.15 | 0.09737 | 283.65 | 0.2
0.08385 | 278.15 | 0.09737 | 283.65 | 0.3
0.08385 | 278.15 | 0.09737 | 283.65 | 0.4
0.08385 | 278.15 | 0.09737 | 283.65 | 0.5
0.08385 | 278.15 | 0.09737 | 283.65 | 0.6
0.08385 | 278.15 | 0.09737 | 283.65 | 0.7
0.08385 | 278.15 | 0.09737 | 283.65 | 0.8
0.08385 | 278.15 | 0.09737 | 283.65 | 0.9
0.08385 | 278.15 | 0.09737 | 283.65 | 1
0.08385 | 278.15 | 0.09737 | 284.15 | 0.15
0.08385 | 278.15 | 0.09737 | 284.15 | 0.2
0.08385 | 278.15 | 0.09737 | 284.15 | 0.3
0.08385 | 278.15 | 0.09737 | 284.15 | 0.4
0.08385 | 278.15 | 0.09737 | 284.15 | 0.5
0.08385 | 278.15 | 0.09737 | 284.15 | 0.6
0.08385 | 278.15 | 0.09737 | 284.15 | 0.7
0.08385 | 278.15 | 0.09737 | 284.15 | 0.8
0.08385 | 278.15 | 0.09737 | 284.15 | 0.9
0.08385 | 278.15 | 0.09737 | 284.15 | 1
0.08385 | 278.15 | 0.09737 | 284.65 | 0.15
0.08385 | 278.15 | 0.09737 | 284.65 | 0.2
0.08385 | 278.15 | 0.09737 | 284.65 | 0.3
0.08385 | 278.15 | 0.09737 | 284.65 | 0.4
0.08385 | 278.15 | 0.09737 | 284.65 | 0.5
0.08385 | 278.15 | 0.09737 | 284.65 | 0.6
0.08385 | 278.15 | 0.09737 | 284.65 | 0.7
0.08385 | 278.15 | 0.09737 | 284.65 | 0.8
0.08385 | 278.15 | 0.09737 | 284.65 | 0.9
0.08385 | 278.15 | 0.09737 | 284.65 | 1
0.08385 | 278.15 | 0.09737 | 285.15 | 0.15
0.08385 | 278.15 | 0.09737 | 285.15 | 0.2
0.08385 | 278.15 | 0.09737 | 285.15 | 0.3
0.08385 | 278.15 | 0.09737 | 285.15 | 0.4
0.08385 | 278.15 | 0.09737 | 285.15 | 0.5
0.08385 | 278.15 | 0.09737 | 285.15 | 0.6
0.08385 | 278.15 | 0.09737 | 285.15 | 0.7
0.08385 | 278.15 | 0.09737 | 285.15 | 0.8
0.08385 | 278.15 | 0.09737 | 285.15 | 0.9
0.08385 | 278.15 | 0.09737 | 285.15 | 1
0.08385 | 278.15 | 0.09737 | 285.65 | 0.15
0.08385 | 278.15 | 0.09737 | 285.65 | 0.2
0.08385 | 278.15 | 0.09737 | 285.65 | 0.3
0.08385 | 278.15 | 0.09737 | 285.65 | 0.4
0.08385 | 278.15 | 0.09737 | 285.65 | 0.5
0.08385 | 278.15 | 0.09737 | 285.65 | 0.6
0.08385 | 278.15 | 0.09737 | 285.65 | 0.7
0.08385 | 278.15 | 0.09737 | 285.65 | 0.8
0.08385 | 278.15 | 0.09737 | 285.65 | 0.9
0.08385 | 278.15 | 0.09737 | 285.65 | 1
0.08385 | 278.15 | 0.09737 | 286.15 | 0.15
0.08385 | 278.15 | 0.09737 | 286.15 | 0.2
0.08385 | 278.15 | 0.09737 | 286.15 | 0.3
0.08385 | 278.15 | 0.09737 | 286.15 | 0.4
0.08385 | 278.15 | 0.09737 | 286.15 | 0.5
0.08385 | 278.15 | 0.09737 | 286.15 | 0.6
0.08385 | 278.15 | 0.09737 | 286.15 | 0.7
0.08385 | 278.15 | 0.09737 | 286.15 | 0.8
0.08385 | 278.15 | 0.09737 | 286.15 | 0.9
0.08385 | 278.15 | 0.09737 | 286.15 | 1
0.08385 | 278.15 | 0.09737 | 286.65 | 0.15
0.08385 | 278.15 | 0.09737 | 286.65 | 0.2
0.08385 | 278.15 | 0.09737 | 286.65 | 0.3
0.08385 | 278.15 | 0.09737 | 286.65 | 0.4
0.08385 | 278.15 | 0.09737 | 286.65 | 0.5
0.08385 | 278.15 | 0.09737 | 286.65 | 0.6
0.08385 | 278.15 | 0.09737 | 286.65 | 0.7
0.08385 | 278.15 | 0.09737 | 286.65 | 0.8
0.08385 | 278.15 | 0.09737 | 286.65 | 0.9
0.08385 | 278.15 | 0.09737 | 286.65 | 1
0.08385 | 278.15 | 0.09737 | 287.15 | 0.15
0.08385 | 278.15 | 0.09737 | 287.15 | 0.2
0.08385 | 278.15 | 0.09737 | 287.15 | 0.3
0.08385 | 278.15 | 0.09737 | 287.15 | 0.4
0.08385 | 278.15 | 0.09737 | 287.15 | 0.5
0.08385 | 278.15 | 0.09737 | 287.15 | 0.6
0.08385 | 278.15 | 0.09737 | 287.15 | 0.7
0.08385 | 278.15 | 0.09737 | 287.15 | 0.8
0.08385 | 278.15 | 0.09737 | 287.15 | 0.9
0.08385 | 278.15 | 0.09737 | 287.15 | 1
0.08385 | 278.15 | 0.09737 | 287.65 | 0.15
0.08385 | 278.15 | 0.09737 | 287.65 | 0.2
0.08385 | 278.15 | 0.09737 | 287.65 | 0.3
0.08385 | 278.15 | 0.09737 | 287.65 | 0.4
0.08385 | 278.15 | 0.09737 | 287.65 | 0.5
0.08385 | 278.15 | 0.09737 | 287.65 | 0.6
0.08385 | 278.15 | 0.09737 | 287.65 | 0.7
0.08385 | 278.15 | 0.09737 | 287.65 | 0.8
0.08385 | 278.15 | 0.09737 | 287.65 | 0.9
0.08385 | 278.15 | 0.09737 | 287.65 | 1
0.08385 | 278.15 | 0.09737 | 288.15 | 0.15
0.08385 | 278.15 | 0.09737 | 288.15 | 0.2
0.08385 | 278.15 | 0.09737 | 288.15 | 0.3
0.08385 | 278.15 | 0.09737 | 288.15 | 0.4
0.08385 | 278.15 | 0.09737 | 288.15 | 0.5
0.08385 | 278.15 | 0.09737 | 288.15 | 0.6
0.08385 | 278.15 | 0.09737 | 288.15 | 0.7
0.08385 | 278.15 | 0.09737 | 288.15 | 0.8
0.08385 | 278.15 | 0.09737 | 288.15 | 0.9
0.08385 | 278.15 | 0.09737 | 288.15 | 1
0.08385 | 278.15 | 0.09737 | 288.65 | 0.15
0.08385 | 278.15 | 0.09737 | 288.65 | 0.2
0.08385 | 278.15 | 0.09737 | 288.65 | 0.3
0.08385 | 278.15 | 0.09737 | 288.65 | 0.4
0.08385 | 278.15 | 0.09737 | 288.65 | 0.5
0.08385 | 278.15 | 0.09737 | 288.65 | 0.6
0.08385 | 278.15 | 0.09737 | 288.65 | 0.7
0.08385 | 278.15 | 0.09737 | 288.65 | 0.8
0.08385 | 278.15 | 0.09737 | 288.65 | 0.9
0.08385 | 278.15 | 0.09737 | 288.65 | 1
0.08385 | 278.15 | 0.09737 | 289.15 | 0.15
0.08385 | 278.15 | 0.09737 | 289.15 | 0.2
0.08385 | 278.15 | 0.09737 | 289.15 | 0.3
0.08385 | 278.15 | 0.09737 | 289.15 | 0.4
0.08385 | 278.15 | 0.09737 | 289.15 | 0.5
0.08385 | 278.15 | 0.09737 | 289.15 | 0.6
0.08385 | 278.15 | 0.09737 | 289.15 | 0.7
0.08385 | 278.15 | 0.09737 | 289.15 | 0.8
0.08385 | 278.15 | 0.09737 | 289.15 | 0.9
0.08385 | 278.15 | 0.09737 | 289.15 | 1
0.08385 | 278.15 | 0.09737 | 289.65 | 0.15
0.08385 | 278.15 | 0.09737 | 289.65 | 0.2
0.08385 | 278.15 | 0.09737 | 289.65 | 0.3
0.08385 | 278.15 | 0.09737 | 289.65 | 0.4
0.08385 | 278.15 | 0.09737 | 289.65 | 0.5
0.08385 | 278.15 | 0.09737 | 289.65 | 0.6
0.08385 | 278.15 | 0.09737 | 289.65 | 0.7
0.08385 | 278.15 | 0.09737 | 289.65 | 0.8
0.08385 | 278.15 | 0.09737 | 289.65 | 0.9
0.08385 | 278.15 | 0.09737 | 289.65 | 1
0.08385 | 278.15 | 0.09737 | 290.15 | 0.15
0.08385 | 278.15 | 0.09737 | 290.15 | 0.2
0.08385 | 278.15 | 0.09737 | 290.15 | 0.3
0.08385 | 278.15 | 0.09737 | 290.15 | 0.4
0.08385 | 278.15 | 0.09737 | 290.15 | 0.5
0.08385 | 278.15 | 0.09737 | 290.15 | 0.6
0.08385 | 278.15 | 0.09737 | 290.15 | 0.7
0.08385 | 278.15 | 0.09737 | 290.15 | 0.8
0.08385 | 278.15 | 0.09737 | 290.15 | 0.9
0.08385 | 278.15 | 0.09737 | 290.15 | 1
0.08385 | 278.15 | 0.09737 | 290.65 | 0.15
0.08385 | 278.15 | 0.09737 | 290.65 | 0.2
0.08385 | 278.15 | 0.09737 | 290.65 | 0.3
0.08385 | 278.15 | 0.09737 | 290.65 | 0.4
0.08385 | 278.15 | 0.09737 | 290.65 | 0.5
0.08385 | 278.15 | 0.09737 | 290.65 | 0.6
0.08385 | 278.15 | 0.09737 | 290.65 | 0.7
0.08385 | 278.15 | 0.09737 | 290.65 | 0.8
0.08385 | 278.15 | 0.09737 | 290.65 | 0.9
0.08385 | 278.15 | 0.09737 | 290.65 | 1
0.08385 | 278.15 | 0.09737 | 291.15 | 0.15
0.08385 | 278.15 | 0.09737 | 291.15 | 0.2
0.08385 | 278.15 | 0.09737 | 291.15 | 0.3
0.08385 | 278.15 | 0.09737 | 291.15 | 0.4
0.08385 | 278.15 | 0.09737 | 291.15 | 0.5
0.08385 | 278.15 | 0.09737 | 291.15 | 0.6
0.08385 | 278.15 | 0.09737 | 291.15 | 0.7
0.08385 | 278.15 | 0.09737 | 291.15 | 0.8
0.08385 | 278.15 | 0.09737 | 291.15 | 0.9
0.08385 | 278.15 | 0.09737 | 291.15 | 1
0.08385 | 278.15 | 0.09737 | 294.15 | 0.15
0.08385 | 278.15 | 0.09737 | 294.15 | 0.2
0.08385 | 278.15 | 0.09737 | 294.15 | 0.3
0.08385 | 278.15 | 0.09737 | 294.15 | 0.4
0.08385 | 278.15 | 0.09737 | 294.15 | 0.5
0.08385 | 278.15 | 0.09737 | 294.15 | 0.6
0.08385 | 278.15 | 0.09737 | 294.15 | 0.7
0.08385 | 278.15 | 0.09737 | 294.15 | 0.8
0.08385 | 278.15 | 0.09737 | 294.15 | 0.9
0.08385 | 278.15 | 0.09737 | 294.15 | 1
0.08385 | 278.15 | 0.09737 | 297.15 | 0.15
0.08385 | 278.15 | 0.09737 | 297.15 | 0.2
0.08385 | 278.15 | 0.09737 | 297.15 | 0.3
0.08385 | 278.15 | 0.09737 | 297.15 | 0.4
0.08385 | 278.15 | 0.09737 | 297.15 | 0.5
0.08385 | 278.15 | 0.09737 | 297.15 | 0.6
0.08385 | 278.15 | 0.09737 | 297.15 | 0.7
0.08385 | 278.15 | 0.09737 | 297.15 | 0.8
0.08385 | 278.15 | 0.09737 | 297.15 | 0.9
0.08385 | 278.15 | 0.09737 | 297.15 | 1
0.08385 | 278.15 | 0.09737 | 300.15 | 0.15
0.08385 | 278.15 | 0.09737 | 300.15 | 0.2
0.08385 | 278.15 | 0.09737 | 300.15 | 0.3
0.08385 | 278.15 | 0.09737 | 300.15 | 0.4
0.08385 | 278.15 | 0.09737 | 300.15 | 0.5
0.08385 | 278.15 | 0.09737 | 300.15 | 0.6
0.08385 | 278.15 | 0.09737 | 300.15 | 0.7
0.08385 | 278.15 | 0.09737 | 300.15 | 0.8
0.08385 | 278.15 | 0.09737 | 300.15 | 0.9
0.08385 | 278.15 | 0.09737 | 300.15 | 1
0.08385 | 278.15 | 0.09737 | 303.15 | 0.15
0.08385 | 278.15 | 0.09737 | 303.15 | 0.2
0.08385 | 278.15 | 0.09737 | 303.15 | 0.3
0.08385 | 278.15 | 0.09737 | 303.15 | 0.4
0.08385 | 278.15 | 0.09737 | 303.15 | 0.5
0.08385 | 278.15 | 0.09737 | 303.15 | 0.6
0.08385 | 278.15 | 0.09737 | 303.15 | 0.7
0.08385 | 278.15 | 0.09737 | 303.15 | 0.8
0.08385 | 278.15 | 0.09737 | 303.15 | 0.9
0.08385 | 278.15 | 0.09737 | 303.15 | 1
0.08385 | 278.15 | 0.115 | 283.65 | 0.15
0.08385 | 278.15 | 0.115 | 283.65 | 0.2
0.08385 | 278.15 | 0.115 | 283.65 | 0.3
0.08385 | 278.15 | 0.115 | 283.65 | 0.4
0.08385 | 278.15 | 0.115 | 283.65 | 0.5
0.08385 | 278.15 | 0.115 | 283.65 | 0.6
0.08385 | 278.15 | 0.115 | 283.65 | 0.7
0.08385 | 278.15 | 0.115 | 283.65 | 0.8
0.08385 | 278.15 | 0.115 | 283.65 | 0.9
0.08385 | 278.15 | 0.115 | 283.65 | 1
0.08385 | 278.15 | 0.115 | 284.15 | 0.15
0.08385 | 278.15 | 0.115 | 284.15 | 0.2
0.08385 | 278.15 | 0.115 | 284.15 | 0.3
0.08385 | 278.15 | 0.115 | 284.15 | 0.4
0.08385 | 278.15 | 0.115 | 284.15 | 0.5
0.08385 | 278.15 | 0.115 | 284.15 | 0.6
0.08385 | 278.15 | 0.115 | 284.15 | 0.7
0.08385 | 278.15 | 0.115 | 284.15 | 0.8
0.08385 | 278.15 | 0.115 | 284.15 | 0.9
0.08385 | 278.15 | 0.115 | 284.15 | 1
0.08385 | 278.15 | 0.115 | 284.65 | 0.15
0.08385 | 278.15 | 0.115 | 284.65 | 0.2
0.08385 | 278.15 | 0.115 | 284.65 | 0.3
0.08385 | 278.15 | 0.115 | 284.65 | 0.4
0.08385 | 278.15 | 0.115 | 284.65 | 0.5
0.08385 | 278.15 | 0.115 | 284.65 | 0.6
0.08385 | 278.15 | 0.115 | 284.65 | 0.7
0.08385 | 278.15 | 0.115 | 284.65 | 0.8
0.08385 | 278.15 | 0.115 | 284.65 | 0.9
0.08385 | 278.15 | 0.115 | 284.65 | 1
0.08385 | 278.15 | 0.115 | 285.15 | 0.15
0.08385 | 278.15 | 0.115 | 285.15 | 0.2
0.08385 | 278.15 | 0.115 | 285.15 | 0.3
0.08385 | 278.15 | 0.115 | 285.15 | 0.4
0.08385 | 278.15 | 0.115 | 285.15 | 0.5
0.08385 | 278.15 | 0.115 | 285.15 | 0.6
0.08385 | 278.15 | 0.115 | 285.15 | 0.7
0.08385 | 278.15 | 0.115 | 285.15 | 0.8
0.08385 | 278.15 | 0.115 | 285.15 | 0.9
0.08385 | 278.15 | 0.115 | 285.15 | 1
0.08385 | 278.15 | 0.115 | 285.65 | 0.15
0.08385 | 278.15 | 0.115 | 285.65 | 0.2
0.08385 | 278.15 | 0.115 | 285.65 | 0.3
0.08385 | 278.15 | 0.115 | 285.65 | 0.4
0.08385 | 278.15 | 0.115 | 285.65 | 0.5
0.08385 | 278.15 | 0.115 | 285.65 | 0.6
0.08385 | 278.15 | 0.115 | 285.65 | 0.7
0.08385 | 278.15 | 0.115 | 285.65 | 0.8
0.08385 | 278.15 | 0.115 | 285.65 | 0.9
0.08385 | 278.15 | 0.115 | 285.65 | 1
0.08385 | 278.15 | 0.115 | 286.15 | 0.15
0.08385 | 278.15 | 0.115 | 286.15 | 0.2
0.08385 | 278.15 | 0.115 | 286.15 | 0.3
0.08385 | 278.15 | 0.115 | 286.15 | 0.4
0.08385 | 278.15 | 0.115 | 286.15 | 0.5
0.08385 | 278.15 | 0.115 | 286.15 | 0.6
0.08385 | 278.15 | 0.115 | 286.15 | 0.7
0.08385 | 278.15 | 0.115 | 286.15 | 0.8
0.08385 | 278.15 | 0.115 | 286.15 | 0.9
0.08385 | 278.15 | 0.115 | 286.15 | 1
0.08385 | 278.15 | 0.115 | 286.65 | 0.15
0.08385 | 278.15 | 0.115 | 286.65 | 0.2
0.08385 | 278.15 | 0.115 | 286.65 | 0.3
0.08385 | 278.15 | 0.115 | 286.65 | 0.4
0.08385 | 278.15 | 0.115 | 286.65 | 0.5
0.08385 | 278.15 | 0.115 | 286.65 | 0.6
0.08385 | 278.15 | 0.115 | 286.65 | 0.7
0.08385 | 278.15 | 0.115 | 286.65 | 0.8
0.08385 | 278.15 | 0.115 | 286.65 | 0.9
0.08385 | 278.15 | 0.115 | 286.65 | 1
0.08385 | 278.15 | 0.115 | 287.15 | 0.15
0.08385 | 278.15 | 0.115 | 287.15 | 0.2
0.08385 | 278.15 | 0.115 | 287.15 | 0.3
0.08385 | 278.15 | 0.115 | 287.15 | 0.4
0.08385 | 278.15 | 0.115 | 287.15 | 0.5
0.08385 | 278.15 | 0.115 | 287.15 | 0.6
0.08385 | 278.15 | 0.115 | 287.15 | 0.7
0.08385 | 278.15 | 0.115 | 287.15 | 0.8
0.08385 | 278.15 | 0.115 | 287.15 | 0.9
0.08385 | 278.15 | 0.115 | 287.15 | 1
0.08385 | 278.15 | 0.115 | 287.65 | 0.15
0.08385 | 278.15 | 0.115 | 287.65 | 0.2
0.08385 | 278.15 | 0.115 | 287.65 | 0.3
0.08385 | 278.15 | 0.115 | 287.65 | 0.4
0.08385 | 278.15 | 0.115 | 287.65 | 0.5
0.08385 | 278.15 | 0.115 | 287.65 | 0.6
0.08385 | 278.15 | 0.115 | 287.65 | 0.7
0.08385 | 278.15 | 0.115 | 287.65 | 0.8
0.08385 | 278.15 | 0.115 | 287.65 | 0.9
0.08385 | 278.15 | 0.115 | 287.65 | 1
0.08385 | 278.15 | 0.115 | 288.15 | 0.15
0.08385 | 278.15 | 0.115 | 288.15 | 0.2
0.08385 | 278.15 | 0.115 | 288.15 | 0.3
0.08385 | 278.15 | 0.115 | 288.15 | 0.4
0.08385 | 278.15 | 0.115 | 288.15 | 0.5
0.08385 | 278.15 | 0.115 | 288.15 | 0.6
0.08385 | 278.15 | 0.115 | 288.15 | 0.7
0.08385 | 278.15 | 0.115 | 288.15 | 0.8
0.08385 | 278.15 | 0.115 | 288.15 | 0.9
0.08385 | 278.15 | 0.115 | 288.15 | 1
0.08385 | 278.15 | 0.115 | 288.65 | 0.15
0.08385 | 278.15 | 0.115 | 288.65 | 0.2
0.08385 | 278.15 | 0.115 | 288.65 | 0.3
0.08385 | 278.15 | 0.115 | 288.65 | 0.4
0.08385 | 278.15 | 0.115 | 288.65 | 0.5
0.08385 | 278.15 | 0.115 | 288.65 | 0.6
0.08385 | 278.15 | 0.115 | 288.65 | 0.7
0.08385 | 278.15 | 0.115 | 288.65 | 0.8
0.08385 | 278.15 | 0.115 | 288.65 | 0.9
0.08385 | 278.15 | 0.115 | 288.65 | 1
0.08385 | 278.15 | 0.115 | 289.15 | 0.15
0.08385 | 278.15 | 0.115 | 289.15 | 0.2
0.08385 | 278.15 | 0.115 | 289.15 | 0.3
0.08385 | 278.15 | 0.115 | 289.15 | 0.4
0.08385 | 278.15 | 0.115 | 289.15 | 0.5
0.08385 | 278.15 | 0.115 | 289.15 | 0.6
0.08385 | 278.15 | 0.115 | 289.15 | 0.7
0.08385 | 278.15 | 0.115 | 289.15 | 0.8
0.08385 | 278.15 | 0.115 | 289.15 | 0.9
0.08385 | 278.15 | 0.115 | 289.15 | 1
0.08385 | 278.15 | 0.115 | 289.65 | 0.15
0.08385 | 278.15 | 0.115 | 289.65 | 0.2
0.08385 | 278.15 | 0.115 | 289.65 | 0.3
0.08385 | 278.15 | 0.115 | 289.65 | 0.4
0.08385 | 278.15 | 0.115 | 289.65 | 0.5
0.08385 | 278.15 | 0.115 | 289.65 | 0.6
0.08385 | 278.15 | 0.115 | 289.65 | 0.7
0.08385 | 278.15 | 0.115 | 289.65 | 0.8
0.08385 | 278.15 | 0.115 | 289.65 | 0.9
0.08385 | 278.15 | 0.115 | 289.65 | 1
0.08385 | 278.15 | 0.115 | 290.15 | 0.15
0.08385 | 278.15 | 0.115 | 290.15 | 0.2
0.08385 | 278.15 | 0.115 | 290.15 | 0.3
0.08385 | 278.15 | 0.115 | 290.15 | 0.4
0.08385 | 278.15 | 0.115 | 290.15 | 0.5
0.08385 | 278.15 | 0.115 | 290.15 | 0.6
0.08385 | 278.15 | 0.115 | 290.15 | 0.7
0.08385 | 278.15 | 0.115 | 290.15 | 0.8
0.08385 | 278.15 | 0.115 | 290.15 | 0.9
0.08385 | 278.15 | 0.115 | 290.15 | 1
0.08385 | 278.15 | 0.115 | 290.65 | 0.15
0.08385 | 278.15 | 0.115 | 290.65 | 0.2
0.08385 | 278.15 | 0.115 | 290.65 | 0.3
0.08385 | 278.15 | 0.115 | 290.65 | 0.4
0.08385 | 278.15 | 0.115 | 290.65 | 0.5
0.08385 | 278.15 | 0.115 | 290.65 | 0.6
0.08385 | 278.15 | 0.115 | 290.65 | 0.7
0.08385 | 278.15 | 0.115 | 290.65 | 0.8
0.08385 | 278.15 | 0.115 | 290.65 | 0.9
0.08385 | 278.15 | 0.115 | 290.65 | 1
0.08385 | 278.15 | 0.115 | 291.15 | 0.15
0.08385 | 278.15 | 0.115 | 291.15 | 0.2
0.08385 | 278.15 | 0.115 | 291.15 | 0.3
0.08385 | 278.15 | 0.115 | 291.15 | 0.4
0.08385 | 278.15 | 0.115 | 291.15 | 0.5
0.08385 | 278.15 | 0.115 | 291.15 | 0.6
0.08385 | 278.15 | 0.115 | 291.15 | 0.7
0.08385 | 278.15 | 0.115 | 291.15 | 0.8
0.08385 | 278.15 | 0.115 | 291.15 | 0.9
0.08385 | 278.15 | 0.115 | 291.15 | 1
0.08385 | 278.15 | 0.115 | 294.15 | 0.15
0.08385 | 278.15 | 0.115 | 294.15 | 0.2
0.08385 | 278.15 | 0.115 | 294.15 | 0.3
0.08385 | 278.15 | 0.115 | 294.15 | 0.4
0.08385 | 278.15 | 0.115 | 294.15 | 0.5
0.08385 | 278.15 | 0.115 | 294.15 | 0.6
0.08385 | 278.15 | 0.115 | 294.15 | 0.7
0.08385 | 278.15 | 0.115 | 294.15 | 0.8
0.08385 | 278.15 | 0.115 | 294.15 | 0.9
0.08385 | 278.15 | 0.115 | 294.15 | 1
0.08385 | 278.15 | 0.115 | 297.15 | 0.15
0.08385 | 278.15 | 0.115 | 297.15 | 0.2
0.08385 | 278.15 | 0.115 | 297.15 | 0.3
0.08385 | 278.15 | 0.115 | 297.15 | 0.4
0.08385 | 278.15 | 0.115 | 297.15 | 0.5
0.08385 | 278.15 | 0.115 | 297.15 | 0.6
0.08385 | 278.15 | 0.115 | 297.15 | 0.7
0.08385 | 278.15 | 0.115 | 297.15 | 0.8
0.08385 | 278.15 | 0.115 | 297.15 | 0.9
0.08385 | 278.15 | 0.115 | 297.15 | 1
0.08385 | 278.15 | 0.115 | 300.15 | 0.15
0.08385 | 278.15 | 0.115 | 300.15 | 0.2
0.08385 | 278.15 | 0.115 | 300.15 | 0.3
0.08385 | 278.15 | 0.115 | 300.15 | 0.4
0.08385 | 278.15 | 0.115 | 300.15 | 0.5
0.08385 | 278.15 | 0.115 | 300.15 | 0.6
0.08385 | 278.15 | 0.115 | 300.15 | 0.7
0.08385 | 278.15 | 0.115 | 300.15 | 0.8
0.08385 | 278.15 | 0.115 | 300.15 | 0.9
0.08385 | 278.15 | 0.115 | 300.15 | 1
0.08385 | 278.15 | 0.115 | 303.15 | 0.15
0.08385 | 278.15 | 0.115 | 303.15 | 0.2
0.08385 | 278.15 | 0.115 | 303.15 | 0.3
0.08385 | 278.15 | 0.115 | 303.15 | 0.4
0.08385 | 278.15 | 0.115 | 303.15 | 0.5
0.08385 | 278.15 | 0.115 | 303.15 | 0.6
0.08385 | 278.15 | 0.115 | 303.15 | 0.7
0.08385 | 278.15 | 0.115 | 303.15 | 0.8
0.08385 | 278.15 | 0.115 | 303.15 | 0.9
0.08385 | 278.15 | 0.115 | 303.15 | 1
0.08385 | 280.15 | 0.00115 | 283.65 | 0.15
0.08385 | 280.15 | 0.00115 | 283.65 | 0.2
0.08385 | 280.15 | 0.00115 | 283.65 | 0.3
0.08385 | 280.15 | 0.00115 | 283.65 | 0.4
0.08385 | 280.15 | 0.00115 | 283.65 | 0.5
0.08385 | 280.15 | 0.00115 | 283.65 | 0.6
0.08385 | 280.15 | 0.00115 | 283.65 | 0.7
0.08385 | 280.15 | 0.00115 | 283.65 | 0.8
0.08385 | 280.15 | 0.00115 | 283.65 | 0.9
0.08385 | 280.15 | 0.00115 | 283.65 | 1
0.08385 | 280.15 | 0.00115 | 284.15 | 0.15
0.08385 | 280.15 | 0.00115 | 284.15 | 0.2
0.08385 | 280.15 | 0.00115 | 284.15 | 0.3
0.08385 | 280.15 | 0.00115 | 284.15 | 0.4
0.08385 | 280.15 | 0.00115 | 284.15 | 0.5
0.08385 | 280.15 | 0.00115 | 284.15 | 0.6
0.08385 | 280.15 | 0.00115 | 284.15 | 0.7
0.08385 | 280.15 | 0.00115 | 284.15 | 0.8
0.08385 | 280.15 | 0.00115 | 284.15 | 0.9
0.08385 | 280.15 | 0.00115 | 284.15 | 1
0.08385 | 280.15 | 0.00115 | 284.65 | 0.15
0.08385 | 280.15 | 0.00115 | 284.65 | 0.2
0.08385 | 280.15 | 0.00115 | 284.65 | 0.3
0.08385 | 280.15 | 0.00115 | 284.65 | 0.4
0.08385 | 280.15 | 0.00115 | 284.65 | 0.5
0.08385 | 280.15 | 0.00115 | 284.65 | 0.6
0.08385 | 280.15 | 0.00115 | 284.65 | 0.7
0.08385 | 280.15 | 0.00115 | 284.65 | 0.8
0.08385 | 280.15 | 0.00115 | 284.65 | 0.9
0.08385 | 280.15 | 0.00115 | 284.65 | 1
0.08385 | 280.15 | 0.00115 | 285.15 | 0.15
0.08385 | 280.15 | 0.00115 | 285.15 | 0.2
0.08385 | 280.15 | 0.00115 | 285.15 | 0.3
0.08385 | 280.15 | 0.00115 | 285.15 | 0.4
0.08385 | 280.15 | 0.00115 | 285.15 | 0.5
0.08385 | 280.15 | 0.00115 | 285.15 | 0.6
0.08385 | 280.15 | 0.00115 | 285.15 | 0.7
0.08385 | 280.15 | 0.00115 | 285.15 | 0.8
0.08385 | 280.15 | 0.00115 | 285.15 | 0.9
0.08385 | 280.15 | 0.00115 | 285.15 | 1
0.08385 | 280.15 | 0.00115 | 285.65 | 0.15
0.08385 | 280.15 | 0.00115 | 285.65 | 0.2
0.08385 | 280.15 | 0.00115 | 285.65 | 0.3
0.08385 | 280.15 | 0.00115 | 285.65 | 0.4
0.08385 | 280.15 | 0.00115 | 285.65 | 0.5
0.08385 | 280.15 | 0.00115 | 285.65 | 0.6
0.08385 | 280.15 | 0.00115 | 285.65 | 0.7
0.08385 | 280.15 | 0.00115 | 285.65 | 0.8
0.08385 | 280.15 | 0.00115 | 285.65 | 0.9
0.08385 | 280.15 | 0.00115 | 285.65 | 1
0.08385 | 280.15 | 0.00115 | 286.15 | 0.15
0.08385 | 280.15 | 0.00115 | 286.15 | 0.2
0.08385 | 280.15 | 0.00115 | 286.15 | 0.3
0.08385 | 280.15 | 0.00115 | 286.15 | 0.4
0.08385 | 280.15 | 0.00115 | 286.15 | 0.5
0.08385 | 280.15 | 0.00115 | 286.15 | 0.6
0.08385 | 280.15 | 0.00115 | 286.15 | 0.7
0.08385 | 280.15 | 0.00115 | 286.15 | 0.8
0.08385 | 280.15 | 0.00115 | 286.15 | 0.9
0.08385 | 280.15 | 0.00115 | 286.15 | 1
0.08385 | 280.15 | 0.00115 | 286.65 | 0.15
0.08385 | 280.15 | 0.00115 | 286.65 | 0.2
0.08385 | 280.15 | 0.00115 | 286.65 | 0.3
0.08385 | 280.15 | 0.00115 | 286.65 | 0.4
0.08385 | 280.15 | 0.00115 | 286.65 | 0.5
0.08385 | 280.15 | 0.00115 | 286.65 | 0.6
0.08385 | 280.15 | 0.00115 | 286.65 | 0.7
0.08385 | 280.15 | 0.00115 | 286.65 | 0.8
0.08385 | 280.15 | 0.00115 | 286.65 | 0.9
0.08385 | 280.15 | 0.00115 | 286.65 | 1
0.08385 | 280.15 | 0.00115 | 287.15 | 0.15
0.08385 | 280.15 | 0.00115 | 287.15 | 0.2
0.08385 | 280.15 | 0.00115 | 287.15 | 0.3
0.08385 | 280.15 | 0.00115 | 287.15 | 0.4
0.08385 | 280.15 | 0.00115 | 287.15 | 0.5
0.08385 | 280.15 | 0.00115 | 287.15 | 0.6
0.08385 | 280.15 | 0.00115 | 287.15 | 0.7
0.08385 | 280.15 | 0.00115 | 287.15 | 0.8
0.08385 | 280.15 | 0.00115 | 287.15 | 0.9
0.08385 | 280.15 | 0.00115 | 287.15 | 1
0.08385 | 280.15 | 0.00115 | 287.65 | 0.15
0.08385 | 280.15 | 0.00115 | 287.65 | 0.2
0.08385 | 280.15 | 0.00115 | 287.65 | 0.3
0.08385 | 280.15 | 0.00115 | 287.65 | 0.4
0.08385 | 280.15 | 0.00115 | 287.65 | 0.5
0.08385 | 280.15 | 0.00115 | 287.65 | 0.6
0.08385 | 280.15 | 0.00115 | 287.65 | 0.7
0.08385 | 280.15 | 0.00115 | 287.65 | 0.8
0.08385 | 280.15 | 0.00115 | 287.65 | 0.9
0.08385 | 280.15 | 0.00115 | 287.65 | 1
0.08385 | 280.15 | 0.00115 | 288.15 | 0.15
0.08385 | 280.15 | 0.00115 | 288.15 | 0.2
0.08385 | 280.15 | 0.00115 | 288.15 | 0.3
0.08385 | 280.15 | 0.00115 | 288.15 | 0.4
0.08385 | 280.15 | 0.00115 | 288.15 | 0.5
0.08385 | 280.15 | 0.00115 | 288.15 | 0.6
0.08385 | 280.15 | 0.00115 | 288.15 | 0.7
0.08385 | 280.15 | 0.00115 | 288.15 | 0.8
0.08385 | 280.15 | 0.00115 | 288.15 | 0.9
0.08385 | 280.15 | 0.00115 | 288.15 | 1
0.08385 | 280.15 | 0.00115 | 288.65 | 0.15
0.08385 | 280.15 | 0.00115 | 288.65 | 0.2
0.08385 | 280.15 | 0.00115 | 288.65 | 0.3
0.08385 | 280.15 | 0.00115 | 288.65 | 0.4
0.08385 | 280.15 | 0.00115 | 288.65 | 0.5
0.08385 | 280.15 | 0.00115 | 288.65 | 0.6
0.08385 | 280.15 | 0.00115 | 288.65 | 0.7
0.08385 | 280.15 | 0.00115 | 288.65 | 0.8
0.08385 | 280.15 | 0.00115 | 288.65 | 0.9
0.08385 | 280.15 | 0.00115 | 288.65 | 1
0.08385 | 280.15 | 0.00115 | 289.15 | 0.15
0.08385 | 280.15 | 0.00115 | 289.15 | 0.2
0.08385 | 280.15 | 0.00115 | 289.15 | 0.3
0.08385 | 280.15 | 0.00115 | 289.15 | 0.4
0.08385 | 280.15 | 0.00115 | 289.15 | 0.5
0.08385 | 280.15 | 0.00115 | 289.15 | 0.6
0.08385 | 280.15 | 0.00115 | 289.15 | 0.7
0.08385 | 280.15 | 0.00115 | 289.15 | 0.8
0.08385 | 280.15 | 0.00115 | 289.15 | 0.9
0.08385 | 280.15 | 0.00115 | 289.15 | 1
0.08385 | 280.15 | 0.00115 | 289.65 | 0.15
0.08385 | 280.15 | 0.00115 | 289.65 | 0.2
0.08385 | 280.15 | 0.00115 | 289.65 | 0.3
0.08385 | 280.15 | 0.00115 | 289.65 | 0.4
0.08385 | 280.15 | 0.00115 | 289.65 | 0.5
0.08385 | 280.15 | 0.00115 | 289.65 | 0.6
0.08385 | 280.15 | 0.00115 | 289.65 | 0.7
0.08385 | 280.15 | 0.00115 | 289.65 | 0.8
0.08385 | 280.15 | 0.00115 | 289.65 | 0.9
0.08385 | 280.15 | 0.00115 | 289.65 | 1
0.08385 | 280.15 | 0.00115 | 290.15 | 0.15
0.08385 | 280.15 | 0.00115 | 290.15 | 0.2
0.08385 | 280.15 | 0.00115 | 290.15 | 0.3
0.08385 | 280.15 | 0.00115 | 290.15 | 0.4
0.08385 | 280.15 | 0.00115 | 290.15 | 0.5
0.08385 | 280.15 | 0.00115 | 290.15 | 0.6
0.08385 | 280.15 | 0.00115 | 290.15 | 0.7
0.08385 | 280.15 | 0.00115 | 290.15 | 0.8
0.08385 | 280.15 | 0.00115 | 290.15 | 0.9
0.08385 | 280.15 | 0.00115 | 290.15 | 1
0.08385 | 280.15 | 0.00115 | 290.65 | 0.15
0.08385 | 280.15 | 0.00115 | 290.65 | 0.2
0.08385 | 280.15 | 0.00115 | 290.65 | 0.3
0.08385 | 280.15 | 0.00115 | 290.65 | 0.4
0.08385 | 280.15 | 0.00115 | 290.65 | 0.5
0.08385 | 280.15 | 0.00115 | 290.65 | 0.6
0.08385 | 280.15 | 0.00115 | 290.65 | 0.7
0.08385 | 280.15 | 0.00115 | 290.65 | 0.8
0.08385 | 280.15 | 0.00115 | 290.65 | 0.9
0.08385 | 280.15 | 0.00115 | 290.65 | 1
0.08385 | 280.15 | 0.00115 | 291.15 | 0.15
0.08385 | 280.15 | 0.00115 | 291.15 | 0.2
0.08385 | 280.15 | 0.00115 | 291.15 | 0.3
0.08385 | 280.15 | 0.00115 | 291.15 | 0.4
0.08385 | 280.15 | 0.00115 | 291.15 | 0.5
0.08385 | 280.15 | 0.00115 | 291.15 | 0.6
0.08385 | 280.15 | 0.00115 | 291.15 | 0.7
0.08385 | 280.15 | 0.00115 | 291.15 | 0.8
0.08385 | 280.15 | 0.00115 | 291.15 | 0.9
0.08385 | 280.15 | 0.00115 | 291.15 | 1
0.08385 | 280.15 | 0.00115 | 294.15 | 0.15
0.08385 | 280.15 | 0.00115 | 294.15 | 0.2
0.08385 | 280.15 | 0.00115 | 294.15 | 0.3
0.08385 | 280.15 | 0.00115 | 294.15 | 0.4
0.08385 | 280.15 | 0.00115 | 294.15 | 0.5
0.08385 | 280.15 | 0.00115 | 294.15 | 0.6
0.08385 | 280.15 | 0.00115 | 294.15 | 0.7
0.08385 | 280.15 | 0.00115 | 294.15 | 0.8
0.08385 | 280.15 | 0.00115 | 294.15 | 0.9
0.08385 | 280.15 | 0.00115 | 294.15 | 1
0.08385 | 280.15 | 0.00115 | 297.15 | 0.15
0.08385 | 280.15 | 0.00115 | 297.15 | 0.2
0.08385 | 280.15 | 0.00115 | 297.15 | 0.3
0.08385 | 280.15 | 0.00115 | 297.15 | 0.4
0.08385 | 280.15 | 0.00115 | 297.15 | 0.5
0.08385 | 280.15 | 0.00115 | 297.15 | 0.6
0.08385 | 280.15 | 0.00115 | 297.15 | 0.7
0.08385 | 280.15 | 0.00115 | 297.15 | 0.8
0.08385 | 280.15 | 0.00115 | 297.15 | 0.9
0.08385 | 280.15 | 0.00115 | 297.15 | 1
0.08385 | 280.15 | 0.00115 | 300.15 | 0.15
0.08385 | 280.15 | 0.00115 | 300.15 | 0.2
0.08385 | 280.15 | 0.00115 | 300.15 | 0.3
0.08385 | 280.15 | 0.00115 | 300.15 | 0.4
0.08385 | 280.15 | 0.00115 | 300.15 | 0.5
0.08385 | 280.15 | 0.00115 | 300.15 | 0.6
0.08385 | 280.15 | 0.00115 | 300.15 | 0.7
0.08385 | 280.15 | 0.00115 | 300.15 | 0.8
0.08385 | 280.15 | 0.00115 | 300.15 | 0.9
0.08385 | 280.15 | 0.00115 | 300.15 | 1
0.08385 | 280.15 | 0.00115 | 303.15 | 0.15
0.08385 | 280.15 | 0.00115 | 303.15 | 0.2
0.08385 | 280.15 | 0.00115 | 303.15 | 0.3
0.08385 | 280.15 | 0.00115 | 303.15 | 0.4
0.08385 | 280.15 | 0.00115 | 303.15 | 0.5
0.08385 | 280.15 | 0.00115 | 303.15 | 0.6
0.08385 | 280.15 | 0.00115 | 303.15 | 0.7
0.08385 | 280.15 | 0.00115 | 303.15 | 0.8
0.08385 | 280.15 | 0.00115 | 303.15 | 0.9
0.08385 | 280.15 | 0.00115 | 303.15 | 1
0.08385 | 280.15 | 0.077 | 283.65 | 0.15
0.08385 | 280.15 | 0.077 | 283.65 | 0.2
0.08385 | 280.15 | 0.077 | 283.65 | 0.3
0.08385 | 280.15 | 0.077 | 283.65 | 0.4
0.08385 | 280.15 | 0.077 | 283.65 | 0.5
0.08385 | 280.15 | 0.077 | 283.65 | 0.6
0.08385 | 280.15 | 0.077 | 283.65 | 0.7
0.08385 | 280.15 | 0.077 | 283.65 | 0.8
0.08385 | 280.15 | 0.077 | 283.65 | 0.9
0.08385 | 280.15 | 0.077 | 283.65 | 1
0.08385 | 280.15 | 0.077 | 284.15 | 0.15
0.08385 | 280.15 | 0.077 | 284.15 | 0.2
0.08385 | 280.15 | 0.077 | 284.15 | 0.3
0.08385 | 280.15 | 0.077 | 284.15 | 0.4
0.08385 | 280.15 | 0.077 | 284.15 | 0.5
0.08385 | 280.15 | 0.077 | 284.15 | 0.6
0.08385 | 280.15 | 0.077 | 284.15 | 0.7
0.08385 | 280.15 | 0.077 | 284.15 | 0.8
0.08385 | 280.15 | 0.077 | 284.15 | 0.9
0.08385 | 280.15 | 0.077 | 284.15 | 1
0.08385 | 280.15 | 0.077 | 284.65 | 0.15
0.08385 | 280.15 | 0.077 | 284.65 | 0.2
0.08385 | 280.15 | 0.077 | 284.65 | 0.3
0.08385 | 280.15 | 0.077 | 284.65 | 0.4
0.08385 | 280.15 | 0.077 | 284.65 | 0.5
0.08385 | 280.15 | 0.077 | 284.65 | 0.6
0.08385 | 280.15 | 0.077 | 284.65 | 0.7
0.08385 | 280.15 | 0.077 | 284.65 | 0.8
0.08385 | 280.15 | 0.077 | 284.65 | 0.9
0.08385 | 280.15 | 0.077 | 284.65 | 1
0.08385 | 280.15 | 0.077 | 285.15 | 0.15
0.08385 | 280.15 | 0.077 | 285.15 | 0.2
0.08385 | 280.15 | 0.077 | 285.15 | 0.3
0.08385 | 280.15 | 0.077 | 285.15 | 0.4
0.08385 | 280.15 | 0.077 | 285.15 | 0.5
0.08385 | 280.15 | 0.077 | 285.15 | 0.6
0.08385 | 280.15 | 0.077 | 285.15 | 0.7
0.08385 | 280.15 | 0.077 | 285.15 | 0.8
0.08385 | 280.15 | 0.077 | 285.15 | 0.9
0.08385 | 280.15 | 0.077 | 285.15 | 1
0.08385 | 280.15 | 0.077 | 285.65 | 0.15
0.08385 | 280.15 | 0.077 | 285.65 | 0.2
0.08385 | 280.15 | 0.077 | 285.65 | 0.3
0.08385 | 280.15 | 0.077 | 285.65 | 0.4
0.08385 | 280.15 | 0.077 | 285.65 | 0.5
0.08385 | 280.15 | 0.077 | 285.65 | 0.6
0.08385 | 280.15 | 0.077 | 285.65 | 0.7
0.08385 | 280.15 | 0.077 | 285.65 | 0.8
0.08385 | 280.15 | 0.077 | 285.65 | 0.9
0.08385 | 280.15 | 0.077 | 285.65 | 1
0.08385 | 280.15 | 0.077 | 286.15 | 0.15
0.08385 | 280.15 | 0.077 | 286.15 | 0.2
0.08385 | 280.15 | 0.077 | 286.15 | 0.3
0.08385 | 280.15 | 0.077 | 286.15 | 0.4
0.08385 | 280.15 | 0.077 | 286.15 | 0.5
0.08385 | 280.15 | 0.077 | 286.15 | 0.6
0.08385 | 280.15 | 0.077 | 286.15 | 0.7
0.08385 | 280.15 | 0.077 | 286.15 | 0.8
0.08385 | 280.15 | 0.077 | 286.15 | 0.9
0.08385 | 280.15 | 0.077 | 286.15 | 1
0.08385 | 280.15 | 0.077 | 286.65 | 0.15
0.08385 | 280.15 | 0.077 | 286.65 | 0.2
0.08385 | 280.15 | 0.077 | 286.65 | 0.3
0.08385 | 280.15 | 0.077 | 286.65 | 0.4
0.08385 | 280.15 | 0.077 | 286.65 | 0.5
0.08385 | 280.15 | 0.077 | 286.65 | 0.6
0.08385 | 280.15 | 0.077 | 286.65 | 0.7
0.08385 | 280.15 | 0.077 | 286.65 | 0.8
0.08385 | 280.15 | 0.077 | 286.65 | 0.9
0.08385 | 280.15 | 0.077 | 286.65 | 1
0.08385 | 280.15 | 0.077 | 287.15 | 0.15
0.08385 | 280.15 | 0.077 | 287.15 | 0.2
0.08385 | 280.15 | 0.077 | 287.15 | 0.3
0.08385 | 280.15 | 0.077 | 287.15 | 0.4
0.08385 | 280.15 | 0.077 | 287.15 | 0.5
0.08385 | 280.15 | 0.077 | 287.15 | 0.6
0.08385 | 280.15 | 0.077 | 287.15 | 0.7
0.08385 | 280.15 | 0.077 | 287.15 | 0.8
0.08385 | 280.15 | 0.077 | 287.15 | 0.9
0.08385 | 280.15 | 0.077 | 287.15 | 1
0.08385 | 280.15 | 0.077 | 287.65 | 0.15
0.08385 | 280.15 | 0.077 | 287.65 | 0.2
0.08385 | 280.15 | 0.077 | 287.65 | 0.3
0.08385 | 280.15 | 0.077 | 287.65 | 0.4
0.08385 | 280.15 | 0.077 | 287.65 | 0.5
0.08385 | 280.15 | 0.077 | 287.65 | 0.6
0.08385 | 280.15 | 0.077 | 287.65 | 0.7
0.08385 | 280.15 | 0.077 | 287.65 | 0.8
0.08385 | 280.15 | 0.077 | 287.65 | 0.9
0.08385 | 280.15 | 0.077 | 287.65 | 1
0.08385 | 280.15 | 0.077 | 288.15 | 0.15
0.08385 | 280.15 | 0.077 | 288.15 | 0.2
0.08385 | 280.15 | 0.077 | 288.15 | 0.3
0.08385 | 280.15 | 0.077 | 288.15 | 0.4
0.08385 | 280.15 | 0.077 | 288.15 | 0.5
0.08385 | 280.15 | 0.077 | 288.15 | 0.6
0.08385 | 280.15 | 0.077 | 288.15 | 0.7
0.08385 | 280.15 | 0.077 | 288.15 | 0.8
0.08385 | 280.15 | 0.077 | 288.15 | 0.9
0.08385 | 280.15 | 0.077 | 288.15 | 1
0.08385 | 280.15 | 0.077 | 288.65 | 0.15
0.08385 | 280.15 | 0.077 | 288.65 | 0.2
0.08385 | 280.15 | 0.077 | 288.65 | 0.3
0.08385 | 280.15 | 0.077 | 288.65 | 0.4
0.08385 | 280.15 | 0.077 | 288.65 | 0.5
0.08385 | 280.15 | 0.077 | 288.65 | 0.6
0.08385 | 280.15 | 0.077 | 288.65 | 0.7
0.08385 | 280.15 | 0.077 | 288.65 | 0.8
0.08385 | 280.15 | 0.077 | 288.65 | 0.9
0.08385 | 280.15 | 0.077 | 288.65 | 1
0.08385 | 280.15 | 0.077 | 289.15 | 0.15
0.08385 | 280.15 | 0.077 | 289.15 | 0.2
0.08385 | 280.15 | 0.077 | 289.15 | 0.3
0.08385 | 280.15 | 0.077 | 289.15 | 0.4
0.08385 | 280.15 | 0.077 | 289.15 | 0.5
0.08385 | 280.15 | 0.077 | 289.15 | 0.6
0.08385 | 280.15 | 0.077 | 289.15 | 0.7
0.08385 | 280.15 | 0.077 | 289.15 | 0.8
0.08385 | 280.15 | 0.077 | 289.15 | 0.9
0.08385 | 280.15 | 0.077 | 289.15 | 1
0.08385 | 280.15 | 0.077 | 289.65 | 0.15
0.08385 | 280.15 | 0.077 | 289.65 | 0.2
0.08385 | 280.15 | 0.077 | 289.65 | 0.3
0.08385 | 280.15 | 0.077 | 289.65 | 0.4
0.08385 | 280.15 | 0.077 | 289.65 | 0.5
0.08385 | 280.15 | 0.077 | 289.65 | 0.6
0.08385 | 280.15 | 0.077 | 289.65 | 0.7
0.08385 | 280.15 | 0.077 | 289.65 | 0.8
0.08385 | 280.15 | 0.077 | 289.65 | 0.9
0.08385 | 280.15 | 0.077 | 289.65 | 1
0.08385 | 280.15 | 0.077 | 290.15 | 0.15
0.08385 | 280.15 | 0.077 | 290.15 | 0.2
0.08385 | 280.15 | 0.077 | 290.15 | 0.3
0.08385 | 280.15 | 0.077 | 290.15 | 0.4
0.08385 | 280.15 | 0.077 | 290.15 | 0.5
0.08385 | 280.15 | 0.077 | 290.15 | 0.6
0.08385 | 280.15 | 0.077 | 290.15 | 0.7
0.08385 | 280.15 | 0.077 | 290.15 | 0.8
0.08385 | 280.15 | 0.077 | 290.15 | 0.9
0.08385 | 280.15 | 0.077 | 290.15 | 1
0.08385 | 280.15 | 0.077 | 290.65 | 0.15
0.08385 | 280.15 | 0.077 | 290.65 | 0.2
0.08385 | 280.15 | 0.077 | 290.65 | 0.3
0.08385 | 280.15 | 0.077 | 290.65 | 0.4
0.08385 | 280.15 | 0.077 | 290.65 | 0.5
0.08385 | 280.15 | 0.077 | 290.65 | 0.6
0.08385 | 280.15 | 0.077 | 290.65 | 0.7
0.08385 | 280.15 | 0.077 | 290.65 | 0.8
0.08385 | 280.15 | 0.077 | 290.65 | 0.9
0.08385 | 280.15 | 0.077 | 290.65 | 1
0.08385 | 280.15 | 0.077 | 291.15 | 0.15
0.08385 | 280.15 | 0.077 | 291.15 | 0.2
0.08385 | 280.15 | 0.077 | 291.15 | 0.3
0.08385 | 280.15 | 0.077 | 291.15 | 0.4
0.08385 | 280.15 | 0.077 | 291.15 | 0.5
0.08385 | 280.15 | 0.077 | 291.15 | 0.6
0.08385 | 280.15 | 0.077 | 291.15 | 0.7
0.08385 | 280.15 | 0.077 | 291.15 | 0.8
0.08385 | 280.15 | 0.077 | 291.15 | 0.9
0.08385 | 280.15 | 0.077 | 291.15 | 1
0.08385 | 280.15 | 0.077 | 294.15 | 0.15
0.08385 | 280.15 | 0.077 | 294.15 | 0.2
0.08385 | 280.15 | 0.077 | 294.15 | 0.3
0.08385 | 280.15 | 0.077 | 294.15 | 0.4
0.08385 | 280.15 | 0.077 | 294.15 | 0.5
0.08385 | 280.15 | 0.077 | 294.15 | 0.6
0.08385 | 280.15 | 0.077 | 294.15 | 0.7
0.08385 | 280.15 | 0.077 | 294.15 | 0.8
0.08385 | 280.15 | 0.077 | 294.15 | 0.9
0.08385 | 280.15 | 0.077 | 294.15 | 1
0.08385 | 280.15 | 0.077 | 297.15 | 0.15
0.08385 | 280.15 | 0.077 | 297.15 | 0.2
0.08385 | 280.15 | 0.077 | 297.15 | 0.3
0.08385 | 280.15 | 0.077 | 297.15 | 0.4
0.08385 | 280.15 | 0.077 | 297.15 | 0.5
0.08385 | 280.15 | 0.077 | 297.15 | 0.6
0.08385 | 280.15 | 0.077 | 297.15 | 0.7
0.08385 | 280.15 | 0.077 | 297.15 | 0.8
0.08385 | 280.15 | 0.077 | 297.15 | 0.9
0.08385 | 280.15 | 0.077 | 297.15 | 1
0.08385 | 280.15 | 0.077 | 300.15 | 0.15
0.08385 | 280.15 | 0.077 | 300.15 | 0.2
0.08385 | 280.15 | 0.077 | 300.15 | 0.3
0.08385 | 280.15 | 0.077 | 300.15 | 0.4
0.08385 | 280.15 | 0.077 | 300.15 | 0.5
0.08385 | 280.15 | 0.077 | 300.15 | 0.6
0.08385 | 280.15 | 0.077 | 300.15 | 0.7
0.08385 | 280.15 | 0.077 | 300.15 | 0.8
0.08385 | 280.15 | 0.077 | 300.15 | 0.9
0.08385 | 280.15 | 0.077 | 300.15 | 1
0.08385 | 280.15 | 0.077 | 303.15 | 0.15
0.08385 | 280.15 | 0.077 | 303.15 | 0.2
0.08385 | 280.15 | 0.077 | 303.15 | 0.3
0.08385 | 280.15 | 0.077 | 303.15 | 0.4
0.08385 | 280.15 | 0.077 | 303.15 | 0.5
0.08385 | 280.15 | 0.077 | 303.15 | 0.6
0.08385 | 280.15 | 0.077 | 303.15 | 0.7
0.08385 | 280.15 | 0.077 | 303.15 | 0.8
0.08385 | 280.15 | 0.077 | 303.15 | 0.9
0.08385 | 280.15 | 0.077 | 303.15 | 1
0.08385 | 280.15 | 0.09437 | 283.65 | 0.15
0.08385 | 280.15 | 0.09437 | 283.65 | 0.2
0.08385 | 280.15 | 0.09437 | 283.65 | 0.3
0.08385 | 280.15 | 0.09437 | 283.65 | 0.4
0.08385 | 280.15 | 0.09437 | 283.65 | 0.5
0.08385 | 280.15 | 0.09437 | 283.65 | 0.6
0.08385 | 280.15 | 0.09437 | 283.65 | 0.7
0.08385 | 280.15 | 0.09437 | 283.65 | 0.8
0.08385 | 280.15 | 0.09437 | 283.65 | 0.9
0.08385 | 280.15 | 0.09437 | 283.65 | 1
0.08385 | 280.15 | 0.09437 | 284.15 | 0.15
0.08385 | 280.15 | 0.09437 | 284.15 | 0.2
0.08385 | 280.15 | 0.09437 | 284.15 | 0.3
0.08385 | 280.15 | 0.09437 | 284.15 | 0.4
0.08385 | 280.15 | 0.09437 | 284.15 | 0.5
0.08385 | 280.15 | 0.09437 | 284.15 | 0.6
0.08385 | 280.15 | 0.09437 | 284.15 | 0.7
0.08385 | 280.15 | 0.09437 | 284.15 | 0.8
0.08385 | 280.15 | 0.09437 | 284.15 | 0.9
0.08385 | 280.15 | 0.09437 | 284.15 | 1
0.08385 | 280.15 | 0.09437 | 284.65 | 0.15
0.08385 | 280.15 | 0.09437 | 284.65 | 0.2
0.08385 | 280.15 | 0.09437 | 284.65 | 0.3
0.08385 | 280.15 | 0.09437 | 284.65 | 0.4
0.08385 | 280.15 | 0.09437 | 284.65 | 0.5
0.08385 | 280.15 | 0.09437 | 284.65 | 0.6
0.08385 | 280.15 | 0.09437 | 284.65 | 0.7
0.08385 | 280.15 | 0.09437 | 284.65 | 0.8
0.08385 | 280.15 | 0.09437 | 284.65 | 0.9
0.08385 | 280.15 | 0.09437 | 284.65 | 1
0.08385 | 280.15 | 0.09437 | 285.15 | 0.15
0.08385 | 280.15 | 0.09437 | 285.15 | 0.2
0.08385 | 280.15 | 0.09437 | 285.15 | 0.3
0.08385 | 280.15 | 0.09437 | 285.15 | 0.4
0.08385 | 280.15 | 0.09437 | 285.15 | 0.5
0.08385 | 280.15 | 0.09437 | 285.15 | 0.6
0.08385 | 280.15 | 0.09437 | 285.15 | 0.7
0.08385 | 280.15 | 0.09437 | 285.15 | 0.8
0.08385 | 280.15 | 0.09437 | 285.15 | 0.9
0.08385 | 280.15 | 0.09437 | 285.15 | 1
0.08385 | 280.15 | 0.09437 | 285.65 | 0.15
0.08385 | 280.15 | 0.09437 | 285.65 | 0.2
0.08385 | 280.15 | 0.09437 | 285.65 | 0.3
0.08385 | 280.15 | 0.09437 | 285.65 | 0.4
0.08385 | 280.15 | 0.09437 | 285.65 | 0.5
0.08385 | 280.15 | 0.09437 | 285.65 | 0.6
0.08385 | 280.15 | 0.09437 | 285.65 | 0.7
0.08385 | 280.15 | 0.09437 | 285.65 | 0.8
0.08385 | 280.15 | 0.09437 | 285.65 | 0.9
0.08385 | 280.15 | 0.09437 | 285.65 | 1
0.08385 | 280.15 | 0.09437 | 286.15 | 0.15
0.08385 | 280.15 | 0.09437 | 286.15 | 0.2
0.08385 | 280.15 | 0.09437 | 286.15 | 0.3
0.08385 | 280.15 | 0.09437 | 286.15 | 0.4
0.08385 | 280.15 | 0.09437 | 286.15 | 0.5
0.08385 | 280.15 | 0.09437 | 286.15 | 0.6
0.08385 | 280.15 | 0.09437 | 286.15 | 0.7
0.08385 | 280.15 | 0.09437 | 286.15 | 0.8
0.08385 | 280.15 | 0.09437 | 286.15 | 0.9
0.08385 | 280.15 | 0.09437 | 286.15 | 1
0.08385 | 280.15 | 0.09437 | 286.65 | 0.15
0.08385 | 280.15 | 0.09437 | 286.65 | 0.2
0.08385 | 280.15 | 0.09437 | 286.65 | 0.3
0.08385 | 280.15 | 0.09437 | 286.65 | 0.4
0.08385 | 280.15 | 0.09437 | 286.65 | 0.5
0.08385 | 280.15 | 0.09437 | 286.65 | 0.6
0.08385 | 280.15 | 0.09437 | 286.65 | 0.7
0.08385 | 280.15 | 0.09437 | 286.65 | 0.8
0.08385 | 280.15 | 0.09437 | 286.65 | 0.9
0.08385 | 280.15 | 0.09437 | 286.65 | 1
0.08385 | 280.15 | 0.09437 | 287.15 | 0.15
0.08385 | 280.15 | 0.09437 | 287.15 | 0.2
0.08385 | 280.15 | 0.09437 | 287.15 | 0.3
0.08385 | 280.15 | 0.09437 | 287.15 | 0.4
0.08385 | 280.15 | 0.09437 | 287.15 | 0.5
0.08385 | 280.15 | 0.09437 | 287.15 | 0.6
0.08385 | 280.15 | 0.09437 | 287.15 | 0.7
0.08385 | 280.15 | 0.09437 | 287.15 | 0.8
0.08385 | 280.15 | 0.09437 | 287.15 | 0.9
0.08385 | 280.15 | 0.09437 | 287.15 | 1
0.08385 | 280.15 | 0.09437 | 287.65 | 0.15
0.08385 | 280.15 | 0.09437 | 287.65 | 0.2
0.08385 | 280.15 | 0.09437 | 287.65 | 0.3
0.08385 | 280.15 | 0.09437 | 287.65 | 0.4
0.08385 | 280.15 | 0.09437 | 287.65 | 0.5
0.08385 | 280.15 | 0.09437 | 287.65 | 0.6
0.08385 | 280.15 | 0.09437 | 287.65 | 0.7
0.08385 | 280.15 | 0.09437 | 287.65 | 0.8
0.08385 | 280.15 | 0.09437 | 287.65 | 0.9
0.08385 | 280.15 | 0.09437 | 287.65 | 1
0.08385 | 280.15 | 0.09437 | 288.15 | 0.15
0.08385 | 280.15 | 0.09437 | 288.15 | 0.2
0.08385 | 280.15 | 0.09437 | 288.15 | 0.3
0.08385 | 280.15 | 0.09437 | 288.15 | 0.4
0.08385 | 280.15 | 0.09437 | 288.15 | 0.5
0.08385 | 280.15 | 0.09437 | 288.15 | 0.6
0.08385 | 280.15 | 0.09437 | 288.15 | 0.7
0.08385 | 280.15 | 0.09437 | 288.15 | 0.8
0.08385 | 280.15 | 0.09437 | 288.15 | 0.9
0.08385 | 280.15 | 0.09437 | 288.15 | 1
0.08385 | 280.15 | 0.09437 | 288.65 | 0.15
0.08385 | 280.15 | 0.09437 | 288.65 | 0.2
0.08385 | 280.15 | 0.09437 | 288.65 | 0.3
0.08385 | 280.15 | 0.09437 | 288.65 | 0.4
0.08385 | 280.15 | 0.09437 | 288.65 | 0.5
0.08385 | 280.15 | 0.09437 | 288.65 | 0.6
0.08385 | 280.15 | 0.09437 | 288.65 | 0.7
0.08385 | 280.15 | 0.09437 | 288.65 | 0.8
0.08385 | 280.15 | 0.09437 | 288.65 | 0.9
0.08385 | 280.15 | 0.09437 | 288.65 | 1
0.08385 | 280.15 | 0.09437 | 289.15 | 0.15
0.08385 | 280.15 | 0.09437 | 289.15 | 0.2
0.08385 | 280.15 | 0.09437 | 289.15 | 0.3
0.08385 | 280.15 | 0.09437 | 289.15 | 0.4
0.08385 | 280.15 | 0.09437 | 289.15 | 0.5
0.08385 | 280.15 | 0.09437 | 289.15 | 0.6
0.08385 | 280.15 | 0.09437 | 289.15 | 0.7
0.08385 | 280.15 | 0.09437 | 289.15 | 0.8
0.08385 | 280.15 | 0.09437 | 289.15 | 0.9
0.08385 | 280.15 | 0.09437 | 289.15 | 1
0.08385 | 280.15 | 0.09437 | 289.65 | 0.15
0.08385 | 280.15 | 0.09437 | 289.65 | 0.2
0.08385 | 280.15 | 0.09437 | 289.65 | 0.3
0.08385 | 280.15 | 0.09437 | 289.65 | 0.4
0.08385 | 280.15 | 0.09437 | 289.65 | 0.5
0.08385 | 280.15 | 0.09437 | 289.65 | 0.6
0.08385 | 280.15 | 0.09437 | 289.65 | 0.7
0.08385 | 280.15 | 0.09437 | 289.65 | 0.8
0.08385 | 280.15 | 0.09437 | 289.65 | 0.9
0.08385 | 280.15 | 0.09437 | 289.65 | 1
0.08385 | 280.15 | 0.09437 | 290.15 | 0.15
0.08385 | 280.15 | 0.09437 | 290.15 | 0.2
0.08385 | 280.15 | 0.09437 | 290.15 | 0.3
0.08385 | 280.15 | 0.09437 | 290.15 | 0.4
0.08385 | 280.15 | 0.09437 | 290.15 | 0.5
0.08385 | 280.15 | 0.09437 | 290.15 | 0.6
0.08385 | 280.15 | 0.09437 | 290.15 | 0.7
0.08385 | 280.15 | 0.09437 | 290.15 | 0.8
0.08385 | 280.15 | 0.09437 | 290.15 | 0.9
0.08385 | 280.15 | 0.09437 | 290.15 | 1
0.08385 | 280.15 | 0.09437 | 290.65 | 0.15
0.08385 | 280.15 | 0.09437 | 290.65 | 0.2
0.08385 | 280.15 | 0.09437 | 290.65 | 0.3
0.08385 | 280.15 | 0.09437 | 290.65 | 0.4
0.08385 | 280.15 | 0.09437 | 290.65 | 0.5
0.08385 | 280.15 | 0.09437 | 290.65 | 0.6
0.08385 | 280.15 | 0.09437 | 290.65 | 0.7
0.08385 | 280.15 | 0.09437 | 290.65 | 0.8
0.08385 | 280.15 | 0.09437 | 290.65 | 0.9
0.08385 | 280.15 | 0.09437 | 290.65 | 1
0.08385 | 280.15 | 0.09437 | 291.15 | 0.15
0.08385 | 280.15 | 0.09437 | 291.15 | 0.2
0.08385 | 280.15 | 0.09437 | 291.15 | 0.3
0.08385 | 280.15 | 0.09437 | 291.15 | 0.4
0.08385 | 280.15 | 0.09437 | 291.15 | 0.5
0.08385 | 280.15 | 0.09437 | 291.15 | 0.6
0.08385 | 280.15 | 0.09437 | 291.15 | 0.7
0.08385 | 280.15 | 0.09437 | 291.15 | 0.8
0.08385 | 280.15 | 0.09437 | 291.15 | 0.9
0.08385 | 280.15 | 0.09437 | 291.15 | 1
0.08385 | 280.15 | 0.09437 | 294.15 | 0.15
0.08385 | 280.15 | 0.09437 | 294.15 | 0.2
0.08385 | 280.15 | 0.09437 | 294.15 | 0.3
0.08385 | 280.15 | 0.09437 | 294.15 | 0.4
0.08385 | 280.15 | 0.09437 | 294.15 | 0.5
0.08385 | 280.15 | 0.09437 | 294.15 | 0.6
0.08385 | 280.15 | 0.09437 | 294.15 | 0.7
0.08385 | 280.15 | 0.09437 | 294.15 | 0.8
0.08385 | 280.15 | 0.09437 | 294.15 | 0.9
0.08385 | 280.15 | 0.09437 | 294.15 | 1
0.08385 | 280.15 | 0.09437 | 297.15 | 0.15
0.08385 | 280.15 | 0.09437 | 297.15 | 0.2
0.08385 | 280.15 | 0.09437 | 297.15 | 0.3
0.08385 | 280.15 | 0.09437 | 297.15 | 0.4
0.08385 | 280.15 | 0.09437 | 297.15 | 0.5
0.08385 | 280.15 | 0.09437 | 297.15 | 0.6
0.08385 | 280.15 | 0.09437 | 297.15 | 0.7
0.08385 | 280.15 | 0.09437 | 297.15 | 0.8
0.08385 | 280.15 | 0.09437 | 297.15 | 0.9
0.08385 | 280.15 | 0.09437 | 297.15 | 1
0.08385 | 280.15 | 0.09437 | 300.15 | 0.15
0.08385 | 280.15 | 0.09437 | 300.15 | 0.2
0.08385 | 280.15 | 0.09437 | 300.15 | 0.3
0.08385 | 280.15 | 0.09437 | 300.15 | 0.4
0.08385 | 280.15 | 0.09437 | 300.15 | 0.5
0.08385 | 280.15 | 0.09437 | 300.15 | 0.6
0.08385 | 280.15 | 0.09437 | 300.15 | 0.7
0.08385 | 280.15 | 0.09437 | 300.15 | 0.8
0.08385 | 280.15 | 0.09437 | 300.15 | 0.9
0.08385 | 280.15 | 0.09437 | 300.15 | 1
0.08385 | 280.15 | 0.09437 | 303.15 | 0.15
0.08385 | 280.15 | 0.09437 | 303.15 | 0.2
0.08385 | 280.15 | 0.09437 | 303.15 | 0.3
0.08385 | 280.15 | 0.09437 | 303.15 | 0.4
0.08385 | 280.15 | 0.09437 | 303.15 | 0.5
0.08385 | 280.15 | 0.09437 | 303.15 | 0.6
0.08385 | 280.15 | 0.09437 | 303.15 | 0.7
0.08385 | 280.15 | 0.09437 | 303.15 | 0.8
0.08385 | 280.15 | 0.09437 | 303.15 | 0.9
0.08385 | 280.15 | 0.09437 | 303.15 | 1
0.08385 | 280.15 | 0.09644 | 283.65 | 0.15
0.08385 | 280.15 | 0.09644 | 283.65 | 0.2
0.08385 | 280.15 | 0.09644 | 283.65 | 0.3
0.08385 | 280.15 | 0.09644 | 283.65 | 0.4
0.08385 | 280.15 | 0.09644 | 283.65 | 0.5
0.08385 | 280.15 | 0.09644 | 283.65 | 0.6
0.08385 | 280.15 | 0.09644 | 283.65 | 0.7
0.08385 | 280.15 | 0.09644 | 283.65 | 0.8
0.08385 | 280.15 | 0.09644 | 283.65 | 0.9
0.08385 | 280.15 | 0.09644 | 283.65 | 1
0.08385 | 280.15 | 0.09644 | 284.15 | 0.15
0.08385 | 280.15 | 0.09644 | 284.15 | 0.2
0.08385 | 280.15 | 0.09644 | 284.15 | 0.3
0.08385 | 280.15 | 0.09644 | 284.15 | 0.4
0.08385 | 280.15 | 0.09644 | 284.15 | 0.5
0.08385 | 280.15 | 0.09644 | 284.15 | 0.6
0.08385 | 280.15 | 0.09644 | 284.15 | 0.7
0.08385 | 280.15 | 0.09644 | 284.15 | 0.8
0.08385 | 280.15 | 0.09644 | 284.15 | 0.9
0.08385 | 280.15 | 0.09644 | 284.15 | 1
0.08385 | 280.15 | 0.09644 | 284.65 | 0.15
0.08385 | 280.15 | 0.09644 | 284.65 | 0.2
0.08385 | 280.15 | 0.09644 | 284.65 | 0.3
0.08385 | 280.15 | 0.09644 | 284.65 | 0.4
0.08385 | 280.15 | 0.09644 | 284.65 | 0.5
0.08385 | 280.15 | 0.09644 | 284.65 | 0.6
0.08385 | 280.15 | 0.09644 | 284.65 | 0.7
0.08385 | 280.15 | 0.09644 | 284.65 | 0.8
0.08385 | 280.15 | 0.09644 | 284.65 | 0.9
0.08385 | 280.15 | 0.09644 | 284.65 | 1
0.08385 | 280.15 | 0.09644 | 285.15 | 0.15
0.08385 | 280.15 | 0.09644 | 285.15 | 0.2
0.08385 | 280.15 | 0.09644 | 285.15 | 0.3
0.08385 | 280.15 | 0.09644 | 285.15 | 0.4
0.08385 | 280.15 | 0.09644 | 285.15 | 0.5
0.08385 | 280.15 | 0.09644 | 285.15 | 0.6
0.08385 | 280.15 | 0.09644 | 285.15 | 0.7
0.08385 | 280.15 | 0.09644 | 285.15 | 0.8
0.08385 | 280.15 | 0.09644 | 285.15 | 0.9
0.08385 | 280.15 | 0.09644 | 285.15 | 1
0.08385 | 280.15 | 0.09644 | 285.65 | 0.15
0.08385 | 280.15 | 0.09644 | 285.65 | 0.2
0.08385 | 280.15 | 0.09644 | 285.65 | 0.3
0.08385 | 280.15 | 0.09644 | 285.65 | 0.4
0.08385 | 280.15 | 0.09644 | 285.65 | 0.5
0.08385 | 280.15 | 0.09644 | 285.65 | 0.6
0.08385 | 280.15 | 0.09644 | 285.65 | 0.7
0.08385 | 280.15 | 0.09644 | 285.65 | 0.8
0.08385 | 280.15 | 0.09644 | 285.65 | 0.9
0.08385 | 280.15 | 0.09644 | 285.65 | 1
0.08385 | 280.15 | 0.09644 | 286.15 | 0.15
0.08385 | 280.15 | 0.09644 | 286.15 | 0.2
0.08385 | 280.15 | 0.09644 | 286.15 | 0.3
0.08385 | 280.15 | 0.09644 | 286.15 | 0.4
0.08385 | 280.15 | 0.09644 | 286.15 | 0.5
0.08385 | 280.15 | 0.09644 | 286.15 | 0.6
0.08385 | 280.15 | 0.09644 | 286.15 | 0.7
0.08385 | 280.15 | 0.09644 | 286.15 | 0.8
0.08385 | 280.15 | 0.09644 | 286.15 | 0.9
0.08385 | 280.15 | 0.09644 | 286.15 | 1
0.08385 | 280.15 | 0.09644 | 286.65 | 0.15
0.08385 | 280.15 | 0.09644 | 286.65 | 0.2
0.08385 | 280.15 | 0.09644 | 286.65 | 0.3
0.08385 | 280.15 | 0.09644 | 286.65 | 0.4
0.08385 | 280.15 | 0.09644 | 286.65 | 0.5
0.08385 | 280.15 | 0.09644 | 286.65 | 0.6
0.08385 | 280.15 | 0.09644 | 286.65 | 0.7
0.08385 | 280.15 | 0.09644 | 286.65 | 0.8
0.08385 | 280.15 | 0.09644 | 286.65 | 0.9
0.08385 | 280.15 | 0.09644 | 286.65 | 1
0.08385 | 280.15 | 0.09644 | 287.15 | 0.15
0.08385 | 280.15 | 0.09644 | 287.15 | 0.2
0.08385 | 280.15 | 0.09644 | 287.15 | 0.3
0.08385 | 280.15 | 0.09644 | 287.15 | 0.4
0.08385 | 280.15 | 0.09644 | 287.15 | 0.5
0.08385 | 280.15 | 0.09644 | 287.15 | 0.6
0.08385 | 280.15 | 0.09644 | 287.15 | 0.7
0.08385 | 280.15 | 0.09644 | 287.15 | 0.8
0.08385 | 280.15 | 0.09644 | 287.15 | 0.9
0.08385 | 280.15 | 0.09644 | 287.15 | 1
0.08385 | 280.15 | 0.09644 | 287.65 | 0.15
0.08385 | 280.15 | 0.09644 | 287.65 | 0.2
0.08385 | 280.15 | 0.09644 | 287.65 | 0.3
0.08385 | 280.15 | 0.09644 | 287.65 | 0.4
0.08385 | 280.15 | 0.09644 | 287.65 | 0.5
0.08385 | 280.15 | 0.09644 | 287.65 | 0.6
0.08385 | 280.15 | 0.09644 | 287.65 | 0.7
0.08385 | 280.15 | 0.09644 | 287.65 | 0.8
0.08385 | 280.15 | 0.09644 | 287.65 | 0.9
0.08385 | 280.15 | 0.09644 | 287.65 | 1
0.08385 | 280.15 | 0.09644 | 288.15 | 0.15
0.08385 | 280.15 | 0.09644 | 288.15 | 0.2
0.08385 | 280.15 | 0.09644 | 288.15 | 0.3
0.08385 | 280.15 | 0.09644 | 288.15 | 0.4
0.08385 | 280.15 | 0.09644 | 288.15 | 0.5
0.08385 | 280.15 | 0.09644 | 288.15 | 0.6
0.08385 | 280.15 | 0.09644 | 288.15 | 0.7
0.08385 | 280.15 | 0.09644 | 288.15 | 0.8
0.08385 | 280.15 | 0.09644 | 288.15 | 0.9
0.08385 | 280.15 | 0.09644 | 288.15 | 1
0.08385 | 280.15 | 0.09644 | 288.65 | 0.15
0.08385 | 280.15 | 0.09644 | 288.65 | 0.2
0.08385 | 280.15 | 0.09644 | 288.65 | 0.3
0.08385 | 280.15 | 0.09644 | 288.65 | 0.4
0.08385 | 280.15 | 0.09644 | 288.65 | 0.5
0.08385 | 280.15 | 0.09644 | 288.65 | 0.6
0.08385 | 280.15 | 0.09644 | 288.65 | 0.7
0.08385 | 280.15 | 0.09644 | 288.65 | 0.8
0.08385 | 280.15 | 0.09644 | 288.65 | 0.9
0.08385 | 280.15 | 0.09644 | 288.65 | 1
0.08385 | 280.15 | 0.09644 | 289.15 | 0.15
0.08385 | 280.15 | 0.09644 | 289.15 | 0.2
0.08385 | 280.15 | 0.09644 | 289.15 | 0.3
0.08385 | 280.15 | 0.09644 | 289.15 | 0.4
0.08385 | 280.15 | 0.09644 | 289.15 | 0.5
0.08385 | 280.15 | 0.09644 | 289.15 | 0.6
0.08385 | 280.15 | 0.09644 | 289.15 | 0.7
0.08385 | 280.15 | 0.09644 | 289.15 | 0.8
0.08385 | 280.15 | 0.09644 | 289.15 | 0.9
0.08385 | 280.15 | 0.09644 | 289.15 | 1
0.08385 | 280.15 | 0.09644 | 289.65 | 0.15
0.08385 | 280.15 | 0.09644 | 289.65 | 0.2
0.08385 | 280.15 | 0.09644 | 289.65 | 0.3
0.08385 | 280.15 | 0.09644 | 289.65 | 0.4
0.08385 | 280.15 | 0.09644 | 289.65 | 0.5
0.08385 | 280.15 | 0.09644 | 289.65 | 0.6
0.08385 | 280.15 | 0.09644 | 289.65 | 0.7
0.08385 | 280.15 | 0.09644 | 289.65 | 0.8
0.08385 | 280.15 | 0.09644 | 289.65 | 0.9
0.08385 | 280.15 | 0.09644 | 289.65 | 1
0.08385 | 280.15 | 0.09644 | 290.15 | 0.15
0.08385 | 280.15 | 0.09644 | 290.15 | 0.2
0.08385 | 280.15 | 0.09644 | 290.15 | 0.3
0.08385 | 280.15 | 0.09644 | 290.15 | 0.4
0.08385 | 280.15 | 0.09644 | 290.15 | 0.5
0.08385 | 280.15 | 0.09644 | 290.15 | 0.6
0.08385 | 280.15 | 0.09644 | 290.15 | 0.7
0.08385 | 280.15 | 0.09644 | 290.15 | 0.8
0.08385 | 280.15 | 0.09644 | 290.15 | 0.9
0.08385 | 280.15 | 0.09644 | 290.15 | 1
0.08385 | 280.15 | 0.09644 | 290.65 | 0.15
0.08385 | 280.15 | 0.09644 | 290.65 | 0.2
0.08385 | 280.15 | 0.09644 | 290.65 | 0.3
0.08385 | 280.15 | 0.09644 | 290.65 | 0.4
0.08385 | 280.15 | 0.09644 | 290.65 | 0.5
0.08385 | 280.15 | 0.09644 | 290.65 | 0.6
0.08385 | 280.15 | 0.09644 | 290.65 | 0.7
0.08385 | 280.15 | 0.09644 | 290.65 | 0.8
0.08385 | 280.15 | 0.09644 | 290.65 | 0.9
0.08385 | 280.15 | 0.09644 | 290.65 | 1
0.08385 | 280.15 | 0.09644 | 291.15 | 0.15
0.08385 | 280.15 | 0.09644 | 291.15 | 0.2
0.08385 | 280.15 | 0.09644 | 291.15 | 0.3
0.08385 | 280.15 | 0.09644 | 291.15 | 0.4
0.08385 | 280.15 | 0.09644 | 291.15 | 0.5
0.08385 | 280.15 | 0.09644 | 291.15 | 0.6
0.08385 | 280.15 | 0.09644 | 291.15 | 0.7
0.08385 | 280.15 | 0.09644 | 291.15 | 0.8
0.08385 | 280.15 | 0.09644 | 291.15 | 0.9
0.08385 | 280.15 | 0.09644 | 291.15 | 1
0.08385 | 280.15 | 0.09644 | 294.15 | 0.15
0.08385 | 280.15 | 0.09644 | 294.15 | 0.2
0.08385 | 280.15 | 0.09644 | 294.15 | 0.3
0.08385 | 280.15 | 0.09644 | 294.15 | 0.4
0.08385 | 280.15 | 0.09644 | 294.15 | 0.5
0.08385 | 280.15 | 0.09644 | 294.15 | 0.6
0.08385 | 280.15 | 0.09644 | 294.15 | 0.7
0.08385 | 280.15 | 0.09644 | 294.15 | 0.8
0.08385 | 280.15 | 0.09644 | 294.15 | 0.9
0.08385 | 280.15 | 0.09644 | 294.15 | 1
0.08385 | 280.15 | 0.09644 | 297.15 | 0.15
0.08385 | 280.15 | 0.09644 | 297.15 | 0.2
0.08385 | 280.15 | 0.09644 | 297.15 | 0.3
0.08385 | 280.15 | 0.09644 | 297.15 | 0.4
0.08385 | 280.15 | 0.09644 | 297.15 | 0.5
0.08385 | 280.15 | 0.09644 | 297.15 | 0.6
0.08385 | 280.15 | 0.09644 | 297.15 | 0.7
0.08385 | 280.15 | 0.09644 | 297.15 | 0.8
0.08385 | 280.15 | 0.09644 | 297.15 | 0.9
0.08385 | 280.15 | 0.09644 | 297.15 | 1
0.08385 | 280.15 | 0.09644 | 300.15 | 0.15
0.08385 | 280.15 | 0.09644 | 300.15 | 0.2
0.08385 | 280.15 | 0.09644 | 300.15 | 0.3
0.08385 | 280.15 | 0.09644 | 300.15 | 0.4
0.08385 | 280.15 | 0.09644 | 300.15 | 0.5
0.08385 | 280.15 | 0.09644 | 300.15 | 0.6
0.08385 | 280.15 | 0.09644 | 300.15 | 0.7
0.08385 | 280.15 | 0.09644 | 300.15 | 0.8
0.08385 | 280.15 | 0.09644 | 300.15 | 0.9
0.08385 | 280.15 | 0.09644 | 300.15 | 1
0.08385 | 280.15 | 0.09644 | 303.15 | 0.15
0.08385 | 280.15 | 0.09644 | 303.15 | 0.2
0.08385 | 280.15 | 0.09644 | 303.15 | 0.3
0.08385 | 280.15 | 0.09644 | 303.15 | 0.4
0.08385 | 280.15 | 0.09644 | 303.15 | 0.5
0.08385 | 280.15 | 0.09644 | 303.15 | 0.6
0.08385 | 280.15 | 0.09644 | 303.15 | 0.7
0.08385 | 280.15 | 0.09644 | 303.15 | 0.8
0.08385 | 280.15 | 0.09644 | 303.15 | 0.9
0.08385 | 280.15 | 0.09644 | 303.15 | 1
0.08385 | 280.15 | 0.09737 | 283.65 | 0.15
0.08385 | 280.15 | 0.09737 | 283.65 | 0.2
0.08385 | 280.15 | 0.09737 | 283.65 | 0.3
0.08385 | 280.15 | 0.09737 | 283.65 | 0.4
0.08385 | 280.15 | 0.09737 | 283.65 | 0.5
0.08385 | 280.15 | 0.09737 | 283.65 | 0.6
0.08385 | 280.15 | 0.09737 | 283.65 | 0.7
0.08385 | 280.15 | 0.09737 | 283.65 | 0.8
0.08385 | 280.15 | 0.09737 | 283.65 | 0.9
0.08385 | 280.15 | 0.09737 | 283.65 | 1
0.08385 | 280.15 | 0.09737 | 284.15 | 0.15
0.08385 | 280.15 | 0.09737 | 284.15 | 0.2
0.08385 | 280.15 | 0.09737 | 284.15 | 0.3
0.08385 | 280.15 | 0.09737 | 284.15 | 0.4
0.08385 | 280.15 | 0.09737 | 284.15 | 0.5
0.08385 | 280.15 | 0.09737 | 284.15 | 0.6
0.08385 | 280.15 | 0.09737 | 284.15 | 0.7
0.08385 | 280.15 | 0.09737 | 284.15 | 0.8
0.08385 | 280.15 | 0.09737 | 284.15 | 0.9
0.08385 | 280.15 | 0.09737 | 284.15 | 1
0.08385 | 280.15 | 0.09737 | 284.65 | 0.15
0.08385 | 280.15 | 0.09737 | 284.65 | 0.2
0.08385 | 280.15 | 0.09737 | 284.65 | 0.3
0.08385 | 280.15 | 0.09737 | 284.65 | 0.4
0.08385 | 280.15 | 0.09737 | 284.65 | 0.5
0.08385 | 280.15 | 0.09737 | 284.65 | 0.6
0.08385 | 280.15 | 0.09737 | 284.65 | 0.7
0.08385 | 280.15 | 0.09737 | 284.65 | 0.8
0.08385 | 280.15 | 0.09737 | 284.65 | 0.9
0.08385 | 280.15 | 0.09737 | 284.65 | 1
0.08385 | 280.15 | 0.09737 | 285.15 | 0.15
0.08385 | 280.15 | 0.09737 | 285.15 | 0.2
0.08385 | 280.15 | 0.09737 | 285.15 | 0.3
0.08385 | 280.15 | 0.09737 | 285.15 | 0.4
0.08385 | 280.15 | 0.09737 | 285.15 | 0.5
0.08385 | 280.15 | 0.09737 | 285.15 | 0.6
0.08385 | 280.15 | 0.09737 | 285.15 | 0.7
0.08385 | 280.15 | 0.09737 | 285.15 | 0.8
0.08385 | 280.15 | 0.09737 | 285.15 | 0.9
0.08385 | 280.15 | 0.09737 | 285.15 | 1
0.08385 | 280.15 | 0.09737 | 285.65 | 0.15
0.08385 | 280.15 | 0.09737 | 285.65 | 0.2
0.08385 | 280.15 | 0.09737 | 285.65 | 0.3
0.08385 | 280.15 | 0.09737 | 285.65 | 0.4
0.08385 | 280.15 | 0.09737 | 285.65 | 0.5
0.08385 | 280.15 | 0.09737 | 285.65 | 0.6
0.08385 | 280.15 | 0.09737 | 285.65 | 0.7
0.08385 | 280.15 | 0.09737 | 285.65 | 0.8
0.08385 | 280.15 | 0.09737 | 285.65 | 0.9
0.08385 | 280.15 | 0.09737 | 285.65 | 1
0.08385 | 280.15 | 0.09737 | 286.15 | 0.15
0.08385 | 280.15 | 0.09737 | 286.15 | 0.2
0.08385 | 280.15 | 0.09737 | 286.15 | 0.3
0.08385 | 280.15 | 0.09737 | 286.15 | 0.4
0.08385 | 280.15 | 0.09737 | 286.15 | 0.5
0.08385 | 280.15 | 0.09737 | 286.15 | 0.6
0.08385 | 280.15 | 0.09737 | 286.15 | 0.7
0.08385 | 280.15 | 0.09737 | 286.15 | 0.8
0.08385 | 280.15 | 0.09737 | 286.15 | 0.9
0.08385 | 280.15 | 0.09737 | 286.15 | 1
0.08385 | 280.15 | 0.09737 | 286.65 | 0.15
0.08385 | 280.15 | 0.09737 | 286.65 | 0.2
0.08385 | 280.15 | 0.09737 | 286.65 | 0.3
0.08385 | 280.15 | 0.09737 | 286.65 | 0.4
0.08385 | 280.15 | 0.09737 | 286.65 | 0.5
0.08385 | 280.15 | 0.09737 | 286.65 | 0.6
0.08385 | 280.15 | 0.09737 | 286.65 | 0.7
0.08385 | 280.15 | 0.09737 | 286.65 | 0.8
0.08385 | 280.15 | 0.09737 | 286.65 | 0.9
0.08385 | 280.15 | 0.09737 | 286.65 | 1
0.08385 | 280.15 | 0.09737 | 287.15 | 0.15
0.08385 | 280.15 | 0.09737 | 287.15 | 0.2
0.08385 | 280.15 | 0.09737 | 287.15 | 0.3
0.08385 | 280.15 | 0.09737 | 287.15 | 0.4
0.08385 | 280.15 | 0.09737 | 287.15 | 0.5
0.08385 | 280.15 | 0.09737 | 287.15 | 0.6
0.08385 | 280.15 | 0.09737 | 287.15 | 0.7
0.08385 | 280.15 | 0.09737 | 287.15 | 0.8
0.08385 | 280.15 | 0.09737 | 287.15 | 0.9
0.08385 | 280.15 | 0.09737 | 287.15 | 1
0.08385 | 280.15 | 0.09737 | 287.65 | 0.15
0.08385 | 280.15 | 0.09737 | 287.65 | 0.2
0.08385 | 280.15 | 0.09737 | 287.65 | 0.3
0.08385 | 280.15 | 0.09737 | 287.65 | 0.4
0.08385 | 280.15 | 0.09737 | 287.65 | 0.5
0.08385 | 280.15 | 0.09737 | 287.65 | 0.6
0.08385 | 280.15 | 0.09737 | 287.65 | 0.7
0.08385 | 280.15 | 0.09737 | 287.65 | 0.8
0.08385 | 280.15 | 0.09737 | 287.65 | 0.9
0.08385 | 280.15 | 0.09737 | 287.65 | 1
0.08385 | 280.15 | 0.09737 | 288.15 | 0.15
0.08385 | 280.15 | 0.09737 | 288.15 | 0.2
0.08385 | 280.15 | 0.09737 | 288.15 | 0.3
0.08385 | 280.15 | 0.09737 | 288.15 | 0.4
0.08385 | 280.15 | 0.09737 | 288.15 | 0.5
0.08385 | 280.15 | 0.09737 | 288.15 | 0.6
0.08385 | 280.15 | 0.09737 | 288.15 | 0.7
0.08385 | 280.15 | 0.09737 | 288.15 | 0.8
0.08385 | 280.15 | 0.09737 | 288.15 | 0.9
0.08385 | 280.15 | 0.09737 | 288.15 | 1
0.08385 | 280.15 | 0.09737 | 288.65 | 0.15
0.08385 | 280.15 | 0.09737 | 288.65 | 0.2
0.08385 | 280.15 | 0.09737 | 288.65 | 0.3
0.08385 | 280.15 | 0.09737 | 288.65 | 0.4
0.08385 | 280.15 | 0.09737 | 288.65 | 0.5
0.08385 | 280.15 | 0.09737 | 288.65 | 0.6
0.08385 | 280.15 | 0.09737 | 288.65 | 0.7
0.08385 | 280.15 | 0.09737 | 288.65 | 0.8
0.08385 | 280.15 | 0.09737 | 288.65 | 0.9
0.08385 | 280.15 | 0.09737 | 288.65 | 1
0.08385 | 280.15 | 0.09737 | 289.15 | 0.15
0.08385 | 280.15 | 0.09737 | 289.15 | 0.2
0.08385 | 280.15 | 0.09737 | 289.15 | 0.3
0.08385 | 280.15 | 0.09737 | 289.15 | 0.4
0.08385 | 280.15 | 0.09737 | 289.15 | 0.5
0.08385 | 280.15 | 0.09737 | 289.15 | 0.6
0.08385 | 280.15 | 0.09737 | 289.15 | 0.7
0.08385 | 280.15 | 0.09737 | 289.15 | 0.8
0.08385 | 280.15 | 0.09737 | 289.15 | 0.9
0.08385 | 280.15 | 0.09737 | 289.15 | 1
0.08385 | 280.15 | 0.09737 | 289.65 | 0.15
0.08385 | 280.15 | 0.09737 | 289.65 | 0.2
0.08385 | 280.15 | 0.09737 | 289.65 | 0.3
0.08385 | 280.15 | 0.09737 | 289.65 | 0.4
0.08385 | 280.15 | 0.09737 | 289.65 | 0.5
0.08385 | 280.15 | 0.09737 | 289.65 | 0.6
0.08385 | 280.15 | 0.09737 | 289.65 | 0.7
0.08385 | 280.15 | 0.09737 | 289.65 | 0.8
0.08385 | 280.15 | 0.09737 | 289.65 | 0.9
0.08385 | 280.15 | 0.09737 | 289.65 | 1
0.08385 | 280.15 | 0.09737 | 290.15 | 0.15
0.08385 | 280.15 | 0.09737 | 290.15 | 0.2
0.08385 | 280.15 | 0.09737 | 290.15 | 0.3
0.08385 | 280.15 | 0.09737 | 290.15 | 0.4
0.08385 | 280.15 | 0.09737 | 290.15 | 0.5
0.08385 | 280.15 | 0.09737 | 290.15 | 0.6
0.08385 | 280.15 | 0.09737 | 290.15 | 0.7
0.08385 | 280.15 | 0.09737 | 290.15 | 0.8
0.08385 | 280.15 | 0.09737 | 290.15 | 0.9
0.08385 | 280.15 | 0.09737 | 290.15 | 1
0.08385 | 280.15 | 0.09737 | 290.65 | 0.15
0.08385 | 280.15 | 0.09737 | 290.65 | 0.2
0.08385 | 280.15 | 0.09737 | 290.65 | 0.3
0.08385 | 280.15 | 0.09737 | 290.65 | 0.4
0.08385 | 280.15 | 0.09737 | 290.65 | 0.5
0.08385 | 280.15 | 0.09737 | 290.65 | 0.6
0.08385 | 280.15 | 0.09737 | 290.65 | 0.7
0.08385 | 280.15 | 0.09737 | 290.65 | 0.8
0.08385 | 280.15 | 0.09737 | 290.65 | 0.9
0.08385 | 280.15 | 0.09737 | 290.65 | 1
0.08385 | 280.15 | 0.09737 | 291.15 | 0.15
0.08385 | 280.15 | 0.09737 | 291.15 | 0.2
0.08385 | 280.15 | 0.09737 | 291.15 | 0.3
0.08385 | 280.15 | 0.09737 | 291.15 | 0.4
0.08385 | 280.15 | 0.09737 | 291.15 | 0.5
0.08385 | 280.15 | 0.09737 | 291.15 | 0.6
0.08385 | 280.15 | 0.09737 | 291.15 | 0.7
0.08385 | 280.15 | 0.09737 | 291.15 | 0.8
0.08385 | 280.15 | 0.09737 | 291.15 | 0.9
0.08385 | 280.15 | 0.09737 | 291.15 | 1
0.08385 | 280.15 | 0.09737 | 294.15 | 0.15
0.08385 | 280.15 | 0.09737 | 294.15 | 0.2
0.08385 | 280.15 | 0.09737 | 294.15 | 0.3
0.08385 | 280.15 | 0.09737 | 294.15 | 0.4
0.08385 | 280.15 | 0.09737 | 294.15 | 0.5
0.08385 | 280.15 | 0.09737 | 294.15 | 0.6
0.08385 | 280.15 | 0.09737 | 294.15 | 0.7
0.08385 | 280.15 | 0.09737 | 294.15 | 0.8
0.08385 | 280.15 | 0.09737 | 294.15 | 0.9
0.08385 | 280.15 | 0.09737 | 294.15 | 1
0.08385 | 280.15 | 0.09737 | 297.15 | 0.15
0.08385 | 280.15 | 0.09737 | 297.15 | 0.2
0.08385 | 280.15 | 0.09737 | 297.15 | 0.3
0.08385 | 280.15 | 0.09737 | 297.15 | 0.4
0.08385 | 280.15 | 0.09737 | 297.15 | 0.5
0.08385 | 280.15 | 0.09737 | 297.15 | 0.6
0.08385 | 280.15 | 0.09737 | 297.15 | 0.7
0.08385 | 280.15 | 0.09737 | 297.15 | 0.8
0.08385 | 280.15 | 0.09737 | 297.15 | 0.9
0.08385 | 280.15 | 0.09737 | 297.15 | 1
0.08385 | 280.15 | 0.09737 | 300.15 | 0.15
0.08385 | 280.15 | 0.09737 | 300.15 | 0.2
0.08385 | 280.15 | 0.09737 | 300.15 | 0.3
0.08385 | 280.15 | 0.09737 | 300.15 | 0.4
0.08385 | 280.15 | 0.09737 | 300.15 | 0.5
0.08385 | 280.15 | 0.09737 | 300.15 | 0.6
0.08385 | 280.15 | 0.09737 | 300.15 | 0.7
0.08385 | 280.15 | 0.09737 | 300.15 | 0.8
0.08385 | 280.15 | 0.09737 | 300.15 | 0.9
0.08385 | 280.15 | 0.09737 | 300.15 | 1
0.08385 | 280.15 | 0.09737 | 303.15 | 0.15
0.08385 | 280.15 | 0.09737 | 303.15 | 0.2
0.08385 | 280.15 | 0.09737 | 303.15 | 0.3
0.08385 | 280.15 | 0.09737 | 303.15 | 0.4
0.08385 | 280.15 | 0.09737 | 303.15 | 0.5
0.08385 | 280.15 | 0.09737 | 303.15 | 0.6
0.08385 | 280.15 | 0.09737 | 303.15 | 0.7
0.08385 | 280.15 | 0.09737 | 303.15 | 0.8
0.08385 | 280.15 | 0.09737 | 303.15 | 0.9
0.08385 | 280.15 | 0.09737 | 303.15 | 1
0.08385 | 280.15 | 0.115 | 283.65 | 0.15
0.08385 | 280.15 | 0.115 | 283.65 | 0.2
0.08385 | 280.15 | 0.115 | 283.65 | 0.3
0.08385 | 280.15 | 0.115 | 283.65 | 0.4
0.08385 | 280.15 | 0.115 | 283.65 | 0.5
0.08385 | 280.15 | 0.115 | 283.65 | 0.6
0.08385 | 280.15 | 0.115 | 283.65 | 0.7
0.08385 | 280.15 | 0.115 | 283.65 | 0.8
0.08385 | 280.15 | 0.115 | 283.65 | 0.9
0.08385 | 280.15 | 0.115 | 283.65 | 1
0.08385 | 280.15 | 0.115 | 284.15 | 0.15
0.08385 | 280.15 | 0.115 | 284.15 | 0.2
0.08385 | 280.15 | 0.115 | 284.15 | 0.3
0.08385 | 280.15 | 0.115 | 284.15 | 0.4
0.08385 | 280.15 | 0.115 | 284.15 | 0.5
0.08385 | 280.15 | 0.115 | 284.15 | 0.6
0.08385 | 280.15 | 0.115 | 284.15 | 0.7
0.08385 | 280.15 | 0.115 | 284.15 | 0.8
0.08385 | 280.15 | 0.115 | 284.15 | 0.9
0.08385 | 280.15 | 0.115 | 284.15 | 1
0.08385 | 280.15 | 0.115 | 284.65 | 0.15
0.08385 | 280.15 | 0.115 | 284.65 | 0.2
0.08385 | 280.15 | 0.115 | 284.65 | 0.3
0.08385 | 280.15 | 0.115 | 284.65 | 0.4
0.08385 | 280.15 | 0.115 | 284.65 | 0.5
0.08385 | 280.15 | 0.115 | 284.65 | 0.6
0.08385 | 280.15 | 0.115 | 284.65 | 0.7
0.08385 | 280.15 | 0.115 | 284.65 | 0.8
0.08385 | 280.15 | 0.115 | 284.65 | 0.9
0.08385 | 280.15 | 0.115 | 284.65 | 1
0.08385 | 280.15 | 0.115 | 285.15 | 0.15
0.08385 | 280.15 | 0.115 | 285.15 | 0.2
0.08385 | 280.15 | 0.115 | 285.15 | 0.3
0.08385 | 280.15 | 0.115 | 285.15 | 0.4
0.08385 | 280.15 | 0.115 | 285.15 | 0.5
0.08385 | 280.15 | 0.115 | 285.15 | 0.6
0.08385 | 280.15 | 0.115 | 285.15 | 0.7
0.08385 | 280.15 | 0.115 | 285.15 | 0.8
0.08385 | 280.15 | 0.115 | 285.15 | 0.9
0.08385 | 280.15 | 0.115 | 285.15 | 1
0.08385 | 280.15 | 0.115 | 285.65 | 0.15
0.08385 | 280.15 | 0.115 | 285.65 | 0.2
0.08385 | 280.15 | 0.115 | 285.65 | 0.3
0.08385 | 280.15 | 0.115 | 285.65 | 0.4
0.08385 | 280.15 | 0.115 | 285.65 | 0.5
0.08385 | 280.15 | 0.115 | 285.65 | 0.6
0.08385 | 280.15 | 0.115 | 285.65 | 0.7
0.08385 | 280.15 | 0.115 | 285.65 | 0.8
0.08385 | 280.15 | 0.115 | 285.65 | 0.9
0.08385 | 280.15 | 0.115 | 285.65 | 1
0.08385 | 280.15 | 0.115 | 286.15 | 0.15
0.08385 | 280.15 | 0.115 | 286.15 | 0.2
0.08385 | 280.15 | 0.115 | 286.15 | 0.3
0.08385 | 280.15 | 0.115 | 286.15 | 0.4
0.08385 | 280.15 | 0.115 | 286.15 | 0.5
0.08385 | 280.15 | 0.115 | 286.15 | 0.6
0.08385 | 280.15 | 0.115 | 286.15 | 0.7
0.08385 | 280.15 | 0.115 | 286.15 | 0.8
0.08385 | 280.15 | 0.115 | 286.15 | 0.9
0.08385 | 280.15 | 0.115 | 286.15 | 1
0.08385 | 280.15 | 0.115 | 286.65 | 0.15
0.08385 | 280.15 | 0.115 | 286.65 | 0.2
0.08385 | 280.15 | 0.115 | 286.65 | 0.3
0.08385 | 280.15 | 0.115 | 286.65 | 0.4
0.08385 | 280.15 | 0.115 | 286.65 | 0.5
0.08385 | 280.15 | 0.115 | 286.65 | 0.6
0.08385 | 280.15 | 0.115 | 286.65 | 0.7
0.08385 | 280.15 | 0.115 | 286.65 | 0.8
0.08385 | 280.15 | 0.115 | 286.65 | 0.9
0.08385 | 280.15 | 0.115 | 286.65 | 1
0.08385 | 280.15 | 0.115 | 287.15 | 0.15
0.08385 | 280.15 | 0.115 | 287.15 | 0.2
0.08385 | 280.15 | 0.115 | 287.15 | 0.3
0.08385 | 280.15 | 0.115 | 287.15 | 0.4
0.08385 | 280.15 | 0.115 | 287.15 | 0.5
0.08385 | 280.15 | 0.115 | 287.15 | 0.6
0.08385 | 280.15 | 0.115 | 287.15 | 0.7
0.08385 | 280.15 | 0.115 | 287.15 | 0.8
0.08385 | 280.15 | 0.115 | 287.15 | 0.9
0.08385 | 280.15 | 0.115 | 287.15 | 1
0.08385 | 280.15 | 0.115 | 287.65 | 0.15
0.08385 | 280.15 | 0.115 | 287.65 | 0.2
0.08385 | 280.15 | 0.115 | 287.65 | 0.3
0.08385 | 280.15 | 0.115 | 287.65 | 0.4
0.08385 | 280.15 | 0.115 | 287.65 | 0.5
0.08385 | 280.15 | 0.115 | 287.65 | 0.6
0.08385 | 280.15 | 0.115 | 287.65 | 0.7
0.08385 | 280.15 | 0.115 | 287.65 | 0.8
0.08385 | 280.15 | 0.115 | 287.65 | 0.9
0.08385 | 280.15 | 0.115 | 287.65 | 1
0.08385 | 280.15 | 0.115 | 288.15 | 0.15
0.08385 | 280.15 | 0.115 | 288.15 | 0.2
0.08385 | 280.15 | 0.115 | 288.15 | 0.3
0.08385 | 280.15 | 0.115 | 288.15 | 0.4
0.08385 | 280.15 | 0.115 | 288.15 | 0.5
0.08385 | 280.15 | 0.115 | 288.15 | 0.6
0.08385 | 280.15 | 0.115 | 288.15 | 0.7
0.08385 | 280.15 | 0.115 | 288.15 | 0.8
0.08385 | 280.15 | 0.115 | 288.15 | 0.9
0.08385 | 280.15 | 0.115 | 288.15 | 1
0.08385 | 280.15 | 0.115 | 288.65 | 0.15
0.08385 | 280.15 | 0.115 | 288.65 | 0.2
0.08385 | 280.15 | 0.115 | 288.65 | 0.3
0.08385 | 280.15 | 0.115 | 288.65 | 0.4
0.08385 | 280.15 | 0.115 | 288.65 | 0.5
0.08385 | 280.15 | 0.115 | 288.65 | 0.6
0.08385 | 280.15 | 0.115 | 288.65 | 0.7
0.08385 | 280.15 | 0.115 | 288.65 | 0.8
0.08385 | 280.15 | 0.115 | 288.65 | 0.9
0.08385 | 280.15 | 0.115 | 288.65 | 1
0.08385 | 280.15 | 0.115 | 289.15 | 0.15
0.08385 | 280.15 | 0.115 | 289.15 | 0.2
0.08385 | 280.15 | 0.115 | 289.15 | 0.3
0.08385 | 280.15 | 0.115 | 289.15 | 0.4
0.08385 | 280.15 | 0.115 | 289.15 | 0.5
0.08385 | 280.15 | 0.115 | 289.15 | 0.6
0.08385 | 280.15 | 0.115 | 289.15 | 0.7
0.08385 | 280.15 | 0.115 | 289.15 | 0.8
0.08385 | 280.15 | 0.115 | 289.15 | 0.9
0.08385 | 280.15 | 0.115 | 289.15 | 1
0.08385 | 280.15 | 0.115 | 289.65 | 0.15
0.08385 | 280.15 | 0.115 | 289.65 | 0.2
0.08385 | 280.15 | 0.115 | 289.65 | 0.3
0.08385 | 280.15 | 0.115 | 289.65 | 0.4
0.08385 | 280.15 | 0.115 | 289.65 | 0.5
0.08385 | 280.15 | 0.115 | 289.65 | 0.6
0.08385 | 280.15 | 0.115 | 289.65 | 0.7
0.08385 | 280.15 | 0.115 | 289.65 | 0.8
0.08385 | 280.15 | 0.115 | 289.65 | 0.9
0.08385 | 280.15 | 0.115 | 289.65 | 1
0.08385 | 280.15 | 0.115 | 290.15 | 0.15
0.08385 | 280.15 | 0.115 | 290.15 | 0.2
0.08385 | 280.15 | 0.115 | 290.15 | 0.3
0.08385 | 280.15 | 0.115 | 290.15 | 0.4
0.08385 | 280.15 | 0.115 | 290.15 | 0.5
0.08385 | 280.15 | 0.115 | 290.15 | 0.6
0.08385 | 280.15 | 0.115 | 290.15 | 0.7
0.08385 | 280.15 | 0.115 | 290.15 | 0.8
0.08385 | 280.15 | 0.115 | 290.15 | 0.9
0.08385 | 280.15 | 0.115 | 290.15 | 1
0.08385 | 280.15 | 0.115 | 290.65 | 0.15
0.08385 | 280.15 | 0.115 | 290.65 | 0.2
0.08385 | 280.15 | 0.115 | 290.65 | 0.3
0.08385 | 280.15 | 0.115 | 290.65 | 0.4
0.08385 | 280.15 | 0.115 | 290.65 | 0.5
0.08385 | 280.15 | 0.115 | 290.65 | 0.6
0.08385 | 280.15 | 0.115 | 290.65 | 0.7
0.08385 | 280.15 | 0.115 | 290.65 | 0.8
0.08385 | 280.15 | 0.115 | 290.65 | 0.9
0.08385 | 280.15 | 0.115 | 290.65 | 1
0.08385 | 280.15 | 0.115 | 291.15 | 0.15
0.08385 | 280.15 | 0.115 | 291.15 | 0.2
0.08385 | 280.15 | 0.115 | 291.15 | 0.3
0.08385 | 280.15 | 0.115 | 291.15 | 0.4
0.08385 | 280.15 | 0.115 | 291.15 | 0.5
0.08385 | 280.15 | 0.115 | 291.15 | 0.6
0.08385 | 280.15 | 0.115 | 291.15 | 0.7
0.08385 | 280.15 | 0.115 | 291.15 | 0.8
0.08385 | 280.15 | 0.115 | 291.15 | 0.9
0.08385 | 280.15 | 0.115 | 291.15 | 1
0.08385 | 280.15 | 0.115 | 294.15 | 0.15
0.08385 | 280.15 | 0.115 | 294.15 | 0.2
0.08385 | 280.15 | 0.115 | 294.15 | 0.3
0.08385 | 280.15 | 0.115 | 294.15 | 0.4
0.08385 | 280.15 | 0.115 | 294.15 | 0.5
0.08385 | 280.15 | 0.115 | 294.15 | 0.6
0.08385 | 280.15 | 0.115 | 294.15 | 0.7
0.08385 | 280.15 | 0.115 | 294.15 | 0.8
0.08385 | 280.15 | 0.115 | 294.15 | 0.9
0.08385 | 280.15 | 0.115 | 294.15 | 1
0.08385 | 280.15 | 0.115 | 297.15 | 0.15
0.08385 | 280.15 | 0.115 | 297.15 | 0.2
0.08385 | 280.15 | 0.115 | 297.15 | 0.3
0.08385 | 280.15 | 0.115 | 297.15 | 0.4
0.08385 | 280.15 | 0.115 | 297.15 | 0.5
0.08385 | 280.15 | 0.115 | 297.15 | 0.6
0.08385 | 280.15 | 0.115 | 297.15 | 0.7
0.08385 | 280.15 | 0.115 | 297.15 | 0.8
0.08385 | 280.15 | 0.115 | 297.15 | 0.9
0.08385 | 280.15 | 0.115 | 297.15 | 1
0.08385 | 280.15 | 0.115 | 300.15 | 0.15
0.08385 | 280.15 | 0.115 | 300.15 | 0.2
0.08385 | 280.15 | 0.115 | 300.15 | 0.3
0.08385 | 280.15 | 0.115 | 300.15 | 0.4
0.08385 | 280.15 | 0.115 | 300.15 | 0.5
0.08385 | 280.15 | 0.115 | 300.15 | 0.6
0.08385 | 280.15 | 0.115 | 300.15 | 0.7
0.08385 | 280.15 | 0.115 | 300.15 | 0.8
0.08385 | 280.15 | 0.115 | 300.15 | 0.9
0.08385 | 280.15 | 0.115 | 300.15 | 1
0.08385 | 280.15 | 0.115 | 303.15 | 0.15
0.08385 | 280.15 | 0.115 | 303.15 | 0.2
0.08385 | 280.15 | 0.115 | 303.15 | 0.3
0.08385 | 280.15 | 0.115 | 303.15 | 0.4
0.08385 | 280.15 | 0.115 | 303.15 | 0.5
0.08385 | 280.15 | 0.115 | 303.15 | 0.6
0.08385 | 280.15 | 0.115 | 303.15 | 0.7
0.08385 | 280.15 | 0.115 | 303.15 | 0.8
0.08385 | 280.15 | 0.115 | 303.15 | 0.9
0.08385 | 280.15 | 0.115 | 303.15 | 1
0.08385 | 282.15 | 0.00115 | 283.65 | 0.15
0.08385 | 282.15 | 0.00115 | 283.65 | 0.2
0.08385 | 282.15 | 0.00115 | 283.65 | 0.3
0.08385 | 282.15 | 0.00115 | 283.65 | 0.4
0.08385 | 282.15 | 0.00115 | 283.65 | 0.5
0.08385 | 282.15 | 0.00115 | 283.65 | 0.6
0.08385 | 282.15 | 0.00115 | 283.65 | 0.7
0.08385 | 282.15 | 0.00115 | 283.65 | 0.8
0.08385 | 282.15 | 0.00115 | 283.65 | 0.9
0.08385 | 282.15 | 0.00115 | 283.65 | 1
0.08385 | 282.15 | 0.00115 | 284.15 | 0.15
0.08385 | 282.15 | 0.00115 | 284.15 | 0.2
0.08385 | 282.15 | 0.00115 | 284.15 | 0.3
0.08385 | 282.15 | 0.00115 | 284.15 | 0.4
0.08385 | 282.15 | 0.00115 | 284.15 | 0.5
0.08385 | 282.15 | 0.00115 | 284.15 | 0.6
0.08385 | 282.15 | 0.00115 | 284.15 | 0.7
0.08385 | 282.15 | 0.00115 | 284.15 | 0.8
0.08385 | 282.15 | 0.00115 | 284.15 | 0.9
0.08385 | 282.15 | 0.00115 | 284.15 | 1
0.08385 | 282.15 | 0.00115 | 284.65 | 0.15
0.08385 | 282.15 | 0.00115 | 284.65 | 0.2
0.08385 | 282.15 | 0.00115 | 284.65 | 0.3
0.08385 | 282.15 | 0.00115 | 284.65 | 0.4
0.08385 | 282.15 | 0.00115 | 284.65 | 0.5
0.08385 | 282.15 | 0.00115 | 284.65 | 0.6
0.08385 | 282.15 | 0.00115 | 284.65 | 0.7
0.08385 | 282.15 | 0.00115 | 284.65 | 0.8
0.08385 | 282.15 | 0.00115 | 284.65 | 0.9
0.08385 | 282.15 | 0.00115 | 284.65 | 1
0.08385 | 282.15 | 0.00115 | 285.15 | 0.15
0.08385 | 282.15 | 0.00115 | 285.15 | 0.2
0.08385 | 282.15 | 0.00115 | 285.15 | 0.3
0.08385 | 282.15 | 0.00115 | 285.15 | 0.4
0.08385 | 282.15 | 0.00115 | 285.15 | 0.5
0.08385 | 282.15 | 0.00115 | 285.15 | 0.6
0.08385 | 282.15 | 0.00115 | 285.15 | 0.7
0.08385 | 282.15 | 0.00115 | 285.15 | 0.8
0.08385 | 282.15 | 0.00115 | 285.15 | 0.9
0.08385 | 282.15 | 0.00115 | 285.15 | 1
0.08385 | 282.15 | 0.00115 | 285.65 | 0.15
0.08385 | 282.15 | 0.00115 | 285.65 | 0.2
0.08385 | 282.15 | 0.00115 | 285.65 | 0.3
0.08385 | 282.15 | 0.00115 | 285.65 | 0.4
0.08385 | 282.15 | 0.00115 | 285.65 | 0.5
0.08385 | 282.15 | 0.00115 | 285.65 | 0.6
0.08385 | 282.15 | 0.00115 | 285.65 | 0.7
0.08385 | 282.15 | 0.00115 | 285.65 | 0.8
0.08385 | 282.15 | 0.00115 | 285.65 | 0.9
0.08385 | 282.15 | 0.00115 | 285.65 | 1
0.08385 | 282.15 | 0.00115 | 286.15 | 0.15
0.08385 | 282.15 | 0.00115 | 286.15 | 0.2
0.08385 | 282.15 | 0.00115 | 286.15 | 0.3
0.08385 | 282.15 | 0.00115 | 286.15 | 0.4
0.08385 | 282.15 | 0.00115 | 286.15 | 0.5
0.08385 | 282.15 | 0.00115 | 286.15 | 0.6
0.08385 | 282.15 | 0.00115 | 286.15 | 0.7
0.08385 | 282.15 | 0.00115 | 286.15 | 0.8
0.08385 | 282.15 | 0.00115 | 286.15 | 0.9
0.08385 | 282.15 | 0.00115 | 286.15 | 1
0.08385 | 282.15 | 0.00115 | 286.65 | 0.15
0.08385 | 282.15 | 0.00115 | 286.65 | 0.2
0.08385 | 282.15 | 0.00115 | 286.65 | 0.3
0.08385 | 282.15 | 0.00115 | 286.65 | 0.4
0.08385 | 282.15 | 0.00115 | 286.65 | 0.5
0.08385 | 282.15 | 0.00115 | 286.65 | 0.6
0.08385 | 282.15 | 0.00115 | 286.65 | 0.7
0.08385 | 282.15 | 0.00115 | 286.65 | 0.8
0.08385 | 282.15 | 0.00115 | 286.65 | 0.9
0.08385 | 282.15 | 0.00115 | 286.65 | 1
0.08385 | 282.15 | 0.00115 | 287.15 | 0.15
0.08385 | 282.15 | 0.00115 | 287.15 | 0.2
0.08385 | 282.15 | 0.00115 | 287.15 | 0.3
0.08385 | 282.15 | 0.00115 | 287.15 | 0.4
0.08385 | 282.15 | 0.00115 | 287.15 | 0.5
0.08385 | 282.15 | 0.00115 | 287.15 | 0.6
0.08385 | 282.15 | 0.00115 | 287.15 | 0.7
0.08385 | 282.15 | 0.00115 | 287.15 | 0.8
0.08385 | 282.15 | 0.00115 | 287.15 | 0.9
0.08385 | 282.15 | 0.00115 | 287.15 | 1
0.08385 | 282.15 | 0.00115 | 287.65 | 0.15
0.08385 | 282.15 | 0.00115 | 287.65 | 0.2
0.08385 | 282.15 | 0.00115 | 287.65 | 0.3
0.08385 | 282.15 | 0.00115 | 287.65 | 0.4
0.08385 | 282.15 | 0.00115 | 287.65 | 0.5
0.08385 | 282.15 | 0.00115 | 287.65 | 0.6
0.08385 | 282.15 | 0.00115 | 287.65 | 0.7
0.08385 | 282.15 | 0.00115 | 287.65 | 0.8
0.08385 | 282.15 | 0.00115 | 287.65 | 0.9
0.08385 | 282.15 | 0.00115 | 287.65 | 1
0.08385 | 282.15 | 0.00115 | 288.15 | 0.15
0.08385 | 282.15 | 0.00115 | 288.15 | 0.2
0.08385 | 282.15 | 0.00115 | 288.15 | 0.3
0.08385 | 282.15 | 0.00115 | 288.15 | 0.4
0.08385 | 282.15 | 0.00115 | 288.15 | 0.5
0.08385 | 282.15 | 0.00115 | 288.15 | 0.6
0.08385 | 282.15 | 0.00115 | 288.15 | 0.7
0.08385 | 282.15 | 0.00115 | 288.15 | 0.8
0.08385 | 282.15 | 0.00115 | 288.15 | 0.9
0.08385 | 282.15 | 0.00115 | 288.15 | 1
0.08385 | 282.15 | 0.00115 | 288.65 | 0.15
0.08385 | 282.15 | 0.00115 | 288.65 | 0.2
0.08385 | 282.15 | 0.00115 | 288.65 | 0.3
0.08385 | 282.15 | 0.00115 | 288.65 | 0.4
0.08385 | 282.15 | 0.00115 | 288.65 | 0.5
0.08385 | 282.15 | 0.00115 | 288.65 | 0.6
0.08385 | 282.15 | 0.00115 | 288.65 | 0.7
0.08385 | 282.15 | 0.00115 | 288.65 | 0.8
0.08385 | 282.15 | 0.00115 | 288.65 | 0.9
0.08385 | 282.15 | 0.00115 | 288.65 | 1
0.08385 | 282.15 | 0.00115 | 289.15 | 0.15
0.08385 | 282.15 | 0.00115 | 289.15 | 0.2
0.08385 | 282.15 | 0.00115 | 289.15 | 0.3
0.08385 | 282.15 | 0.00115 | 289.15 | 0.4
0.08385 | 282.15 | 0.00115 | 289.15 | 0.5
0.08385 | 282.15 | 0.00115 | 289.15 | 0.6
0.08385 | 282.15 | 0.00115 | 289.15 | 0.7
0.08385 | 282.15 | 0.00115 | 289.15 | 0.8
0.08385 | 282.15 | 0.00115 | 289.15 | 0.9
0.08385 | 282.15 | 0.00115 | 289.15 | 1
0.08385 | 282.15 | 0.00115 | 289.65 | 0.15
0.08385 | 282.15 | 0.00115 | 289.65 | 0.2
0.08385 | 282.15 | 0.00115 | 289.65 | 0.3
0.08385 | 282.15 | 0.00115 | 289.65 | 0.4
0.08385 | 282.15 | 0.00115 | 289.65 | 0.5
0.08385 | 282.15 | 0.00115 | 289.65 | 0.6
0.08385 | 282.15 | 0.00115 | 289.65 | 0.7
0.08385 | 282.15 | 0.00115 | 289.65 | 0.8
0.08385 | 282.15 | 0.00115 | 289.65 | 0.9
0.08385 | 282.15 | 0.00115 | 289.65 | 1
0.08385 | 282.15 | 0.00115 | 290.15 | 0.15
0.08385 | 282.15 | 0.00115 | 290.15 | 0.2
0.08385 | 282.15 | 0.00115 | 290.15 | 0.3
0.08385 | 282.15 | 0.00115 | 290.15 | 0.4
0.08385 | 282.15 | 0.00115 | 290.15 | 0.5
0.08385 | 282.15 | 0.00115 | 290.15 | 0.6
0.08385 | 282.15 | 0.00115 | 290.15 | 0.7
0.08385 | 282.15 | 0.00115 | 290.15 | 0.8
0.08385 | 282.15 | 0.00115 | 290.15 | 0.9
0.08385 | 282.15 | 0.00115 | 290.15 | 1
0.08385 | 282.15 | 0.00115 | 290.65 | 0.15
0.08385 | 282.15 | 0.00115 | 290.65 | 0.2
0.08385 | 282.15 | 0.00115 | 290.65 | 0.3
0.08385 | 282.15 | 0.00115 | 290.65 | 0.4
0.08385 | 282.15 | 0.00115 | 290.65 | 0.5
0.08385 | 282.15 | 0.00115 | 290.65 | 0.6
0.08385 | 282.15 | 0.00115 | 290.65 | 0.7
0.08385 | 282.15 | 0.00115 | 290.65 | 0.8
0.08385 | 282.15 | 0.00115 | 290.65 | 0.9
0.08385 | 282.15 | 0.00115 | 290.65 | 1
0.08385 | 282.15 | 0.00115 | 291.15 | 0.15
0.08385 | 282.15 | 0.00115 | 291.15 | 0.2
0.08385 | 282.15 | 0.00115 | 291.15 | 0.3
0.08385 | 282.15 | 0.00115 | 291.15 | 0.4
0.08385 | 282.15 | 0.00115 | 291.15 | 0.5
0.08385 | 282.15 | 0.00115 | 291.15 | 0.6
0.08385 | 282.15 | 0.00115 | 291.15 | 0.7
0.08385 | 282.15 | 0.00115 | 291.15 | 0.8
0.08385 | 282.15 | 0.00115 | 291.15 | 0.9
0.08385 | 282.15 | 0.00115 | 291.15 | 1
0.08385 | 282.15 | 0.00115 | 294.15 | 0.15
0.08385 | 282.15 | 0.00115 | 294.15 | 0.2
0.08385 | 282.15 | 0.00115 | 294.15 | 0.3
0.08385 | 282.15 | 0.00115 | 294.15 | 0.4
0.08385 | 282.15 | 0.00115 | 294.15 | 0.5
0.08385 | 282.15 | 0.00115 | 294.15 | 0.6
0.08385 | 282.15 | 0.00115 | 294.15 | 0.7
0.08385 | 282.15 | 0.00115 | 294.15 | 0.8
0.08385 | 282.15 | 0.00115 | 294.15 | 0.9
0.08385 | 282.15 | 0.00115 | 294.15 | 1
0.08385 | 282.15 | 0.00115 | 297.15 | 0.15
0.08385 | 282.15 | 0.00115 | 297.15 | 0.2
0.08385 | 282.15 | 0.00115 | 297.15 | 0.3
0.08385 | 282.15 | 0.00115 | 297.15 | 0.4
0.08385 | 282.15 | 0.00115 | 297.15 | 0.5
0.08385 | 282.15 | 0.00115 | 297.15 | 0.6
0.08385 | 282.15 | 0.00115 | 297.15 | 0.7
0.08385 | 282.15 | 0.00115 | 297.15 | 0.8
0.08385 | 282.15 | 0.00115 | 297.15 | 0.9
0.08385 | 282.15 | 0.00115 | 297.15 | 1
0.08385 | 282.15 | 0.00115 | 300.15 | 0.15
0.08385 | 282.15 | 0.00115 | 300.15 | 0.2
0.08385 | 282.15 | 0.00115 | 300.15 | 0.3
0.08385 | 282.15 | 0.00115 | 300.15 | 0.4
0.08385 | 282.15 | 0.00115 | 300.15 | 0.5
0.08385 | 282.15 | 0.00115 | 300.15 | 0.6
0.08385 | 282.15 | 0.00115 | 300.15 | 0.7
0.08385 | 282.15 | 0.00115 | 300.15 | 0.8
0.08385 | 282.15 | 0.00115 | 300.15 | 0.9
0.08385 | 282.15 | 0.00115 | 300.15 | 1
0.08385 | 282.15 | 0.00115 | 303.15 | 0.15
0.08385 | 282.15 | 0.00115 | 303.15 | 0.2
0.08385 | 282.15 | 0.00115 | 303.15 | 0.3
0.08385 | 282.15 | 0.00115 | 303.15 | 0.4
0.08385 | 282.15 | 0.00115 | 303.15 | 0.5
0.08385 | 282.15 | 0.00115 | 303.15 | 0.6
0.08385 | 282.15 | 0.00115 | 303.15 | 0.7
0.08385 | 282.15 | 0.00115 | 303.15 | 0.8
0.08385 | 282.15 | 0.00115 | 303.15 | 0.9
0.08385 | 282.15 | 0.00115 | 303.15 | 1
0.08385 | 282.15 | 0.077 | 283.65 | 0.15
0.08385 | 282.15 | 0.077 | 283.65 | 0.2
0.08385 | 282.15 | 0.077 | 283.65 | 0.3
0.08385 | 282.15 | 0.077 | 283.65 | 0.4
0.08385 | 282.15 | 0.077 | 283.65 | 0.5
0.08385 | 282.15 | 0.077 | 283.65 | 0.6
0.08385 | 282.15 | 0.077 | 283.65 | 0.7
0.08385 | 282.15 | 0.077 | 283.65 | 0.8
0.08385 | 282.15 | 0.077 | 283.65 | 0.9
0.08385 | 282.15 | 0.077 | 283.65 | 1
0.08385 | 282.15 | 0.077 | 284.15 | 0.15
0.08385 | 282.15 | 0.077 | 284.15 | 0.2
0.08385 | 282.15 | 0.077 | 284.15 | 0.3
0.08385 | 282.15 | 0.077 | 284.15 | 0.4
0.08385 | 282.15 | 0.077 | 284.15 | 0.5
0.08385 | 282.15 | 0.077 | 284.15 | 0.6
0.08385 | 282.15 | 0.077 | 284.15 | 0.7
0.08385 | 282.15 | 0.077 | 284.15 | 0.8
0.08385 | 282.15 | 0.077 | 284.15 | 0.9
0.08385 | 282.15 | 0.077 | 284.15 | 1
0.08385 | 282.15 | 0.077 | 284.65 | 0.15
0.08385 | 282.15 | 0.077 | 284.65 | 0.2
0.08385 | 282.15 | 0.077 | 284.65 | 0.3
0.08385 | 282.15 | 0.077 | 284.65 | 0.4
0.08385 | 282.15 | 0.077 | 284.65 | 0.5
0.08385 | 282.15 | 0.077 | 284.65 | 0.6
0.08385 | 282.15 | 0.077 | 284.65 | 0.7
0.08385 | 282.15 | 0.077 | 284.65 | 0.8
0.08385 | 282.15 | 0.077 | 284.65 | 0.9
0.08385 | 282.15 | 0.077 | 284.65 | 1
0.08385 | 282.15 | 0.077 | 285.15 | 0.15
0.08385 | 282.15 | 0.077 | 285.15 | 0.2
0.08385 | 282.15 | 0.077 | 285.15 | 0.3
0.08385 | 282.15 | 0.077 | 285.15 | 0.4
0.08385 | 282.15 | 0.077 | 285.15 | 0.5
0.08385 | 282.15 | 0.077 | 285.15 | 0.6
0.08385 | 282.15 | 0.077 | 285.15 | 0.7
0.08385 | 282.15 | 0.077 | 285.15 | 0.8
0.08385 | 282.15 | 0.077 | 285.15 | 0.9
0.08385 | 282.15 | 0.077 | 285.15 | 1
0.08385 | 282.15 | 0.077 | 285.65 | 0.15
0.08385 | 282.15 | 0.077 | 285.65 | 0.2
0.08385 | 282.15 | 0.077 | 285.65 | 0.3
0.08385 | 282.15 | 0.077 | 285.65 | 0.4
0.08385 | 282.15 | 0.077 | 285.65 | 0.5
0.08385 | 282.15 | 0.077 | 285.65 | 0.6
0.08385 | 282.15 | 0.077 | 285.65 | 0.7
0.08385 | 282.15 | 0.077 | 285.65 | 0.8
0.08385 | 282.15 | 0.077 | 285.65 | 0.9
0.08385 | 282.15 | 0.077 | 285.65 | 1
0.08385 | 282.15 | 0.077 | 286.15 | 0.15
0.08385 | 282.15 | 0.077 | 286.15 | 0.2
0.08385 | 282.15 | 0.077 | 286.15 | 0.3
0.08385 | 282.15 | 0.077 | 286.15 | 0.4
0.08385 | 282.15 | 0.077 | 286.15 | 0.5
0.08385 | 282.15 | 0.077 | 286.15 | 0.6
0.08385 | 282.15 | 0.077 | 286.15 | 0.7
0.08385 | 282.15 | 0.077 | 286.15 | 0.8
0.08385 | 282.15 | 0.077 | 286.15 | 0.9
0.08385 | 282.15 | 0.077 | 286.15 | 1
0.08385 | 282.15 | 0.077 | 286.65 | 0.15
0.08385 | 282.15 | 0.077 | 286.65 | 0.2
0.08385 | 282.15 | 0.077 | 286.65 | 0.3
0.08385 | 282.15 | 0.077 | 286.65 | 0.4
0.08385 | 282.15 | 0.077 | 286.65 | 0.5
0.08385 | 282.15 | 0.077 | 286.65 | 0.6
0.08385 | 282.15 | 0.077 | 286.65 | 0.7
0.08385 | 282.15 | 0.077 | 286.65 | 0.8
0.08385 | 282.15 | 0.077 | 286.65 | 0.9
0.08385 | 282.15 | 0.077 | 286.65 | 1
0.08385 | 282.15 | 0.077 | 287.15 | 0.15
0.08385 | 282.15 | 0.077 | 287.15 | 0.2
0.08385 | 282.15 | 0.077 | 287.15 | 0.3
0.08385 | 282.15 | 0.077 | 287.15 | 0.4
0.08385 | 282.15 | 0.077 | 287.15 | 0.5
0.08385 | 282.15 | 0.077 | 287.15 | 0.6
0.08385 | 282.15 | 0.077 | 287.15 | 0.7
0.08385 | 282.15 | 0.077 | 287.15 | 0.8
0.08385 | 282.15 | 0.077 | 287.15 | 0.9
0.08385 | 282.15 | 0.077 | 287.15 | 1
0.08385 | 282.15 | 0.077 | 287.65 | 0.15
0.08385 | 282.15 | 0.077 | 287.65 | 0.2
0.08385 | 282.15 | 0.077 | 287.65 | 0.3
0.08385 | 282.15 | 0.077 | 287.65 | 0.4
0.08385 | 282.15 | 0.077 | 287.65 | 0.5
0.08385 | 282.15 | 0.077 | 287.65 | 0.6
0.08385 | 282.15 | 0.077 | 287.65 | 0.7
0.08385 | 282.15 | 0.077 | 287.65 | 0.8
0.08385 | 282.15 | 0.077 | 287.65 | 0.9
0.08385 | 282.15 | 0.077 | 287.65 | 1
0.08385 | 282.15 | 0.077 | 288.15 | 0.15
0.08385 | 282.15 | 0.077 | 288.15 | 0.2
0.08385 | 282.15 | 0.077 | 288.15 | 0.3
0.08385 | 282.15 | 0.077 | 288.15 | 0.4
0.08385 | 282.15 | 0.077 | 288.15 | 0.5
0.08385 | 282.15 | 0.077 | 288.15 | 0.6
0.08385 | 282.15 | 0.077 | 288.15 | 0.7
0.08385 | 282.15 | 0.077 | 288.15 | 0.8
0.08385 | 282.15 | 0.077 | 288.15 | 0.9
0.08385 | 282.15 | 0.077 | 288.15 | 1
0.08385 | 282.15 | 0.077 | 288.65 | 0.15
0.08385 | 282.15 | 0.077 | 288.65 | 0.2
0.08385 | 282.15 | 0.077 | 288.65 | 0.3
0.08385 | 282.15 | 0.077 | 288.65 | 0.4
0.08385 | 282.15 | 0.077 | 288.65 | 0.5
0.08385 | 282.15 | 0.077 | 288.65 | 0.6
0.08385 | 282.15 | 0.077 | 288.65 | 0.7
0.08385 | 282.15 | 0.077 | 288.65 | 0.8
0.08385 | 282.15 | 0.077 | 288.65 | 0.9
0.08385 | 282.15 | 0.077 | 288.65 | 1
0.08385 | 282.15 | 0.077 | 289.15 | 0.15
0.08385 | 282.15 | 0.077 | 289.15 | 0.2
0.08385 | 282.15 | 0.077 | 289.15 | 0.3
0.08385 | 282.15 | 0.077 | 289.15 | 0.4
0.08385 | 282.15 | 0.077 | 289.15 | 0.5
0.08385 | 282.15 | 0.077 | 289.15 | 0.6
0.08385 | 282.15 | 0.077 | 289.15 | 0.7
0.08385 | 282.15 | 0.077 | 289.15 | 0.8
0.08385 | 282.15 | 0.077 | 289.15 | 0.9
0.08385 | 282.15 | 0.077 | 289.15 | 1
0.08385 | 282.15 | 0.077 | 289.65 | 0.15
0.08385 | 282.15 | 0.077 | 289.65 | 0.2
0.08385 | 282.15 | 0.077 | 289.65 | 0.3
0.08385 | 282.15 | 0.077 | 289.65 | 0.4
0.08385 | 282.15 | 0.077 | 289.65 | 0.5
0.08385 | 282.15 | 0.077 | 289.65 | 0.6
0.08385 | 282.15 | 0.077 | 289.65 | 0.7
0.08385 | 282.15 | 0.077 | 289.65 | 0.8
0.08385 | 282.15 | 0.077 | 289.65 | 0.9
0.08385 | 282.15 | 0.077 | 289.65 | 1
0.08385 | 282.15 | 0.077 | 290.15 | 0.15
0.08385 | 282.15 | 0.077 | 290.15 | 0.2
0.08385 | 282.15 | 0.077 | 290.15 | 0.3
0.08385 | 282.15 | 0.077 | 290.15 | 0.4
0.08385 | 282.15 | 0.077 | 290.15 | 0.5
0.08385 | 282.15 | 0.077 | 290.15 | 0.6
0.08385 | 282.15 | 0.077 | 290.15 | 0.7
0.08385 | 282.15 | 0.077 | 290.15 | 0.8
0.08385 | 282.15 | 0.077 | 290.15 | 0.9
0.08385 | 282.15 | 0.077 | 290.15 | 1
0.08385 | 282.15 | 0.077 | 290.65 | 0.15
0.08385 | 282.15 | 0.077 | 290.65 | 0.2
0.08385 | 282.15 | 0.077 | 290.65 | 0.3
0.08385 | 282.15 | 0.077 | 290.65 | 0.4
0.08385 | 282.15 | 0.077 | 290.65 | 0.5
0.08385 | 282.15 | 0.077 | 290.65 | 0.6
0.08385 | 282.15 | 0.077 | 290.65 | 0.7
0.08385 | 282.15 | 0.077 | 290.65 | 0.8
0.08385 | 282.15 | 0.077 | 290.65 | 0.9
0.08385 | 282.15 | 0.077 | 290.65 | 1
0.08385 | 282.15 | 0.077 | 291.15 | 0.15
0.08385 | 282.15 | 0.077 | 291.15 | 0.2
0.08385 | 282.15 | 0.077 | 291.15 | 0.3
0.08385 | 282.15 | 0.077 | 291.15 | 0.4
0.08385 | 282.15 | 0.077 | 291.15 | 0.5
0.08385 | 282.15 | 0.077 | 291.15 | 0.6
0.08385 | 282.15 | 0.077 | 291.15 | 0.7
0.08385 | 282.15 | 0.077 | 291.15 | 0.8
0.08385 | 282.15 | 0.077 | 291.15 | 0.9
0.08385 | 282.15 | 0.077 | 291.15 | 1
0.08385 | 282.15 | 0.077 | 294.15 | 0.15
0.08385 | 282.15 | 0.077 | 294.15 | 0.2
0.08385 | 282.15 | 0.077 | 294.15 | 0.3
0.08385 | 282.15 | 0.077 | 294.15 | 0.4
0.08385 | 282.15 | 0.077 | 294.15 | 0.5
0.08385 | 282.15 | 0.077 | 294.15 | 0.6
0.08385 | 282.15 | 0.077 | 294.15 | 0.7
0.08385 | 282.15 | 0.077 | 294.15 | 0.8
0.08385 | 282.15 | 0.077 | 294.15 | 0.9
0.08385 | 282.15 | 0.077 | 294.15 | 1
0.08385 | 282.15 | 0.077 | 297.15 | 0.15
0.08385 | 282.15 | 0.077 | 297.15 | 0.2
0.08385 | 282.15 | 0.077 | 297.15 | 0.3
0.08385 | 282.15 | 0.077 | 297.15 | 0.4
0.08385 | 282.15 | 0.077 | 297.15 | 0.5
0.08385 | 282.15 | 0.077 | 297.15 | 0.6
0.08385 | 282.15 | 0.077 | 297.15 | 0.7
0.08385 | 282.15 | 0.077 | 297.15 | 0.8
0.08385 | 282.15 | 0.077 | 297.15 | 0.9
0.08385 | 282.15 | 0.077 | 297.15 | 1
0.08385 | 282.15 | 0.077 | 300.15 | 0.15
0.08385 | 282.15 | 0.077 | 300.15 | 0.2
0.08385 | 282.15 | 0.077 | 300.15 | 0.3
0.08385 | 282.15 | 0.077 | 300.15 | 0.4
0.08385 | 282.15 | 0.077 | 300.15 | 0.5
0.08385 | 282.15 | 0.077 | 300.15 | 0.6
0.08385 | 282.15 | 0.077 | 300.15 | 0.7
0.08385 | 282.15 | 0.077 | 300.15 | 0.8
0.08385 | 282.15 | 0.077 | 300.15 | 0.9
0.08385 | 282.15 | 0.077 | 300.15 | 1
0.08385 | 282.15 | 0.077 | 303.15 | 0.15
0.08385 | 282.15 | 0.077 | 303.15 | 0.2
0.08385 | 282.15 | 0.077 | 303.15 | 0.3
0.08385 | 282.15 | 0.077 | 303.15 | 0.4
0.08385 | 282.15 | 0.077 | 303.15 | 0.5
0.08385 | 282.15 | 0.077 | 303.15 | 0.6
0.08385 | 282.15 | 0.077 | 303.15 | 0.7
0.08385 | 282.15 | 0.077 | 303.15 | 0.8
0.08385 | 282.15 | 0.077 | 303.15 | 0.9
0.08385 | 282.15 | 0.077 | 303.15 | 1
0.08385 | 282.15 | 0.09437 | 283.65 | 0.15
0.08385 | 282.15 | 0.09437 | 283.65 | 0.2
0.08385 | 282.15 | 0.09437 | 283.65 | 0.3
0.08385 | 282.15 | 0.09437 | 283.65 | 0.4
0.08385 | 282.15 | 0.09437 | 283.65 | 0.5
0.08385 | 282.15 | 0.09437 | 283.65 | 0.6
0.08385 | 282.15 | 0.09437 | 283.65 | 0.7
0.08385 | 282.15 | 0.09437 | 283.65 | 0.8
0.08385 | 282.15 | 0.09437 | 283.65 | 0.9
0.08385 | 282.15 | 0.09437 | 283.65 | 1
0.08385 | 282.15 | 0.09437 | 284.15 | 0.15
0.08385 | 282.15 | 0.09437 | 284.15 | 0.2
0.08385 | 282.15 | 0.09437 | 284.15 | 0.3
0.08385 | 282.15 | 0.09437 | 284.15 | 0.4
0.08385 | 282.15 | 0.09437 | 284.15 | 0.5
0.08385 | 282.15 | 0.09437 | 284.15 | 0.6
0.08385 | 282.15 | 0.09437 | 284.15 | 0.7
0.08385 | 282.15 | 0.09437 | 284.15 | 0.8
0.08385 | 282.15 | 0.09437 | 284.15 | 0.9
0.08385 | 282.15 | 0.09437 | 284.15 | 1
0.08385 | 282.15 | 0.09437 | 284.65 | 0.15
0.08385 | 282.15 | 0.09437 | 284.65 | 0.2
0.08385 | 282.15 | 0.09437 | 284.65 | 0.3
0.08385 | 282.15 | 0.09437 | 284.65 | 0.4
0.08385 | 282.15 | 0.09437 | 284.65 | 0.5
0.08385 | 282.15 | 0.09437 | 284.65 | 0.6
0.08385 | 282.15 | 0.09437 | 284.65 | 0.7
0.08385 | 282.15 | 0.09437 | 284.65 | 0.8
0.08385 | 282.15 | 0.09437 | 284.65 | 0.9
0.08385 | 282.15 | 0.09437 | 284.65 | 1
0.08385 | 282.15 | 0.09437 | 285.15 | 0.15
0.08385 | 282.15 | 0.09437 | 285.15 | 0.2
0.08385 | 282.15 | 0.09437 | 285.15 | 0.3
0.08385 | 282.15 | 0.09437 | 285.15 | 0.4
0.08385 | 282.15 | 0.09437 | 285.15 | 0.5
0.08385 | 282.15 | 0.09437 | 285.15 | 0.6
0.08385 | 282.15 | 0.09437 | 285.15 | 0.7
0.08385 | 282.15 | 0.09437 | 285.15 | 0.8
0.08385 | 282.15 | 0.09437 | 285.15 | 0.9
0.08385 | 282.15 | 0.09437 | 285.15 | 1
0.08385 | 282.15 | 0.09437 | 285.65 | 0.15
0.08385 | 282.15 | 0.09437 | 285.65 | 0.2
0.08385 | 282.15 | 0.09437 | 285.65 | 0.3
0.08385 | 282.15 | 0.09437 | 285.65 | 0.4
0.08385 | 282.15 | 0.09437 | 285.65 | 0.5
0.08385 | 282.15 | 0.09437 | 285.65 | 0.6
0.08385 | 282.15 | 0.09437 | 285.65 | 0.7
0.08385 | 282.15 | 0.09437 | 285.65 | 0.8
0.08385 | 282.15 | 0.09437 | 285.65 | 0.9
0.08385 | 282.15 | 0.09437 | 285.65 | 1
0.08385 | 282.15 | 0.09437 | 286.15 | 0.15
0.08385 | 282.15 | 0.09437 | 286.15 | 0.2
0.08385 | 282.15 | 0.09437 | 286.15 | 0.3
0.08385 | 282.15 | 0.09437 | 286.15 | 0.4
0.08385 | 282.15 | 0.09437 | 286.15 | 0.5
0.08385 | 282.15 | 0.09437 | 286.15 | 0.6
0.08385 | 282.15 | 0.09437 | 286.15 | 0.7
0.08385 | 282.15 | 0.09437 | 286.15 | 0.8
0.08385 | 282.15 | 0.09437 | 286.15 | 0.9
0.08385 | 282.15 | 0.09437 | 286.15 | 1
0.08385 | 282.15 | 0.09437 | 286.65 | 0.15
0.08385 | 282.15 | 0.09437 | 286.65 | 0.2
0.08385 | 282.15 | 0.09437 | 286.65 | 0.3
0.08385 | 282.15 | 0.09437 | 286.65 | 0.4
0.08385 | 282.15 | 0.09437 | 286.65 | 0.5
0.08385 | 282.15 | 0.09437 | 286.65 | 0.6
0.08385 | 282.15 | 0.09437 | 286.65 | 0.7
0.08385 | 282.15 | 0.09437 | 286.65 | 0.8
0.08385 | 282.15 | 0.09437 | 286.65 | 0.9
0.08385 | 282.15 | 0.09437 | 286.65 | 1
0.08385 | 282.15 | 0.09437 | 287.15 | 0.15
0.08385 | 282.15 | 0.09437 | 287.15 | 0.2
0.08385 | 282.15 | 0.09437 | 287.15 | 0.3
0.08385 | 282.15 | 0.09437 | 287.15 | 0.4
0.08385 | 282.15 | 0.09437 | 287.15 | 0.5
0.08385 | 282.15 | 0.09437 | 287.15 | 0.6
0.08385 | 282.15 | 0.09437 | 287.15 | 0.7
0.08385 | 282.15 | 0.09437 | 287.15 | 0.8
0.08385 | 282.15 | 0.09437 | 287.15 | 0.9
0.08385 | 282.15 | 0.09437 | 287.15 | 1
0.08385 | 282.15 | 0.09437 | 287.65 | 0.15
0.08385 | 282.15 | 0.09437 | 287.65 | 0.2
0.08385 | 282.15 | 0.09437 | 287.65 | 0.3
0.08385 | 282.15 | 0.09437 | 287.65 | 0.4
0.08385 | 282.15 | 0.09437 | 287.65 | 0.5
0.08385 | 282.15 | 0.09437 | 287.65 | 0.6
0.08385 | 282.15 | 0.09437 | 287.65 | 0.7
0.08385 | 282.15 | 0.09437 | 287.65 | 0.8
0.08385 | 282.15 | 0.09437 | 287.65 | 0.9
0.08385 | 282.15 | 0.09437 | 287.65 | 1
0.08385 | 282.15 | 0.09437 | 288.15 | 0.15
0.08385 | 282.15 | 0.09437 | 288.15 | 0.2
0.08385 | 282.15 | 0.09437 | 288.15 | 0.3
0.08385 | 282.15 | 0.09437 | 288.15 | 0.4
0.08385 | 282.15 | 0.09437 | 288.15 | 0.5
0.08385 | 282.15 | 0.09437 | 288.15 | 0.6
0.08385 | 282.15 | 0.09437 | 288.15 | 0.7
0.08385 | 282.15 | 0.09437 | 288.15 | 0.8
0.08385 | 282.15 | 0.09437 | 288.15 | 0.9
0.08385 | 282.15 | 0.09437 | 288.15 | 1
0.08385 | 282.15 | 0.09437 | 288.65 | 0.15
0.08385 | 282.15 | 0.09437 | 288.65 | 0.2
0.08385 | 282.15 | 0.09437 | 288.65 | 0.3
0.08385 | 282.15 | 0.09437 | 288.65 | 0.4
0.08385 | 282.15 | 0.09437 | 288.65 | 0.5
0.08385 | 282.15 | 0.09437 | 288.65 | 0.6
0.08385 | 282.15 | 0.09437 | 288.65 | 0.7
0.08385 | 282.15 | 0.09437 | 288.65 | 0.8
0.08385 | 282.15 | 0.09437 | 288.65 | 0.9
0.08385 | 282.15 | 0.09437 | 288.65 | 1
0.08385 | 282.15 | 0.09437 | 289.15 | 0.15
0.08385 | 282.15 | 0.09437 | 289.15 | 0.2
0.08385 | 282.15 | 0.09437 | 289.15 | 0.3
0.08385 | 282.15 | 0.09437 | 289.15 | 0.4
0.08385 | 282.15 | 0.09437 | 289.15 | 0.5
0.08385 | 282.15 | 0.09437 | 289.15 | 0.6
0.08385 | 282.15 | 0.09437 | 289.15 | 0.7
0.08385 | 282.15 | 0.09437 | 289.15 | 0.8
0.08385 | 282.15 | 0.09437 | 289.15 | 0.9
0.08385 | 282.15 | 0.09437 | 289.15 | 1
0.08385 | 282.15 | 0.09437 | 289.65 | 0.15
0.08385 | 282.15 | 0.09437 | 289.65 | 0.2
0.08385 | 282.15 | 0.09437 | 289.65 | 0.3
0.08385 | 282.15 | 0.09437 | 289.65 | 0.4
0.08385 | 282.15 | 0.09437 | 289.65 | 0.5
0.08385 | 282.15 | 0.09437 | 289.65 | 0.6
0.08385 | 282.15 | 0.09437 | 289.65 | 0.7
0.08385 | 282.15 | 0.09437 | 289.65 | 0.8
0.08385 | 282.15 | 0.09437 | 289.65 | 0.9
0.08385 | 282.15 | 0.09437 | 289.65 | 1
0.08385 | 282.15 | 0.09437 | 290.15 | 0.15
0.08385 | 282.15 | 0.09437 | 290.15 | 0.2
0.08385 | 282.15 | 0.09437 | 290.15 | 0.3
0.08385 | 282.15 | 0.09437 | 290.15 | 0.4
0.08385 | 282.15 | 0.09437 | 290.15 | 0.5
0.08385 | 282.15 | 0.09437 | 290.15 | 0.6
0.08385 | 282.15 | 0.09437 | 290.15 | 0.7
0.08385 | 282.15 | 0.09437 | 290.15 | 0.8
0.08385 | 282.15 | 0.09437 | 290.15 | 0.9
0.08385 | 282.15 | 0.09437 | 290.15 | 1
0.08385 | 282.15 | 0.09437 | 290.65 | 0.15
0.08385 | 282.15 | 0.09437 | 290.65 | 0.2
0.08385 | 282.15 | 0.09437 | 290.65 | 0.3
0.08385 | 282.15 | 0.09437 | 290.65 | 0.4
0.08385 | 282.15 | 0.09437 | 290.65 | 0.5
0.08385 | 282.15 | 0.09437 | 290.65 | 0.6
0.08385 | 282.15 | 0.09437 | 290.65 | 0.7
0.08385 | 282.15 | 0.09437 | 290.65 | 0.8
0.08385 | 282.15 | 0.09437 | 290.65 | 0.9
0.08385 | 282.15 | 0.09437 | 290.65 | 1
0.08385 | 282.15 | 0.09437 | 291.15 | 0.15
0.08385 | 282.15 | 0.09437 | 291.15 | 0.2
0.08385 | 282.15 | 0.09437 | 291.15 | 0.3
0.08385 | 282.15 | 0.09437 | 291.15 | 0.4
0.08385 | 282.15 | 0.09437 | 291.15 | 0.5
0.08385 | 282.15 | 0.09437 | 291.15 | 0.6
0.08385 | 282.15 | 0.09437 | 291.15 | 0.7
0.08385 | 282.15 | 0.09437 | 291.15 | 0.8
0.08385 | 282.15 | 0.09437 | 291.15 | 0.9
0.08385 | 282.15 | 0.09437 | 291.15 | 1
0.08385 | 282.15 | 0.09437 | 294.15 | 0.15
0.08385 | 282.15 | 0.09437 | 294.15 | 0.2
0.08385 | 282.15 | 0.09437 | 294.15 | 0.3
0.08385 | 282.15 | 0.09437 | 294.15 | 0.4
0.08385 | 282.15 | 0.09437 | 294.15 | 0.5
0.08385 | 282.15 | 0.09437 | 294.15 | 0.6
0.08385 | 282.15 | 0.09437 | 294.15 | 0.7
0.08385 | 282.15 | 0.09437 | 294.15 | 0.8
0.08385 | 282.15 | 0.09437 | 294.15 | 0.9
0.08385 | 282.15 | 0.09437 | 294.15 | 1
0.08385 | 282.15 | 0.09437 | 297.15 | 0.15
0.08385 | 282.15 | 0.09437 | 297.15 | 0.2
0.08385 | 282.15 | 0.09437 | 297.15 | 0.3
0.08385 | 282.15 | 0.09437 | 297.15 | 0.4
0.08385 | 282.15 | 0.09437 | 297.15 | 0.5
0.08385 | 282.15 | 0.09437 | 297.15 | 0.6
0.08385 | 282.15 | 0.09437 | 297.15 | 0.7
0.08385 | 282.15 | 0.09437 | 297.15 | 0.8
0.08385 | 282.15 | 0.09437 | 297.15 | 0.9
0.08385 | 282.15 | 0.09437 | 297.15 | 1
0.08385 | 282.15 | 0.09437 | 300.15 | 0.15
0.08385 | 282.15 | 0.09437 | 300.15 | 0.2
0.08385 | 282.15 | 0.09437 | 300.15 | 0.3
0.08385 | 282.15 | 0.09437 | 300.15 | 0.4
0.08385 | 282.15 | 0.09437 | 300.15 | 0.5
0.08385 | 282.15 | 0.09437 | 300.15 | 0.6
0.08385 | 282.15 | 0.09437 | 300.15 | 0.7
0.08385 | 282.15 | 0.09437 | 300.15 | 0.8
0.08385 | 282.15 | 0.09437 | 300.15 | 0.9
0.08385 | 282.15 | 0.09437 | 300.15 | 1
0.08385 | 282.15 | 0.09437 | 303.15 | 0.15
0.08385 | 282.15 | 0.09437 | 303.15 | 0.2
0.08385 | 282.15 | 0.09437 | 303.15 | 0.3
0.08385 | 282.15 | 0.09437 | 303.15 | 0.4
0.08385 | 282.15 | 0.09437 | 303.15 | 0.5
0.08385 | 282.15 | 0.09437 | 303.15 | 0.6
0.08385 | 282.15 | 0.09437 | 303.15 | 0.7
0.08385 | 282.15 | 0.09437 | 303.15 | 0.8
0.08385 | 282.15 | 0.09437 | 303.15 | 0.9
0.08385 | 282.15 | 0.09437 | 303.15 | 1
0.08385 | 282.15 | 0.09644 | 283.65 | 0.15
0.08385 | 282.15 | 0.09644 | 283.65 | 0.2
0.08385 | 282.15 | 0.09644 | 283.65 | 0.3
0.08385 | 282.15 | 0.09644 | 283.65 | 0.4
0.08385 | 282.15 | 0.09644 | 283.65 | 0.5
0.08385 | 282.15 | 0.09644 | 283.65 | 0.6
0.08385 | 282.15 | 0.09644 | 283.65 | 0.7
0.08385 | 282.15 | 0.09644 | 283.65 | 0.8
0.08385 | 282.15 | 0.09644 | 283.65 | 0.9
0.08385 | 282.15 | 0.09644 | 283.65 | 1
0.08385 | 282.15 | 0.09644 | 284.15 | 0.15
0.08385 | 282.15 | 0.09644 | 284.15 | 0.2
0.08385 | 282.15 | 0.09644 | 284.15 | 0.3
0.08385 | 282.15 | 0.09644 | 284.15 | 0.4
0.08385 | 282.15 | 0.09644 | 284.15 | 0.5
0.08385 | 282.15 | 0.09644 | 284.15 | 0.6
0.08385 | 282.15 | 0.09644 | 284.15 | 0.7
0.08385 | 282.15 | 0.09644 | 284.15 | 0.8
0.08385 | 282.15 | 0.09644 | 284.15 | 0.9
0.08385 | 282.15 | 0.09644 | 284.15 | 1
0.08385 | 282.15 | 0.09644 | 284.65 | 0.15
0.08385 | 282.15 | 0.09644 | 284.65 | 0.2
0.08385 | 282.15 | 0.09644 | 284.65 | 0.3
0.08385 | 282.15 | 0.09644 | 284.65 | 0.4
0.08385 | 282.15 | 0.09644 | 284.65 | 0.5
0.08385 | 282.15 | 0.09644 | 284.65 | 0.6
0.08385 | 282.15 | 0.09644 | 284.65 | 0.7
0.08385 | 282.15 | 0.09644 | 284.65 | 0.8
0.08385 | 282.15 | 0.09644 | 284.65 | 0.9
0.08385 | 282.15 | 0.09644 | 284.65 | 1
0.08385 | 282.15 | 0.09644 | 285.15 | 0.15
0.08385 | 282.15 | 0.09644 | 285.15 | 0.2
0.08385 | 282.15 | 0.09644 | 285.15 | 0.3
0.08385 | 282.15 | 0.09644 | 285.15 | 0.4
0.08385 | 282.15 | 0.09644 | 285.15 | 0.5
0.08385 | 282.15 | 0.09644 | 285.15 | 0.6
0.08385 | 282.15 | 0.09644 | 285.15 | 0.7
0.08385 | 282.15 | 0.09644 | 285.15 | 0.8
0.08385 | 282.15 | 0.09644 | 285.15 | 0.9
0.08385 | 282.15 | 0.09644 | 285.15 | 1
0.08385 | 282.15 | 0.09644 | 285.65 | 0.15
0.08385 | 282.15 | 0.09644 | 285.65 | 0.2
0.08385 | 282.15 | 0.09644 | 285.65 | 0.3
0.08385 | 282.15 | 0.09644 | 285.65 | 0.4
0.08385 | 282.15 | 0.09644 | 285.65 | 0.5
0.08385 | 282.15 | 0.09644 | 285.65 | 0.6
0.08385 | 282.15 | 0.09644 | 285.65 | 0.7
0.08385 | 282.15 | 0.09644 | 285.65 | 0.8
0.08385 | 282.15 | 0.09644 | 285.65 | 0.9
0.08385 | 282.15 | 0.09644 | 285.65 | 1
0.08385 | 282.15 | 0.09644 | 286.15 | 0.15
0.08385 | 282.15 | 0.09644 | 286.15 | 0.2
0.08385 | 282.15 | 0.09644 | 286.15 | 0.3
0.08385 | 282.15 | 0.09644 | 286.15 | 0.4
0.08385 | 282.15 | 0.09644 | 286.15 | 0.5
0.08385 | 282.15 | 0.09644 | 286.15 | 0.6
0.08385 | 282.15 | 0.09644 | 286.15 | 0.7
0.08385 | 282.15 | 0.09644 | 286.15 | 0.8
0.08385 | 282.15 | 0.09644 | 286.15 | 0.9
0.08385 | 282.15 | 0.09644 | 286.15 | 1
0.08385 | 282.15 | 0.09644 | 286.65 | 0.15
0.08385 | 282.15 | 0.09644 | 286.65 | 0.2
0.08385 | 282.15 | 0.09644 | 286.65 | 0.3
0.08385 | 282.15 | 0.09644 | 286.65 | 0.4
0.08385 | 282.15 | 0.09644 | 286.65 | 0.5
0.08385 | 282.15 | 0.09644 | 286.65 | 0.6
0.08385 | 282.15 | 0.09644 | 286.65 | 0.7
0.08385 | 282.15 | 0.09644 | 286.65 | 0.8
0.08385 | 282.15 | 0.09644 | 286.65 | 0.9
0.08385 | 282.15 | 0.09644 | 286.65 | 1
0.08385 | 282.15 | 0.09644 | 287.15 | 0.15
0.08385 | 282.15 | 0.09644 | 287.15 | 0.2
0.08385 | 282.15 | 0.09644 | 287.15 | 0.3
0.08385 | 282.15 | 0.09644 | 287.15 | 0.4
0.08385 | 282.15 | 0.09644 | 287.15 | 0.5
0.08385 | 282.15 | 0.09644 | 287.15 | 0.6
0.08385 | 282.15 | 0.09644 | 287.15 | 0.7
0.08385 | 282.15 | 0.09644 | 287.15 | 0.8
0.08385 | 282.15 | 0.09644 | 287.15 | 0.9
0.08385 | 282.15 | 0.09644 | 287.15 | 1
0.08385 | 282.15 | 0.09644 | 287.65 | 0.15
0.08385 | 282.15 | 0.09644 | 287.65 | 0.2
0.08385 | 282.15 | 0.09644 | 287.65 | 0.3
0.08385 | 282.15 | 0.09644 | 287.65 | 0.4
0.08385 | 282.15 | 0.09644 | 287.65 | 0.5
0.08385 | 282.15 | 0.09644 | 287.65 | 0.6
0.08385 | 282.15 | 0.09644 | 287.65 | 0.7
0.08385 | 282.15 | 0.09644 | 287.65 | 0.8
0.08385 | 282.15 | 0.09644 | 287.65 | 0.9
0.08385 | 282.15 | 0.09644 | 287.65 | 1
0.08385 | 282.15 | 0.09644 | 288.15 | 0.15
0.08385 | 282.15 | 0.09644 | 288.15 | 0.2
0.08385 | 282.15 | 0.09644 | 288.15 | 0.3
0.08385 | 282.15 | 0.09644 | 288.15 | 0.4
0.08385 | 282.15 | 0.09644 | 288.15 | 0.5
0.08385 | 282.15 | 0.09644 | 288.15 | 0.6
0.08385 | 282.15 | 0.09644 | 288.15 | 0.7
0.08385 | 282.15 | 0.09644 | 288.15 | 0.8
0.08385 | 282.15 | 0.09644 | 288.15 | 0.9
0.08385 | 282.15 | 0.09644 | 288.15 | 1
0.08385 | 282.15 | 0.09644 | 288.65 | 0.15
0.08385 | 282.15 | 0.09644 | 288.65 | 0.2
0.08385 | 282.15 | 0.09644 | 288.65 | 0.3
0.08385 | 282.15 | 0.09644 | 288.65 | 0.4
0.08385 | 282.15 | 0.09644 | 288.65 | 0.5
0.08385 | 282.15 | 0.09644 | 288.65 | 0.6
0.08385 | 282.15 | 0.09644 | 288.65 | 0.7
0.08385 | 282.15 | 0.09644 | 288.65 | 0.8
0.08385 | 282.15 | 0.09644 | 288.65 | 0.9
0.08385 | 282.15 | 0.09644 | 288.65 | 1
0.08385 | 282.15 | 0.09644 | 289.15 | 0.15
0.08385 | 282.15 | 0.09644 | 289.15 | 0.2
0.08385 | 282.15 | 0.09644 | 289.15 | 0.3
0.08385 | 282.15 | 0.09644 | 289.15 | 0.4
0.08385 | 282.15 | 0.09644 | 289.15 | 0.5
0.08385 | 282.15 | 0.09644 | 289.15 | 0.6
0.08385 | 282.15 | 0.09644 | 289.15 | 0.7
0.08385 | 282.15 | 0.09644 | 289.15 | 0.8
0.08385 | 282.15 | 0.09644 | 289.15 | 0.9
0.08385 | 282.15 | 0.09644 | 289.15 | 1
0.08385 | 282.15 | 0.09644 | 289.65 | 0.15
0.08385 | 282.15 | 0.09644 | 289.65 | 0.2
0.08385 | 282.15 | 0.09644 | 289.65 | 0.3
0.08385 | 282.15 | 0.09644 | 289.65 | 0.4
0.08385 | 282.15 | 0.09644 | 289.65 | 0.5
0.08385 | 282.15 | 0.09644 | 289.65 | 0.6
0.08385 | 282.15 | 0.09644 | 289.65 | 0.7
0.08385 | 282.15 | 0.09644 | 289.65 | 0.8
0.08385 | 282.15 | 0.09644 | 289.65 | 0.9
0.08385 | 282.15 | 0.09644 | 289.65 | 1
0.08385 | 282.15 | 0.09644 | 290.15 | 0.15
0.08385 | 282.15 | 0.09644 | 290.15 | 0.2
0.08385 | 282.15 | 0.09644 | 290.15 | 0.3
0.08385 | 282.15 | 0.09644 | 290.15 | 0.4
0.08385 | 282.15 | 0.09644 | 290.15 | 0.5
0.08385 | 282.15 | 0.09644 | 290.15 | 0.6
0.08385 | 282.15 | 0.09644 | 290.15 | 0.7
0.08385 | 282.15 | 0.09644 | 290.15 | 0.8
0.08385 | 282.15 | 0.09644 | 290.15 | 0.9
0.08385 | 282.15 | 0.09644 | 290.15 | 1
0.08385 | 282.15 | 0.09644 | 290.65 | 0.15
0.08385 | 282.15 | 0.09644 | 290.65 | 0.2
0.08385 | 282.15 | 0.09644 | 290.65 | 0.3
0.08385 | 282.15 | 0.09644 | 290.65 | 0.4
0.08385 | 282.15 | 0.09644 | 290.65 | 0.5
0.08385 | 282.15 | 0.09644 | 290.65 | 0.6
0.08385 | 282.15 | 0.09644 | 290.65 | 0.7
0.08385 | 282.15 | 0.09644 | 290.65 | 0.8
0.08385 | 282.15 | 0.09644 | 290.65 | 0.9
0.08385 | 282.15 | 0.09644 | 290.65 | 1
0.08385 | 282.15 | 0.09644 | 291.15 | 0.15
0.08385 | 282.15 | 0.09644 | 291.15 | 0.2
0.08385 | 282.15 | 0.09644 | 291.15 | 0.3
0.08385 | 282.15 | 0.09644 | 291.15 | 0.4
0.08385 | 282.15 | 0.09644 | 291.15 | 0.5
0.08385 | 282.15 | 0.09644 | 291.15 | 0.6
0.08385 | 282.15 | 0.09644 | 291.15 | 0.7
0.08385 | 282.15 | 0.09644 | 291.15 | 0.8
0.08385 | 282.15 | 0.09644 | 291.15 | 0.9
0.08385 | 282.15 | 0.09644 | 291.15 | 1
0.08385 | 282.15 | 0.09644 | 294.15 | 0.15
0.08385 | 282.15 | 0.09644 | 294.15 | 0.2
0.08385 | 282.15 | 0.09644 | 294.15 | 0.3
0.08385 | 282.15 | 0.09644 | 294.15 | 0.4
0.08385 | 282.15 | 0.09644 | 294.15 | 0.5
0.08385 | 282.15 | 0.09644 | 294.15 | 0.6
0.08385 | 282.15 | 0.09644 | 294.15 | 0.7
0.08385 | 282.15 | 0.09644 | 294.15 | 0.8
0.08385 | 282.15 | 0.09644 | 294.15 | 0.9
0.08385 | 282.15 | 0.09644 | 294.15 | 1
0.08385 | 282.15 | 0.09644 | 297.15 | 0.15
0.08385 | 282.15 | 0.09644 | 297.15 | 0.2
0.08385 | 282.15 | 0.09644 | 297.15 | 0.3
0.08385 | 282.15 | 0.09644 | 297.15 | 0.4
0.08385 | 282.15 | 0.09644 | 297.15 | 0.5
0.08385 | 282.15 | 0.09644 | 297.15 | 0.6
0.08385 | 282.15 | 0.09644 | 297.15 | 0.7
0.08385 | 282.15 | 0.09644 | 297.15 | 0.8
0.08385 | 282.15 | 0.09644 | 297.15 | 0.9
0.08385 | 282.15 | 0.09644 | 297.15 | 1
0.08385 | 282.15 | 0.09644 | 300.15 | 0.15
0.08385 | 282.15 | 0.09644 | 300.15 | 0.2
0.08385 | 282.15 | 0.09644 | 300.15 | 0.3
0.08385 | 282.15 | 0.09644 | 300.15 | 0.4
0.08385 | 282.15 | 0.09644 | 300.15 | 0.5
0.08385 | 282.15 | 0.09644 | 300.15 | 0.6
0.08385 | 282.15 | 0.09644 | 300.15 | 0.7
0.08385 | 282.15 | 0.09644 | 300.15 | 0.8
0.08385 | 282.15 | 0.09644 | 300.15 | 0.9
0.08385 | 282.15 | 0.09644 | 300.15 | 1
0.08385 | 282.15 | 0.09644 | 303.15 | 0.15
0.08385 | 282.15 | 0.09644 | 303.15 | 0.2
0.08385 | 282.15 | 0.09644 | 303.15 | 0.3
0.08385 | 282.15 | 0.09644 | 303.15 | 0.4
0.08385 | 282.15 | 0.09644 | 303.15 | 0.5
0.08385 | 282.15 | 0.09644 | 303.15 | 0.6
0.08385 | 282.15 | 0.09644 | 303.15 | 0.7
0.08385 | 282.15 | 0.09644 | 303.15 | 0.8
0.08385 | 282.15 | 0.09644 | 303.15 | 0.9
0.08385 | 282.15 | 0.09644 | 303.15 | 1
0.08385 | 282.15 | 0.09737 | 283.65 | 0.15
0.08385 | 282.15 | 0.09737 | 283.65 | 0.2
0.08385 | 282.15 | 0.09737 | 283.65 | 0.3
0.08385 | 282.15 | 0.09737 | 283.65 | 0.4
0.08385 | 282.15 | 0.09737 | 283.65 | 0.5
0.08385 | 282.15 | 0.09737 | 283.65 | 0.6
0.08385 | 282.15 | 0.09737 | 283.65 | 0.7
0.08385 | 282.15 | 0.09737 | 283.65 | 0.8
0.08385 | 282.15 | 0.09737 | 283.65 | 0.9
0.08385 | 282.15 | 0.09737 | 283.65 | 1
0.08385 | 282.15 | 0.09737 | 284.15 | 0.15
0.08385 | 282.15 | 0.09737 | 284.15 | 0.2
0.08385 | 282.15 | 0.09737 | 284.15 | 0.3
0.08385 | 282.15 | 0.09737 | 284.15 | 0.4
0.08385 | 282.15 | 0.09737 | 284.15 | 0.5
0.08385 | 282.15 | 0.09737 | 284.15 | 0.6
0.08385 | 282.15 | 0.09737 | 284.15 | 0.7
0.08385 | 282.15 | 0.09737 | 284.15 | 0.8
0.08385 | 282.15 | 0.09737 | 284.15 | 0.9
0.08385 | 282.15 | 0.09737 | 284.15 | 1
0.08385 | 282.15 | 0.09737 | 284.65 | 0.15
0.08385 | 282.15 | 0.09737 | 284.65 | 0.2
0.08385 | 282.15 | 0.09737 | 284.65 | 0.3
0.08385 | 282.15 | 0.09737 | 284.65 | 0.4
0.08385 | 282.15 | 0.09737 | 284.65 | 0.5
0.08385 | 282.15 | 0.09737 | 284.65 | 0.6
0.08385 | 282.15 | 0.09737 | 284.65 | 0.7
0.08385 | 282.15 | 0.09737 | 284.65 | 0.8
0.08385 | 282.15 | 0.09737 | 284.65 | 0.9
0.08385 | 282.15 | 0.09737 | 284.65 | 1
0.08385 | 282.15 | 0.09737 | 285.15 | 0.15
0.08385 | 282.15 | 0.09737 | 285.15 | 0.2
0.08385 | 282.15 | 0.09737 | 285.15 | 0.3
0.08385 | 282.15 | 0.09737 | 285.15 | 0.4
0.08385 | 282.15 | 0.09737 | 285.15 | 0.5
0.08385 | 282.15 | 0.09737 | 285.15 | 0.6
0.08385 | 282.15 | 0.09737 | 285.15 | 0.7
0.08385 | 282.15 | 0.09737 | 285.15 | 0.8
0.08385 | 282.15 | 0.09737 | 285.15 | 0.9
0.08385 | 282.15 | 0.09737 | 285.15 | 1
0.08385 | 282.15 | 0.09737 | 285.65 | 0.15
0.08385 | 282.15 | 0.09737 | 285.65 | 0.2
0.08385 | 282.15 | 0.09737 | 285.65 | 0.3
0.08385 | 282.15 | 0.09737 | 285.65 | 0.4
0.08385 | 282.15 | 0.09737 | 285.65 | 0.5
0.08385 | 282.15 | 0.09737 | 285.65 | 0.6
0.08385 | 282.15 | 0.09737 | 285.65 | 0.7
0.08385 | 282.15 | 0.09737 | 285.65 | 0.8
0.08385 | 282.15 | 0.09737 | 285.65 | 0.9
0.08385 | 282.15 | 0.09737 | 285.65 | 1
0.08385 | 282.15 | 0.09737 | 286.15 | 0.15
0.08385 | 282.15 | 0.09737 | 286.15 | 0.2
0.08385 | 282.15 | 0.09737 | 286.15 | 0.3
0.08385 | 282.15 | 0.09737 | 286.15 | 0.4
0.08385 | 282.15 | 0.09737 | 286.15 | 0.5
0.08385 | 282.15 | 0.09737 | 286.15 | 0.6
0.08385 | 282.15 | 0.09737 | 286.15 | 0.7
0.08385 | 282.15 | 0.09737 | 286.15 | 0.8
0.08385 | 282.15 | 0.09737 | 286.15 | 0.9
0.08385 | 282.15 | 0.09737 | 286.15 | 1
0.08385 | 282.15 | 0.09737 | 286.65 | 0.15
0.08385 | 282.15 | 0.09737 | 286.65 | 0.2
0.08385 | 282.15 | 0.09737 | 286.65 | 0.3
0.08385 | 282.15 | 0.09737 | 286.65 | 0.4
0.08385 | 282.15 | 0.09737 | 286.65 | 0.5
0.08385 | 282.15 | 0.09737 | 286.65 | 0.6
0.08385 | 282.15 | 0.09737 | 286.65 | 0.7
0.08385 | 282.15 | 0.09737 | 286.65 | 0.8
0.08385 | 282.15 | 0.09737 | 286.65 | 0.9
0.08385 | 282.15 | 0.09737 | 286.65 | 1
0.08385 | 282.15 | 0.09737 | 287.15 | 0.15
0.08385 | 282.15 | 0.09737 | 287.15 | 0.2
0.08385 | 282.15 | 0.09737 | 287.15 | 0.3
0.08385 | 282.15 | 0.09737 | 287.15 | 0.4
0.08385 | 282.15 | 0.09737 | 287.15 | 0.5
0.08385 | 282.15 | 0.09737 | 287.15 | 0.6
0.08385 | 282.15 | 0.09737 | 287.15 | 0.7
0.08385 | 282.15 | 0.09737 | 287.15 | 0.8
0.08385 | 282.15 | 0.09737 | 287.15 | 0.9
0.08385 | 282.15 | 0.09737 | 287.15 | 1
0.08385 | 282.15 | 0.09737 | 287.65 | 0.15
0.08385 | 282.15 | 0.09737 | 287.65 | 0.2
0.08385 | 282.15 | 0.09737 | 287.65 | 0.3
0.08385 | 282.15 | 0.09737 | 287.65 | 0.4
0.08385 | 282.15 | 0.09737 | 287.65 | 0.5
0.08385 | 282.15 | 0.09737 | 287.65 | 0.6
0.08385 | 282.15 | 0.09737 | 287.65 | 0.7
0.08385 | 282.15 | 0.09737 | 287.65 | 0.8
0.08385 | 282.15 | 0.09737 | 287.65 | 0.9
0.08385 | 282.15 | 0.09737 | 287.65 | 1
0.08385 | 282.15 | 0.09737 | 288.15 | 0.15
0.08385 | 282.15 | 0.09737 | 288.15 | 0.2
0.08385 | 282.15 | 0.09737 | 288.15 | 0.3
0.08385 | 282.15 | 0.09737 | 288.15 | 0.4
0.08385 | 282.15 | 0.09737 | 288.15 | 0.5
0.08385 | 282.15 | 0.09737 | 288.15 | 0.6
0.08385 | 282.15 | 0.09737 | 288.15 | 0.7
0.08385 | 282.15 | 0.09737 | 288.15 | 0.8
0.08385 | 282.15 | 0.09737 | 288.15 | 0.9
0.08385 | 282.15 | 0.09737 | 288.15 | 1
0.08385 | 282.15 | 0.09737 | 288.65 | 0.15
0.08385 | 282.15 | 0.09737 | 288.65 | 0.2
0.08385 | 282.15 | 0.09737 | 288.65 | 0.3
0.08385 | 282.15 | 0.09737 | 288.65 | 0.4
0.08385 | 282.15 | 0.09737 | 288.65 | 0.5
0.08385 | 282.15 | 0.09737 | 288.65 | 0.6
0.08385 | 282.15 | 0.09737 | 288.65 | 0.7
0.08385 | 282.15 | 0.09737 | 288.65 | 0.8
0.08385 | 282.15 | 0.09737 | 288.65 | 0.9
0.08385 | 282.15 | 0.09737 | 288.65 | 1
0.08385 | 282.15 | 0.09737 | 289.15 | 0.15
0.08385 | 282.15 | 0.09737 | 289.15 | 0.2
0.08385 | 282.15 | 0.09737 | 289.15 | 0.3
0.08385 | 282.15 | 0.09737 | 289.15 | 0.4
0.08385 | 282.15 | 0.09737 | 289.15 | 0.5
0.08385 | 282.15 | 0.09737 | 289.15 | 0.6
0.08385 | 282.15 | 0.09737 | 289.15 | 0.7
0.08385 | 282.15 | 0.09737 | 289.15 | 0.8
0.08385 | 282.15 | 0.09737 | 289.15 | 0.9
0.08385 | 282.15 | 0.09737 | 289.15 | 1
0.08385 | 282.15 | 0.09737 | 289.65 | 0.15
0.08385 | 282.15 | 0.09737 | 289.65 | 0.2
0.08385 | 282.15 | 0.09737 | 289.65 | 0.3
0.08385 | 282.15 | 0.09737 | 289.65 | 0.4
0.08385 | 282.15 | 0.09737 | 289.65 | 0.5
0.08385 | 282.15 | 0.09737 | 289.65 | 0.6
0.08385 | 282.15 | 0.09737 | 289.65 | 0.7
0.08385 | 282.15 | 0.09737 | 289.65 | 0.8
0.08385 | 282.15 | 0.09737 | 289.65 | 0.9
0.08385 | 282.15 | 0.09737 | 289.65 | 1
0.08385 | 282.15 | 0.09737 | 290.15 | 0.15
0.08385 | 282.15 | 0.09737 | 290.15 | 0.2
0.08385 | 282.15 | 0.09737 | 290.15 | 0.3
0.08385 | 282.15 | 0.09737 | 290.15 | 0.4
0.08385 | 282.15 | 0.09737 | 290.15 | 0.5
0.08385 | 282.15 | 0.09737 | 290.15 | 0.6
0.08385 | 282.15 | 0.09737 | 290.15 | 0.7
0.08385 | 282.15 | 0.09737 | 290.15 | 0.8
0.08385 | 282.15 | 0.09737 | 290.15 | 0.9
0.08385 | 282.15 | 0.09737 | 290.15 | 1
0.08385 | 282.15 | 0.09737 | 290.65 | 0.15
0.08385 | 282.15 | 0.09737 | 290.65 | 0.2
0.08385 | 282.15 | 0.09737 | 290.65 | 0.3
0.08385 | 282.15 | 0.09737 | 290.65 | 0.4
0.08385 | 282.15 | 0.09737 | 290.65 | 0.5
0.08385 | 282.15 | 0.09737 | 290.65 | 0.6
0.08385 | 282.15 | 0.09737 | 290.65 | 0.7
0.08385 | 282.15 | 0.09737 | 290.65 | 0.8
0.08385 | 282.15 | 0.09737 | 290.65 | 0.9
0.08385 | 282.15 | 0.09737 | 290.65 | 1
0.08385 | 282.15 | 0.09737 | 291.15 | 0.15
0.08385 | 282.15 | 0.09737 | 291.15 | 0.2
0.08385 | 282.15 | 0.09737 | 291.15 | 0.3
0.08385 | 282.15 | 0.09737 | 291.15 | 0.4
0.08385 | 282.15 | 0.09737 | 291.15 | 0.5
0.08385 | 282.15 | 0.09737 | 291.15 | 0.6
0.08385 | 282.15 | 0.09737 | 291.15 | 0.7
0.08385 | 282.15 | 0.09737 | 291.15 | 0.8
0.08385 | 282.15 | 0.09737 | 291.15 | 0.9
0.08385 | 282.15 | 0.09737 | 291.15 | 1
0.08385 | 282.15 | 0.09737 | 294.15 | 0.15
0.08385 | 282.15 | 0.09737 | 294.15 | 0.2
0.08385 | 282.15 | 0.09737 | 294.15 | 0.3
0.08385 | 282.15 | 0.09737 | 294.15 | 0.4
0.08385 | 282.15 | 0.09737 | 294.15 | 0.5
0.08385 | 282.15 | 0.09737 | 294.15 | 0.6
0.08385 | 282.15 | 0.09737 | 294.15 | 0.7
0.08385 | 282.15 | 0.09737 | 294.15 | 0.8
0.08385 | 282.15 | 0.09737 | 294.15 | 0.9
0.08385 | 282.15 | 0.09737 | 294.15 | 1
0.08385 | 282.15 | 0.09737 | 297.15 | 0.15
0.08385 | 282.15 | 0.09737 | 297.15 | 0.2
0.08385 | 282.15 | 0.09737 | 297.15 | 0.3
0.08385 | 282.15 | 0.09737 | 297.15 | 0.4
0.08385 | 282.15 | 0.09737 | 297.15 | 0.5
0.08385 | 282.15 | 0.09737 | 297.15 | 0.6
0.08385 | 282.15 | 0.09737 | 297.15 | 0.7
0.08385 | 282.15 | 0.09737 | 297.15 | 0.8
0.08385 | 282.15 | 0.09737 | 297.15 | 0.9
0.08385 | 282.15 | 0.09737 | 297.15 | 1
0.08385 | 282.15 | 0.09737 | 300.15 | 0.15
0.08385 | 282.15 | 0.09737 | 300.15 | 0.2
0.08385 | 282.15 | 0.09737 | 300.15 | 0.3
0.08385 | 282.15 | 0.09737 | 300.15 | 0.4
0.08385 | 282.15 | 0.09737 | 300.15 | 0.5
0.08385 | 282.15 | 0.09737 | 300.15 | 0.6
0.08385 | 282.15 | 0.09737 | 300.15 | 0.7
0.08385 | 282.15 | 0.09737 | 300.15 | 0.8
0.08385 | 282.15 | 0.09737 | 300.15 | 0.9
0.08385 | 282.15 | 0.09737 | 300.15 | 1
0.08385 | 282.15 | 0.09737 | 303.15 | 0.15
0.08385 | 282.15 | 0.09737 | 303.15 | 0.2
0.08385 | 282.15 | 0.09737 | 303.15 | 0.3
0.08385 | 282.15 | 0.09737 | 303.15 | 0.4
0.08385 | 282.15 | 0.09737 | 303.15 | 0.5
0.08385 | 282.15 | 0.09737 | 303.15 | 0.6
0.08385 | 282.15 | 0.09737 | 303.15 | 0.7
0.08385 | 282.15 | 0.09737 | 303.15 | 0.8
0.08385 | 282.15 | 0.09737 | 303.15 | 0.9
0.08385 | 282.15 | 0.09737 | 303.15 | 1
0.08385 | 282.15 | 0.115 | 283.65 | 0.15
0.08385 | 282.15 | 0.115 | 283.65 | 0.2
0.08385 | 282.15 | 0.115 | 283.65 | 0.3
0.08385 | 282.15 | 0.115 | 283.65 | 0.4
0.08385 | 282.15 | 0.115 | 283.65 | 0.5
0.08385 | 282.15 | 0.115 | 283.65 | 0.6
0.08385 | 282.15 | 0.115 | 283.65 | 0.7
0.08385 | 282.15 | 0.115 | 283.65 | 0.8
0.08385 | 282.15 | 0.115 | 283.65 | 0.9
0.08385 | 282.15 | 0.115 | 283.65 | 1
0.08385 | 282.15 | 0.115 | 284.15 | 0.15
0.08385 | 282.15 | 0.115 | 284.15 | 0.2
0.08385 | 282.15 | 0.115 | 284.15 | 0.3
0.08385 | 282.15 | 0.115 | 284.15 | 0.4
0.08385 | 282.15 | 0.115 | 284.15 | 0.5
0.08385 | 282.15 | 0.115 | 284.15 | 0.6
0.08385 | 282.15 | 0.115 | 284.15 | 0.7
0.08385 | 282.15 | 0.115 | 284.15 | 0.8
0.08385 | 282.15 | 0.115 | 284.15 | 0.9
0.08385 | 282.15 | 0.115 | 284.15 | 1
0.08385 | 282.15 | 0.115 | 284.65 | 0.15
0.08385 | 282.15 | 0.115 | 284.65 | 0.2
0.08385 | 282.15 | 0.115 | 284.65 | 0.3
0.08385 | 282.15 | 0.115 | 284.65 | 0.4
0.08385 | 282.15 | 0.115 | 284.65 | 0.5
0.08385 | 282.15 | 0.115 | 284.65 | 0.6
0.08385 | 282.15 | 0.115 | 284.65 | 0.7
0.08385 | 282.15 | 0.115 | 284.65 | 0.8
0.08385 | 282.15 | 0.115 | 284.65 | 0.9
0.08385 | 282.15 | 0.115 | 284.65 | 1
0.08385 | 282.15 | 0.115 | 285.15 | 0.15
0.08385 | 282.15 | 0.115 | 285.15 | 0.2
0.08385 | 282.15 | 0.115 | 285.15 | 0.3
0.08385 | 282.15 | 0.115 | 285.15 | 0.4
0.08385 | 282.15 | 0.115 | 285.15 | 0.5
0.08385 | 282.15 | 0.115 | 285.15 | 0.6
0.08385 | 282.15 | 0.115 | 285.15 | 0.7
0.08385 | 282.15 | 0.115 | 285.15 | 0.8
0.08385 | 282.15 | 0.115 | 285.15 | 0.9
0.08385 | 282.15 | 0.115 | 285.15 | 1
0.08385 | 282.15 | 0.115 | 285.65 | 0.15
0.08385 | 282.15 | 0.115 | 285.65 | 0.2
0.08385 | 282.15 | 0.115 | 285.65 | 0.3
0.08385 | 282.15 | 0.115 | 285.65 | 0.4
0.08385 | 282.15 | 0.115 | 285.65 | 0.5
0.08385 | 282.15 | 0.115 | 285.65 | 0.6
0.08385 | 282.15 | 0.115 | 285.65 | 0.7
0.08385 | 282.15 | 0.115 | 285.65 | 0.8
0.08385 | 282.15 | 0.115 | 285.65 | 0.9
0.08385 | 282.15 | 0.115 | 285.65 | 1
0.08385 | 282.15 | 0.115 | 286.15 | 0.15
0.08385 | 282.15 | 0.115 | 286.15 | 0.2
0.08385 | 282.15 | 0.115 | 286.15 | 0.3
0.08385 | 282.15 | 0.115 | 286.15 | 0.4
0.08385 | 282.15 | 0.115 | 286.15 | 0.5
0.08385 | 282.15 | 0.115 | 286.15 | 0.6
0.08385 | 282.15 | 0.115 | 286.15 | 0.7
0.08385 | 282.15 | 0.115 | 286.15 | 0.8
0.08385 | 282.15 | 0.115 | 286.15 | 0.9
0.08385 | 282.15 | 0.115 | 286.15 | 1
0.08385 | 282.15 | 0.115 | 286.65 | 0.15
0.08385 | 282.15 | 0.115 | 286.65 | 0.2
0.08385 | 282.15 | 0.115 | 286.65 | 0.3
0.08385 | 282.15 | 0.115 | 286.65 | 0.4
0.08385 | 282.15 | 0.115 | 286.65 | 0.5
0.08385 | 282.15 | 0.115 | 286.65 | 0.6
0.08385 | 282.15 | 0.115 | 286.65 | 0.7
0.08385 | 282.15 | 0.115 | 286.65 | 0.8
0.08385 | 282.15 | 0.115 | 286.65 | 0.9
0.08385 | 282.15 | 0.115 | 286.65 | 1
0.08385 | 282.15 | 0.115 | 287.15 | 0.15
0.08385 | 282.15 | 0.115 | 287.15 | 0.2
0.08385 | 282.15 | 0.115 | 287.15 | 0.3
0.08385 | 282.15 | 0.115 | 287.15 | 0.4
0.08385 | 282.15 | 0.115 | 287.15 | 0.5
0.08385 | 282.15 | 0.115 | 287.15 | 0.6
0.08385 | 282.15 | 0.115 | 287.15 | 0.7
0.08385 | 282.15 | 0.115 | 287.15 | 0.8
0.08385 | 282.15 | 0.115 | 287.15 | 0.9
0.08385 | 282.15 | 0.115 | 287.15 | 1
0.08385 | 282.15 | 0.115 | 287.65 | 0.15
0.08385 | 282.15 | 0.115 | 287.65 | 0.2
0.08385 | 282.15 | 0.115 | 287.65 | 0.3
0.08385 | 282.15 | 0.115 | 287.65 | 0.4
0.08385 | 282.15 | 0.115 | 287.65 | 0.5
0.08385 | 282.15 | 0.115 | 287.65 | 0.6
0.08385 | 282.15 | 0.115 | 287.65 | 0.7
0.08385 | 282.15 | 0.115 | 287.65 | 0.8
0.08385 | 282.15 | 0.115 | 287.65 | 0.9
0.08385 | 282.15 | 0.115 | 287.65 | 1
0.08385 | 282.15 | 0.115 | 288.15 | 0.15
0.08385 | 282.15 | 0.115 | 288.15 | 0.2
0.08385 | 282.15 | 0.115 | 288.15 | 0.3
0.08385 | 282.15 | 0.115 | 288.15 | 0.4
0.08385 | 282.15 | 0.115 | 288.15 | 0.5
0.08385 | 282.15 | 0.115 | 288.15 | 0.6
0.08385 | 282.15 | 0.115 | 288.15 | 0.7
0.08385 | 282.15 | 0.115 | 288.15 | 0.8
0.08385 | 282.15 | 0.115 | 288.15 | 0.9
0.08385 | 282.15 | 0.115 | 288.15 | 1
0.08385 | 282.15 | 0.115 | 288.65 | 0.15
0.08385 | 282.15 | 0.115 | 288.65 | 0.2
0.08385 | 282.15 | 0.115 | 288.65 | 0.3
0.08385 | 282.15 | 0.115 | 288.65 | 0.4
0.08385 | 282.15 | 0.115 | 288.65 | 0.5
0.08385 | 282.15 | 0.115 | 288.65 | 0.6
0.08385 | 282.15 | 0.115 | 288.65 | 0.7
0.08385 | 282.15 | 0.115 | 288.65 | 0.8
0.08385 | 282.15 | 0.115 | 288.65 | 0.9
0.08385 | 282.15 | 0.115 | 288.65 | 1
0.08385 | 282.15 | 0.115 | 289.15 | 0.15
0.08385 | 282.15 | 0.115 | 289.15 | 0.2
0.08385 | 282.15 | 0.115 | 289.15 | 0.3
0.08385 | 282.15 | 0.115 | 289.15 | 0.4
0.08385 | 282.15 | 0.115 | 289.15 | 0.5
0.08385 | 282.15 | 0.115 | 289.15 | 0.6
0.08385 | 282.15 | 0.115 | 289.15 | 0.7
0.08385 | 282.15 | 0.115 | 289.15 | 0.8
0.08385 | 282.15 | 0.115 | 289.15 | 0.9
0.08385 | 282.15 | 0.115 | 289.15 | 1
0.08385 | 282.15 | 0.115 | 289.65 | 0.15
0.08385 | 282.15 | 0.115 | 289.65 | 0.2
0.08385 | 282.15 | 0.115 | 289.65 | 0.3
0.08385 | 282.15 | 0.115 | 289.65 | 0.4
0.08385 | 282.15 | 0.115 | 289.65 | 0.5
0.08385 | 282.15 | 0.115 | 289.65 | 0.6
0.08385 | 282.15 | 0.115 | 289.65 | 0.7
0.08385 | 282.15 | 0.115 | 289.65 | 0.8
0.08385 | 282.15 | 0.115 | 289.65 | 0.9
0.08385 | 282.15 | 0.115 | 289.65 | 1
0.08385 | 282.15 | 0.115 | 290.15 | 0.15
0.08385 | 282.15 | 0.115 | 290.15 | 0.2
0.08385 | 282.15 | 0.115 | 290.15 | 0.3
0.08385 | 282.15 | 0.115 | 290.15 | 0.4
0.08385 | 282.15 | 0.115 | 290.15 | 0.5
0.08385 | 282.15 | 0.115 | 290.15 | 0.6
0.08385 | 282.15 | 0.115 | 290.15 | 0.7
0.08385 | 282.15 | 0.115 | 290.15 | 0.8
0.08385 | 282.15 | 0.115 | 290.15 | 0.9
0.08385 | 282.15 | 0.115 | 290.15 | 1
0.08385 | 282.15 | 0.115 | 290.65 | 0.15
0.08385 | 282.15 | 0.115 | 290.65 | 0.2
0.08385 | 282.15 | 0.115 | 290.65 | 0.3
0.08385 | 282.15 | 0.115 | 290.65 | 0.4
0.08385 | 282.15 | 0.115 | 290.65 | 0.5
0.08385 | 282.15 | 0.115 | 290.65 | 0.6
0.08385 | 282.15 | 0.115 | 290.65 | 0.7
0.08385 | 282.15 | 0.115 | 290.65 | 0.8
0.08385 | 282.15 | 0.115 | 290.65 | 0.9
0.08385 | 282.15 | 0.115 | 290.65 | 1
0.08385 | 282.15 | 0.115 | 291.15 | 0.15
0.08385 | 282.15 | 0.115 | 291.15 | 0.2
0.08385 | 282.15 | 0.115 | 291.15 | 0.3
0.08385 | 282.15 | 0.115 | 291.15 | 0.4
0.08385 | 282.15 | 0.115 | 291.15 | 0.5
0.08385 | 282.15 | 0.115 | 291.15 | 0.6
0.08385 | 282.15 | 0.115 | 291.15 | 0.7
0.08385 | 282.15 | 0.115 | 291.15 | 0.8
0.08385 | 282.15 | 0.115 | 291.15 | 0.9
0.08385 | 282.15 | 0.115 | 291.15 | 1
0.08385 | 282.15 | 0.115 | 294.15 | 0.15
0.08385 | 282.15 | 0.115 | 294.15 | 0.2
0.08385 | 282.15 | 0.115 | 294.15 | 0.3
0.08385 | 282.15 | 0.115 | 294.15 | 0.4
0.08385 | 282.15 | 0.115 | 294.15 | 0.5
0.08385 | 282.15 | 0.115 | 294.15 | 0.6
0.08385 | 282.15 | 0.115 | 294.15 | 0.7
0.08385 | 282.15 | 0.115 | 294.15 | 0.8
0.08385 | 282.15 | 0.115 | 294.15 | 0.9
0.08385 | 282.15 | 0.115 | 294.15 | 1
0.08385 | 282.15 | 0.115 | 297.15 | 0.15
0.08385 | 282.15 | 0.115 | 297.15 | 0.2
0.08385 | 282.15 | 0.115 | 297.15 | 0.3
0.08385 | 282.15 | 0.115 | 297.15 | 0.4
0.08385 | 282.15 | 0.115 | 297.15 | 0.5
0.08385 | 282.15 | 0.115 | 297.15 | 0.6
0.08385 | 282.15 | 0.115 | 297.15 | 0.7
0.08385 | 282.15 | 0.115 | 297.15 | 0.8
0.08385 | 282.15 | 0.115 | 297.15 | 0.9
0.08385 | 282.15 | 0.115 | 297.15 | 1
0.08385 | 282.15 | 0.115 | 300.15 | 0.15
0.08385 | 282.15 | 0.115 | 300.15 | 0.2
0.08385 | 282.15 | 0.115 | 300.15 | 0.3
0.08385 | 282.15 | 0.115 | 300.15 | 0.4
0.08385 | 282.15 | 0.115 | 300.15 | 0.5
0.08385 | 282.15 | 0.115 | 300.15 | 0.6
0.08385 | 282.15 | 0.115 | 300.15 | 0.7
0.08385 | 282.15 | 0.115 | 300.15 | 0.8
0.08385 | 282.15 | 0.115 | 300.15 | 0.9
0.08385 | 282.15 | 0.115 | 300.15 | 1
0.08385 | 282.15 | 0.115 | 303.15 | 0.15
0.08385 | 282.15 | 0.115 | 303.15 | 0.2
0.08385 | 282.15 | 0.115 | 303.15 | 0.3
0.08385 | 282.15 | 0.115 | 303.15 | 0.4
0.08385 | 282.15 | 0.115 | 303.15 | 0.5
0.08385 | 282.15 | 0.115 | 303.15 | 0.6
0.08385 | 282.15 | 0.115 | 303.15 | 0.7
0.08385 | 282.15 | 0.115 | 303.15 | 0.8
0.08385 | 282.15 | 0.115 | 303.15 | 0.9
0.08385 | 282.15 | 0.115 | 303.15 | 1
0.1398 | 278.15 | 0.00115 | 283.65 | 0.15
0.1398 | 278.15 | 0.00115 | 283.65 | 0.2
0.1398 | 278.15 | 0.00115 | 283.65 | 0.3
0.1398 | 278.15 | 0.00115 | 283.65 | 0.4
0.1398 | 278.15 | 0.00115 | 283.65 | 0.5
0.1398 | 278.15 | 0.00115 | 283.65 | 0.6
0.1398 | 278.15 | 0.00115 | 283.65 | 0.7
0.1398 | 278.15 | 0.00115 | 283.65 | 0.8
0.1398 | 278.15 | 0.00115 | 283.65 | 0.9
0.1398 | 278.15 | 0.00115 | 283.65 | 1
0.1398 | 278.15 | 0.00115 | 284.15 | 0.15
0.1398 | 278.15 | 0.00115 | 284.15 | 0.2
0.1398 | 278.15 | 0.00115 | 284.15 | 0.3
0.1398 | 278.15 | 0.00115 | 284.15 | 0.4
0.1398 | 278.15 | 0.00115 | 284.15 | 0.5
0.1398 | 278.15 | 0.00115 | 284.15 | 0.6
0.1398 | 278.15 | 0.00115 | 284.15 | 0.7
0.1398 | 278.15 | 0.00115 | 284.15 | 0.8
0.1398 | 278.15 | 0.00115 | 284.15 | 0.9
0.1398 | 278.15 | 0.00115 | 284.15 | 1
0.1398 | 278.15 | 0.00115 | 284.65 | 0.15
0.1398 | 278.15 | 0.00115 | 284.65 | 0.2
0.1398 | 278.15 | 0.00115 | 284.65 | 0.3
0.1398 | 278.15 | 0.00115 | 284.65 | 0.4
0.1398 | 278.15 | 0.00115 | 284.65 | 0.5
0.1398 | 278.15 | 0.00115 | 284.65 | 0.6
0.1398 | 278.15 | 0.00115 | 284.65 | 0.7
0.1398 | 278.15 | 0.00115 | 284.65 | 0.8
0.1398 | 278.15 | 0.00115 | 284.65 | 0.9
0.1398 | 278.15 | 0.00115 | 284.65 | 1
0.1398 | 278.15 | 0.00115 | 285.15 | 0.15
0.1398 | 278.15 | 0.00115 | 285.15 | 0.2
0.1398 | 278.15 | 0.00115 | 285.15 | 0.3
0.1398 | 278.15 | 0.00115 | 285.15 | 0.4
0.1398 | 278.15 | 0.00115 | 285.15 | 0.5
0.1398 | 278.15 | 0.00115 | 285.15 | 0.6
0.1398 | 278.15 | 0.00115 | 285.15 | 0.7
0.1398 | 278.15 | 0.00115 | 285.15 | 0.8
0.1398 | 278.15 | 0.00115 | 285.15 | 0.9
0.1398 | 278.15 | 0.00115 | 285.15 | 1
0.1398 | 278.15 | 0.00115 | 285.65 | 0.15
0.1398 | 278.15 | 0.00115 | 285.65 | 0.2
0.1398 | 278.15 | 0.00115 | 285.65 | 0.3
0.1398 | 278.15 | 0.00115 | 285.65 | 0.4
0.1398 | 278.15 | 0.00115 | 285.65 | 0.5
0.1398 | 278.15 | 0.00115 | 285.65 | 0.6
0.1398 | 278.15 | 0.00115 | 285.65 | 0.7
0.1398 | 278.15 | 0.00115 | 285.65 | 0.8
0.1398 | 278.15 | 0.00115 | 285.65 | 0.9
0.1398 | 278.15 | 0.00115 | 285.65 | 1
0.1398 | 278.15 | 0.00115 | 286.15 | 0.15
0.1398 | 278.15 | 0.00115 | 286.15 | 0.2
0.1398 | 278.15 | 0.00115 | 286.15 | 0.3
0.1398 | 278.15 | 0.00115 | 286.15 | 0.4
0.1398 | 278.15 | 0.00115 | 286.15 | 0.5
0.1398 | 278.15 | 0.00115 | 286.15 | 0.6
0.1398 | 278.15 | 0.00115 | 286.15 | 0.7
0.1398 | 278.15 | 0.00115 | 286.15 | 0.8
0.1398 | 278.15 | 0.00115 | 286.15 | 0.9
0.1398 | 278.15 | 0.00115 | 286.15 | 1
0.1398 | 278.15 | 0.00115 | 286.65 | 0.15
0.1398 | 278.15 | 0.00115 | 286.65 | 0.2
0.1398 | 278.15 | 0.00115 | 286.65 | 0.3
0.1398 | 278.15 | 0.00115 | 286.65 | 0.4
0.1398 | 278.15 | 0.00115 | 286.65 | 0.5
0.1398 | 278.15 | 0.00115 | 286.65 | 0.6
0.1398 | 278.15 | 0.00115 | 286.65 | 0.7
0.1398 | 278.15 | 0.00115 | 286.65 | 0.8
0.1398 | 278.15 | 0.00115 | 286.65 | 0.9
0.1398 | 278.15 | 0.00115 | 286.65 | 1
0.1398 | 278.15 | 0.00115 | 287.15 | 0.15
0.1398 | 278.15 | 0.00115 | 287.15 | 0.2
0.1398 | 278.15 | 0.00115 | 287.15 | 0.3
0.1398 | 278.15 | 0.00115 | 287.15 | 0.4
0.1398 | 278.15 | 0.00115 | 287.15 | 0.5
0.1398 | 278.15 | 0.00115 | 287.15 | 0.6
0.1398 | 278.15 | 0.00115 | 287.15 | 0.7
0.1398 | 278.15 | 0.00115 | 287.15 | 0.8
0.1398 | 278.15 | 0.00115 | 287.15 | 0.9
0.1398 | 278.15 | 0.00115 | 287.15 | 1
0.1398 | 278.15 | 0.00115 | 287.65 | 0.15
0.1398 | 278.15 | 0.00115 | 287.65 | 0.2
0.1398 | 278.15 | 0.00115 | 287.65 | 0.3
0.1398 | 278.15 | 0.00115 | 287.65 | 0.4
0.1398 | 278.15 | 0.00115 | 287.65 | 0.5
0.1398 | 278.15 | 0.00115 | 287.65 | 0.6
0.1398 | 278.15 | 0.00115 | 287.65 | 0.7
0.1398 | 278.15 | 0.00115 | 287.65 | 0.8
0.1398 | 278.15 | 0.00115 | 287.65 | 0.9
0.1398 | 278.15 | 0.00115 | 287.65 | 1
0.1398 | 278.15 | 0.00115 | 288.15 | 0.15
0.1398 | 278.15 | 0.00115 | 288.15 | 0.2
0.1398 | 278.15 | 0.00115 | 288.15 | 0.3
0.1398 | 278.15 | 0.00115 | 288.15 | 0.4
0.1398 | 278.15 | 0.00115 | 288.15 | 0.5
0.1398 | 278.15 | 0.00115 | 288.15 | 0.6
0.1398 | 278.15 | 0.00115 | 288.15 | 0.7
0.1398 | 278.15 | 0.00115 | 288.15 | 0.8
0.1398 | 278.15 | 0.00115 | 288.15 | 0.9
0.1398 | 278.15 | 0.00115 | 288.15 | 1
0.1398 | 278.15 | 0.00115 | 288.65 | 0.15
0.1398 | 278.15 | 0.00115 | 288.65 | 0.2
0.1398 | 278.15 | 0.00115 | 288.65 | 0.3
0.1398 | 278.15 | 0.00115 | 288.65 | 0.4
0.1398 | 278.15 | 0.00115 | 288.65 | 0.5
0.1398 | 278.15 | 0.00115 | 288.65 | 0.6
0.1398 | 278.15 | 0.00115 | 288.65 | 0.7
0.1398 | 278.15 | 0.00115 | 288.65 | 0.8
0.1398 | 278.15 | 0.00115 | 288.65 | 0.9
0.1398 | 278.15 | 0.00115 | 288.65 | 1
0.1398 | 278.15 | 0.00115 | 289.15 | 0.15
0.1398 | 278.15 | 0.00115 | 289.15 | 0.2
0.1398 | 278.15 | 0.00115 | 289.15 | 0.3
0.1398 | 278.15 | 0.00115 | 289.15 | 0.4
0.1398 | 278.15 | 0.00115 | 289.15 | 0.5
0.1398 | 278.15 | 0.00115 | 289.15 | 0.6
0.1398 | 278.15 | 0.00115 | 289.15 | 0.7
0.1398 | 278.15 | 0.00115 | 289.15 | 0.8
0.1398 | 278.15 | 0.00115 | 289.15 | 0.9
0.1398 | 278.15 | 0.00115 | 289.15 | 1
0.1398 | 278.15 | 0.00115 | 289.65 | 0.15
0.1398 | 278.15 | 0.00115 | 289.65 | 0.2
0.1398 | 278.15 | 0.00115 | 289.65 | 0.3
0.1398 | 278.15 | 0.00115 | 289.65 | 0.4
0.1398 | 278.15 | 0.00115 | 289.65 | 0.5
0.1398 | 278.15 | 0.00115 | 289.65 | 0.6
0.1398 | 278.15 | 0.00115 | 289.65 | 0.7
0.1398 | 278.15 | 0.00115 | 289.65 | 0.8
0.1398 | 278.15 | 0.00115 | 289.65 | 0.9
0.1398 | 278.15 | 0.00115 | 289.65 | 1
0.1398 | 278.15 | 0.00115 | 290.15 | 0.15
0.1398 | 278.15 | 0.00115 | 290.15 | 0.2
0.1398 | 278.15 | 0.00115 | 290.15 | 0.3
0.1398 | 278.15 | 0.00115 | 290.15 | 0.4
0.1398 | 278.15 | 0.00115 | 290.15 | 0.5
0.1398 | 278.15 | 0.00115 | 290.15 | 0.6
0.1398 | 278.15 | 0.00115 | 290.15 | 0.7
0.1398 | 278.15 | 0.00115 | 290.15 | 0.8
0.1398 | 278.15 | 0.00115 | 290.15 | 0.9
0.1398 | 278.15 | 0.00115 | 290.15 | 1
0.1398 | 278.15 | 0.00115 | 290.65 | 0.15
0.1398 | 278.15 | 0.00115 | 290.65 | 0.2
0.1398 | 278.15 | 0.00115 | 290.65 | 0.3
0.1398 | 278.15 | 0.00115 | 290.65 | 0.4
0.1398 | 278.15 | 0.00115 | 290.65 | 0.5
0.1398 | 278.15 | 0.00115 | 290.65 | 0.6
0.1398 | 278.15 | 0.00115 | 290.65 | 0.7
0.1398 | 278.15 | 0.00115 | 290.65 | 0.8
0.1398 | 278.15 | 0.00115 | 290.65 | 0.9
0.1398 | 278.15 | 0.00115 | 290.65 | 1
0.1398 | 278.15 | 0.00115 | 291.15 | 0.15
0.1398 | 278.15 | 0.00115 | 291.15 | 0.2
0.1398 | 278.15 | 0.00115 | 291.15 | 0.3
0.1398 | 278.15 | 0.00115 | 291.15 | 0.4
0.1398 | 278.15 | 0.00115 | 291.15 | 0.5
0.1398 | 278.15 | 0.00115 | 291.15 | 0.6
0.1398 | 278.15 | 0.00115 | 291.15 | 0.7
0.1398 | 278.15 | 0.00115 | 291.15 | 0.8
0.1398 | 278.15 | 0.00115 | 291.15 | 0.9
0.1398 | 278.15 | 0.00115 | 291.15 | 1
0.1398 | 278.15 | 0.00115 | 294.15 | 0.15
0.1398 | 278.15 | 0.00115 | 294.15 | 0.2
0.1398 | 278.15 | 0.00115 | 294.15 | 0.3
0.1398 | 278.15 | 0.00115 | 294.15 | 0.4
0.1398 | 278.15 | 0.00115 | 294.15 | 0.5
0.1398 | 278.15 | 0.00115 | 294.15 | 0.6
0.1398 | 278.15 | 0.00115 | 294.15 | 0.7
0.1398 | 278.15 | 0.00115 | 294.15 | 0.8
0.1398 | 278.15 | 0.00115 | 294.15 | 0.9
0.1398 | 278.15 | 0.00115 | 294.15 | 1
0.1398 | 278.15 | 0.00115 | 297.15 | 0.15
0.1398 | 278.15 | 0.00115 | 297.15 | 0.2
0.1398 | 278.15 | 0.00115 | 297.15 | 0.3
0.1398 | 278.15 | 0.00115 | 297.15 | 0.4
0.1398 | 278.15 | 0.00115 | 297.15 | 0.5
0.1398 | 278.15 | 0.00115 | 297.15 | 0.6
0.1398 | 278.15 | 0.00115 | 297.15 | 0.7
0.1398 | 278.15 | 0.00115 | 297.15 | 0.8
0.1398 | 278.15 | 0.00115 | 297.15 | 0.9
0.1398 | 278.15 | 0.00115 | 297.15 | 1
0.1398 | 278.15 | 0.00115 | 300.15 | 0.15
0.1398 | 278.15 | 0.00115 | 300.15 | 0.2
0.1398 | 278.15 | 0.00115 | 300.15 | 0.3
0.1398 | 278.15 | 0.00115 | 300.15 | 0.4
0.1398 | 278.15 | 0.00115 | 300.15 | 0.5
0.1398 | 278.15 | 0.00115 | 300.15 | 0.6
0.1398 | 278.15 | 0.00115 | 300.15 | 0.7
0.1398 | 278.15 | 0.00115 | 300.15 | 0.8
0.1398 | 278.15 | 0.00115 | 300.15 | 0.9
0.1398 | 278.15 | 0.00115 | 300.15 | 1
0.1398 | 278.15 | 0.00115 | 303.15 | 0.15
0.1398 | 278.15 | 0.00115 | 303.15 | 0.2
0.1398 | 278.15 | 0.00115 | 303.15 | 0.3
0.1398 | 278.15 | 0.00115 | 303.15 | 0.4
0.1398 | 278.15 | 0.00115 | 303.15 | 0.5
0.1398 | 278.15 | 0.00115 | 303.15 | 0.6
0.1398 | 278.15 | 0.00115 | 303.15 | 0.7
0.1398 | 278.15 | 0.00115 | 303.15 | 0.8
0.1398 | 278.15 | 0.00115 | 303.15 | 0.9
0.1398 | 278.15 | 0.00115 | 303.15 | 1
0.1398 | 278.15 | 0.077 | 283.65 | 0.15
0.1398 | 278.15 | 0.077 | 283.65 | 0.2
0.1398 | 278.15 | 0.077 | 283.65 | 0.3
0.1398 | 278.15 | 0.077 | 283.65 | 0.4
0.1398 | 278.15 | 0.077 | 283.65 | 0.5
0.1398 | 278.15 | 0.077 | 283.65 | 0.6
0.1398 | 278.15 | 0.077 | 283.65 | 0.7
0.1398 | 278.15 | 0.077 | 283.65 | 0.8
0.1398 | 278.15 | 0.077 | 283.65 | 0.9
0.1398 | 278.15 | 0.077 | 283.65 | 1
0.1398 | 278.15 | 0.077 | 284.15 | 0.15
0.1398 | 278.15 | 0.077 | 284.15 | 0.2
0.1398 | 278.15 | 0.077 | 284.15 | 0.3
0.1398 | 278.15 | 0.077 | 284.15 | 0.4
0.1398 | 278.15 | 0.077 | 284.15 | 0.5
0.1398 | 278.15 | 0.077 | 284.15 | 0.6
0.1398 | 278.15 | 0.077 | 284.15 | 0.7
0.1398 | 278.15 | 0.077 | 284.15 | 0.8
0.1398 | 278.15 | 0.077 | 284.15 | 0.9
0.1398 | 278.15 | 0.077 | 284.15 | 1
0.1398 | 278.15 | 0.077 | 284.65 | 0.15
0.1398 | 278.15 | 0.077 | 284.65 | 0.2
0.1398 | 278.15 | 0.077 | 284.65 | 0.3
0.1398 | 278.15 | 0.077 | 284.65 | 0.4
0.1398 | 278.15 | 0.077 | 284.65 | 0.5
0.1398 | 278.15 | 0.077 | 284.65 | 0.6
0.1398 | 278.15 | 0.077 | 284.65 | 0.7
0.1398 | 278.15 | 0.077 | 284.65 | 0.8
0.1398 | 278.15 | 0.077 | 284.65 | 0.9
0.1398 | 278.15 | 0.077 | 284.65 | 1
0.1398 | 278.15 | 0.077 | 285.15 | 0.15
0.1398 | 278.15 | 0.077 | 285.15 | 0.2
0.1398 | 278.15 | 0.077 | 285.15 | 0.3
0.1398 | 278.15 | 0.077 | 285.15 | 0.4
0.1398 | 278.15 | 0.077 | 285.15 | 0.5
0.1398 | 278.15 | 0.077 | 285.15 | 0.6
0.1398 | 278.15 | 0.077 | 285.15 | 0.7
0.1398 | 278.15 | 0.077 | 285.15 | 0.8
0.1398 | 278.15 | 0.077 | 285.15 | 0.9
0.1398 | 278.15 | 0.077 | 285.15 | 1
0.1398 | 278.15 | 0.077 | 285.65 | 0.15
0.1398 | 278.15 | 0.077 | 285.65 | 0.2
0.1398 | 278.15 | 0.077 | 285.65 | 0.3
0.1398 | 278.15 | 0.077 | 285.65 | 0.4
0.1398 | 278.15 | 0.077 | 285.65 | 0.5
0.1398 | 278.15 | 0.077 | 285.65 | 0.6
0.1398 | 278.15 | 0.077 | 285.65 | 0.7
0.1398 | 278.15 | 0.077 | 285.65 | 0.8
0.1398 | 278.15 | 0.077 | 285.65 | 0.9
0.1398 | 278.15 | 0.077 | 285.65 | 1
0.1398 | 278.15 | 0.077 | 286.15 | 0.15
0.1398 | 278.15 | 0.077 | 286.15 | 0.2
0.1398 | 278.15 | 0.077 | 286.15 | 0.3
0.1398 | 278.15 | 0.077 | 286.15 | 0.4
0.1398 | 278.15 | 0.077 | 286.15 | 0.5
0.1398 | 278.15 | 0.077 | 286.15 | 0.6
0.1398 | 278.15 | 0.077 | 286.15 | 0.7
0.1398 | 278.15 | 0.077 | 286.15 | 0.8
0.1398 | 278.15 | 0.077 | 286.15 | 0.9
0.1398 | 278.15 | 0.077 | 286.15 | 1
0.1398 | 278.15 | 0.077 | 286.65 | 0.15
0.1398 | 278.15 | 0.077 | 286.65 | 0.2
0.1398 | 278.15 | 0.077 | 286.65 | 0.3
0.1398 | 278.15 | 0.077 | 286.65 | 0.4
0.1398 | 278.15 | 0.077 | 286.65 | 0.5
0.1398 | 278.15 | 0.077 | 286.65 | 0.6
0.1398 | 278.15 | 0.077 | 286.65 | 0.7
0.1398 | 278.15 | 0.077 | 286.65 | 0.8
0.1398 | 278.15 | 0.077 | 286.65 | 0.9
0.1398 | 278.15 | 0.077 | 286.65 | 1
0.1398 | 278.15 | 0.077 | 287.15 | 0.15
0.1398 | 278.15 | 0.077 | 287.15 | 0.2
0.1398 | 278.15 | 0.077 | 287.15 | 0.3
0.1398 | 278.15 | 0.077 | 287.15 | 0.4
0.1398 | 278.15 | 0.077 | 287.15 | 0.5
0.1398 | 278.15 | 0.077 | 287.15 | 0.6
0.1398 | 278.15 | 0.077 | 287.15 | 0.7
0.1398 | 278.15 | 0.077 | 287.15 | 0.8
0.1398 | 278.15 | 0.077 | 287.15 | 0.9
0.1398 | 278.15 | 0.077 | 287.15 | 1
0.1398 | 278.15 | 0.077 | 287.65 | 0.15
0.1398 | 278.15 | 0.077 | 287.65 | 0.2
0.1398 | 278.15 | 0.077 | 287.65 | 0.3
0.1398 | 278.15 | 0.077 | 287.65 | 0.4
0.1398 | 278.15 | 0.077 | 287.65 | 0.5
0.1398 | 278.15 | 0.077 | 287.65 | 0.6
0.1398 | 278.15 | 0.077 | 287.65 | 0.7
0.1398 | 278.15 | 0.077 | 287.65 | 0.8
0.1398 | 278.15 | 0.077 | 287.65 | 0.9
0.1398 | 278.15 | 0.077 | 287.65 | 1
0.1398 | 278.15 | 0.077 | 288.15 | 0.15
0.1398 | 278.15 | 0.077 | 288.15 | 0.2
0.1398 | 278.15 | 0.077 | 288.15 | 0.3
0.1398 | 278.15 | 0.077 | 288.15 | 0.4
0.1398 | 278.15 | 0.077 | 288.15 | 0.5
0.1398 | 278.15 | 0.077 | 288.15 | 0.6
0.1398 | 278.15 | 0.077 | 288.15 | 0.7
0.1398 | 278.15 | 0.077 | 288.15 | 0.8
0.1398 | 278.15 | 0.077 | 288.15 | 0.9
0.1398 | 278.15 | 0.077 | 288.15 | 1
0.1398 | 278.15 | 0.077 | 288.65 | 0.15
0.1398 | 278.15 | 0.077 | 288.65 | 0.2
0.1398 | 278.15 | 0.077 | 288.65 | 0.3
0.1398 | 278.15 | 0.077 | 288.65 | 0.4
0.1398 | 278.15 | 0.077 | 288.65 | 0.5
0.1398 | 278.15 | 0.077 | 288.65 | 0.6
0.1398 | 278.15 | 0.077 | 288.65 | 0.7
0.1398 | 278.15 | 0.077 | 288.65 | 0.8
0.1398 | 278.15 | 0.077 | 288.65 | 0.9
0.1398 | 278.15 | 0.077 | 288.65 | 1
0.1398 | 278.15 | 0.077 | 289.15 | 0.15
0.1398 | 278.15 | 0.077 | 289.15 | 0.2
0.1398 | 278.15 | 0.077 | 289.15 | 0.3
0.1398 | 278.15 | 0.077 | 289.15 | 0.4
0.1398 | 278.15 | 0.077 | 289.15 | 0.5
0.1398 | 278.15 | 0.077 | 289.15 | 0.6
0.1398 | 278.15 | 0.077 | 289.15 | 0.7
0.1398 | 278.15 | 0.077 | 289.15 | 0.8
0.1398 | 278.15 | 0.077 | 289.15 | 0.9
0.1398 | 278.15 | 0.077 | 289.15 | 1
0.1398 | 278.15 | 0.077 | 289.65 | 0.15
0.1398 | 278.15 | 0.077 | 289.65 | 0.2
0.1398 | 278.15 | 0.077 | 289.65 | 0.3
0.1398 | 278.15 | 0.077 | 289.65 | 0.4
0.1398 | 278.15 | 0.077 | 289.65 | 0.5
0.1398 | 278.15 | 0.077 | 289.65 | 0.6
0.1398 | 278.15 | 0.077 | 289.65 | 0.7
0.1398 | 278.15 | 0.077 | 289.65 | 0.8
0.1398 | 278.15 | 0.077 | 289.65 | 0.9
0.1398 | 278.15 | 0.077 | 289.65 | 1
0.1398 | 278.15 | 0.077 | 290.15 | 0.15
0.1398 | 278.15 | 0.077 | 290.15 | 0.2
0.1398 | 278.15 | 0.077 | 290.15 | 0.3
0.1398 | 278.15 | 0.077 | 290.15 | 0.4
0.1398 | 278.15 | 0.077 | 290.15 | 0.5
0.1398 | 278.15 | 0.077 | 290.15 | 0.6
0.1398 | 278.15 | 0.077 | 290.15 | 0.7
0.1398 | 278.15 | 0.077 | 290.15 | 0.8
0.1398 | 278.15 | 0.077 | 290.15 | 0.9
0.1398 | 278.15 | 0.077 | 290.15 | 1
0.1398 | 278.15 | 0.077 | 290.65 | 0.15
0.1398 | 278.15 | 0.077 | 290.65 | 0.2
0.1398 | 278.15 | 0.077 | 290.65 | 0.3
0.1398 | 278.15 | 0.077 | 290.65 | 0.4
0.1398 | 278.15 | 0.077 | 290.65 | 0.5
0.1398 | 278.15 | 0.077 | 290.65 | 0.6
0.1398 | 278.15 | 0.077 | 290.65 | 0.7
0.1398 | 278.15 | 0.077 | 290.65 | 0.8
0.1398 | 278.15 | 0.077 | 290.65 | 0.9
0.1398 | 278.15 | 0.077 | 290.65 | 1
0.1398 | 278.15 | 0.077 | 291.15 | 0.15
0.1398 | 278.15 | 0.077 | 291.15 | 0.2
0.1398 | 278.15 | 0.077 | 291.15 | 0.3
0.1398 | 278.15 | 0.077 | 291.15 | 0.4
0.1398 | 278.15 | 0.077 | 291.15 | 0.5
0.1398 | 278.15 | 0.077 | 291.15 | 0.6
0.1398 | 278.15 | 0.077 | 291.15 | 0.7
0.1398 | 278.15 | 0.077 | 291.15 | 0.8
0.1398 | 278.15 | 0.077 | 291.15 | 0.9
0.1398 | 278.15 | 0.077 | 291.15 | 1
0.1398 | 278.15 | 0.077 | 294.15 | 0.15
0.1398 | 278.15 | 0.077 | 294.15 | 0.2
0.1398 | 278.15 | 0.077 | 294.15 | 0.3
0.1398 | 278.15 | 0.077 | 294.15 | 0.4
0.1398 | 278.15 | 0.077 | 294.15 | 0.5
0.1398 | 278.15 | 0.077 | 294.15 | 0.6
0.1398 | 278.15 | 0.077 | 294.15 | 0.7
0.1398 | 278.15 | 0.077 | 294.15 | 0.8
0.1398 | 278.15 | 0.077 | 294.15 | 0.9
0.1398 | 278.15 | 0.077 | 294.15 | 1
0.1398 | 278.15 | 0.077 | 297.15 | 0.15
0.1398 | 278.15 | 0.077 | 297.15 | 0.2
0.1398 | 278.15 | 0.077 | 297.15 | 0.3
0.1398 | 278.15 | 0.077 | 297.15 | 0.4
0.1398 | 278.15 | 0.077 | 297.15 | 0.5
0.1398 | 278.15 | 0.077 | 297.15 | 0.6
0.1398 | 278.15 | 0.077 | 297.15 | 0.7
0.1398 | 278.15 | 0.077 | 297.15 | 0.8
0.1398 | 278.15 | 0.077 | 297.15 | 0.9
0.1398 | 278.15 | 0.077 | 297.15 | 1
0.1398 | 278.15 | 0.077 | 300.15 | 0.15
0.1398 | 278.15 | 0.077 | 300.15 | 0.2
0.1398 | 278.15 | 0.077 | 300.15 | 0.3
0.1398 | 278.15 | 0.077 | 300.15 | 0.4
0.1398 | 278.15 | 0.077 | 300.15 | 0.5
0.1398 | 278.15 | 0.077 | 300.15 | 0.6
0.1398 | 278.15 | 0.077 | 300.15 | 0.7
0.1398 | 278.15 | 0.077 | 300.15 | 0.8
0.1398 | 278.15 | 0.077 | 300.15 | 0.9
0.1398 | 278.15 | 0.077 | 300.15 | 1
0.1398 | 278.15 | 0.077 | 303.15 | 0.15
0.1398 | 278.15 | 0.077 | 303.15 | 0.2
0.1398 | 278.15 | 0.077 | 303.15 | 0.3
0.1398 | 278.15 | 0.077 | 303.15 | 0.4
0.1398 | 278.15 | 0.077 | 303.15 | 0.5
0.1398 | 278.15 | 0.077 | 303.15 | 0.6
0.1398 | 278.15 | 0.077 | 303.15 | 0.7
0.1398 | 278.15 | 0.077 | 303.15 | 0.8
0.1398 | 278.15 | 0.077 | 303.15 | 0.9
0.1398 | 278.15 | 0.077 | 303.15 | 1
0.1398 | 278.15 | 0.09437 | 283.65 | 0.15
0.1398 | 278.15 | 0.09437 | 283.65 | 0.2
0.1398 | 278.15 | 0.09437 | 283.65 | 0.3
0.1398 | 278.15 | 0.09437 | 283.65 | 0.4
0.1398 | 278.15 | 0.09437 | 283.65 | 0.5
0.1398 | 278.15 | 0.09437 | 283.65 | 0.6
0.1398 | 278.15 | 0.09437 | 283.65 | 0.7
0.1398 | 278.15 | 0.09437 | 283.65 | 0.8
0.1398 | 278.15 | 0.09437 | 283.65 | 0.9
0.1398 | 278.15 | 0.09437 | 283.65 | 1
0.1398 | 278.15 | 0.09437 | 284.15 | 0.15
0.1398 | 278.15 | 0.09437 | 284.15 | 0.2
0.1398 | 278.15 | 0.09437 | 284.15 | 0.3
0.1398 | 278.15 | 0.09437 | 284.15 | 0.4
0.1398 | 278.15 | 0.09437 | 284.15 | 0.5
0.1398 | 278.15 | 0.09437 | 284.15 | 0.6
0.1398 | 278.15 | 0.09437 | 284.15 | 0.7
0.1398 | 278.15 | 0.09437 | 284.15 | 0.8
0.1398 | 278.15 | 0.09437 | 284.15 | 0.9
0.1398 | 278.15 | 0.09437 | 284.15 | 1
0.1398 | 278.15 | 0.09437 | 284.65 | 0.15
0.1398 | 278.15 | 0.09437 | 284.65 | 0.2
0.1398 | 278.15 | 0.09437 | 284.65 | 0.3
0.1398 | 278.15 | 0.09437 | 284.65 | 0.4
0.1398 | 278.15 | 0.09437 | 284.65 | 0.5
0.1398 | 278.15 | 0.09437 | 284.65 | 0.6
0.1398 | 278.15 | 0.09437 | 284.65 | 0.7
0.1398 | 278.15 | 0.09437 | 284.65 | 0.8
0.1398 | 278.15 | 0.09437 | 284.65 | 0.9
0.1398 | 278.15 | 0.09437 | 284.65 | 1
0.1398 | 278.15 | 0.09437 | 285.15 | 0.15
0.1398 | 278.15 | 0.09437 | 285.15 | 0.2
0.1398 | 278.15 | 0.09437 | 285.15 | 0.3
0.1398 | 278.15 | 0.09437 | 285.15 | 0.4
0.1398 | 278.15 | 0.09437 | 285.15 | 0.5
0.1398 | 278.15 | 0.09437 | 285.15 | 0.6
0.1398 | 278.15 | 0.09437 | 285.15 | 0.7
0.1398 | 278.15 | 0.09437 | 285.15 | 0.8
0.1398 | 278.15 | 0.09437 | 285.15 | 0.9
0.1398 | 278.15 | 0.09437 | 285.15 | 1
0.1398 | 278.15 | 0.09437 | 285.65 | 0.15
0.1398 | 278.15 | 0.09437 | 285.65 | 0.2
0.1398 | 278.15 | 0.09437 | 285.65 | 0.3
0.1398 | 278.15 | 0.09437 | 285.65 | 0.4
0.1398 | 278.15 | 0.09437 | 285.65 | 0.5
0.1398 | 278.15 | 0.09437 | 285.65 | 0.6
0.1398 | 278.15 | 0.09437 | 285.65 | 0.7
0.1398 | 278.15 | 0.09437 | 285.65 | 0.8
0.1398 | 278.15 | 0.09437 | 285.65 | 0.9
0.1398 | 278.15 | 0.09437 | 285.65 | 1
0.1398 | 278.15 | 0.09437 | 286.15 | 0.15
0.1398 | 278.15 | 0.09437 | 286.15 | 0.2
0.1398 | 278.15 | 0.09437 | 286.15 | 0.3
0.1398 | 278.15 | 0.09437 | 286.15 | 0.4
0.1398 | 278.15 | 0.09437 | 286.15 | 0.5
0.1398 | 278.15 | 0.09437 | 286.15 | 0.6
0.1398 | 278.15 | 0.09437 | 286.15 | 0.7
0.1398 | 278.15 | 0.09437 | 286.15 | 0.8
0.1398 | 278.15 | 0.09437 | 286.15 | 0.9
0.1398 | 278.15 | 0.09437 | 286.15 | 1
0.1398 | 278.15 | 0.09437 | 286.65 | 0.15
0.1398 | 278.15 | 0.09437 | 286.65 | 0.2
0.1398 | 278.15 | 0.09437 | 286.65 | 0.3
0.1398 | 278.15 | 0.09437 | 286.65 | 0.4
0.1398 | 278.15 | 0.09437 | 286.65 | 0.5
0.1398 | 278.15 | 0.09437 | 286.65 | 0.6
0.1398 | 278.15 | 0.09437 | 286.65 | 0.7
0.1398 | 278.15 | 0.09437 | 286.65 | 0.8
0.1398 | 278.15 | 0.09437 | 286.65 | 0.9
0.1398 | 278.15 | 0.09437 | 286.65 | 1
0.1398 | 278.15 | 0.09437 | 287.15 | 0.15
0.1398 | 278.15 | 0.09437 | 287.15 | 0.2
0.1398 | 278.15 | 0.09437 | 287.15 | 0.3
0.1398 | 278.15 | 0.09437 | 287.15 | 0.4
0.1398 | 278.15 | 0.09437 | 287.15 | 0.5
0.1398 | 278.15 | 0.09437 | 287.15 | 0.6
0.1398 | 278.15 | 0.09437 | 287.15 | 0.7
0.1398 | 278.15 | 0.09437 | 287.15 | 0.8
0.1398 | 278.15 | 0.09437 | 287.15 | 0.9
0.1398 | 278.15 | 0.09437 | 287.15 | 1
0.1398 | 278.15 | 0.09437 | 287.65 | 0.15
0.1398 | 278.15 | 0.09437 | 287.65 | 0.2
0.1398 | 278.15 | 0.09437 | 287.65 | 0.3
0.1398 | 278.15 | 0.09437 | 287.65 | 0.4
0.1398 | 278.15 | 0.09437 | 287.65 | 0.5
0.1398 | 278.15 | 0.09437 | 287.65 | 0.6
0.1398 | 278.15 | 0.09437 | 287.65 | 0.7
0.1398 | 278.15 | 0.09437 | 287.65 | 0.8
0.1398 | 278.15 | 0.09437 | 287.65 | 0.9
0.1398 | 278.15 | 0.09437 | 287.65 | 1
0.1398 | 278.15 | 0.09437 | 288.15 | 0.15
0.1398 | 278.15 | 0.09437 | 288.15 | 0.2
0.1398 | 278.15 | 0.09437 | 288.15 | 0.3
0.1398 | 278.15 | 0.09437 | 288.15 | 0.4
0.1398 | 278.15 | 0.09437 | 288.15 | 0.5
0.1398 | 278.15 | 0.09437 | 288.15 | 0.6
0.1398 | 278.15 | 0.09437 | 288.15 | 0.7
0.1398 | 278.15 | 0.09437 | 288.15 | 0.8
0.1398 | 278.15 | 0.09437 | 288.15 | 0.9
0.1398 | 278.15 | 0.09437 | 288.15 | 1
0.1398 | 278.15 | 0.09437 | 288.65 | 0.15
0.1398 | 278.15 | 0.09437 | 288.65 | 0.2
0.1398 | 278.15 | 0.09437 | 288.65 | 0.3
0.1398 | 278.15 | 0.09437 | 288.65 | 0.4
0.1398 | 278.15 | 0.09437 | 288.65 | 0.5
0.1398 | 278.15 | 0.09437 | 288.65 | 0.6
0.1398 | 278.15 | 0.09437 | 288.65 | 0.7
0.1398 | 278.15 | 0.09437 | 288.65 | 0.8
0.1398 | 278.15 | 0.09437 | 288.65 | 0.9
0.1398 | 278.15 | 0.09437 | 288.65 | 1
0.1398 | 278.15 | 0.09437 | 289.15 | 0.15
0.1398 | 278.15 | 0.09437 | 289.15 | 0.2
0.1398 | 278.15 | 0.09437 | 289.15 | 0.3
0.1398 | 278.15 | 0.09437 | 289.15 | 0.4
0.1398 | 278.15 | 0.09437 | 289.15 | 0.5
0.1398 | 278.15 | 0.09437 | 289.15 | 0.6
0.1398 | 278.15 | 0.09437 | 289.15 | 0.7
0.1398 | 278.15 | 0.09437 | 289.15 | 0.8
0.1398 | 278.15 | 0.09437 | 289.15 | 0.9
0.1398 | 278.15 | 0.09437 | 289.15 | 1
0.1398 | 278.15 | 0.09437 | 289.65 | 0.15
0.1398 | 278.15 | 0.09437 | 289.65 | 0.2
0.1398 | 278.15 | 0.09437 | 289.65 | 0.3
0.1398 | 278.15 | 0.09437 | 289.65 | 0.4
0.1398 | 278.15 | 0.09437 | 289.65 | 0.5
0.1398 | 278.15 | 0.09437 | 289.65 | 0.6
0.1398 | 278.15 | 0.09437 | 289.65 | 0.7
0.1398 | 278.15 | 0.09437 | 289.65 | 0.8
0.1398 | 278.15 | 0.09437 | 289.65 | 0.9
0.1398 | 278.15 | 0.09437 | 289.65 | 1
0.1398 | 278.15 | 0.09437 | 290.15 | 0.15
0.1398 | 278.15 | 0.09437 | 290.15 | 0.2
0.1398 | 278.15 | 0.09437 | 290.15 | 0.3
0.1398 | 278.15 | 0.09437 | 290.15 | 0.4
0.1398 | 278.15 | 0.09437 | 290.15 | 0.5
0.1398 | 278.15 | 0.09437 | 290.15 | 0.6
0.1398 | 278.15 | 0.09437 | 290.15 | 0.7
0.1398 | 278.15 | 0.09437 | 290.15 | 0.8
0.1398 | 278.15 | 0.09437 | 290.15 | 0.9
0.1398 | 278.15 | 0.09437 | 290.15 | 1
0.1398 | 278.15 | 0.09437 | 290.65 | 0.15
0.1398 | 278.15 | 0.09437 | 290.65 | 0.2
0.1398 | 278.15 | 0.09437 | 290.65 | 0.3
0.1398 | 278.15 | 0.09437 | 290.65 | 0.4
0.1398 | 278.15 | 0.09437 | 290.65 | 0.5
0.1398 | 278.15 | 0.09437 | 290.65 | 0.6
0.1398 | 278.15 | 0.09437 | 290.65 | 0.7
0.1398 | 278.15 | 0.09437 | 290.65 | 0.8
0.1398 | 278.15 | 0.09437 | 290.65 | 0.9
0.1398 | 278.15 | 0.09437 | 290.65 | 1
0.1398 | 278.15 | 0.09437 | 291.15 | 0.15
0.1398 | 278.15 | 0.09437 | 291.15 | 0.2
0.1398 | 278.15 | 0.09437 | 291.15 | 0.3
0.1398 | 278.15 | 0.09437 | 291.15 | 0.4
0.1398 | 278.15 | 0.09437 | 291.15 | 0.5
0.1398 | 278.15 | 0.09437 | 291.15 | 0.6
0.1398 | 278.15 | 0.09437 | 291.15 | 0.7
0.1398 | 278.15 | 0.09437 | 291.15 | 0.8
0.1398 | 278.15 | 0.09437 | 291.15 | 0.9
0.1398 | 278.15 | 0.09437 | 291.15 | 1
0.1398 | 278.15 | 0.09437 | 294.15 | 0.15
0.1398 | 278.15 | 0.09437 | 294.15 | 0.2
0.1398 | 278.15 | 0.09437 | 294.15 | 0.3
0.1398 | 278.15 | 0.09437 | 294.15 | 0.4
0.1398 | 278.15 | 0.09437 | 294.15 | 0.5
0.1398 | 278.15 | 0.09437 | 294.15 | 0.6
0.1398 | 278.15 | 0.09437 | 294.15 | 0.7
0.1398 | 278.15 | 0.09437 | 294.15 | 0.8
0.1398 | 278.15 | 0.09437 | 294.15 | 0.9
0.1398 | 278.15 | 0.09437 | 294.15 | 1
0.1398 | 278.15 | 0.09437 | 297.15 | 0.15
0.1398 | 278.15 | 0.09437 | 297.15 | 0.2
0.1398 | 278.15 | 0.09437 | 297.15 | 0.3
0.1398 | 278.15 | 0.09437 | 297.15 | 0.4
0.1398 | 278.15 | 0.09437 | 297.15 | 0.5
0.1398 | 278.15 | 0.09437 | 297.15 | 0.6
0.1398 | 278.15 | 0.09437 | 297.15 | 0.7
0.1398 | 278.15 | 0.09437 | 297.15 | 0.8
0.1398 | 278.15 | 0.09437 | 297.15 | 0.9
0.1398 | 278.15 | 0.09437 | 297.15 | 1
0.1398 | 278.15 | 0.09437 | 300.15 | 0.15
0.1398 | 278.15 | 0.09437 | 300.15 | 0.2
0.1398 | 278.15 | 0.09437 | 300.15 | 0.3
0.1398 | 278.15 | 0.09437 | 300.15 | 0.4
0.1398 | 278.15 | 0.09437 | 300.15 | 0.5
0.1398 | 278.15 | 0.09437 | 300.15 | 0.6
0.1398 | 278.15 | 0.09437 | 300.15 | 0.7
0.1398 | 278.15 | 0.09437 | 300.15 | 0.8
0.1398 | 278.15 | 0.09437 | 300.15 | 0.9
0.1398 | 278.15 | 0.09437 | 300.15 | 1
0.1398 | 278.15 | 0.09437 | 303.15 | 0.15
0.1398 | 278.15 | 0.09437 | 303.15 | 0.2
0.1398 | 278.15 | 0.09437 | 303.15 | 0.3
0.1398 | 278.15 | 0.09437 | 303.15 | 0.4
0.1398 | 278.15 | 0.09437 | 303.15 | 0.5
0.1398 | 278.15 | 0.09437 | 303.15 | 0.6
0.1398 | 278.15 | 0.09437 | 303.15 | 0.7
0.1398 | 278.15 | 0.09437 | 303.15 | 0.8
0.1398 | 278.15 | 0.09437 | 303.15 | 0.9
0.1398 | 278.15 | 0.09437 | 303.15 | 1
0.1398 | 278.15 | 0.09644 | 283.65 | 0.15
0.1398 | 278.15 | 0.09644 | 283.65 | 0.2
0.1398 | 278.15 | 0.09644 | 283.65 | 0.3
0.1398 | 278.15 | 0.09644 | 283.65 | 0.4
0.1398 | 278.15 | 0.09644 | 283.65 | 0.5
0.1398 | 278.15 | 0.09644 | 283.65 | 0.6
0.1398 | 278.15 | 0.09644 | 283.65 | 0.7
0.1398 | 278.15 | 0.09644 | 283.65 | 0.8
0.1398 | 278.15 | 0.09644 | 283.65 | 0.9
0.1398 | 278.15 | 0.09644 | 283.65 | 1
0.1398 | 278.15 | 0.09644 | 284.15 | 0.15
0.1398 | 278.15 | 0.09644 | 284.15 | 0.2
0.1398 | 278.15 | 0.09644 | 284.15 | 0.3
0.1398 | 278.15 | 0.09644 | 284.15 | 0.4
0.1398 | 278.15 | 0.09644 | 284.15 | 0.5
0.1398 | 278.15 | 0.09644 | 284.15 | 0.6
0.1398 | 278.15 | 0.09644 | 284.15 | 0.7
0.1398 | 278.15 | 0.09644 | 284.15 | 0.8
0.1398 | 278.15 | 0.09644 | 284.15 | 0.9
0.1398 | 278.15 | 0.09644 | 284.15 | 1
0.1398 | 278.15 | 0.09644 | 284.65 | 0.15
0.1398 | 278.15 | 0.09644 | 284.65 | 0.2
0.1398 | 278.15 | 0.09644 | 284.65 | 0.3
0.1398 | 278.15 | 0.09644 | 284.65 | 0.4
0.1398 | 278.15 | 0.09644 | 284.65 | 0.5
0.1398 | 278.15 | 0.09644 | 284.65 | 0.6
0.1398 | 278.15 | 0.09644 | 284.65 | 0.7
0.1398 | 278.15 | 0.09644 | 284.65 | 0.8
0.1398 | 278.15 | 0.09644 | 284.65 | 0.9
0.1398 | 278.15 | 0.09644 | 284.65 | 1
0.1398 | 278.15 | 0.09644 | 285.15 | 0.15
0.1398 | 278.15 | 0.09644 | 285.15 | 0.2
0.1398 | 278.15 | 0.09644 | 285.15 | 0.3
0.1398 | 278.15 | 0.09644 | 285.15 | 0.4
0.1398 | 278.15 | 0.09644 | 285.15 | 0.5
0.1398 | 278.15 | 0.09644 | 285.15 | 0.6
0.1398 | 278.15 | 0.09644 | 285.15 | 0.7
0.1398 | 278.15 | 0.09644 | 285.15 | 0.8
0.1398 | 278.15 | 0.09644 | 285.15 | 0.9
0.1398 | 278.15 | 0.09644 | 285.15 | 1
0.1398 | 278.15 | 0.09644 | 285.65 | 0.15
0.1398 | 278.15 | 0.09644 | 285.65 | 0.2
0.1398 | 278.15 | 0.09644 | 285.65 | 0.3
0.1398 | 278.15 | 0.09644 | 285.65 | 0.4
0.1398 | 278.15 | 0.09644 | 285.65 | 0.5
0.1398 | 278.15 | 0.09644 | 285.65 | 0.6
0.1398 | 278.15 | 0.09644 | 285.65 | 0.7
0.1398 | 278.15 | 0.09644 | 285.65 | 0.8
0.1398 | 278.15 | 0.09644 | 285.65 | 0.9
0.1398 | 278.15 | 0.09644 | 285.65 | 1
0.1398 | 278.15 | 0.09644 | 286.15 | 0.15
0.1398 | 278.15 | 0.09644 | 286.15 | 0.2
0.1398 | 278.15 | 0.09644 | 286.15 | 0.3
0.1398 | 278.15 | 0.09644 | 286.15 | 0.4
0.1398 | 278.15 | 0.09644 | 286.15 | 0.5
0.1398 | 278.15 | 0.09644 | 286.15 | 0.6
0.1398 | 278.15 | 0.09644 | 286.15 | 0.7
0.1398 | 278.15 | 0.09644 | 286.15 | 0.8
0.1398 | 278.15 | 0.09644 | 286.15 | 0.9
0.1398 | 278.15 | 0.09644 | 286.15 | 1
0.1398 | 278.15 | 0.09644 | 286.65 | 0.15
0.1398 | 278.15 | 0.09644 | 286.65 | 0.2
0.1398 | 278.15 | 0.09644 | 286.65 | 0.3
0.1398 | 278.15 | 0.09644 | 286.65 | 0.4
0.1398 | 278.15 | 0.09644 | 286.65 | 0.5
0.1398 | 278.15 | 0.09644 | 286.65 | 0.6
0.1398 | 278.15 | 0.09644 | 286.65 | 0.7
0.1398 | 278.15 | 0.09644 | 286.65 | 0.8
0.1398 | 278.15 | 0.09644 | 286.65 | 0.9
0.1398 | 278.15 | 0.09644 | 286.65 | 1
0.1398 | 278.15 | 0.09644 | 287.15 | 0.15
0.1398 | 278.15 | 0.09644 | 287.15 | 0.2
0.1398 | 278.15 | 0.09644 | 287.15 | 0.3
0.1398 | 278.15 | 0.09644 | 287.15 | 0.4
0.1398 | 278.15 | 0.09644 | 287.15 | 0.5
0.1398 | 278.15 | 0.09644 | 287.15 | 0.6
0.1398 | 278.15 | 0.09644 | 287.15 | 0.7
0.1398 | 278.15 | 0.09644 | 287.15 | 0.8
0.1398 | 278.15 | 0.09644 | 287.15 | 0.9
0.1398 | 278.15 | 0.09644 | 287.15 | 1
0.1398 | 278.15 | 0.09644 | 287.65 | 0.15
0.1398 | 278.15 | 0.09644 | 287.65 | 0.2
0.1398 | 278.15 | 0.09644 | 287.65 | 0.3
0.1398 | 278.15 | 0.09644 | 287.65 | 0.4
0.1398 | 278.15 | 0.09644 | 287.65 | 0.5
0.1398 | 278.15 | 0.09644 | 287.65 | 0.6
0.1398 | 278.15 | 0.09644 | 287.65 | 0.7
0.1398 | 278.15 | 0.09644 | 287.65 | 0.8
0.1398 | 278.15 | 0.09644 | 287.65 | 0.9
0.1398 | 278.15 | 0.09644 | 287.65 | 1
0.1398 | 278.15 | 0.09644 | 288.15 | 0.15
0.1398 | 278.15 | 0.09644 | 288.15 | 0.2
0.1398 | 278.15 | 0.09644 | 288.15 | 0.3
0.1398 | 278.15 | 0.09644 | 288.15 | 0.4
0.1398 | 278.15 | 0.09644 | 288.15 | 0.5
0.1398 | 278.15 | 0.09644 | 288.15 | 0.6
0.1398 | 278.15 | 0.09644 | 288.15 | 0.7
0.1398 | 278.15 | 0.09644 | 288.15 | 0.8
0.1398 | 278.15 | 0.09644 | 288.15 | 0.9
0.1398 | 278.15 | 0.09644 | 288.15 | 1
0.1398 | 278.15 | 0.09644 | 288.65 | 0.15
0.1398 | 278.15 | 0.09644 | 288.65 | 0.2
0.1398 | 278.15 | 0.09644 | 288.65 | 0.3
0.1398 | 278.15 | 0.09644 | 288.65 | 0.4
0.1398 | 278.15 | 0.09644 | 288.65 | 0.5
0.1398 | 278.15 | 0.09644 | 288.65 | 0.6
0.1398 | 278.15 | 0.09644 | 288.65 | 0.7
0.1398 | 278.15 | 0.09644 | 288.65 | 0.8
0.1398 | 278.15 | 0.09644 | 288.65 | 0.9
0.1398 | 278.15 | 0.09644 | 288.65 | 1
0.1398 | 278.15 | 0.09644 | 289.15 | 0.15
0.1398 | 278.15 | 0.09644 | 289.15 | 0.2
0.1398 | 278.15 | 0.09644 | 289.15 | 0.3
0.1398 | 278.15 | 0.09644 | 289.15 | 0.4
0.1398 | 278.15 | 0.09644 | 289.15 | 0.5
0.1398 | 278.15 | 0.09644 | 289.15 | 0.6
0.1398 | 278.15 | 0.09644 | 289.15 | 0.7
0.1398 | 278.15 | 0.09644 | 289.15 | 0.8
0.1398 | 278.15 | 0.09644 | 289.15 | 0.9
0.1398 | 278.15 | 0.09644 | 289.15 | 1
0.1398 | 278.15 | 0.09644 | 289.65 | 0.15
0.1398 | 278.15 | 0.09644 | 289.65 | 0.2
0.1398 | 278.15 | 0.09644 | 289.65 | 0.3
0.1398 | 278.15 | 0.09644 | 289.65 | 0.4
0.1398 | 278.15 | 0.09644 | 289.65 | 0.5
0.1398 | 278.15 | 0.09644 | 289.65 | 0.6
0.1398 | 278.15 | 0.09644 | 289.65 | 0.7
0.1398 | 278.15 | 0.09644 | 289.65 | 0.8
0.1398 | 278.15 | 0.09644 | 289.65 | 0.9
0.1398 | 278.15 | 0.09644 | 289.65 | 1
0.1398 | 278.15 | 0.09644 | 290.15 | 0.15
0.1398 | 278.15 | 0.09644 | 290.15 | 0.2
0.1398 | 278.15 | 0.09644 | 290.15 | 0.3
0.1398 | 278.15 | 0.09644 | 290.15 | 0.4
0.1398 | 278.15 | 0.09644 | 290.15 | 0.5
0.1398 | 278.15 | 0.09644 | 290.15 | 0.6
0.1398 | 278.15 | 0.09644 | 290.15 | 0.7
0.1398 | 278.15 | 0.09644 | 290.15 | 0.8
0.1398 | 278.15 | 0.09644 | 290.15 | 0.9
0.1398 | 278.15 | 0.09644 | 290.15 | 1
0.1398 | 278.15 | 0.09644 | 290.65 | 0.15
0.1398 | 278.15 | 0.09644 | 290.65 | 0.2
0.1398 | 278.15 | 0.09644 | 290.65 | 0.3
0.1398 | 278.15 | 0.09644 | 290.65 | 0.4
0.1398 | 278.15 | 0.09644 | 290.65 | 0.5
0.1398 | 278.15 | 0.09644 | 290.65 | 0.6
0.1398 | 278.15 | 0.09644 | 290.65 | 0.7
0.1398 | 278.15 | 0.09644 | 290.65 | 0.8
0.1398 | 278.15 | 0.09644 | 290.65 | 0.9
0.1398 | 278.15 | 0.09644 | 290.65 | 1
0.1398 | 278.15 | 0.09644 | 291.15 | 0.15
0.1398 | 278.15 | 0.09644 | 291.15 | 0.2
0.1398 | 278.15 | 0.09644 | 291.15 | 0.3
0.1398 | 278.15 | 0.09644 | 291.15 | 0.4
0.1398 | 278.15 | 0.09644 | 291.15 | 0.5
0.1398 | 278.15 | 0.09644 | 291.15 | 0.6
0.1398 | 278.15 | 0.09644 | 291.15 | 0.7
0.1398 | 278.15 | 0.09644 | 291.15 | 0.8
0.1398 | 278.15 | 0.09644 | 291.15 | 0.9
0.1398 | 278.15 | 0.09644 | 291.15 | 1
0.1398 | 278.15 | 0.09644 | 294.15 | 0.15
0.1398 | 278.15 | 0.09644 | 294.15 | 0.2
0.1398 | 278.15 | 0.09644 | 294.15 | 0.3
0.1398 | 278.15 | 0.09644 | 294.15 | 0.4
0.1398 | 278.15 | 0.09644 | 294.15 | 0.5
0.1398 | 278.15 | 0.09644 | 294.15 | 0.6
0.1398 | 278.15 | 0.09644 | 294.15 | 0.7
0.1398 | 278.15 | 0.09644 | 294.15 | 0.8
0.1398 | 278.15 | 0.09644 | 294.15 | 0.9
0.1398 | 278.15 | 0.09644 | 294.15 | 1
0.1398 | 278.15 | 0.09644 | 297.15 | 0.15
0.1398 | 278.15 | 0.09644 | 297.15 | 0.2
0.1398 | 278.15 | 0.09644 | 297.15 | 0.3
0.1398 | 278.15 | 0.09644 | 297.15 | 0.4
0.1398 | 278.15 | 0.09644 | 297.15 | 0.5
0.1398 | 278.15 | 0.09644 | 297.15 | 0.6
0.1398 | 278.15 | 0.09644 | 297.15 | 0.7
0.1398 | 278.15 | 0.09644 | 297.15 | 0.8
0.1398 | 278.15 | 0.09644 | 297.15 | 0.9
0.1398 | 278.15 | 0.09644 | 297.15 | 1
0.1398 | 278.15 | 0.09644 | 300.15 | 0.15
0.1398 | 278.15 | 0.09644 | 300.15 | 0.2
0.1398 | 278.15 | 0.09644 | 300.15 | 0.3
0.1398 | 278.15 | 0.09644 | 300.15 | 0.4
0.1398 | 278.15 | 0.09644 | 300.15 | 0.5
0.1398 | 278.15 | 0.09644 | 300.15 | 0.6
0.1398 | 278.15 | 0.09644 | 300.15 | 0.7
0.1398 | 278.15 | 0.09644 | 300.15 | 0.8
0.1398 | 278.15 | 0.09644 | 300.15 | 0.9
0.1398 | 278.15 | 0.09644 | 300.15 | 1
0.1398 | 278.15 | 0.09644 | 303.15 | 0.15
0.1398 | 278.15 | 0.09644 | 303.15 | 0.2
0.1398 | 278.15 | 0.09644 | 303.15 | 0.3
0.1398 | 278.15 | 0.09644 | 303.15 | 0.4
0.1398 | 278.15 | 0.09644 | 303.15 | 0.5
0.1398 | 278.15 | 0.09644 | 303.15 | 0.6
0.1398 | 278.15 | 0.09644 | 303.15 | 0.7
0.1398 | 278.15 | 0.09644 | 303.15 | 0.8
0.1398 | 278.15 | 0.09644 | 303.15 | 0.9
0.1398 | 278.15 | 0.09644 | 303.15 | 1
0.1398 | 278.15 | 0.09737 | 283.65 | 0.15
0.1398 | 278.15 | 0.09737 | 283.65 | 0.2
0.1398 | 278.15 | 0.09737 | 283.65 | 0.3
0.1398 | 278.15 | 0.09737 | 283.65 | 0.4
0.1398 | 278.15 | 0.09737 | 283.65 | 0.5
0.1398 | 278.15 | 0.09737 | 283.65 | 0.6
0.1398 | 278.15 | 0.09737 | 283.65 | 0.7
0.1398 | 278.15 | 0.09737 | 283.65 | 0.8
0.1398 | 278.15 | 0.09737 | 283.65 | 0.9
0.1398 | 278.15 | 0.09737 | 283.65 | 1
0.1398 | 278.15 | 0.09737 | 284.15 | 0.15
0.1398 | 278.15 | 0.09737 | 284.15 | 0.2
0.1398 | 278.15 | 0.09737 | 284.15 | 0.3
0.1398 | 278.15 | 0.09737 | 284.15 | 0.4
0.1398 | 278.15 | 0.09737 | 284.15 | 0.5
0.1398 | 278.15 | 0.09737 | 284.15 | 0.6
0.1398 | 278.15 | 0.09737 | 284.15 | 0.7
0.1398 | 278.15 | 0.09737 | 284.15 | 0.8
0.1398 | 278.15 | 0.09737 | 284.15 | 0.9
0.1398 | 278.15 | 0.09737 | 284.15 | 1
0.1398 | 278.15 | 0.09737 | 284.65 | 0.15
0.1398 | 278.15 | 0.09737 | 284.65 | 0.2
0.1398 | 278.15 | 0.09737 | 284.65 | 0.3
0.1398 | 278.15 | 0.09737 | 284.65 | 0.4
0.1398 | 278.15 | 0.09737 | 284.65 | 0.5
0.1398 | 278.15 | 0.09737 | 284.65 | 0.6
0.1398 | 278.15 | 0.09737 | 284.65 | 0.7
0.1398 | 278.15 | 0.09737 | 284.65 | 0.8
0.1398 | 278.15 | 0.09737 | 284.65 | 0.9
0.1398 | 278.15 | 0.09737 | 284.65 | 1
0.1398 | 278.15 | 0.09737 | 285.15 | 0.15
0.1398 | 278.15 | 0.09737 | 285.15 | 0.2
0.1398 | 278.15 | 0.09737 | 285.15 | 0.3
0.1398 | 278.15 | 0.09737 | 285.15 | 0.4
0.1398 | 278.15 | 0.09737 | 285.15 | 0.5
0.1398 | 278.15 | 0.09737 | 285.15 | 0.6
0.1398 | 278.15 | 0.09737 | 285.15 | 0.7
0.1398 | 278.15 | 0.09737 | 285.15 | 0.8
0.1398 | 278.15 | 0.09737 | 285.15 | 0.9
0.1398 | 278.15 | 0.09737 | 285.15 | 1
0.1398 | 278.15 | 0.09737 | 285.65 | 0.15
0.1398 | 278.15 | 0.09737 | 285.65 | 0.2
0.1398 | 278.15 | 0.09737 | 285.65 | 0.3
0.1398 | 278.15 | 0.09737 | 285.65 | 0.4
0.1398 | 278.15 | 0.09737 | 285.65 | 0.5
0.1398 | 278.15 | 0.09737 | 285.65 | 0.6
0.1398 | 278.15 | 0.09737 | 285.65 | 0.7
0.1398 | 278.15 | 0.09737 | 285.65 | 0.8
0.1398 | 278.15 | 0.09737 | 285.65 | 0.9
0.1398 | 278.15 | 0.09737 | 285.65 | 1
0.1398 | 278.15 | 0.09737 | 286.15 | 0.15
0.1398 | 278.15 | 0.09737 | 286.15 | 0.2
0.1398 | 278.15 | 0.09737 | 286.15 | 0.3
0.1398 | 278.15 | 0.09737 | 286.15 | 0.4
0.1398 | 278.15 | 0.09737 | 286.15 | 0.5
0.1398 | 278.15 | 0.09737 | 286.15 | 0.6
0.1398 | 278.15 | 0.09737 | 286.15 | 0.7
0.1398 | 278.15 | 0.09737 | 286.15 | 0.8
0.1398 | 278.15 | 0.09737 | 286.15 | 0.9
0.1398 | 278.15 | 0.09737 | 286.15 | 1
0.1398 | 278.15 | 0.09737 | 286.65 | 0.15
0.1398 | 278.15 | 0.09737 | 286.65 | 0.2
0.1398 | 278.15 | 0.09737 | 286.65 | 0.3
0.1398 | 278.15 | 0.09737 | 286.65 | 0.4
0.1398 | 278.15 | 0.09737 | 286.65 | 0.5
0.1398 | 278.15 | 0.09737 | 286.65 | 0.6
0.1398 | 278.15 | 0.09737 | 286.65 | 0.7
0.1398 | 278.15 | 0.09737 | 286.65 | 0.8
0.1398 | 278.15 | 0.09737 | 286.65 | 0.9
0.1398 | 278.15 | 0.09737 | 286.65 | 1
0.1398 | 278.15 | 0.09737 | 287.15 | 0.15
0.1398 | 278.15 | 0.09737 | 287.15 | 0.2
0.1398 | 278.15 | 0.09737 | 287.15 | 0.3
0.1398 | 278.15 | 0.09737 | 287.15 | 0.4
0.1398 | 278.15 | 0.09737 | 287.15 | 0.5
0.1398 | 278.15 | 0.09737 | 287.15 | 0.6
0.1398 | 278.15 | 0.09737 | 287.15 | 0.7
0.1398 | 278.15 | 0.09737 | 287.15 | 0.8
0.1398 | 278.15 | 0.09737 | 287.15 | 0.9
0.1398 | 278.15 | 0.09737 | 287.15 | 1
0.1398 | 278.15 | 0.09737 | 287.65 | 0.15
0.1398 | 278.15 | 0.09737 | 287.65 | 0.2
0.1398 | 278.15 | 0.09737 | 287.65 | 0.3
0.1398 | 278.15 | 0.09737 | 287.65 | 0.4
0.1398 | 278.15 | 0.09737 | 287.65 | 0.5
0.1398 | 278.15 | 0.09737 | 287.65 | 0.6
0.1398 | 278.15 | 0.09737 | 287.65 | 0.7
0.1398 | 278.15 | 0.09737 | 287.65 | 0.8
0.1398 | 278.15 | 0.09737 | 287.65 | 0.9
0.1398 | 278.15 | 0.09737 | 287.65 | 1
0.1398 | 278.15 | 0.09737 | 288.15 | 0.15
0.1398 | 278.15 | 0.09737 | 288.15 | 0.2
0.1398 | 278.15 | 0.09737 | 288.15 | 0.3
0.1398 | 278.15 | 0.09737 | 288.15 | 0.4
0.1398 | 278.15 | 0.09737 | 288.15 | 0.5
0.1398 | 278.15 | 0.09737 | 288.15 | 0.6
0.1398 | 278.15 | 0.09737 | 288.15 | 0.7
0.1398 | 278.15 | 0.09737 | 288.15 | 0.8
0.1398 | 278.15 | 0.09737 | 288.15 | 0.9
0.1398 | 278.15 | 0.09737 | 288.15 | 1
0.1398 | 278.15 | 0.09737 | 288.65 | 0.15
0.1398 | 278.15 | 0.09737 | 288.65 | 0.2
0.1398 | 278.15 | 0.09737 | 288.65 | 0.3
0.1398 | 278.15 | 0.09737 | 288.65 | 0.4
0.1398 | 278.15 | 0.09737 | 288.65 | 0.5
0.1398 | 278.15 | 0.09737 | 288.65 | 0.6
0.1398 | 278.15 | 0.09737 | 288.65 | 0.7
0.1398 | 278.15 | 0.09737 | 288.65 | 0.8
0.1398 | 278.15 | 0.09737 | 288.65 | 0.9
0.1398 | 278.15 | 0.09737 | 288.65 | 1
0.1398 | 278.15 | 0.09737 | 289.15 | 0.15
0.1398 | 278.15 | 0.09737 | 289.15 | 0.2
0.1398 | 278.15 | 0.09737 | 289.15 | 0.3
0.1398 | 278.15 | 0.09737 | 289.15 | 0.4
0.1398 | 278.15 | 0.09737 | 289.15 | 0.5
0.1398 | 278.15 | 0.09737 | 289.15 | 0.6
0.1398 | 278.15 | 0.09737 | 289.15 | 0.7
0.1398 | 278.15 | 0.09737 | 289.15 | 0.8
0.1398 | 278.15 | 0.09737 | 289.15 | 0.9
0.1398 | 278.15 | 0.09737 | 289.15 | 1
0.1398 | 278.15 | 0.09737 | 289.65 | 0.15
0.1398 | 278.15 | 0.09737 | 289.65 | 0.2
0.1398 | 278.15 | 0.09737 | 289.65 | 0.3
0.1398 | 278.15 | 0.09737 | 289.65 | 0.4
0.1398 | 278.15 | 0.09737 | 289.65 | 0.5
0.1398 | 278.15 | 0.09737 | 289.65 | 0.6
0.1398 | 278.15 | 0.09737 | 289.65 | 0.7
0.1398 | 278.15 | 0.09737 | 289.65 | 0.8
0.1398 | 278.15 | 0.09737 | 289.65 | 0.9
0.1398 | 278.15 | 0.09737 | 289.65 | 1
0.1398 | 278.15 | 0.09737 | 290.15 | 0.15
0.1398 | 278.15 | 0.09737 | 290.15 | 0.2
0.1398 | 278.15 | 0.09737 | 290.15 | 0.3
0.1398 | 278.15 | 0.09737 | 290.15 | 0.4
0.1398 | 278.15 | 0.09737 | 290.15 | 0.5
0.1398 | 278.15 | 0.09737 | 290.15 | 0.6
0.1398 | 278.15 | 0.09737 | 290.15 | 0.7
0.1398 | 278.15 | 0.09737 | 290.15 | 0.8
0.1398 | 278.15 | 0.09737 | 290.15 | 0.9
0.1398 | 278.15 | 0.09737 | 290.15 | 1
0.1398 | 278.15 | 0.09737 | 290.65 | 0.15
0.1398 | 278.15 | 0.09737 | 290.65 | 0.2
0.1398 | 278.15 | 0.09737 | 290.65 | 0.3
0.1398 | 278.15 | 0.09737 | 290.65 | 0.4
0.1398 | 278.15 | 0.09737 | 290.65 | 0.5
0.1398 | 278.15 | 0.09737 | 290.65 | 0.6
0.1398 | 278.15 | 0.09737 | 290.65 | 0.7
0.1398 | 278.15 | 0.09737 | 290.65 | 0.8
0.1398 | 278.15 | 0.09737 | 290.65 | 0.9
0.1398 | 278.15 | 0.09737 | 290.65 | 1
0.1398 | 278.15 | 0.09737 | 291.15 | 0.15
0.1398 | 278.15 | 0.09737 | 291.15 | 0.2
0.1398 | 278.15 | 0.09737 | 291.15 | 0.3
0.1398 | 278.15 | 0.09737 | 291.15 | 0.4
0.1398 | 278.15 | 0.09737 | 291.15 | 0.5
0.1398 | 278.15 | 0.09737 | 291.15 | 0.6
0.1398 | 278.15 | 0.09737 | 291.15 | 0.7
0.1398 | 278.15 | 0.09737 | 291.15 | 0.8
0.1398 | 278.15 | 0.09737 | 291.15 | 0.9
0.1398 | 278.15 | 0.09737 | 291.15 | 1
0.1398 | 278.15 | 0.09737 | 294.15 | 0.15
0.1398 | 278.15 | 0.09737 | 294.15 | 0.2
0.1398 | 278.15 | 0.09737 | 294.15 | 0.3
0.1398 | 278.15 | 0.09737 | 294.15 | 0.4
0.1398 | 278.15 | 0.09737 | 294.15 | 0.5
0.1398 | 278.15 | 0.09737 | 294.15 | 0.6
0.1398 | 278.15 | 0.09737 | 294.15 | 0.7
0.1398 | 278.15 | 0.09737 | 294.15 | 0.8
0.1398 | 278.15 | 0.09737 | 294.15 | 0.9
0.1398 | 278.15 | 0.09737 | 294.15 | 1
0.1398 | 278.15 | 0.09737 | 297.15 | 0.15
0.1398 | 278.15 | 0.09737 | 297.15 | 0.2
0.1398 | 278.15 | 0.09737 | 297.15 | 0.3
0.1398 | 278.15 | 0.09737 | 297.15 | 0.4
0.1398 | 278.15 | 0.09737 | 297.15 | 0.5
0.1398 | 278.15 | 0.09737 | 297.15 | 0.6
0.1398 | 278.15 | 0.09737 | 297.15 | 0.7
0.1398 | 278.15 | 0.09737 | 297.15 | 0.8
0.1398 | 278.15 | 0.09737 | 297.15 | 0.9
0.1398 | 278.15 | 0.09737 | 297.15 | 1
0.1398 | 278.15 | 0.09737 | 300.15 | 0.15
0.1398 | 278.15 | 0.09737 | 300.15 | 0.2
0.1398 | 278.15 | 0.09737 | 300.15 | 0.3
0.1398 | 278.15 | 0.09737 | 300.15 | 0.4
0.1398 | 278.15 | 0.09737 | 300.15 | 0.5
0.1398 | 278.15 | 0.09737 | 300.15 | 0.6
0.1398 | 278.15 | 0.09737 | 300.15 | 0.7
0.1398 | 278.15 | 0.09737 | 300.15 | 0.8
0.1398 | 278.15 | 0.09737 | 300.15 | 0.9
0.1398 | 278.15 | 0.09737 | 300.15 | 1
0.1398 | 278.15 | 0.09737 | 303.15 | 0.15
0.1398 | 278.15 | 0.09737 | 303.15 | 0.2
0.1398 | 278.15 | 0.09737 | 303.15 | 0.3
0.1398 | 278.15 | 0.09737 | 303.15 | 0.4
0.1398 | 278.15 | 0.09737 | 303.15 | 0.5
0.1398 | 278.15 | 0.09737 | 303.15 | 0.6
0.1398 | 278.15 | 0.09737 | 303.15 | 0.7
0.1398 | 278.15 | 0.09737 | 303.15 | 0.8
0.1398 | 278.15 | 0.09737 | 303.15 | 0.9
0.1398 | 278.15 | 0.09737 | 303.15 | 1
0.1398 | 278.15 | 0.115 | 283.65 | 0.15
0.1398 | 278.15 | 0.115 | 283.65 | 0.2
0.1398 | 278.15 | 0.115 | 283.65 | 0.3
0.1398 | 278.15 | 0.115 | 283.65 | 0.4
0.1398 | 278.15 | 0.115 | 283.65 | 0.5
0.1398 | 278.15 | 0.115 | 283.65 | 0.6
0.1398 | 278.15 | 0.115 | 283.65 | 0.7
0.1398 | 278.15 | 0.115 | 283.65 | 0.8
0.1398 | 278.15 | 0.115 | 283.65 | 0.9
0.1398 | 278.15 | 0.115 | 283.65 | 1
0.1398 | 278.15 | 0.115 | 284.15 | 0.15
0.1398 | 278.15 | 0.115 | 284.15 | 0.2
0.1398 | 278.15 | 0.115 | 284.15 | 0.3
0.1398 | 278.15 | 0.115 | 284.15 | 0.4
0.1398 | 278.15 | 0.115 | 284.15 | 0.5
0.1398 | 278.15 | 0.115 | 284.15 | 0.6
0.1398 | 278.15 | 0.115 | 284.15 | 0.7
0.1398 | 278.15 | 0.115 | 284.15 | 0.8
0.1398 | 278.15 | 0.115 | 284.15 | 0.9
0.1398 | 278.15 | 0.115 | 284.15 | 1
0.1398 | 278.15 | 0.115 | 284.65 | 0.15
0.1398 | 278.15 | 0.115 | 284.65 | 0.2
0.1398 | 278.15 | 0.115 | 284.65 | 0.3
0.1398 | 278.15 | 0.115 | 284.65 | 0.4
0.1398 | 278.15 | 0.115 | 284.65 | 0.5
0.1398 | 278.15 | 0.115 | 284.65 | 0.6
0.1398 | 278.15 | 0.115 | 284.65 | 0.7
0.1398 | 278.15 | 0.115 | 284.65 | 0.8
0.1398 | 278.15 | 0.115 | 284.65 | 0.9
0.1398 | 278.15 | 0.115 | 284.65 | 1
0.1398 | 278.15 | 0.115 | 285.15 | 0.15
0.1398 | 278.15 | 0.115 | 285.15 | 0.2
0.1398 | 278.15 | 0.115 | 285.15 | 0.3
0.1398 | 278.15 | 0.115 | 285.15 | 0.4
0.1398 | 278.15 | 0.115 | 285.15 | 0.5
0.1398 | 278.15 | 0.115 | 285.15 | 0.6
0.1398 | 278.15 | 0.115 | 285.15 | 0.7
0.1398 | 278.15 | 0.115 | 285.15 | 0.8
0.1398 | 278.15 | 0.115 | 285.15 | 0.9
0.1398 | 278.15 | 0.115 | 285.15 | 1
0.1398 | 278.15 | 0.115 | 285.65 | 0.15
0.1398 | 278.15 | 0.115 | 285.65 | 0.2
0.1398 | 278.15 | 0.115 | 285.65 | 0.3
0.1398 | 278.15 | 0.115 | 285.65 | 0.4
0.1398 | 278.15 | 0.115 | 285.65 | 0.5
0.1398 | 278.15 | 0.115 | 285.65 | 0.6
0.1398 | 278.15 | 0.115 | 285.65 | 0.7
0.1398 | 278.15 | 0.115 | 285.65 | 0.8
0.1398 | 278.15 | 0.115 | 285.65 | 0.9
0.1398 | 278.15 | 0.115 | 285.65 | 1
0.1398 | 278.15 | 0.115 | 286.15 | 0.15
0.1398 | 278.15 | 0.115 | 286.15 | 0.2
0.1398 | 278.15 | 0.115 | 286.15 | 0.3
0.1398 | 278.15 | 0.115 | 286.15 | 0.4
0.1398 | 278.15 | 0.115 | 286.15 | 0.5
0.1398 | 278.15 | 0.115 | 286.15 | 0.6
0.1398 | 278.15 | 0.115 | 286.15 | 0.7
0.1398 | 278.15 | 0.115 | 286.15 | 0.8
0.1398 | 278.15 | 0.115 | 286.15 | 0.9
0.1398 | 278.15 | 0.115 | 286.15 | 1
0.1398 | 278.15 | 0.115 | 286.65 | 0.15
0.1398 | 278.15 | 0.115 | 286.65 | 0.2
0.1398 | 278.15 | 0.115 | 286.65 | 0.3
0.1398 | 278.15 | 0.115 | 286.65 | 0.4
0.1398 | 278.15 | 0.115 | 286.65 | 0.5
0.1398 | 278.15 | 0.115 | 286.65 | 0.6
0.1398 | 278.15 | 0.115 | 286.65 | 0.7
0.1398 | 278.15 | 0.115 | 286.65 | 0.8
0.1398 | 278.15 | 0.115 | 286.65 | 0.9
0.1398 | 278.15 | 0.115 | 286.65 | 1
0.1398 | 278.15 | 0.115 | 287.15 | 0.15
0.1398 | 278.15 | 0.115 | 287.15 | 0.2
0.1398 | 278.15 | 0.115 | 287.15 | 0.3
0.1398 | 278.15 | 0.115 | 287.15 | 0.4
0.1398 | 278.15 | 0.115 | 287.15 | 0.5
0.1398 | 278.15 | 0.115 | 287.15 | 0.6
0.1398 | 278.15 | 0.115 | 287.15 | 0.7
0.1398 | 278.15 | 0.115 | 287.15 | 0.8
0.1398 | 278.15 | 0.115 | 287.15 | 0.9
0.1398 | 278.15 | 0.115 | 287.15 | 1
0.1398 | 278.15 | 0.115 | 287.65 | 0.15
0.1398 | 278.15 | 0.115 | 287.65 | 0.2
0.1398 | 278.15 | 0.115 | 287.65 | 0.3
0.1398 | 278.15 | 0.115 | 287.65 | 0.4
0.1398 | 278.15 | 0.115 | 287.65 | 0.5
0.1398 | 278.15 | 0.115 | 287.65 | 0.6
0.1398 | 278.15 | 0.115 | 287.65 | 0.7
0.1398 | 278.15 | 0.115 | 287.65 | 0.8
0.1398 | 278.15 | 0.115 | 287.65 | 0.9
0.1398 | 278.15 | 0.115 | 287.65 | 1
0.1398 | 278.15 | 0.115 | 288.15 | 0.15
0.1398 | 278.15 | 0.115 | 288.15 | 0.2
0.1398 | 278.15 | 0.115 | 288.15 | 0.3
0.1398 | 278.15 | 0.115 | 288.15 | 0.4
0.1398 | 278.15 | 0.115 | 288.15 | 0.5
0.1398 | 278.15 | 0.115 | 288.15 | 0.6
0.1398 | 278.15 | 0.115 | 288.15 | 0.7
0.1398 | 278.15 | 0.115 | 288.15 | 0.8
0.1398 | 278.15 | 0.115 | 288.15 | 0.9
0.1398 | 278.15 | 0.115 | 288.15 | 1
0.1398 | 278.15 | 0.115 | 288.65 | 0.15
0.1398 | 278.15 | 0.115 | 288.65 | 0.2
0.1398 | 278.15 | 0.115 | 288.65 | 0.3
0.1398 | 278.15 | 0.115 | 288.65 | 0.4
0.1398 | 278.15 | 0.115 | 288.65 | 0.5
0.1398 | 278.15 | 0.115 | 288.65 | 0.6
0.1398 | 278.15 | 0.115 | 288.65 | 0.7
0.1398 | 278.15 | 0.115 | 288.65 | 0.8
0.1398 | 278.15 | 0.115 | 288.65 | 0.9
0.1398 | 278.15 | 0.115 | 288.65 | 1
0.1398 | 278.15 | 0.115 | 289.15 | 0.15
0.1398 | 278.15 | 0.115 | 289.15 | 0.2
0.1398 | 278.15 | 0.115 | 289.15 | 0.3
0.1398 | 278.15 | 0.115 | 289.15 | 0.4
0.1398 | 278.15 | 0.115 | 289.15 | 0.5
0.1398 | 278.15 | 0.115 | 289.15 | 0.6
0.1398 | 278.15 | 0.115 | 289.15 | 0.7
0.1398 | 278.15 | 0.115 | 289.15 | 0.8
0.1398 | 278.15 | 0.115 | 289.15 | 0.9
0.1398 | 278.15 | 0.115 | 289.15 | 1
0.1398 | 278.15 | 0.115 | 289.65 | 0.15
0.1398 | 278.15 | 0.115 | 289.65 | 0.2
0.1398 | 278.15 | 0.115 | 289.65 | 0.3
0.1398 | 278.15 | 0.115 | 289.65 | 0.4
0.1398 | 278.15 | 0.115 | 289.65 | 0.5
0.1398 | 278.15 | 0.115 | 289.65 | 0.6
0.1398 | 278.15 | 0.115 | 289.65 | 0.7
0.1398 | 278.15 | 0.115 | 289.65 | 0.8
0.1398 | 278.15 | 0.115 | 289.65 | 0.9
0.1398 | 278.15 | 0.115 | 289.65 | 1
0.1398 | 278.15 | 0.115 | 290.15 | 0.15
0.1398 | 278.15 | 0.115 | 290.15 | 0.2
0.1398 | 278.15 | 0.115 | 290.15 | 0.3
0.1398 | 278.15 | 0.115 | 290.15 | 0.4
0.1398 | 278.15 | 0.115 | 290.15 | 0.5
0.1398 | 278.15 | 0.115 | 290.15 | 0.6
0.1398 | 278.15 | 0.115 | 290.15 | 0.7
0.1398 | 278.15 | 0.115 | 290.15 | 0.8
0.1398 | 278.15 | 0.115 | 290.15 | 0.9
0.1398 | 278.15 | 0.115 | 290.15 | 1
0.1398 | 278.15 | 0.115 | 290.65 | 0.15
0.1398 | 278.15 | 0.115 | 290.65 | 0.2
0.1398 | 278.15 | 0.115 | 290.65 | 0.3
0.1398 | 278.15 | 0.115 | 290.65 | 0.4
0.1398 | 278.15 | 0.115 | 290.65 | 0.5
0.1398 | 278.15 | 0.115 | 290.65 | 0.6
0.1398 | 278.15 | 0.115 | 290.65 | 0.7
0.1398 | 278.15 | 0.115 | 290.65 | 0.8
0.1398 | 278.15 | 0.115 | 290.65 | 0.9
0.1398 | 278.15 | 0.115 | 290.65 | 1
0.1398 | 278.15 | 0.115 | 291.15 | 0.15
0.1398 | 278.15 | 0.115 | 291.15 | 0.2
0.1398 | 278.15 | 0.115 | 291.15 | 0.3
0.1398 | 278.15 | 0.115 | 291.15 | 0.4
0.1398 | 278.15 | 0.115 | 291.15 | 0.5
0.1398 | 278.15 | 0.115 | 291.15 | 0.6
0.1398 | 278.15 | 0.115 | 291.15 | 0.7
0.1398 | 278.15 | 0.115 | 291.15 | 0.8
0.1398 | 278.15 | 0.115 | 291.15 | 0.9
0.1398 | 278.15 | 0.115 | 291.15 | 1
0.1398 | 278.15 | 0.115 | 294.15 | 0.15
0.1398 | 278.15 | 0.115 | 294.15 | 0.2
0.1398 | 278.15 | 0.115 | 294.15 | 0.3
0.1398 | 278.15 | 0.115 | 294.15 | 0.4
0.1398 | 278.15 | 0.115 | 294.15 | 0.5
0.1398 | 278.15 | 0.115 | 294.15 | 0.6
0.1398 | 278.15 | 0.115 | 294.15 | 0.7
0.1398 | 278.15 | 0.115 | 294.15 | 0.8
0.1398 | 278.15 | 0.115 | 294.15 | 0.9
0.1398 | 278.15 | 0.115 | 294.15 | 1
0.1398 | 278.15 | 0.115 | 297.15 | 0.15
0.1398 | 278.15 | 0.115 | 297.15 | 0.2
0.1398 | 278.15 | 0.115 | 297.15 | 0.3
0.1398 | 278.15 | 0.115 | 297.15 | 0.4
0.1398 | 278.15 | 0.115 | 297.15 | 0.5
0.1398 | 278.15 | 0.115 | 297.15 | 0.6
0.1398 | 278.15 | 0.115 | 297.15 | 0.7
0.1398 | 278.15 | 0.115 | 297.15 | 0.8
0.1398 | 278.15 | 0.115 | 297.15 | 0.9
0.1398 | 278.15 | 0.115 | 297.15 | 1
0.1398 | 278.15 | 0.115 | 300.15 | 0.15
0.1398 | 278.15 | 0.115 | 300.15 | 0.2
0.1398 | 278.15 | 0.115 | 300.15 | 0.3
0.1398 | 278.15 | 0.115 | 300.15 | 0.4
0.1398 | 278.15 | 0.115 | 300.15 | 0.5
0.1398 | 278.15 | 0.115 | 300.15 | 0.6
0.1398 | 278.15 | 0.115 | 300.15 | 0.7
0.1398 | 278.15 | 0.115 | 300.15 | 0.8
0.1398 | 278.15 | 0.115 | 300.15 | 0.9
0.1398 | 278.15 | 0.115 | 300.15 | 1
0.1398 | 278.15 | 0.115 | 303.15 | 0.15
0.1398 | 278.15 | 0.115 | 303.15 | 0.2
0.1398 | 278.15 | 0.115 | 303.15 | 0.3
0.1398 | 278.15 | 0.115 | 303.15 | 0.4
0.1398 | 278.15 | 0.115 | 303.15 | 0.5
0.1398 | 278.15 | 0.115 | 303.15 | 0.6
0.1398 | 278.15 | 0.115 | 303.15 | 0.7
0.1398 | 278.15 | 0.115 | 303.15 | 0.8
0.1398 | 278.15 | 0.115 | 303.15 | 0.9
0.1398 | 278.15 | 0.115 | 303.15 | 1
0.1398 | 280.15 | 0.00115 | 283.65 | 0.15
0.1398 | 280.15 | 0.00115 | 283.65 | 0.2
0.1398 | 280.15 | 0.00115 | 283.65 | 0.3
0.1398 | 280.15 | 0.00115 | 283.65 | 0.4
0.1398 | 280.15 | 0.00115 | 283.65 | 0.5
0.1398 | 280.15 | 0.00115 | 283.65 | 0.6
0.1398 | 280.15 | 0.00115 | 283.65 | 0.7
0.1398 | 280.15 | 0.00115 | 283.65 | 0.8
0.1398 | 280.15 | 0.00115 | 283.65 | 0.9
0.1398 | 280.15 | 0.00115 | 283.65 | 1
0.1398 | 280.15 | 0.00115 | 284.15 | 0.15
0.1398 | 280.15 | 0.00115 | 284.15 | 0.2
0.1398 | 280.15 | 0.00115 | 284.15 | 0.3
0.1398 | 280.15 | 0.00115 | 284.15 | 0.4
0.1398 | 280.15 | 0.00115 | 284.15 | 0.5
0.1398 | 280.15 | 0.00115 | 284.15 | 0.6
0.1398 | 280.15 | 0.00115 | 284.15 | 0.7
0.1398 | 280.15 | 0.00115 | 284.15 | 0.8
0.1398 | 280.15 | 0.00115 | 284.15 | 0.9
0.1398 | 280.15 | 0.00115 | 284.15 | 1
0.1398 | 280.15 | 0.00115 | 284.65 | 0.15
0.1398 | 280.15 | 0.00115 | 284.65 | 0.2
0.1398 | 280.15 | 0.00115 | 284.65 | 0.3
0.1398 | 280.15 | 0.00115 | 284.65 | 0.4
0.1398 | 280.15 | 0.00115 | 284.65 | 0.5
0.1398 | 280.15 | 0.00115 | 284.65 | 0.6
0.1398 | 280.15 | 0.00115 | 284.65 | 0.7
0.1398 | 280.15 | 0.00115 | 284.65 | 0.8
0.1398 | 280.15 | 0.00115 | 284.65 | 0.9
0.1398 | 280.15 | 0.00115 | 284.65 | 1
0.1398 | 280.15 | 0.00115 | 285.15 | 0.15
0.1398 | 280.15 | 0.00115 | 285.15 | 0.2
0.1398 | 280.15 | 0.00115 | 285.15 | 0.3
0.1398 | 280.15 | 0.00115 | 285.15 | 0.4
0.1398 | 280.15 | 0.00115 | 285.15 | 0.5
0.1398 | 280.15 | 0.00115 | 285.15 | 0.6
0.1398 | 280.15 | 0.00115 | 285.15 | 0.7
0.1398 | 280.15 | 0.00115 | 285.15 | 0.8
0.1398 | 280.15 | 0.00115 | 285.15 | 0.9
0.1398 | 280.15 | 0.00115 | 285.15 | 1
0.1398 | 280.15 | 0.00115 | 285.65 | 0.15
0.1398 | 280.15 | 0.00115 | 285.65 | 0.2
0.1398 | 280.15 | 0.00115 | 285.65 | 0.3
0.1398 | 280.15 | 0.00115 | 285.65 | 0.4
0.1398 | 280.15 | 0.00115 | 285.65 | 0.5
0.1398 | 280.15 | 0.00115 | 285.65 | 0.6
0.1398 | 280.15 | 0.00115 | 285.65 | 0.7
0.1398 | 280.15 | 0.00115 | 285.65 | 0.8
0.1398 | 280.15 | 0.00115 | 285.65 | 0.9
0.1398 | 280.15 | 0.00115 | 285.65 | 1
0.1398 | 280.15 | 0.00115 | 286.15 | 0.15
0.1398 | 280.15 | 0.00115 | 286.15 | 0.2
0.1398 | 280.15 | 0.00115 | 286.15 | 0.3
0.1398 | 280.15 | 0.00115 | 286.15 | 0.4
0.1398 | 280.15 | 0.00115 | 286.15 | 0.5
0.1398 | 280.15 | 0.00115 | 286.15 | 0.6
0.1398 | 280.15 | 0.00115 | 286.15 | 0.7
0.1398 | 280.15 | 0.00115 | 286.15 | 0.8
0.1398 | 280.15 | 0.00115 | 286.15 | 0.9
0.1398 | 280.15 | 0.00115 | 286.15 | 1
0.1398 | 280.15 | 0.00115 | 286.65 | 0.15
0.1398 | 280.15 | 0.00115 | 286.65 | 0.2
0.1398 | 280.15 | 0.00115 | 286.65 | 0.3
0.1398 | 280.15 | 0.00115 | 286.65 | 0.4
0.1398 | 280.15 | 0.00115 | 286.65 | 0.5
0.1398 | 280.15 | 0.00115 | 286.65 | 0.6
0.1398 | 280.15 | 0.00115 | 286.65 | 0.7
0.1398 | 280.15 | 0.00115 | 286.65 | 0.8
0.1398 | 280.15 | 0.00115 | 286.65 | 0.9
0.1398 | 280.15 | 0.00115 | 286.65 | 1
0.1398 | 280.15 | 0.00115 | 287.15 | 0.15
0.1398 | 280.15 | 0.00115 | 287.15 | 0.2
0.1398 | 280.15 | 0.00115 | 287.15 | 0.3
0.1398 | 280.15 | 0.00115 | 287.15 | 0.4
0.1398 | 280.15 | 0.00115 | 287.15 | 0.5
0.1398 | 280.15 | 0.00115 | 287.15 | 0.6
0.1398 | 280.15 | 0.00115 | 287.15 | 0.7
0.1398 | 280.15 | 0.00115 | 287.15 | 0.8
0.1398 | 280.15 | 0.00115 | 287.15 | 0.9
0.1398 | 280.15 | 0.00115 | 287.15 | 1
0.1398 | 280.15 | 0.00115 | 287.65 | 0.15
0.1398 | 280.15 | 0.00115 | 287.65 | 0.2
0.1398 | 280.15 | 0.00115 | 287.65 | 0.3
0.1398 | 280.15 | 0.00115 | 287.65 | 0.4
0.1398 | 280.15 | 0.00115 | 287.65 | 0.5
0.1398 | 280.15 | 0.00115 | 287.65 | 0.6
0.1398 | 280.15 | 0.00115 | 287.65 | 0.7
0.1398 | 280.15 | 0.00115 | 287.65 | 0.8
0.1398 | 280.15 | 0.00115 | 287.65 | 0.9
0.1398 | 280.15 | 0.00115 | 287.65 | 1
0.1398 | 280.15 | 0.00115 | 288.15 | 0.15
0.1398 | 280.15 | 0.00115 | 288.15 | 0.2
0.1398 | 280.15 | 0.00115 | 288.15 | 0.3
0.1398 | 280.15 | 0.00115 | 288.15 | 0.4
0.1398 | 280.15 | 0.00115 | 288.15 | 0.5
0.1398 | 280.15 | 0.00115 | 288.15 | 0.6
0.1398 | 280.15 | 0.00115 | 288.15 | 0.7
0.1398 | 280.15 | 0.00115 | 288.15 | 0.8
0.1398 | 280.15 | 0.00115 | 288.15 | 0.9
0.1398 | 280.15 | 0.00115 | 288.15 | 1
0.1398 | 280.15 | 0.00115 | 288.65 | 0.15
0.1398 | 280.15 | 0.00115 | 288.65 | 0.2
0.1398 | 280.15 | 0.00115 | 288.65 | 0.3
0.1398 | 280.15 | 0.00115 | 288.65 | 0.4
0.1398 | 280.15 | 0.00115 | 288.65 | 0.5
0.1398 | 280.15 | 0.00115 | 288.65 | 0.6
0.1398 | 280.15 | 0.00115 | 288.65 | 0.7
0.1398 | 280.15 | 0.00115 | 288.65 | 0.8
0.1398 | 280.15 | 0.00115 | 288.65 | 0.9
0.1398 | 280.15 | 0.00115 | 288.65 | 1
0.1398 | 280.15 | 0.00115 | 289.15 | 0.15
0.1398 | 280.15 | 0.00115 | 289.15 | 0.2
0.1398 | 280.15 | 0.00115 | 289.15 | 0.3
0.1398 | 280.15 | 0.00115 | 289.15 | 0.4
0.1398 | 280.15 | 0.00115 | 289.15 | 0.5
0.1398 | 280.15 | 0.00115 | 289.15 | 0.6
0.1398 | 280.15 | 0.00115 | 289.15 | 0.7
0.1398 | 280.15 | 0.00115 | 289.15 | 0.8
0.1398 | 280.15 | 0.00115 | 289.15 | 0.9
0.1398 | 280.15 | 0.00115 | 289.15 | 1
0.1398 | 280.15 | 0.00115 | 289.65 | 0.15
0.1398 | 280.15 | 0.00115 | 289.65 | 0.2
0.1398 | 280.15 | 0.00115 | 289.65 | 0.3
0.1398 | 280.15 | 0.00115 | 289.65 | 0.4
0.1398 | 280.15 | 0.00115 | 289.65 | 0.5
0.1398 | 280.15 | 0.00115 | 289.65 | 0.6
0.1398 | 280.15 | 0.00115 | 289.65 | 0.7
0.1398 | 280.15 | 0.00115 | 289.65 | 0.8
0.1398 | 280.15 | 0.00115 | 289.65 | 0.9
0.1398 | 280.15 | 0.00115 | 289.65 | 1
0.1398 | 280.15 | 0.00115 | 290.15 | 0.15
0.1398 | 280.15 | 0.00115 | 290.15 | 0.2
0.1398 | 280.15 | 0.00115 | 290.15 | 0.3
0.1398 | 280.15 | 0.00115 | 290.15 | 0.4
0.1398 | 280.15 | 0.00115 | 290.15 | 0.5
0.1398 | 280.15 | 0.00115 | 290.15 | 0.6
0.1398 | 280.15 | 0.00115 | 290.15 | 0.7
0.1398 | 280.15 | 0.00115 | 290.15 | 0.8
0.1398 | 280.15 | 0.00115 | 290.15 | 0.9
0.1398 | 280.15 | 0.00115 | 290.15 | 1
0.1398 | 280.15 | 0.00115 | 290.65 | 0.15
0.1398 | 280.15 | 0.00115 | 290.65 | 0.2
0.1398 | 280.15 | 0.00115 | 290.65 | 0.3
0.1398 | 280.15 | 0.00115 | 290.65 | 0.4
0.1398 | 280.15 | 0.00115 | 290.65 | 0.5
0.1398 | 280.15 | 0.00115 | 290.65 | 0.6
0.1398 | 280.15 | 0.00115 | 290.65 | 0.7
0.1398 | 280.15 | 0.00115 | 290.65 | 0.8
0.1398 | 280.15 | 0.00115 | 290.65 | 0.9
0.1398 | 280.15 | 0.00115 | 290.65 | 1
0.1398 | 280.15 | 0.00115 | 291.15 | 0.15
0.1398 | 280.15 | 0.00115 | 291.15 | 0.2
0.1398 | 280.15 | 0.00115 | 291.15 | 0.3
0.1398 | 280.15 | 0.00115 | 291.15 | 0.4
0.1398 | 280.15 | 0.00115 | 291.15 | 0.5
0.1398 | 280.15 | 0.00115 | 291.15 | 0.6
0.1398 | 280.15 | 0.00115 | 291.15 | 0.7
0.1398 | 280.15 | 0.00115 | 291.15 | 0.8
0.1398 | 280.15 | 0.00115 | 291.15 | 0.9
0.1398 | 280.15 | 0.00115 | 291.15 | 1
0.1398 | 280.15 | 0.00115 | 294.15 | 0.15
0.1398 | 280.15 | 0.00115 | 294.15 | 0.2
0.1398 | 280.15 | 0.00115 | 294.15 | 0.3
0.1398 | 280.15 | 0.00115 | 294.15 | 0.4
0.1398 | 280.15 | 0.00115 | 294.15 | 0.5
0.1398 | 280.15 | 0.00115 | 294.15 | 0.6
0.1398 | 280.15 | 0.00115 | 294.15 | 0.7
0.1398 | 280.15 | 0.00115 | 294.15 | 0.8
0.1398 | 280.15 | 0.00115 | 294.15 | 0.9
0.1398 | 280.15 | 0.00115 | 294.15 | 1
0.1398 | 280.15 | 0.00115 | 297.15 | 0.15
0.1398 | 280.15 | 0.00115 | 297.15 | 0.2
0.1398 | 280.15 | 0.00115 | 297.15 | 0.3
0.1398 | 280.15 | 0.00115 | 297.15 | 0.4
0.1398 | 280.15 | 0.00115 | 297.15 | 0.5
0.1398 | 280.15 | 0.00115 | 297.15 | 0.6
0.1398 | 280.15 | 0.00115 | 297.15 | 0.7
0.1398 | 280.15 | 0.00115 | 297.15 | 0.8
0.1398 | 280.15 | 0.00115 | 297.15 | 0.9
0.1398 | 280.15 | 0.00115 | 297.15 | 1
0.1398 | 280.15 | 0.00115 | 300.15 | 0.15
0.1398 | 280.15 | 0.00115 | 300.15 | 0.2
0.1398 | 280.15 | 0.00115 | 300.15 | 0.3
0.1398 | 280.15 | 0.00115 | 300.15 | 0.4
0.1398 | 280.15 | 0.00115 | 300.15 | 0.5
0.1398 | 280.15 | 0.00115 | 300.15 | 0.6
0.1398 | 280.15 | 0.00115 | 300.15 | 0.7
0.1398 | 280.15 | 0.00115 | 300.15 | 0.8
0.1398 | 280.15 | 0.00115 | 300.15 | 0.9
0.1398 | 280.15 | 0.00115 | 300.15 | 1
0.1398 | 280.15 | 0.00115 | 303.15 | 0.15
0.1398 | 280.15 | 0.00115 | 303.15 | 0.2
0.1398 | 280.15 | 0.00115 | 303.15 | 0.3
0.1398 | 280.15 | 0.00115 | 303.15 | 0.4
0.1398 | 280.15 | 0.00115 | 303.15 | 0.5
0.1398 | 280.15 | 0.00115 | 303.15 | 0.6
0.1398 | 280.15 | 0.00115 | 303.15 | 0.7
0.1398 | 280.15 | 0.00115 | 303.15 | 0.8
0.1398 | 280.15 | 0.00115 | 303.15 | 0.9
0.1398 | 280.15 | 0.00115 | 303.15 | 1
0.1398 | 280.15 | 0.077 | 283.65 | 0.15
0.1398 | 280.15 | 0.077 | 283.65 | 0.2
0.1398 | 280.15 | 0.077 | 283.65 | 0.3
0.1398 | 280.15 | 0.077 | 283.65 | 0.4
0.1398 | 280.15 | 0.077 | 283.65 | 0.5
0.1398 | 280.15 | 0.077 | 283.65 | 0.6
0.1398 | 280.15 | 0.077 | 283.65 | 0.7
0.1398 | 280.15 | 0.077 | 283.65 | 0.8
0.1398 | 280.15 | 0.077 | 283.65 | 0.9
0.1398 | 280.15 | 0.077 | 283.65 | 1
0.1398 | 280.15 | 0.077 | 284.15 | 0.15
0.1398 | 280.15 | 0.077 | 284.15 | 0.2
0.1398 | 280.15 | 0.077 | 284.15 | 0.3
0.1398 | 280.15 | 0.077 | 284.15 | 0.4
0.1398 | 280.15 | 0.077 | 284.15 | 0.5
0.1398 | 280.15 | 0.077 | 284.15 | 0.6
0.1398 | 280.15 | 0.077 | 284.15 | 0.7
0.1398 | 280.15 | 0.077 | 284.15 | 0.8
0.1398 | 280.15 | 0.077 | 284.15 | 0.9
0.1398 | 280.15 | 0.077 | 284.15 | 1
0.1398 | 280.15 | 0.077 | 284.65 | 0.15
0.1398 | 280.15 | 0.077 | 284.65 | 0.2
0.1398 | 280.15 | 0.077 | 284.65 | 0.3
0.1398 | 280.15 | 0.077 | 284.65 | 0.4
0.1398 | 280.15 | 0.077 | 284.65 | 0.5
0.1398 | 280.15 | 0.077 | 284.65 | 0.6
0.1398 | 280.15 | 0.077 | 284.65 | 0.7
0.1398 | 280.15 | 0.077 | 284.65 | 0.8
0.1398 | 280.15 | 0.077 | 284.65 | 0.9
0.1398 | 280.15 | 0.077 | 284.65 | 1
0.1398 | 280.15 | 0.077 | 285.15 | 0.15
0.1398 | 280.15 | 0.077 | 285.15 | 0.2
0.1398 | 280.15 | 0.077 | 285.15 | 0.3
0.1398 | 280.15 | 0.077 | 285.15 | 0.4
0.1398 | 280.15 | 0.077 | 285.15 | 0.5
0.1398 | 280.15 | 0.077 | 285.15 | 0.6
0.1398 | 280.15 | 0.077 | 285.15 | 0.7
0.1398 | 280.15 | 0.077 | 285.15 | 0.8
0.1398 | 280.15 | 0.077 | 285.15 | 0.9
0.1398 | 280.15 | 0.077 | 285.15 | 1
0.1398 | 280.15 | 0.077 | 285.65 | 0.15
0.1398 | 280.15 | 0.077 | 285.65 | 0.2
0.1398 | 280.15 | 0.077 | 285.65 | 0.3
0.1398 | 280.15 | 0.077 | 285.65 | 0.4
0.1398 | 280.15 | 0.077 | 285.65 | 0.5
0.1398 | 280.15 | 0.077 | 285.65 | 0.6
0.1398 | 280.15 | 0.077 | 285.65 | 0.7
0.1398 | 280.15 | 0.077 | 285.65 | 0.8
0.1398 | 280.15 | 0.077 | 285.65 | 0.9
0.1398 | 280.15 | 0.077 | 285.65 | 1
0.1398 | 280.15 | 0.077 | 286.15 | 0.15
0.1398 | 280.15 | 0.077 | 286.15 | 0.2
0.1398 | 280.15 | 0.077 | 286.15 | 0.3
0.1398 | 280.15 | 0.077 | 286.15 | 0.4
0.1398 | 280.15 | 0.077 | 286.15 | 0.5
0.1398 | 280.15 | 0.077 | 286.15 | 0.6
0.1398 | 280.15 | 0.077 | 286.15 | 0.7
0.1398 | 280.15 | 0.077 | 286.15 | 0.8
0.1398 | 280.15 | 0.077 | 286.15 | 0.9
0.1398 | 280.15 | 0.077 | 286.15 | 1
0.1398 | 280.15 | 0.077 | 286.65 | 0.15
0.1398 | 280.15 | 0.077 | 286.65 | 0.2
0.1398 | 280.15 | 0.077 | 286.65 | 0.3
0.1398 | 280.15 | 0.077 | 286.65 | 0.4
0.1398 | 280.15 | 0.077 | 286.65 | 0.5
0.1398 | 280.15 | 0.077 | 286.65 | 0.6
0.1398 | 280.15 | 0.077 | 286.65 | 0.7
0.1398 | 280.15 | 0.077 | 286.65 | 0.8
0.1398 | 280.15 | 0.077 | 286.65 | 0.9
0.1398 | 280.15 | 0.077 | 286.65 | 1
0.1398 | 280.15 | 0.077 | 287.15 | 0.15
0.1398 | 280.15 | 0.077 | 287.15 | 0.2
0.1398 | 280.15 | 0.077 | 287.15 | 0.3
0.1398 | 280.15 | 0.077 | 287.15 | 0.4
0.1398 | 280.15 | 0.077 | 287.15 | 0.5
0.1398 | 280.15 | 0.077 | 287.15 | 0.6
0.1398 | 280.15 | 0.077 | 287.15 | 0.7
0.1398 | 280.15 | 0.077 | 287.15 | 0.8
0.1398 | 280.15 | 0.077 | 287.15 | 0.9
0.1398 | 280.15 | 0.077 | 287.15 | 1
0.1398 | 280.15 | 0.077 | 287.65 | 0.15
0.1398 | 280.15 | 0.077 | 287.65 | 0.2
0.1398 | 280.15 | 0.077 | 287.65 | 0.3
0.1398 | 280.15 | 0.077 | 287.65 | 0.4
0.1398 | 280.15 | 0.077 | 287.65 | 0.5
0.1398 | 280.15 | 0.077 | 287.65 | 0.6
0.1398 | 280.15 | 0.077 | 287.65 | 0.7
0.1398 | 280.15 | 0.077 | 287.65 | 0.8
0.1398 | 280.15 | 0.077 | 287.65 | 0.9
0.1398 | 280.15 | 0.077 | 287.65 | 1
0.1398 | 280.15 | 0.077 | 288.15 | 0.15
0.1398 | 280.15 | 0.077 | 288.15 | 0.2
0.1398 | 280.15 | 0.077 | 288.15 | 0.3
0.1398 | 280.15 | 0.077 | 288.15 | 0.4
0.1398 | 280.15 | 0.077 | 288.15 | 0.5
0.1398 | 280.15 | 0.077 | 288.15 | 0.6
0.1398 | 280.15 | 0.077 | 288.15 | 0.7
0.1398 | 280.15 | 0.077 | 288.15 | 0.8
0.1398 | 280.15 | 0.077 | 288.15 | 0.9
0.1398 | 280.15 | 0.077 | 288.15 | 1
0.1398 | 280.15 | 0.077 | 288.65 | 0.15
0.1398 | 280.15 | 0.077 | 288.65 | 0.2
0.1398 | 280.15 | 0.077 | 288.65 | 0.3
0.1398 | 280.15 | 0.077 | 288.65 | 0.4
0.1398 | 280.15 | 0.077 | 288.65 | 0.5
0.1398 | 280.15 | 0.077 | 288.65 | 0.6
0.1398 | 280.15 | 0.077 | 288.65 | 0.7
0.1398 | 280.15 | 0.077 | 288.65 | 0.8
0.1398 | 280.15 | 0.077 | 288.65 | 0.9
0.1398 | 280.15 | 0.077 | 288.65 | 1
0.1398 | 280.15 | 0.077 | 289.15 | 0.15
0.1398 | 280.15 | 0.077 | 289.15 | 0.2
0.1398 | 280.15 | 0.077 | 289.15 | 0.3
0.1398 | 280.15 | 0.077 | 289.15 | 0.4
0.1398 | 280.15 | 0.077 | 289.15 | 0.5
0.1398 | 280.15 | 0.077 | 289.15 | 0.6
0.1398 | 280.15 | 0.077 | 289.15 | 0.7
0.1398 | 280.15 | 0.077 | 289.15 | 0.8
0.1398 | 280.15 | 0.077 | 289.15 | 0.9
0.1398 | 280.15 | 0.077 | 289.15 | 1
0.1398 | 280.15 | 0.077 | 289.65 | 0.15
0.1398 | 280.15 | 0.077 | 289.65 | 0.2
0.1398 | 280.15 | 0.077 | 289.65 | 0.3
0.1398 | 280.15 | 0.077 | 289.65 | 0.4
0.1398 | 280.15 | 0.077 | 289.65 | 0.5
0.1398 | 280.15 | 0.077 | 289.65 | 0.6
0.1398 | 280.15 | 0.077 | 289.65 | 0.7
0.1398 | 280.15 | 0.077 | 289.65 | 0.8
0.1398 | 280.15 | 0.077 | 289.65 | 0.9
0.1398 | 280.15 | 0.077 | 289.65 | 1
0.1398 | 280.15 | 0.077 | 290.15 | 0.15
0.1398 | 280.15 | 0.077 | 290.15 | 0.2
0.1398 | 280.15 | 0.077 | 290.15 | 0.3
0.1398 | 280.15 | 0.077 | 290.15 | 0.4
0.1398 | 280.15 | 0.077 | 290.15 | 0.5
0.1398 | 280.15 | 0.077 | 290.15 | 0.6
0.1398 | 280.15 | 0.077 | 290.15 | 0.7
0.1398 | 280.15 | 0.077 | 290.15 | 0.8
0.1398 | 280.15 | 0.077 | 290.15 | 0.9
0.1398 | 280.15 | 0.077 | 290.15 | 1
0.1398 | 280.15 | 0.077 | 290.65 | 0.15
0.1398 | 280.15 | 0.077 | 290.65 | 0.2
0.1398 | 280.15 | 0.077 | 290.65 | 0.3
0.1398 | 280.15 | 0.077 | 290.65 | 0.4
0.1398 | 280.15 | 0.077 | 290.65 | 0.5
0.1398 | 280.15 | 0.077 | 290.65 | 0.6
0.1398 | 280.15 | 0.077 | 290.65 | 0.7
0.1398 | 280.15 | 0.077 | 290.65 | 0.8
0.1398 | 280.15 | 0.077 | 290.65 | 0.9
0.1398 | 280.15 | 0.077 | 290.65 | 1
0.1398 | 280.15 | 0.077 | 291.15 | 0.15
0.1398 | 280.15 | 0.077 | 291.15 | 0.2
0.1398 | 280.15 | 0.077 | 291.15 | 0.3
0.1398 | 280.15 | 0.077 | 291.15 | 0.4
0.1398 | 280.15 | 0.077 | 291.15 | 0.5
0.1398 | 280.15 | 0.077 | 291.15 | 0.6
0.1398 | 280.15 | 0.077 | 291.15 | 0.7
0.1398 | 280.15 | 0.077 | 291.15 | 0.8
0.1398 | 280.15 | 0.077 | 291.15 | 0.9
0.1398 | 280.15 | 0.077 | 291.15 | 1
0.1398 | 280.15 | 0.077 | 294.15 | 0.15
0.1398 | 280.15 | 0.077 | 294.15 | 0.2
0.1398 | 280.15 | 0.077 | 294.15 | 0.3
0.1398 | 280.15 | 0.077 | 294.15 | 0.4
0.1398 | 280.15 | 0.077 | 294.15 | 0.5
0.1398 | 280.15 | 0.077 | 294.15 | 0.6
0.1398 | 280.15 | 0.077 | 294.15 | 0.7
0.1398 | 280.15 | 0.077 | 294.15 | 0.8
0.1398 | 280.15 | 0.077 | 294.15 | 0.9
0.1398 | 280.15 | 0.077 | 294.15 | 1
0.1398 | 280.15 | 0.077 | 297.15 | 0.15
0.1398 | 280.15 | 0.077 | 297.15 | 0.2
0.1398 | 280.15 | 0.077 | 297.15 | 0.3
0.1398 | 280.15 | 0.077 | 297.15 | 0.4
0.1398 | 280.15 | 0.077 | 297.15 | 0.5
0.1398 | 280.15 | 0.077 | 297.15 | 0.6
0.1398 | 280.15 | 0.077 | 297.15 | 0.7
0.1398 | 280.15 | 0.077 | 297.15 | 0.8
0.1398 | 280.15 | 0.077 | 297.15 | 0.9
0.1398 | 280.15 | 0.077 | 297.15 | 1
0.1398 | 280.15 | 0.077 | 300.15 | 0.15
0.1398 | 280.15 | 0.077 | 300.15 | 0.2
0.1398 | 280.15 | 0.077 | 300.15 | 0.3
0.1398 | 280.15 | 0.077 | 300.15 | 0.4
0.1398 | 280.15 | 0.077 | 300.15 | 0.5
0.1398 | 280.15 | 0.077 | 300.15 | 0.6
0.1398 | 280.15 | 0.077 | 300.15 | 0.7
0.1398 | 280.15 | 0.077 | 300.15 | 0.8
0.1398 | 280.15 | 0.077 | 300.15 | 0.9
0.1398 | 280.15 | 0.077 | 300.15 | 1
0.1398 | 280.15 | 0.077 | 303.15 | 0.15
0.1398 | 280.15 | 0.077 | 303.15 | 0.2
0.1398 | 280.15 | 0.077 | 303.15 | 0.3
0.1398 | 280.15 | 0.077 | 303.15 | 0.4
0.1398 | 280.15 | 0.077 | 303.15 | 0.5
0.1398 | 280.15 | 0.077 | 303.15 | 0.6
0.1398 | 280.15 | 0.077 | 303.15 | 0.7
0.1398 | 280.15 | 0.077 | 303.15 | 0.8
0.1398 | 280.15 | 0.077 | 303.15 | 0.9
0.1398 | 280.15 | 0.077 | 303.15 | 1
0.1398 | 280.15 | 0.09437 | 283.65 | 0.15
0.1398 | 280.15 | 0.09437 | 283.65 | 0.2
0.1398 | 280.15 | 0.09437 | 283.65 | 0.3
0.1398 | 280.15 | 0.09437 | 283.65 | 0.4
0.1398 | 280.15 | 0.09437 | 283.65 | 0.5
0.1398 | 280.15 | 0.09437 | 283.65 | 0.6
0.1398 | 280.15 | 0.09437 | 283.65 | 0.7
0.1398 | 280.15 | 0.09437 | 283.65 | 0.8
0.1398 | 280.15 | 0.09437 | 283.65 | 0.9
0.1398 | 280.15 | 0.09437 | 283.65 | 1
0.1398 | 280.15 | 0.09437 | 284.15 | 0.15
0.1398 | 280.15 | 0.09437 | 284.15 | 0.2
0.1398 | 280.15 | 0.09437 | 284.15 | 0.3
0.1398 | 280.15 | 0.09437 | 284.15 | 0.4
0.1398 | 280.15 | 0.09437 | 284.15 | 0.5
0.1398 | 280.15 | 0.09437 | 284.15 | 0.6
0.1398 | 280.15 | 0.09437 | 284.15 | 0.7
0.1398 | 280.15 | 0.09437 | 284.15 | 0.8
0.1398 | 280.15 | 0.09437 | 284.15 | 0.9
0.1398 | 280.15 | 0.09437 | 284.15 | 1
0.1398 | 280.15 | 0.09437 | 284.65 | 0.15
0.1398 | 280.15 | 0.09437 | 284.65 | 0.2
0.1398 | 280.15 | 0.09437 | 284.65 | 0.3
0.1398 | 280.15 | 0.09437 | 284.65 | 0.4
0.1398 | 280.15 | 0.09437 | 284.65 | 0.5
0.1398 | 280.15 | 0.09437 | 284.65 | 0.6
0.1398 | 280.15 | 0.09437 | 284.65 | 0.7
0.1398 | 280.15 | 0.09437 | 284.65 | 0.8
0.1398 | 280.15 | 0.09437 | 284.65 | 0.9
0.1398 | 280.15 | 0.09437 | 284.65 | 1
0.1398 | 280.15 | 0.09437 | 285.15 | 0.15
0.1398 | 280.15 | 0.09437 | 285.15 | 0.2
0.1398 | 280.15 | 0.09437 | 285.15 | 0.3
0.1398 | 280.15 | 0.09437 | 285.15 | 0.4
0.1398 | 280.15 | 0.09437 | 285.15 | 0.5
0.1398 | 280.15 | 0.09437 | 285.15 | 0.6
0.1398 | 280.15 | 0.09437 | 285.15 | 0.7
0.1398 | 280.15 | 0.09437 | 285.15 | 0.8
0.1398 | 280.15 | 0.09437 | 285.15 | 0.9
0.1398 | 280.15 | 0.09437 | 285.15 | 1
0.1398 | 280.15 | 0.09437 | 285.65 | 0.15
0.1398 | 280.15 | 0.09437 | 285.65 | 0.2
0.1398 | 280.15 | 0.09437 | 285.65 | 0.3
0.1398 | 280.15 | 0.09437 | 285.65 | 0.4
0.1398 | 280.15 | 0.09437 | 285.65 | 0.5
0.1398 | 280.15 | 0.09437 | 285.65 | 0.6
0.1398 | 280.15 | 0.09437 | 285.65 | 0.7
0.1398 | 280.15 | 0.09437 | 285.65 | 0.8
0.1398 | 280.15 | 0.09437 | 285.65 | 0.9
0.1398 | 280.15 | 0.09437 | 285.65 | 1
0.1398 | 280.15 | 0.09437 | 286.15 | 0.15
0.1398 | 280.15 | 0.09437 | 286.15 | 0.2
0.1398 | 280.15 | 0.09437 | 286.15 | 0.3
0.1398 | 280.15 | 0.09437 | 286.15 | 0.4
0.1398 | 280.15 | 0.09437 | 286.15 | 0.5
0.1398 | 280.15 | 0.09437 | 286.15 | 0.6
0.1398 | 280.15 | 0.09437 | 286.15 | 0.7
0.1398 | 280.15 | 0.09437 | 286.15 | 0.8
0.1398 | 280.15 | 0.09437 | 286.15 | 0.9
0.1398 | 280.15 | 0.09437 | 286.15 | 1
0.1398 | 280.15 | 0.09437 | 286.65 | 0.15
0.1398 | 280.15 | 0.09437 | 286.65 | 0.2
0.1398 | 280.15 | 0.09437 | 286.65 | 0.3
0.1398 | 280.15 | 0.09437 | 286.65 | 0.4
0.1398 | 280.15 | 0.09437 | 286.65 | 0.5
0.1398 | 280.15 | 0.09437 | 286.65 | 0.6
0.1398 | 280.15 | 0.09437 | 286.65 | 0.7
0.1398 | 280.15 | 0.09437 | 286.65 | 0.8
0.1398 | 280.15 | 0.09437 | 286.65 | 0.9
0.1398 | 280.15 | 0.09437 | 286.65 | 1
0.1398 | 280.15 | 0.09437 | 287.15 | 0.15
0.1398 | 280.15 | 0.09437 | 287.15 | 0.2
0.1398 | 280.15 | 0.09437 | 287.15 | 0.3
0.1398 | 280.15 | 0.09437 | 287.15 | 0.4
0.1398 | 280.15 | 0.09437 | 287.15 | 0.5
0.1398 | 280.15 | 0.09437 | 287.15 | 0.6
0.1398 | 280.15 | 0.09437 | 287.15 | 0.7
0.1398 | 280.15 | 0.09437 | 287.15 | 0.8
0.1398 | 280.15 | 0.09437 | 287.15 | 0.9
0.1398 | 280.15 | 0.09437 | 287.15 | 1
0.1398 | 280.15 | 0.09437 | 287.65 | 0.15
0.1398 | 280.15 | 0.09437 | 287.65 | 0.2
0.1398 | 280.15 | 0.09437 | 287.65 | 0.3
0.1398 | 280.15 | 0.09437 | 287.65 | 0.4
0.1398 | 280.15 | 0.09437 | 287.65 | 0.5
0.1398 | 280.15 | 0.09437 | 287.65 | 0.6
0.1398 | 280.15 | 0.09437 | 287.65 | 0.7
0.1398 | 280.15 | 0.09437 | 287.65 | 0.8
0.1398 | 280.15 | 0.09437 | 287.65 | 0.9
0.1398 | 280.15 | 0.09437 | 287.65 | 1
0.1398 | 280.15 | 0.09437 | 288.15 | 0.15
0.1398 | 280.15 | 0.09437 | 288.15 | 0.2
0.1398 | 280.15 | 0.09437 | 288.15 | 0.3
0.1398 | 280.15 | 0.09437 | 288.15 | 0.4
0.1398 | 280.15 | 0.09437 | 288.15 | 0.5
0.1398 | 280.15 | 0.09437 | 288.15 | 0.6
0.1398 | 280.15 | 0.09437 | 288.15 | 0.7
0.1398 | 280.15 | 0.09437 | 288.15 | 0.8
0.1398 | 280.15 | 0.09437 | 288.15 | 0.9
0.1398 | 280.15 | 0.09437 | 288.15 | 1
0.1398 | 280.15 | 0.09437 | 288.65 | 0.15
0.1398 | 280.15 | 0.09437 | 288.65 | 0.2
0.1398 | 280.15 | 0.09437 | 288.65 | 0.3
0.1398 | 280.15 | 0.09437 | 288.65 | 0.4
0.1398 | 280.15 | 0.09437 | 288.65 | 0.5
0.1398 | 280.15 | 0.09437 | 288.65 | 0.6
0.1398 | 280.15 | 0.09437 | 288.65 | 0.7
0.1398 | 280.15 | 0.09437 | 288.65 | 0.8
0.1398 | 280.15 | 0.09437 | 288.65 | 0.9
0.1398 | 280.15 | 0.09437 | 288.65 | 1
0.1398 | 280.15 | 0.09437 | 289.15 | 0.15
0.1398 | 280.15 | 0.09437 | 289.15 | 0.2
0.1398 | 280.15 | 0.09437 | 289.15 | 0.3
0.1398 | 280.15 | 0.09437 | 289.15 | 0.4
0.1398 | 280.15 | 0.09437 | 289.15 | 0.5
0.1398 | 280.15 | 0.09437 | 289.15 | 0.6
0.1398 | 280.15 | 0.09437 | 289.15 | 0.7
0.1398 | 280.15 | 0.09437 | 289.15 | 0.8
0.1398 | 280.15 | 0.09437 | 289.15 | 0.9
0.1398 | 280.15 | 0.09437 | 289.15 | 1
0.1398 | 280.15 | 0.09437 | 289.65 | 0.15
0.1398 | 280.15 | 0.09437 | 289.65 | 0.2
0.1398 | 280.15 | 0.09437 | 289.65 | 0.3
0.1398 | 280.15 | 0.09437 | 289.65 | 0.4
0.1398 | 280.15 | 0.09437 | 289.65 | 0.5
0.1398 | 280.15 | 0.09437 | 289.65 | 0.6
0.1398 | 280.15 | 0.09437 | 289.65 | 0.7
0.1398 | 280.15 | 0.09437 | 289.65 | 0.8
0.1398 | 280.15 | 0.09437 | 289.65 | 0.9
0.1398 | 280.15 | 0.09437 | 289.65 | 1
0.1398 | 280.15 | 0.09437 | 290.15 | 0.15
0.1398 | 280.15 | 0.09437 | 290.15 | 0.2
0.1398 | 280.15 | 0.09437 | 290.15 | 0.3
0.1398 | 280.15 | 0.09437 | 290.15 | 0.4
0.1398 | 280.15 | 0.09437 | 290.15 | 0.5
0.1398 | 280.15 | 0.09437 | 290.15 | 0.6
0.1398 | 280.15 | 0.09437 | 290.15 | 0.7
0.1398 | 280.15 | 0.09437 | 290.15 | 0.8
0.1398 | 280.15 | 0.09437 | 290.15 | 0.9
0.1398 | 280.15 | 0.09437 | 290.15 | 1
0.1398 | 280.15 | 0.09437 | 290.65 | 0.15
0.1398 | 280.15 | 0.09437 | 290.65 | 0.2
0.1398 | 280.15 | 0.09437 | 290.65 | 0.3
0.1398 | 280.15 | 0.09437 | 290.65 | 0.4
0.1398 | 280.15 | 0.09437 | 290.65 | 0.5
0.1398 | 280.15 | 0.09437 | 290.65 | 0.6
0.1398 | 280.15 | 0.09437 | 290.65 | 0.7
0.1398 | 280.15 | 0.09437 | 290.65 | 0.8
0.1398 | 280.15 | 0.09437 | 290.65 | 0.9
0.1398 | 280.15 | 0.09437 | 290.65 | 1
0.1398 | 280.15 | 0.09437 | 291.15 | 0.15
0.1398 | 280.15 | 0.09437 | 291.15 | 0.2
0.1398 | 280.15 | 0.09437 | 291.15 | 0.3
0.1398 | 280.15 | 0.09437 | 291.15 | 0.4
0.1398 | 280.15 | 0.09437 | 291.15 | 0.5
0.1398 | 280.15 | 0.09437 | 291.15 | 0.6
0.1398 | 280.15 | 0.09437 | 291.15 | 0.7
0.1398 | 280.15 | 0.09437 | 291.15 | 0.8
0.1398 | 280.15 | 0.09437 | 291.15 | 0.9
0.1398 | 280.15 | 0.09437 | 291.15 | 1
0.1398 | 280.15 | 0.09437 | 294.15 | 0.15
0.1398 | 280.15 | 0.09437 | 294.15 | 0.2
0.1398 | 280.15 | 0.09437 | 294.15 | 0.3
0.1398 | 280.15 | 0.09437 | 294.15 | 0.4
0.1398 | 280.15 | 0.09437 | 294.15 | 0.5
0.1398 | 280.15 | 0.09437 | 294.15 | 0.6
0.1398 | 280.15 | 0.09437 | 294.15 | 0.7
0.1398 | 280.15 | 0.09437 | 294.15 | 0.8
0.1398 | 280.15 | 0.09437 | 294.15 | 0.9
0.1398 | 280.15 | 0.09437 | 294.15 | 1
0.1398 | 280.15 | 0.09437 | 297.15 | 0.15
0.1398 | 280.15 | 0.09437 | 297.15 | 0.2
0.1398 | 280.15 | 0.09437 | 297.15 | 0.3
0.1398 | 280.15 | 0.09437 | 297.15 | 0.4
0.1398 | 280.15 | 0.09437 | 297.15 | 0.5
0.1398 | 280.15 | 0.09437 | 297.15 | 0.6
0.1398 | 280.15 | 0.09437 | 297.15 | 0.7
0.1398 | 280.15 | 0.09437 | 297.15 | 0.8
0.1398 | 280.15 | 0.09437 | 297.15 | 0.9
0.1398 | 280.15 | 0.09437 | 297.15 | 1
0.1398 | 280.15 | 0.09437 | 300.15 | 0.15
0.1398 | 280.15 | 0.09437 | 300.15 | 0.2
0.1398 | 280.15 | 0.09437 | 300.15 | 0.3
0.1398 | 280.15 | 0.09437 | 300.15 | 0.4
0.1398 | 280.15 | 0.09437 | 300.15 | 0.5
0.1398 | 280.15 | 0.09437 | 300.15 | 0.6
0.1398 | 280.15 | 0.09437 | 300.15 | 0.7
0.1398 | 280.15 | 0.09437 | 300.15 | 0.8
0.1398 | 280.15 | 0.09437 | 300.15 | 0.9
0.1398 | 280.15 | 0.09437 | 300.15 | 1
0.1398 | 280.15 | 0.09437 | 303.15 | 0.15
0.1398 | 280.15 | 0.09437 | 303.15 | 0.2
0.1398 | 280.15 | 0.09437 | 303.15 | 0.3
0.1398 | 280.15 | 0.09437 | 303.15 | 0.4
0.1398 | 280.15 | 0.09437 | 303.15 | 0.5
0.1398 | 280.15 | 0.09437 | 303.15 | 0.6
0.1398 | 280.15 | 0.09437 | 303.15 | 0.7
0.1398 | 280.15 | 0.09437 | 303.15 | 0.8
0.1398 | 280.15 | 0.09437 | 303.15 | 0.9
0.1398 | 280.15 | 0.09437 | 303.15 | 1
0.1398 | 280.15 | 0.09644 | 283.65 | 0.15
0.1398 | 280.15 | 0.09644 | 283.65 | 0.2
0.1398 | 280.15 | 0.09644 | 283.65 | 0.3
0.1398 | 280.15 | 0.09644 | 283.65 | 0.4
0.1398 | 280.15 | 0.09644 | 283.65 | 0.5
0.1398 | 280.15 | 0.09644 | 283.65 | 0.6
0.1398 | 280.15 | 0.09644 | 283.65 | 0.7
0.1398 | 280.15 | 0.09644 | 283.65 | 0.8
0.1398 | 280.15 | 0.09644 | 283.65 | 0.9
0.1398 | 280.15 | 0.09644 | 283.65 | 1
0.1398 | 280.15 | 0.09644 | 284.15 | 0.15
0.1398 | 280.15 | 0.09644 | 284.15 | 0.2
0.1398 | 280.15 | 0.09644 | 284.15 | 0.3
0.1398 | 280.15 | 0.09644 | 284.15 | 0.4
0.1398 | 280.15 | 0.09644 | 284.15 | 0.5
0.1398 | 280.15 | 0.09644 | 284.15 | 0.6
0.1398 | 280.15 | 0.09644 | 284.15 | 0.7
0.1398 | 280.15 | 0.09644 | 284.15 | 0.8
0.1398 | 280.15 | 0.09644 | 284.15 | 0.9
0.1398 | 280.15 | 0.09644 | 284.15 | 1
0.1398 | 280.15 | 0.09644 | 284.65 | 0.15
0.1398 | 280.15 | 0.09644 | 284.65 | 0.2
0.1398 | 280.15 | 0.09644 | 284.65 | 0.3
0.1398 | 280.15 | 0.09644 | 284.65 | 0.4
0.1398 | 280.15 | 0.09644 | 284.65 | 0.5
0.1398 | 280.15 | 0.09644 | 284.65 | 0.6
0.1398 | 280.15 | 0.09644 | 284.65 | 0.7
0.1398 | 280.15 | 0.09644 | 284.65 | 0.8
0.1398 | 280.15 | 0.09644 | 284.65 | 0.9
0.1398 | 280.15 | 0.09644 | 284.65 | 1
0.1398 | 280.15 | 0.09644 | 285.15 | 0.15
0.1398 | 280.15 | 0.09644 | 285.15 | 0.2
0.1398 | 280.15 | 0.09644 | 285.15 | 0.3
0.1398 | 280.15 | 0.09644 | 285.15 | 0.4
0.1398 | 280.15 | 0.09644 | 285.15 | 0.5
0.1398 | 280.15 | 0.09644 | 285.15 | 0.6
0.1398 | 280.15 | 0.09644 | 285.15 | 0.7
0.1398 | 280.15 | 0.09644 | 285.15 | 0.8
0.1398 | 280.15 | 0.09644 | 285.15 | 0.9
0.1398 | 280.15 | 0.09644 | 285.15 | 1
0.1398 | 280.15 | 0.09644 | 285.65 | 0.15
0.1398 | 280.15 | 0.09644 | 285.65 | 0.2
0.1398 | 280.15 | 0.09644 | 285.65 | 0.3
0.1398 | 280.15 | 0.09644 | 285.65 | 0.4
0.1398 | 280.15 | 0.09644 | 285.65 | 0.5
0.1398 | 280.15 | 0.09644 | 285.65 | 0.6
0.1398 | 280.15 | 0.09644 | 285.65 | 0.7
0.1398 | 280.15 | 0.09644 | 285.65 | 0.8
0.1398 | 280.15 | 0.09644 | 285.65 | 0.9
0.1398 | 280.15 | 0.09644 | 285.65 | 1
0.1398 | 280.15 | 0.09644 | 286.15 | 0.15
0.1398 | 280.15 | 0.09644 | 286.15 | 0.2
0.1398 | 280.15 | 0.09644 | 286.15 | 0.3
0.1398 | 280.15 | 0.09644 | 286.15 | 0.4
0.1398 | 280.15 | 0.09644 | 286.15 | 0.5
0.1398 | 280.15 | 0.09644 | 286.15 | 0.6
0.1398 | 280.15 | 0.09644 | 286.15 | 0.7
0.1398 | 280.15 | 0.09644 | 286.15 | 0.8
0.1398 | 280.15 | 0.09644 | 286.15 | 0.9
0.1398 | 280.15 | 0.09644 | 286.15 | 1
0.1398 | 280.15 | 0.09644 | 286.65 | 0.15
0.1398 | 280.15 | 0.09644 | 286.65 | 0.2
0.1398 | 280.15 | 0.09644 | 286.65 | 0.3
0.1398 | 280.15 | 0.09644 | 286.65 | 0.4
0.1398 | 280.15 | 0.09644 | 286.65 | 0.5
0.1398 | 280.15 | 0.09644 | 286.65 | 0.6
0.1398 | 280.15 | 0.09644 | 286.65 | 0.7
0.1398 | 280.15 | 0.09644 | 286.65 | 0.8
0.1398 | 280.15 | 0.09644 | 286.65 | 0.9
0.1398 | 280.15 | 0.09644 | 286.65 | 1
0.1398 | 280.15 | 0.09644 | 287.15 | 0.15
0.1398 | 280.15 | 0.09644 | 287.15 | 0.2
0.1398 | 280.15 | 0.09644 | 287.15 | 0.3
0.1398 | 280.15 | 0.09644 | 287.15 | 0.4
0.1398 | 280.15 | 0.09644 | 287.15 | 0.5
0.1398 | 280.15 | 0.09644 | 287.15 | 0.6
0.1398 | 280.15 | 0.09644 | 287.15 | 0.7
0.1398 | 280.15 | 0.09644 | 287.15 | 0.8
0.1398 | 280.15 | 0.09644 | 287.15 | 0.9
0.1398 | 280.15 | 0.09644 | 287.15 | 1
0.1398 | 280.15 | 0.09644 | 287.65 | 0.15
0.1398 | 280.15 | 0.09644 | 287.65 | 0.2
0.1398 | 280.15 | 0.09644 | 287.65 | 0.3
0.1398 | 280.15 | 0.09644 | 287.65 | 0.4
0.1398 | 280.15 | 0.09644 | 287.65 | 0.5
0.1398 | 280.15 | 0.09644 | 287.65 | 0.6
0.1398 | 280.15 | 0.09644 | 287.65 | 0.7
0.1398 | 280.15 | 0.09644 | 287.65 | 0.8
0.1398 | 280.15 | 0.09644 | 287.65 | 0.9
0.1398 | 280.15 | 0.09644 | 287.65 | 1
0.1398 | 280.15 | 0.09644 | 288.15 | 0.15
0.1398 | 280.15 | 0.09644 | 288.15 | 0.2
0.1398 | 280.15 | 0.09644 | 288.15 | 0.3
0.1398 | 280.15 | 0.09644 | 288.15 | 0.4
0.1398 | 280.15 | 0.09644 | 288.15 | 0.5
0.1398 | 280.15 | 0.09644 | 288.15 | 0.6
0.1398 | 280.15 | 0.09644 | 288.15 | 0.7
0.1398 | 280.15 | 0.09644 | 288.15 | 0.8
0.1398 | 280.15 | 0.09644 | 288.15 | 0.9
0.1398 | 280.15 | 0.09644 | 288.15 | 1
0.1398 | 280.15 | 0.09644 | 288.65 | 0.15
0.1398 | 280.15 | 0.09644 | 288.65 | 0.2
0.1398 | 280.15 | 0.09644 | 288.65 | 0.3
0.1398 | 280.15 | 0.09644 | 288.65 | 0.4
0.1398 | 280.15 | 0.09644 | 288.65 | 0.5
0.1398 | 280.15 | 0.09644 | 288.65 | 0.6
0.1398 | 280.15 | 0.09644 | 288.65 | 0.7
0.1398 | 280.15 | 0.09644 | 288.65 | 0.8
0.1398 | 280.15 | 0.09644 | 288.65 | 0.9
0.1398 | 280.15 | 0.09644 | 288.65 | 1
0.1398 | 280.15 | 0.09644 | 289.15 | 0.15
0.1398 | 280.15 | 0.09644 | 289.15 | 0.2
0.1398 | 280.15 | 0.09644 | 289.15 | 0.3
0.1398 | 280.15 | 0.09644 | 289.15 | 0.4
0.1398 | 280.15 | 0.09644 | 289.15 | 0.5
0.1398 | 280.15 | 0.09644 | 289.15 | 0.6
0.1398 | 280.15 | 0.09644 | 289.15 | 0.7
0.1398 | 280.15 | 0.09644 | 289.15 | 0.8
0.1398 | 280.15 | 0.09644 | 289.15 | 0.9
0.1398 | 280.15 | 0.09644 | 289.15 | 1
0.1398 | 280.15 | 0.09644 | 289.65 | 0.15
0.1398 | 280.15 | 0.09644 | 289.65 | 0.2
0.1398 | 280.15 | 0.09644 | 289.65 | 0.3
0.1398 | 280.15 | 0.09644 | 289.65 | 0.4
0.1398 | 280.15 | 0.09644 | 289.65 | 0.5
0.1398 | 280.15 | 0.09644 | 289.65 | 0.6
0.1398 | 280.15 | 0.09644 | 289.65 | 0.7
0.1398 | 280.15 | 0.09644 | 289.65 | 0.8
0.1398 | 280.15 | 0.09644 | 289.65 | 0.9
0.1398 | 280.15 | 0.09644 | 289.65 | 1
0.1398 | 280.15 | 0.09644 | 290.15 | 0.15
0.1398 | 280.15 | 0.09644 | 290.15 | 0.2
0.1398 | 280.15 | 0.09644 | 290.15 | 0.3
0.1398 | 280.15 | 0.09644 | 290.15 | 0.4
0.1398 | 280.15 | 0.09644 | 290.15 | 0.5
0.1398 | 280.15 | 0.09644 | 290.15 | 0.6
0.1398 | 280.15 | 0.09644 | 290.15 | 0.7
0.1398 | 280.15 | 0.09644 | 290.15 | 0.8
0.1398 | 280.15 | 0.09644 | 290.15 | 0.9
0.1398 | 280.15 | 0.09644 | 290.15 | 1
0.1398 | 280.15 | 0.09644 | 290.65 | 0.15
0.1398 | 280.15 | 0.09644 | 290.65 | 0.2
0.1398 | 280.15 | 0.09644 | 290.65 | 0.3
0.1398 | 280.15 | 0.09644 | 290.65 | 0.4
0.1398 | 280.15 | 0.09644 | 290.65 | 0.5
0.1398 | 280.15 | 0.09644 | 290.65 | 0.6
0.1398 | 280.15 | 0.09644 | 290.65 | 0.7
0.1398 | 280.15 | 0.09644 | 290.65 | 0.8
0.1398 | 280.15 | 0.09644 | 290.65 | 0.9
0.1398 | 280.15 | 0.09644 | 290.65 | 1
0.1398 | 280.15 | 0.09644 | 291.15 | 0.15
0.1398 | 280.15 | 0.09644 | 291.15 | 0.2
0.1398 | 280.15 | 0.09644 | 291.15 | 0.3
0.1398 | 280.15 | 0.09644 | 291.15 | 0.4
0.1398 | 280.15 | 0.09644 | 291.15 | 0.5
0.1398 | 280.15 | 0.09644 | 291.15 | 0.6
0.1398 | 280.15 | 0.09644 | 291.15 | 0.7
0.1398 | 280.15 | 0.09644 | 291.15 | 0.8
0.1398 | 280.15 | 0.09644 | 291.15 | 0.9
0.1398 | 280.15 | 0.09644 | 291.15 | 1
0.1398 | 280.15 | 0.09644 | 294.15 | 0.15
0.1398 | 280.15 | 0.09644 | 294.15 | 0.2
0.1398 | 280.15 | 0.09644 | 294.15 | 0.3
0.1398 | 280.15 | 0.09644 | 294.15 | 0.4
0.1398 | 280.15 | 0.09644 | 294.15 | 0.5
0.1398 | 280.15 | 0.09644 | 294.15 | 0.6
0.1398 | 280.15 | 0.09644 | 294.15 | 0.7
0.1398 | 280.15 | 0.09644 | 294.15 | 0.8
0.1398 | 280.15 | 0.09644 | 294.15 | 0.9
0.1398 | 280.15 | 0.09644 | 294.15 | 1
0.1398 | 280.15 | 0.09644 | 297.15 | 0.15
0.1398 | 280.15 | 0.09644 | 297.15 | 0.2
0.1398 | 280.15 | 0.09644 | 297.15 | 0.3
0.1398 | 280.15 | 0.09644 | 297.15 | 0.4
0.1398 | 280.15 | 0.09644 | 297.15 | 0.5
0.1398 | 280.15 | 0.09644 | 297.15 | 0.6
0.1398 | 280.15 | 0.09644 | 297.15 | 0.7
0.1398 | 280.15 | 0.09644 | 297.15 | 0.8
0.1398 | 280.15 | 0.09644 | 297.15 | 0.9
0.1398 | 280.15 | 0.09644 | 297.15 | 1
0.1398 | 280.15 | 0.09644 | 300.15 | 0.15
0.1398 | 280.15 | 0.09644 | 300.15 | 0.2
0.1398 | 280.15 | 0.09644 | 300.15 | 0.3
0.1398 | 280.15 | 0.09644 | 300.15 | 0.4
0.1398 | 280.15 | 0.09644 | 300.15 | 0.5
0.1398 | 280.15 | 0.09644 | 300.15 | 0.6
0.1398 | 280.15 | 0.09644 | 300.15 | 0.7
0.1398 | 280.15 | 0.09644 | 300.15 | 0.8
0.1398 | 280.15 | 0.09644 | 300.15 | 0.9
0.1398 | 280.15 | 0.09644 | 300.15 | 1
0.1398 | 280.15 | 0.09644 | 303.15 | 0.15
0.1398 | 280.15 | 0.09644 | 303.15 | 0.2
0.1398 | 280.15 | 0.09644 | 303.15 | 0.3
0.1398 | 280.15 | 0.09644 | 303.15 | 0.4
0.1398 | 280.15 | 0.09644 | 303.15 | 0.5
0.1398 | 280.15 | 0.09644 | 303.15 | 0.6
0.1398 | 280.15 | 0.09644 | 303.15 | 0.7
0.1398 | 280.15 | 0.09644 | 303.15 | 0.8
0.1398 | 280.15 | 0.09644 | 303.15 | 0.9
0.1398 | 280.15 | 0.09644 | 303.15 | 1
0.1398 | 280.15 | 0.09737 | 283.65 | 0.15
0.1398 | 280.15 | 0.09737 | 283.65 | 0.2
0.1398 | 280.15 | 0.09737 | 283.65 | 0.3
0.1398 | 280.15 | 0.09737 | 283.65 | 0.4
0.1398 | 280.15 | 0.09737 | 283.65 | 0.5
0.1398 | 280.15 | 0.09737 | 283.65 | 0.6
0.1398 | 280.15 | 0.09737 | 283.65 | 0.7
0.1398 | 280.15 | 0.09737 | 283.65 | 0.8
0.1398 | 280.15 | 0.09737 | 283.65 | 0.9
0.1398 | 280.15 | 0.09737 | 283.65 | 1
0.1398 | 280.15 | 0.09737 | 284.15 | 0.15
0.1398 | 280.15 | 0.09737 | 284.15 | 0.2
0.1398 | 280.15 | 0.09737 | 284.15 | 0.3
0.1398 | 280.15 | 0.09737 | 284.15 | 0.4
0.1398 | 280.15 | 0.09737 | 284.15 | 0.5
0.1398 | 280.15 | 0.09737 | 284.15 | 0.6
0.1398 | 280.15 | 0.09737 | 284.15 | 0.7
0.1398 | 280.15 | 0.09737 | 284.15 | 0.8
0.1398 | 280.15 | 0.09737 | 284.15 | 0.9
0.1398 | 280.15 | 0.09737 | 284.15 | 1
0.1398 | 280.15 | 0.09737 | 284.65 | 0.15
0.1398 | 280.15 | 0.09737 | 284.65 | 0.2
0.1398 | 280.15 | 0.09737 | 284.65 | 0.3
0.1398 | 280.15 | 0.09737 | 284.65 | 0.4
0.1398 | 280.15 | 0.09737 | 284.65 | 0.5
0.1398 | 280.15 | 0.09737 | 284.65 | 0.6
0.1398 | 280.15 | 0.09737 | 284.65 | 0.7
0.1398 | 280.15 | 0.09737 | 284.65 | 0.8
0.1398 | 280.15 | 0.09737 | 284.65 | 0.9
0.1398 | 280.15 | 0.09737 | 284.65 | 1
0.1398 | 280.15 | 0.09737 | 285.15 | 0.15
0.1398 | 280.15 | 0.09737 | 285.15 | 0.2
0.1398 | 280.15 | 0.09737 | 285.15 | 0.3
0.1398 | 280.15 | 0.09737 | 285.15 | 0.4
0.1398 | 280.15 | 0.09737 | 285.15 | 0.5
0.1398 | 280.15 | 0.09737 | 285.15 | 0.6
0.1398 | 280.15 | 0.09737 | 285.15 | 0.7
0.1398 | 280.15 | 0.09737 | 285.15 | 0.8
0.1398 | 280.15 | 0.09737 | 285.15 | 0.9
0.1398 | 280.15 | 0.09737 | 285.15 | 1
0.1398 | 280.15 | 0.09737 | 285.65 | 0.15
0.1398 | 280.15 | 0.09737 | 285.65 | 0.2
0.1398 | 280.15 | 0.09737 | 285.65 | 0.3
0.1398 | 280.15 | 0.09737 | 285.65 | 0.4
0.1398 | 280.15 | 0.09737 | 285.65 | 0.5
0.1398 | 280.15 | 0.09737 | 285.65 | 0.6
0.1398 | 280.15 | 0.09737 | 285.65 | 0.7
0.1398 | 280.15 | 0.09737 | 285.65 | 0.8
0.1398 | 280.15 | 0.09737 | 285.65 | 0.9
0.1398 | 280.15 | 0.09737 | 285.65 | 1
0.1398 | 280.15 | 0.09737 | 286.15 | 0.15
0.1398 | 280.15 | 0.09737 | 286.15 | 0.2
0.1398 | 280.15 | 0.09737 | 286.15 | 0.3
0.1398 | 280.15 | 0.09737 | 286.15 | 0.4
0.1398 | 280.15 | 0.09737 | 286.15 | 0.5
0.1398 | 280.15 | 0.09737 | 286.15 | 0.6
0.1398 | 280.15 | 0.09737 | 286.15 | 0.7
0.1398 | 280.15 | 0.09737 | 286.15 | 0.8
0.1398 | 280.15 | 0.09737 | 286.15 | 0.9
0.1398 | 280.15 | 0.09737 | 286.15 | 1
0.1398 | 280.15 | 0.09737 | 286.65 | 0.15
0.1398 | 280.15 | 0.09737 | 286.65 | 0.2
0.1398 | 280.15 | 0.09737 | 286.65 | 0.3
0.1398 | 280.15 | 0.09737 | 286.65 | 0.4
0.1398 | 280.15 | 0.09737 | 286.65 | 0.5
0.1398 | 280.15 | 0.09737 | 286.65 | 0.6
0.1398 | 280.15 | 0.09737 | 286.65 | 0.7
0.1398 | 280.15 | 0.09737 | 286.65 | 0.8
0.1398 | 280.15 | 0.09737 | 286.65 | 0.9
0.1398 | 280.15 | 0.09737 | 286.65 | 1
0.1398 | 280.15 | 0.09737 | 287.15 | 0.15
0.1398 | 280.15 | 0.09737 | 287.15 | 0.2
0.1398 | 280.15 | 0.09737 | 287.15 | 0.3
0.1398 | 280.15 | 0.09737 | 287.15 | 0.4
0.1398 | 280.15 | 0.09737 | 287.15 | 0.5
0.1398 | 280.15 | 0.09737 | 287.15 | 0.6
0.1398 | 280.15 | 0.09737 | 287.15 | 0.7
0.1398 | 280.15 | 0.09737 | 287.15 | 0.8
0.1398 | 280.15 | 0.09737 | 287.15 | 0.9
0.1398 | 280.15 | 0.09737 | 287.15 | 1
0.1398 | 280.15 | 0.09737 | 287.65 | 0.15
0.1398 | 280.15 | 0.09737 | 287.65 | 0.2
0.1398 | 280.15 | 0.09737 | 287.65 | 0.3
0.1398 | 280.15 | 0.09737 | 287.65 | 0.4
0.1398 | 280.15 | 0.09737 | 287.65 | 0.5
0.1398 | 280.15 | 0.09737 | 287.65 | 0.6
0.1398 | 280.15 | 0.09737 | 287.65 | 0.7
0.1398 | 280.15 | 0.09737 | 287.65 | 0.8
0.1398 | 280.15 | 0.09737 | 287.65 | 0.9
0.1398 | 280.15 | 0.09737 | 287.65 | 1
0.1398 | 280.15 | 0.09737 | 288.15 | 0.15
0.1398 | 280.15 | 0.09737 | 288.15 | 0.2
0.1398 | 280.15 | 0.09737 | 288.15 | 0.3
0.1398 | 280.15 | 0.09737 | 288.15 | 0.4
0.1398 | 280.15 | 0.09737 | 288.15 | 0.5
0.1398 | 280.15 | 0.09737 | 288.15 | 0.6
0.1398 | 280.15 | 0.09737 | 288.15 | 0.7
0.1398 | 280.15 | 0.09737 | 288.15 | 0.8
0.1398 | 280.15 | 0.09737 | 288.15 | 0.9
0.1398 | 280.15 | 0.09737 | 288.15 | 1
0.1398 | 280.15 | 0.09737 | 288.65 | 0.15
0.1398 | 280.15 | 0.09737 | 288.65 | 0.2
0.1398 | 280.15 | 0.09737 | 288.65 | 0.3
0.1398 | 280.15 | 0.09737 | 288.65 | 0.4
0.1398 | 280.15 | 0.09737 | 288.65 | 0.5
0.1398 | 280.15 | 0.09737 | 288.65 | 0.6
0.1398 | 280.15 | 0.09737 | 288.65 | 0.7
0.1398 | 280.15 | 0.09737 | 288.65 | 0.8
0.1398 | 280.15 | 0.09737 | 288.65 | 0.9
0.1398 | 280.15 | 0.09737 | 288.65 | 1
0.1398 | 280.15 | 0.09737 | 289.15 | 0.15
0.1398 | 280.15 | 0.09737 | 289.15 | 0.2
0.1398 | 280.15 | 0.09737 | 289.15 | 0.3
0.1398 | 280.15 | 0.09737 | 289.15 | 0.4
0.1398 | 280.15 | 0.09737 | 289.15 | 0.5
0.1398 | 280.15 | 0.09737 | 289.15 | 0.6
0.1398 | 280.15 | 0.09737 | 289.15 | 0.7
0.1398 | 280.15 | 0.09737 | 289.15 | 0.8
0.1398 | 280.15 | 0.09737 | 289.15 | 0.9
0.1398 | 280.15 | 0.09737 | 289.15 | 1
0.1398 | 280.15 | 0.09737 | 289.65 | 0.15
0.1398 | 280.15 | 0.09737 | 289.65 | 0.2
0.1398 | 280.15 | 0.09737 | 289.65 | 0.3
0.1398 | 280.15 | 0.09737 | 289.65 | 0.4
0.1398 | 280.15 | 0.09737 | 289.65 | 0.5
0.1398 | 280.15 | 0.09737 | 289.65 | 0.6
0.1398 | 280.15 | 0.09737 | 289.65 | 0.7
0.1398 | 280.15 | 0.09737 | 289.65 | 0.8
0.1398 | 280.15 | 0.09737 | 289.65 | 0.9
0.1398 | 280.15 | 0.09737 | 289.65 | 1
0.1398 | 280.15 | 0.09737 | 290.15 | 0.15
0.1398 | 280.15 | 0.09737 | 290.15 | 0.2
0.1398 | 280.15 | 0.09737 | 290.15 | 0.3
0.1398 | 280.15 | 0.09737 | 290.15 | 0.4
0.1398 | 280.15 | 0.09737 | 290.15 | 0.5
0.1398 | 280.15 | 0.09737 | 290.15 | 0.6
0.1398 | 280.15 | 0.09737 | 290.15 | 0.7
0.1398 | 280.15 | 0.09737 | 290.15 | 0.8
0.1398 | 280.15 | 0.09737 | 290.15 | 0.9
0.1398 | 280.15 | 0.09737 | 290.15 | 1
0.1398 | 280.15 | 0.09737 | 290.65 | 0.15
0.1398 | 280.15 | 0.09737 | 290.65 | 0.2
0.1398 | 280.15 | 0.09737 | 290.65 | 0.3
0.1398 | 280.15 | 0.09737 | 290.65 | 0.4
0.1398 | 280.15 | 0.09737 | 290.65 | 0.5
0.1398 | 280.15 | 0.09737 | 290.65 | 0.6
0.1398 | 280.15 | 0.09737 | 290.65 | 0.7
0.1398 | 280.15 | 0.09737 | 290.65 | 0.8
0.1398 | 280.15 | 0.09737 | 290.65 | 0.9
0.1398 | 280.15 | 0.09737 | 290.65 | 1
0.1398 | 280.15 | 0.09737 | 291.15 | 0.15
0.1398 | 280.15 | 0.09737 | 291.15 | 0.2
0.1398 | 280.15 | 0.09737 | 291.15 | 0.3
0.1398 | 280.15 | 0.09737 | 291.15 | 0.4
0.1398 | 280.15 | 0.09737 | 291.15 | 0.5
0.1398 | 280.15 | 0.09737 | 291.15 | 0.6
0.1398 | 280.15 | 0.09737 | 291.15 | 0.7
0.1398 | 280.15 | 0.09737 | 291.15 | 0.8
0.1398 | 280.15 | 0.09737 | 291.15 | 0.9
0.1398 | 280.15 | 0.09737 | 291.15 | 1
0.1398 | 280.15 | 0.09737 | 294.15 | 0.15
0.1398 | 280.15 | 0.09737 | 294.15 | 0.2
0.1398 | 280.15 | 0.09737 | 294.15 | 0.3
0.1398 | 280.15 | 0.09737 | 294.15 | 0.4
0.1398 | 280.15 | 0.09737 | 294.15 | 0.5
0.1398 | 280.15 | 0.09737 | 294.15 | 0.6
0.1398 | 280.15 | 0.09737 | 294.15 | 0.7
0.1398 | 280.15 | 0.09737 | 294.15 | 0.8
0.1398 | 280.15 | 0.09737 | 294.15 | 0.9
0.1398 | 280.15 | 0.09737 | 294.15 | 1
0.1398 | 280.15 | 0.09737 | 297.15 | 0.15
0.1398 | 280.15 | 0.09737 | 297.15 | 0.2
0.1398 | 280.15 | 0.09737 | 297.15 | 0.3
0.1398 | 280.15 | 0.09737 | 297.15 | 0.4
0.1398 | 280.15 | 0.09737 | 297.15 | 0.5
0.1398 | 280.15 | 0.09737 | 297.15 | 0.6
0.1398 | 280.15 | 0.09737 | 297.15 | 0.7
0.1398 | 280.15 | 0.09737 | 297.15 | 0.8
0.1398 | 280.15 | 0.09737 | 297.15 | 0.9
0.1398 | 280.15 | 0.09737 | 297.15 | 1
0.1398 | 280.15 | 0.09737 | 300.15 | 0.15
0.1398 | 280.15 | 0.09737 | 300.15 | 0.2
0.1398 | 280.15 | 0.09737 | 300.15 | 0.3
0.1398 | 280.15 | 0.09737 | 300.15 | 0.4
0.1398 | 280.15 | 0.09737 | 300.15 | 0.5
0.1398 | 280.15 | 0.09737 | 300.15 | 0.6
0.1398 | 280.15 | 0.09737 | 300.15 | 0.7
0.1398 | 280.15 | 0.09737 | 300.15 | 0.8
0.1398 | 280.15 | 0.09737 | 300.15 | 0.9
0.1398 | 280.15 | 0.09737 | 300.15 | 1
0.1398 | 280.15 | 0.09737 | 303.15 | 0.15
0.1398 | 280.15 | 0.09737 | 303.15 | 0.2
0.1398 | 280.15 | 0.09737 | 303.15 | 0.3
0.1398 | 280.15 | 0.09737 | 303.15 | 0.4
0.1398 | 280.15 | 0.09737 | 303.15 | 0.5
0.1398 | 280.15 | 0.09737 | 303.15 | 0.6
0.1398 | 280.15 | 0.09737 | 303.15 | 0.7
0.1398 | 280.15 | 0.09737 | 303.15 | 0.8
0.1398 | 280.15 | 0.09737 | 303.15 | 0.9
0.1398 | 280.15 | 0.09737 | 303.15 | 1
0.1398 | 280.15 | 0.115 | 283.65 | 0.15
0.1398 | 280.15 | 0.115 | 283.65 | 0.2
0.1398 | 280.15 | 0.115 | 283.65 | 0.3
0.1398 | 280.15 | 0.115 | 283.65 | 0.4
0.1398 | 280.15 | 0.115 | 283.65 | 0.5
0.1398 | 280.15 | 0.115 | 283.65 | 0.6
0.1398 | 280.15 | 0.115 | 283.65 | 0.7
0.1398 | 280.15 | 0.115 | 283.65 | 0.8
0.1398 | 280.15 | 0.115 | 283.65 | 0.9
0.1398 | 280.15 | 0.115 | 283.65 | 1
0.1398 | 280.15 | 0.115 | 284.15 | 0.15
0.1398 | 280.15 | 0.115 | 284.15 | 0.2
0.1398 | 280.15 | 0.115 | 284.15 | 0.3
0.1398 | 280.15 | 0.115 | 284.15 | 0.4
0.1398 | 280.15 | 0.115 | 284.15 | 0.5
0.1398 | 280.15 | 0.115 | 284.15 | 0.6
0.1398 | 280.15 | 0.115 | 284.15 | 0.7
0.1398 | 280.15 | 0.115 | 284.15 | 0.8
0.1398 | 280.15 | 0.115 | 284.15 | 0.9
0.1398 | 280.15 | 0.115 | 284.15 | 1
0.1398 | 280.15 | 0.115 | 284.65 | 0.15
0.1398 | 280.15 | 0.115 | 284.65 | 0.2
0.1398 | 280.15 | 0.115 | 284.65 | 0.3
0.1398 | 280.15 | 0.115 | 284.65 | 0.4
0.1398 | 280.15 | 0.115 | 284.65 | 0.5
0.1398 | 280.15 | 0.115 | 284.65 | 0.6
0.1398 | 280.15 | 0.115 | 284.65 | 0.7
0.1398 | 280.15 | 0.115 | 284.65 | 0.8
0.1398 | 280.15 | 0.115 | 284.65 | 0.9
0.1398 | 280.15 | 0.115 | 284.65 | 1
0.1398 | 280.15 | 0.115 | 285.15 | 0.15
0.1398 | 280.15 | 0.115 | 285.15 | 0.2
0.1398 | 280.15 | 0.115 | 285.15 | 0.3
0.1398 | 280.15 | 0.115 | 285.15 | 0.4
0.1398 | 280.15 | 0.115 | 285.15 | 0.5
0.1398 | 280.15 | 0.115 | 285.15 | 0.6
0.1398 | 280.15 | 0.115 | 285.15 | 0.7
0.1398 | 280.15 | 0.115 | 285.15 | 0.8
0.1398 | 280.15 | 0.115 | 285.15 | 0.9
0.1398 | 280.15 | 0.115 | 285.15 | 1
0.1398 | 280.15 | 0.115 | 285.65 | 0.15
0.1398 | 280.15 | 0.115 | 285.65 | 0.2
0.1398 | 280.15 | 0.115 | 285.65 | 0.3
0.1398 | 280.15 | 0.115 | 285.65 | 0.4
0.1398 | 280.15 | 0.115 | 285.65 | 0.5
0.1398 | 280.15 | 0.115 | 285.65 | 0.6
0.1398 | 280.15 | 0.115 | 285.65 | 0.7
0.1398 | 280.15 | 0.115 | 285.65 | 0.8
0.1398 | 280.15 | 0.115 | 285.65 | 0.9
0.1398 | 280.15 | 0.115 | 285.65 | 1
0.1398 | 280.15 | 0.115 | 286.15 | 0.15
0.1398 | 280.15 | 0.115 | 286.15 | 0.2
0.1398 | 280.15 | 0.115 | 286.15 | 0.3
0.1398 | 280.15 | 0.115 | 286.15 | 0.4
0.1398 | 280.15 | 0.115 | 286.15 | 0.5
0.1398 | 280.15 | 0.115 | 286.15 | 0.6
0.1398 | 280.15 | 0.115 | 286.15 | 0.7
0.1398 | 280.15 | 0.115 | 286.15 | 0.8
0.1398 | 280.15 | 0.115 | 286.15 | 0.9
0.1398 | 280.15 | 0.115 | 286.15 | 1
0.1398 | 280.15 | 0.115 | 286.65 | 0.15
0.1398 | 280.15 | 0.115 | 286.65 | 0.2
0.1398 | 280.15 | 0.115 | 286.65 | 0.3
0.1398 | 280.15 | 0.115 | 286.65 | 0.4
0.1398 | 280.15 | 0.115 | 286.65 | 0.5
0.1398 | 280.15 | 0.115 | 286.65 | 0.6
0.1398 | 280.15 | 0.115 | 286.65 | 0.7
0.1398 | 280.15 | 0.115 | 286.65 | 0.8
0.1398 | 280.15 | 0.115 | 286.65 | 0.9
0.1398 | 280.15 | 0.115 | 286.65 | 1
0.1398 | 280.15 | 0.115 | 287.15 | 0.15
0.1398 | 280.15 | 0.115 | 287.15 | 0.2
0.1398 | 280.15 | 0.115 | 287.15 | 0.3
0.1398 | 280.15 | 0.115 | 287.15 | 0.4
0.1398 | 280.15 | 0.115 | 287.15 | 0.5
0.1398 | 280.15 | 0.115 | 287.15 | 0.6
0.1398 | 280.15 | 0.115 | 287.15 | 0.7
0.1398 | 280.15 | 0.115 | 287.15 | 0.8
0.1398 | 280.15 | 0.115 | 287.15 | 0.9
0.1398 | 280.15 | 0.115 | 287.15 | 1
0.1398 | 280.15 | 0.115 | 287.65 | 0.15
0.1398 | 280.15 | 0.115 | 287.65 | 0.2
0.1398 | 280.15 | 0.115 | 287.65 | 0.3
0.1398 | 280.15 | 0.115 | 287.65 | 0.4
0.1398 | 280.15 | 0.115 | 287.65 | 0.5
0.1398 | 280.15 | 0.115 | 287.65 | 0.6
0.1398 | 280.15 | 0.115 | 287.65 | 0.7
0.1398 | 280.15 | 0.115 | 287.65 | 0.8
0.1398 | 280.15 | 0.115 | 287.65 | 0.9
0.1398 | 280.15 | 0.115 | 287.65 | 1
0.1398 | 280.15 | 0.115 | 288.15 | 0.15
0.1398 | 280.15 | 0.115 | 288.15 | 0.2
0.1398 | 280.15 | 0.115 | 288.15 | 0.3
0.1398 | 280.15 | 0.115 | 288.15 | 0.4
0.1398 | 280.15 | 0.115 | 288.15 | 0.5
0.1398 | 280.15 | 0.115 | 288.15 | 0.6
0.1398 | 280.15 | 0.115 | 288.15 | 0.7
0.1398 | 280.15 | 0.115 | 288.15 | 0.8
0.1398 | 280.15 | 0.115 | 288.15 | 0.9
0.1398 | 280.15 | 0.115 | 288.15 | 1
0.1398 | 280.15 | 0.115 | 288.65 | 0.15
0.1398 | 280.15 | 0.115 | 288.65 | 0.2
0.1398 | 280.15 | 0.115 | 288.65 | 0.3
0.1398 | 280.15 | 0.115 | 288.65 | 0.4
0.1398 | 280.15 | 0.115 | 288.65 | 0.5
0.1398 | 280.15 | 0.115 | 288.65 | 0.6
0.1398 | 280.15 | 0.115 | 288.65 | 0.7
0.1398 | 280.15 | 0.115 | 288.65 | 0.8
0.1398 | 280.15 | 0.115 | 288.65 | 0.9
0.1398 | 280.15 | 0.115 | 288.65 | 1
0.1398 | 280.15 | 0.115 | 289.15 | 0.15
0.1398 | 280.15 | 0.115 | 289.15 | 0.2
0.1398 | 280.15 | 0.115 | 289.15 | 0.3
0.1398 | 280.15 | 0.115 | 289.15 | 0.4
0.1398 | 280.15 | 0.115 | 289.15 | 0.5
0.1398 | 280.15 | 0.115 | 289.15 | 0.6
0.1398 | 280.15 | 0.115 | 289.15 | 0.7
0.1398 | 280.15 | 0.115 | 289.15 | 0.8
0.1398 | 280.15 | 0.115 | 289.15 | 0.9
0.1398 | 280.15 | 0.115 | 289.15 | 1
0.1398 | 280.15 | 0.115 | 289.65 | 0.15
0.1398 | 280.15 | 0.115 | 289.65 | 0.2
0.1398 | 280.15 | 0.115 | 289.65 | 0.3
0.1398 | 280.15 | 0.115 | 289.65 | 0.4
0.1398 | 280.15 | 0.115 | 289.65 | 0.5
0.1398 | 280.15 | 0.115 | 289.65 | 0.6
0.1398 | 280.15 | 0.115 | 289.65 | 0.7
0.1398 | 280.15 | 0.115 | 289.65 | 0.8
0.1398 | 280.15 | 0.115 | 289.65 | 0.9
0.1398 | 280.15 | 0.115 | 289.65 | 1
0.1398 | 280.15 | 0.115 | 290.15 | 0.15
0.1398 | 280.15 | 0.115 | 290.15 | 0.2
0.1398 | 280.15 | 0.115 | 290.15 | 0.3
0.1398 | 280.15 | 0.115 | 290.15 | 0.4
0.1398 | 280.15 | 0.115 | 290.15 | 0.5
0.1398 | 280.15 | 0.115 | 290.15 | 0.6
0.1398 | 280.15 | 0.115 | 290.15 | 0.7
0.1398 | 280.15 | 0.115 | 290.15 | 0.8
0.1398 | 280.15 | 0.115 | 290.15 | 0.9
0.1398 | 280.15 | 0.115 | 290.15 | 1
0.1398 | 280.15 | 0.115 | 290.65 | 0.15
0.1398 | 280.15 | 0.115 | 290.65 | 0.2
0.1398 | 280.15 | 0.115 | 290.65 | 0.3
0.1398 | 280.15 | 0.115 | 290.65 | 0.4
0.1398 | 280.15 | 0.115 | 290.65 | 0.5
0.1398 | 280.15 | 0.115 | 290.65 | 0.6
0.1398 | 280.15 | 0.115 | 290.65 | 0.7
0.1398 | 280.15 | 0.115 | 290.65 | 0.8
0.1398 | 280.15 | 0.115 | 290.65 | 0.9
0.1398 | 280.15 | 0.115 | 290.65 | 1
0.1398 | 280.15 | 0.115 | 291.15 | 0.15
0.1398 | 280.15 | 0.115 | 291.15 | 0.2
0.1398 | 280.15 | 0.115 | 291.15 | 0.3
0.1398 | 280.15 | 0.115 | 291.15 | 0.4
0.1398 | 280.15 | 0.115 | 291.15 | 0.5
0.1398 | 280.15 | 0.115 | 291.15 | 0.6
0.1398 | 280.15 | 0.115 | 291.15 | 0.7
0.1398 | 280.15 | 0.115 | 291.15 | 0.8
0.1398 | 280.15 | 0.115 | 291.15 | 0.9
0.1398 | 280.15 | 0.115 | 291.15 | 1
0.1398 | 280.15 | 0.115 | 294.15 | 0.15
0.1398 | 280.15 | 0.115 | 294.15 | 0.2
0.1398 | 280.15 | 0.115 | 294.15 | 0.3
0.1398 | 280.15 | 0.115 | 294.15 | 0.4
0.1398 | 280.15 | 0.115 | 294.15 | 0.5
0.1398 | 280.15 | 0.115 | 294.15 | 0.6
0.1398 | 280.15 | 0.115 | 294.15 | 0.7
0.1398 | 280.15 | 0.115 | 294.15 | 0.8
0.1398 | 280.15 | 0.115 | 294.15 | 0.9
0.1398 | 280.15 | 0.115 | 294.15 | 1
0.1398 | 280.15 | 0.115 | 297.15 | 0.15
0.1398 | 280.15 | 0.115 | 297.15 | 0.2
0.1398 | 280.15 | 0.115 | 297.15 | 0.3
0.1398 | 280.15 | 0.115 | 297.15 | 0.4
0.1398 | 280.15 | 0.115 | 297.15 | 0.5
0.1398 | 280.15 | 0.115 | 297.15 | 0.6
0.1398 | 280.15 | 0.115 | 297.15 | 0.7
0.1398 | 280.15 | 0.115 | 297.15 | 0.8
0.1398 | 280.15 | 0.115 | 297.15 | 0.9
0.1398 | 280.15 | 0.115 | 297.15 | 1
0.1398 | 280.15 | 0.115 | 300.15 | 0.15
0.1398 | 280.15 | 0.115 | 300.15 | 0.2
0.1398 | 280.15 | 0.115 | 300.15 | 0.3
0.1398 | 280.15 | 0.115 | 300.15 | 0.4
0.1398 | 280.15 | 0.115 | 300.15 | 0.5
0.1398 | 280.15 | 0.115 | 300.15 | 0.6
0.1398 | 280.15 | 0.115 | 300.15 | 0.7
0.1398 | 280.15 | 0.115 | 300.15 | 0.8
0.1398 | 280.15 | 0.115 | 300.15 | 0.9
0.1398 | 280.15 | 0.115 | 300.15 | 1
0.1398 | 280.15 | 0.115 | 303.15 | 0.15
0.1398 | 280.15 | 0.115 | 303.15 | 0.2
0.1398 | 280.15 | 0.115 | 303.15 | 0.3
0.1398 | 280.15 | 0.115 | 303.15 | 0.4
0.1398 | 280.15 | 0.115 | 303.15 | 0.5
0.1398 | 280.15 | 0.115 | 303.15 | 0.6
0.1398 | 280.15 | 0.115 | 303.15 | 0.7
0.1398 | 280.15 | 0.115 | 303.15 | 0.8
0.1398 | 280.15 | 0.115 | 303.15 | 0.9
0.1398 | 280.15 | 0.115 | 303.15 | 1
0.1398 | 282.15 | 0.00115 | 283.65 | 0.15
0.1398 | 282.15 | 0.00115 | 283.65 | 0.2
0.1398 | 282.15 | 0.00115 | 283.65 | 0.3
0.1398 | 282.15 | 0.00115 | 283.65 | 0.4
0.1398 | 282.15 | 0.00115 | 283.65 | 0.5
0.1398 | 282.15 | 0.00115 | 283.65 | 0.6
0.1398 | 282.15 | 0.00115 | 283.65 | 0.7
0.1398 | 282.15 | 0.00115 | 283.65 | 0.8
0.1398 | 282.15 | 0.00115 | 283.65 | 0.9
0.1398 | 282.15 | 0.00115 | 283.65 | 1
0.1398 | 282.15 | 0.00115 | 284.15 | 0.15
0.1398 | 282.15 | 0.00115 | 284.15 | 0.2
0.1398 | 282.15 | 0.00115 | 284.15 | 0.3
0.1398 | 282.15 | 0.00115 | 284.15 | 0.4
0.1398 | 282.15 | 0.00115 | 284.15 | 0.5
0.1398 | 282.15 | 0.00115 | 284.15 | 0.6
0.1398 | 282.15 | 0.00115 | 284.15 | 0.7
0.1398 | 282.15 | 0.00115 | 284.15 | 0.8
0.1398 | 282.15 | 0.00115 | 284.15 | 0.9
0.1398 | 282.15 | 0.00115 | 284.15 | 1
0.1398 | 282.15 | 0.00115 | 284.65 | 0.15
0.1398 | 282.15 | 0.00115 | 284.65 | 0.2
0.1398 | 282.15 | 0.00115 | 284.65 | 0.3
0.1398 | 282.15 | 0.00115 | 284.65 | 0.4
0.1398 | 282.15 | 0.00115 | 284.65 | 0.5
0.1398 | 282.15 | 0.00115 | 284.65 | 0.6
0.1398 | 282.15 | 0.00115 | 284.65 | 0.7
0.1398 | 282.15 | 0.00115 | 284.65 | 0.8
0.1398 | 282.15 | 0.00115 | 284.65 | 0.9
0.1398 | 282.15 | 0.00115 | 284.65 | 1
0.1398 | 282.15 | 0.00115 | 285.15 | 0.15
0.1398 | 282.15 | 0.00115 | 285.15 | 0.2
0.1398 | 282.15 | 0.00115 | 285.15 | 0.3
0.1398 | 282.15 | 0.00115 | 285.15 | 0.4
0.1398 | 282.15 | 0.00115 | 285.15 | 0.5
0.1398 | 282.15 | 0.00115 | 285.15 | 0.6
0.1398 | 282.15 | 0.00115 | 285.15 | 0.7
0.1398 | 282.15 | 0.00115 | 285.15 | 0.8
0.1398 | 282.15 | 0.00115 | 285.15 | 0.9
0.1398 | 282.15 | 0.00115 | 285.15 | 1
0.1398 | 282.15 | 0.00115 | 285.65 | 0.15
0.1398 | 282.15 | 0.00115 | 285.65 | 0.2
0.1398 | 282.15 | 0.00115 | 285.65 | 0.3
0.1398 | 282.15 | 0.00115 | 285.65 | 0.4
0.1398 | 282.15 | 0.00115 | 285.65 | 0.5
0.1398 | 282.15 | 0.00115 | 285.65 | 0.6
0.1398 | 282.15 | 0.00115 | 285.65 | 0.7
0.1398 | 282.15 | 0.00115 | 285.65 | 0.8
0.1398 | 282.15 | 0.00115 | 285.65 | 0.9
0.1398 | 282.15 | 0.00115 | 285.65 | 1
0.1398 | 282.15 | 0.00115 | 286.15 | 0.15
0.1398 | 282.15 | 0.00115 | 286.15 | 0.2
0.1398 | 282.15 | 0.00115 | 286.15 | 0.3
0.1398 | 282.15 | 0.00115 | 286.15 | 0.4
0.1398 | 282.15 | 0.00115 | 286.15 | 0.5
0.1398 | 282.15 | 0.00115 | 286.15 | 0.6
0.1398 | 282.15 | 0.00115 | 286.15 | 0.7
0.1398 | 282.15 | 0.00115 | 286.15 | 0.8
0.1398 | 282.15 | 0.00115 | 286.15 | 0.9
0.1398 | 282.15 | 0.00115 | 286.15 | 1
0.1398 | 282.15 | 0.00115 | 286.65 | 0.15
0.1398 | 282.15 | 0.00115 | 286.65 | 0.2
0.1398 | 282.15 | 0.00115 | 286.65 | 0.3
0.1398 | 282.15 | 0.00115 | 286.65 | 0.4
0.1398 | 282.15 | 0.00115 | 286.65 | 0.5
0.1398 | 282.15 | 0.00115 | 286.65 | 0.6
0.1398 | 282.15 | 0.00115 | 286.65 | 0.7
0.1398 | 282.15 | 0.00115 | 286.65 | 0.8
0.1398 | 282.15 | 0.00115 | 286.65 | 0.9
0.1398 | 282.15 | 0.00115 | 286.65 | 1
0.1398 | 282.15 | 0.00115 | 287.15 | 0.15
0.1398 | 282.15 | 0.00115 | 287.15 | 0.2
0.1398 | 282.15 | 0.00115 | 287.15 | 0.3
0.1398 | 282.15 | 0.00115 | 287.15 | 0.4
0.1398 | 282.15 | 0.00115 | 287.15 | 0.5
0.1398 | 282.15 | 0.00115 | 287.15 | 0.6
0.1398 | 282.15 | 0.00115 | 287.15 | 0.7
0.1398 | 282.15 | 0.00115 | 287.15 | 0.8
0.1398 | 282.15 | 0.00115 | 287.15 | 0.9
0.1398 | 282.15 | 0.00115 | 287.15 | 1
0.1398 | 282.15 | 0.00115 | 287.65 | 0.15
0.1398 | 282.15 | 0.00115 | 287.65 | 0.2
0.1398 | 282.15 | 0.00115 | 287.65 | 0.3
0.1398 | 282.15 | 0.00115 | 287.65 | 0.4
0.1398 | 282.15 | 0.00115 | 287.65 | 0.5
0.1398 | 282.15 | 0.00115 | 287.65 | 0.6
0.1398 | 282.15 | 0.00115 | 287.65 | 0.7
0.1398 | 282.15 | 0.00115 | 287.65 | 0.8
0.1398 | 282.15 | 0.00115 | 287.65 | 0.9
0.1398 | 282.15 | 0.00115 | 287.65 | 1
0.1398 | 282.15 | 0.00115 | 288.15 | 0.15
0.1398 | 282.15 | 0.00115 | 288.15 | 0.2
0.1398 | 282.15 | 0.00115 | 288.15 | 0.3
0.1398 | 282.15 | 0.00115 | 288.15 | 0.4
0.1398 | 282.15 | 0.00115 | 288.15 | 0.5
0.1398 | 282.15 | 0.00115 | 288.15 | 0.6
0.1398 | 282.15 | 0.00115 | 288.15 | 0.7
0.1398 | 282.15 | 0.00115 | 288.15 | 0.8
0.1398 | 282.15 | 0.00115 | 288.15 | 0.9
0.1398 | 282.15 | 0.00115 | 288.15 | 1
0.1398 | 282.15 | 0.00115 | 288.65 | 0.15
0.1398 | 282.15 | 0.00115 | 288.65 | 0.2
0.1398 | 282.15 | 0.00115 | 288.65 | 0.3
0.1398 | 282.15 | 0.00115 | 288.65 | 0.4
0.1398 | 282.15 | 0.00115 | 288.65 | 0.5
0.1398 | 282.15 | 0.00115 | 288.65 | 0.6
0.1398 | 282.15 | 0.00115 | 288.65 | 0.7
0.1398 | 282.15 | 0.00115 | 288.65 | 0.8
0.1398 | 282.15 | 0.00115 | 288.65 | 0.9
0.1398 | 282.15 | 0.00115 | 288.65 | 1
0.1398 | 282.15 | 0.00115 | 289.15 | 0.15
0.1398 | 282.15 | 0.00115 | 289.15 | 0.2
0.1398 | 282.15 | 0.00115 | 289.15 | 0.3
0.1398 | 282.15 | 0.00115 | 289.15 | 0.4
0.1398 | 282.15 | 0.00115 | 289.15 | 0.5
0.1398 | 282.15 | 0.00115 | 289.15 | 0.6
0.1398 | 282.15 | 0.00115 | 289.15 | 0.7
0.1398 | 282.15 | 0.00115 | 289.15 | 0.8
0.1398 | 282.15 | 0.00115 | 289.15 | 0.9
0.1398 | 282.15 | 0.00115 | 289.15 | 1
0.1398 | 282.15 | 0.00115 | 289.65 | 0.15
0.1398 | 282.15 | 0.00115 | 289.65 | 0.2
0.1398 | 282.15 | 0.00115 | 289.65 | 0.3
0.1398 | 282.15 | 0.00115 | 289.65 | 0.4
0.1398 | 282.15 | 0.00115 | 289.65 | 0.5
0.1398 | 282.15 | 0.00115 | 289.65 | 0.6
0.1398 | 282.15 | 0.00115 | 289.65 | 0.7
0.1398 | 282.15 | 0.00115 | 289.65 | 0.8
0.1398 | 282.15 | 0.00115 | 289.65 | 0.9
0.1398 | 282.15 | 0.00115 | 289.65 | 1
0.1398 | 282.15 | 0.00115 | 290.15 | 0.15
0.1398 | 282.15 | 0.00115 | 290.15 | 0.2
0.1398 | 282.15 | 0.00115 | 290.15 | 0.3
0.1398 | 282.15 | 0.00115 | 290.15 | 0.4
0.1398 | 282.15 | 0.00115 | 290.15 | 0.5
0.1398 | 282.15 | 0.00115 | 290.15 | 0.6
0.1398 | 282.15 | 0.00115 | 290.15 | 0.7
0.1398 | 282.15 | 0.00115 | 290.15 | 0.8
0.1398 | 282.15 | 0.00115 | 290.15 | 0.9
0.1398 | 282.15 | 0.00115 | 290.15 | 1
0.1398 | 282.15 | 0.00115 | 290.65 | 0.15
0.1398 | 282.15 | 0.00115 | 290.65 | 0.2
0.1398 | 282.15 | 0.00115 | 290.65 | 0.3
0.1398 | 282.15 | 0.00115 | 290.65 | 0.4
0.1398 | 282.15 | 0.00115 | 290.65 | 0.5
0.1398 | 282.15 | 0.00115 | 290.65 | 0.6
0.1398 | 282.15 | 0.00115 | 290.65 | 0.7
0.1398 | 282.15 | 0.00115 | 290.65 | 0.8
0.1398 | 282.15 | 0.00115 | 290.65 | 0.9
0.1398 | 282.15 | 0.00115 | 290.65 | 1
0.1398 | 282.15 | 0.00115 | 291.15 | 0.15
0.1398 | 282.15 | 0.00115 | 291.15 | 0.2
0.1398 | 282.15 | 0.00115 | 291.15 | 0.3
0.1398 | 282.15 | 0.00115 | 291.15 | 0.4
0.1398 | 282.15 | 0.00115 | 291.15 | 0.5
0.1398 | 282.15 | 0.00115 | 291.15 | 0.6
0.1398 | 282.15 | 0.00115 | 291.15 | 0.7
0.1398 | 282.15 | 0.00115 | 291.15 | 0.8
0.1398 | 282.15 | 0.00115 | 291.15 | 0.9
0.1398 | 282.15 | 0.00115 | 291.15 | 1
0.1398 | 282.15 | 0.00115 | 294.15 | 0.15
0.1398 | 282.15 | 0.00115 | 294.15 | 0.2
0.1398 | 282.15 | 0.00115 | 294.15 | 0.3
0.1398 | 282.15 | 0.00115 | 294.15 | 0.4
0.1398 | 282.15 | 0.00115 | 294.15 | 0.5
0.1398 | 282.15 | 0.00115 | 294.15 | 0.6
0.1398 | 282.15 | 0.00115 | 294.15 | 0.7
0.1398 | 282.15 | 0.00115 | 294.15 | 0.8
0.1398 | 282.15 | 0.00115 | 294.15 | 0.9
0.1398 | 282.15 | 0.00115 | 294.15 | 1
0.1398 | 282.15 | 0.00115 | 297.15 | 0.15
0.1398 | 282.15 | 0.00115 | 297.15 | 0.2
0.1398 | 282.15 | 0.00115 | 297.15 | 0.3
0.1398 | 282.15 | 0.00115 | 297.15 | 0.4
0.1398 | 282.15 | 0.00115 | 297.15 | 0.5
0.1398 | 282.15 | 0.00115 | 297.15 | 0.6
0.1398 | 282.15 | 0.00115 | 297.15 | 0.7
0.1398 | 282.15 | 0.00115 | 297.15 | 0.8
0.1398 | 282.15 | 0.00115 | 297.15 | 0.9
0.1398 | 282.15 | 0.00115 | 297.15 | 1
0.1398 | 282.15 | 0.00115 | 300.15 | 0.15
0.1398 | 282.15 | 0.00115 | 300.15 | 0.2
0.1398 | 282.15 | 0.00115 | 300.15 | 0.3
0.1398 | 282.15 | 0.00115 | 300.15 | 0.4
0.1398 | 282.15 | 0.00115 | 300.15 | 0.5
0.1398 | 282.15 | 0.00115 | 300.15 | 0.6
0.1398 | 282.15 | 0.00115 | 300.15 | 0.7
0.1398 | 282.15 | 0.00115 | 300.15 | 0.8
0.1398 | 282.15 | 0.00115 | 300.15 | 0.9
0.1398 | 282.15 | 0.00115 | 300.15 | 1
0.1398 | 282.15 | 0.00115 | 303.15 | 0.15
0.1398 | 282.15 | 0.00115 | 303.15 | 0.2
0.1398 | 282.15 | 0.00115 | 303.15 | 0.3
0.1398 | 282.15 | 0.00115 | 303.15 | 0.4
0.1398 | 282.15 | 0.00115 | 303.15 | 0.5
0.1398 | 282.15 | 0.00115 | 303.15 | 0.6
0.1398 | 282.15 | 0.00115 | 303.15 | 0.7
0.1398 | 282.15 | 0.00115 | 303.15 | 0.8
0.1398 | 282.15 | 0.00115 | 303.15 | 0.9
0.1398 | 282.15 | 0.00115 | 303.15 | 1
0.1398 | 282.15 | 0.077 | 283.65 | 0.15
0.1398 | 282.15 | 0.077 | 283.65 | 0.2
0.1398 | 282.15 | 0.077 | 283.65 | 0.3
0.1398 | 282.15 | 0.077 | 283.65 | 0.4
0.1398 | 282.15 | 0.077 | 283.65 | 0.5
0.1398 | 282.15 | 0.077 | 283.65 | 0.6
0.1398 | 282.15 | 0.077 | 283.65 | 0.7
0.1398 | 282.15 | 0.077 | 283.65 | 0.8
0.1398 | 282.15 | 0.077 | 283.65 | 0.9
0.1398 | 282.15 | 0.077 | 283.65 | 1
0.1398 | 282.15 | 0.077 | 284.15 | 0.15
0.1398 | 282.15 | 0.077 | 284.15 | 0.2
0.1398 | 282.15 | 0.077 | 284.15 | 0.3
0.1398 | 282.15 | 0.077 | 284.15 | 0.4
0.1398 | 282.15 | 0.077 | 284.15 | 0.5
0.1398 | 282.15 | 0.077 | 284.15 | 0.6
0.1398 | 282.15 | 0.077 | 284.15 | 0.7
0.1398 | 282.15 | 0.077 | 284.15 | 0.8
0.1398 | 282.15 | 0.077 | 284.15 | 0.9
0.1398 | 282.15 | 0.077 | 284.15 | 1
0.1398 | 282.15 | 0.077 | 284.65 | 0.15
0.1398 | 282.15 | 0.077 | 284.65 | 0.2
0.1398 | 282.15 | 0.077 | 284.65 | 0.3
0.1398 | 282.15 | 0.077 | 284.65 | 0.4
0.1398 | 282.15 | 0.077 | 284.65 | 0.5
0.1398 | 282.15 | 0.077 | 284.65 | 0.6
0.1398 | 282.15 | 0.077 | 284.65 | 0.7
0.1398 | 282.15 | 0.077 | 284.65 | 0.8
0.1398 | 282.15 | 0.077 | 284.65 | 0.9
0.1398 | 282.15 | 0.077 | 284.65 | 1
0.1398 | 282.15 | 0.077 | 285.15 | 0.15
0.1398 | 282.15 | 0.077 | 285.15 | 0.2
0.1398 | 282.15 | 0.077 | 285.15 | 0.3
0.1398 | 282.15 | 0.077 | 285.15 | 0.4
0.1398 | 282.15 | 0.077 | 285.15 | 0.5
0.1398 | 282.15 | 0.077 | 285.15 | 0.6
0.1398 | 282.15 | 0.077 | 285.15 | 0.7
0.1398 | 282.15 | 0.077 | 285.15 | 0.8
0.1398 | 282.15 | 0.077 | 285.15 | 0.9
0.1398 | 282.15 | 0.077 | 285.15 | 1
0.1398 | 282.15 | 0.077 | 285.65 | 0.15
0.1398 | 282.15 | 0.077 | 285.65 | 0.2
0.1398 | 282.15 | 0.077 | 285.65 | 0.3
0.1398 | 282.15 | 0.077 | 285.65 | 0.4
0.1398 | 282.15 | 0.077 | 285.65 | 0.5
0.1398 | 282.15 | 0.077 | 285.65 | 0.6
0.1398 | 282.15 | 0.077 | 285.65 | 0.7
0.1398 | 282.15 | 0.077 | 285.65 | 0.8
0.1398 | 282.15 | 0.077 | 285.65 | 0.9
0.1398 | 282.15 | 0.077 | 285.65 | 1
0.1398 | 282.15 | 0.077 | 286.15 | 0.15
0.1398 | 282.15 | 0.077 | 286.15 | 0.2
0.1398 | 282.15 | 0.077 | 286.15 | 0.3
0.1398 | 282.15 | 0.077 | 286.15 | 0.4
0.1398 | 282.15 | 0.077 | 286.15 | 0.5
0.1398 | 282.15 | 0.077 | 286.15 | 0.6
0.1398 | 282.15 | 0.077 | 286.15 | 0.7
0.1398 | 282.15 | 0.077 | 286.15 | 0.8
0.1398 | 282.15 | 0.077 | 286.15 | 0.9
0.1398 | 282.15 | 0.077 | 286.15 | 1
0.1398 | 282.15 | 0.077 | 286.65 | 0.15
0.1398 | 282.15 | 0.077 | 286.65 | 0.2
0.1398 | 282.15 | 0.077 | 286.65 | 0.3
0.1398 | 282.15 | 0.077 | 286.65 | 0.4
0.1398 | 282.15 | 0.077 | 286.65 | 0.5
0.1398 | 282.15 | 0.077 | 286.65 | 0.6
0.1398 | 282.15 | 0.077 | 286.65 | 0.7
0.1398 | 282.15 | 0.077 | 286.65 | 0.8
0.1398 | 282.15 | 0.077 | 286.65 | 0.9
0.1398 | 282.15 | 0.077 | 286.65 | 1
0.1398 | 282.15 | 0.077 | 287.15 | 0.15
0.1398 | 282.15 | 0.077 | 287.15 | 0.2
0.1398 | 282.15 | 0.077 | 287.15 | 0.3
0.1398 | 282.15 | 0.077 | 287.15 | 0.4
0.1398 | 282.15 | 0.077 | 287.15 | 0.5
0.1398 | 282.15 | 0.077 | 287.15 | 0.6
0.1398 | 282.15 | 0.077 | 287.15 | 0.7
0.1398 | 282.15 | 0.077 | 287.15 | 0.8
0.1398 | 282.15 | 0.077 | 287.15 | 0.9
0.1398 | 282.15 | 0.077 | 287.15 | 1
0.1398 | 282.15 | 0.077 | 287.65 | 0.15
0.1398 | 282.15 | 0.077 | 287.65 | 0.2
0.1398 | 282.15 | 0.077 | 287.65 | 0.3
0.1398 | 282.15 | 0.077 | 287.65 | 0.4
0.1398 | 282.15 | 0.077 | 287.65 | 0.5
0.1398 | 282.15 | 0.077 | 287.65 | 0.6
0.1398 | 282.15 | 0.077 | 287.65 | 0.7
0.1398 | 282.15 | 0.077 | 287.65 | 0.8
0.1398 | 282.15 | 0.077 | 287.65 | 0.9
0.1398 | 282.15 | 0.077 | 287.65 | 1
0.1398 | 282.15 | 0.077 | 288.15 | 0.15
0.1398 | 282.15 | 0.077 | 288.15 | 0.2
0.1398 | 282.15 | 0.077 | 288.15 | 0.3
0.1398 | 282.15 | 0.077 | 288.15 | 0.4
0.1398 | 282.15 | 0.077 | 288.15 | 0.5
0.1398 | 282.15 | 0.077 | 288.15 | 0.6
0.1398 | 282.15 | 0.077 | 288.15 | 0.7
0.1398 | 282.15 | 0.077 | 288.15 | 0.8
0.1398 | 282.15 | 0.077 | 288.15 | 0.9
0.1398 | 282.15 | 0.077 | 288.15 | 1
0.1398 | 282.15 | 0.077 | 288.65 | 0.15
0.1398 | 282.15 | 0.077 | 288.65 | 0.2
0.1398 | 282.15 | 0.077 | 288.65 | 0.3
0.1398 | 282.15 | 0.077 | 288.65 | 0.4
0.1398 | 282.15 | 0.077 | 288.65 | 0.5
0.1398 | 282.15 | 0.077 | 288.65 | 0.6
0.1398 | 282.15 | 0.077 | 288.65 | 0.7
0.1398 | 282.15 | 0.077 | 288.65 | 0.8
0.1398 | 282.15 | 0.077 | 288.65 | 0.9
0.1398 | 282.15 | 0.077 | 288.65 | 1
0.1398 | 282.15 | 0.077 | 289.15 | 0.15
0.1398 | 282.15 | 0.077 | 289.15 | 0.2
0.1398 | 282.15 | 0.077 | 289.15 | 0.3
0.1398 | 282.15 | 0.077 | 289.15 | 0.4
0.1398 | 282.15 | 0.077 | 289.15 | 0.5
0.1398 | 282.15 | 0.077 | 289.15 | 0.6
0.1398 | 282.15 | 0.077 | 289.15 | 0.7
0.1398 | 282.15 | 0.077 | 289.15 | 0.8
0.1398 | 282.15 | 0.077 | 289.15 | 0.9
0.1398 | 282.15 | 0.077 | 289.15 | 1
0.1398 | 282.15 | 0.077 | 289.65 | 0.15
0.1398 | 282.15 | 0.077 | 289.65 | 0.2
0.1398 | 282.15 | 0.077 | 289.65 | 0.3
0.1398 | 282.15 | 0.077 | 289.65 | 0.4
0.1398 | 282.15 | 0.077 | 289.65 | 0.5
0.1398 | 282.15 | 0.077 | 289.65 | 0.6
0.1398 | 282.15 | 0.077 | 289.65 | 0.7
0.1398 | 282.15 | 0.077 | 289.65 | 0.8
0.1398 | 282.15 | 0.077 | 289.65 | 0.9
0.1398 | 282.15 | 0.077 | 289.65 | 1
0.1398 | 282.15 | 0.077 | 290.15 | 0.15
0.1398 | 282.15 | 0.077 | 290.15 | 0.2
0.1398 | 282.15 | 0.077 | 290.15 | 0.3
0.1398 | 282.15 | 0.077 | 290.15 | 0.4
0.1398 | 282.15 | 0.077 | 290.15 | 0.5
0.1398 | 282.15 | 0.077 | 290.15 | 0.6
0.1398 | 282.15 | 0.077 | 290.15 | 0.7
0.1398 | 282.15 | 0.077 | 290.15 | 0.8
0.1398 | 282.15 | 0.077 | 290.15 | 0.9
0.1398 | 282.15 | 0.077 | 290.15 | 1
0.1398 | 282.15 | 0.077 | 290.65 | 0.15
0.1398 | 282.15 | 0.077 | 290.65 | 0.2
0.1398 | 282.15 | 0.077 | 290.65 | 0.3
0.1398 | 282.15 | 0.077 | 290.65 | 0.4
0.1398 | 282.15 | 0.077 | 290.65 | 0.5
0.1398 | 282.15 | 0.077 | 290.65 | 0.6
0.1398 | 282.15 | 0.077 | 290.65 | 0.7
0.1398 | 282.15 | 0.077 | 290.65 | 0.8
0.1398 | 282.15 | 0.077 | 290.65 | 0.9
0.1398 | 282.15 | 0.077 | 290.65 | 1
0.1398 | 282.15 | 0.077 | 291.15 | 0.15
0.1398 | 282.15 | 0.077 | 291.15 | 0.2
0.1398 | 282.15 | 0.077 | 291.15 | 0.3
0.1398 | 282.15 | 0.077 | 291.15 | 0.4
0.1398 | 282.15 | 0.077 | 291.15 | 0.5
0.1398 | 282.15 | 0.077 | 291.15 | 0.6
0.1398 | 282.15 | 0.077 | 291.15 | 0.7
0.1398 | 282.15 | 0.077 | 291.15 | 0.8
0.1398 | 282.15 | 0.077 | 291.15 | 0.9
0.1398 | 282.15 | 0.077 | 291.15 | 1
0.1398 | 282.15 | 0.077 | 294.15 | 0.15
0.1398 | 282.15 | 0.077 | 294.15 | 0.2
0.1398 | 282.15 | 0.077 | 294.15 | 0.3
0.1398 | 282.15 | 0.077 | 294.15 | 0.4
0.1398 | 282.15 | 0.077 | 294.15 | 0.5
0.1398 | 282.15 | 0.077 | 294.15 | 0.6
0.1398 | 282.15 | 0.077 | 294.15 | 0.7
0.1398 | 282.15 | 0.077 | 294.15 | 0.8
0.1398 | 282.15 | 0.077 | 294.15 | 0.9
0.1398 | 282.15 | 0.077 | 294.15 | 1
0.1398 | 282.15 | 0.077 | 297.15 | 0.15
0.1398 | 282.15 | 0.077 | 297.15 | 0.2
0.1398 | 282.15 | 0.077 | 297.15 | 0.3
0.1398 | 282.15 | 0.077 | 297.15 | 0.4
0.1398 | 282.15 | 0.077 | 297.15 | 0.5
0.1398 | 282.15 | 0.077 | 297.15 | 0.6
0.1398 | 282.15 | 0.077 | 297.15 | 0.7
0.1398 | 282.15 | 0.077 | 297.15 | 0.8
0.1398 | 282.15 | 0.077 | 297.15 | 0.9
0.1398 | 282.15 | 0.077 | 297.15 | 1
0.1398 | 282.15 | 0.077 | 300.15 | 0.15
0.1398 | 282.15 | 0.077 | 300.15 | 0.2
0.1398 | 282.15 | 0.077 | 300.15 | 0.3
0.1398 | 282.15 | 0.077 | 300.15 | 0.4
0.1398 | 282.15 | 0.077 | 300.15 | 0.5
0.1398 | 282.15 | 0.077 | 300.15 | 0.6
0.1398 | 282.15 | 0.077 | 300.15 | 0.7
0.1398 | 282.15 | 0.077 | 300.15 | 0.8
0.1398 | 282.15 | 0.077 | 300.15 | 0.9
0.1398 | 282.15 | 0.077 | 300.15 | 1
0.1398 | 282.15 | 0.077 | 303.15 | 0.15
0.1398 | 282.15 | 0.077 | 303.15 | 0.2
0.1398 | 282.15 | 0.077 | 303.15 | 0.3
0.1398 | 282.15 | 0.077 | 303.15 | 0.4
0.1398 | 282.15 | 0.077 | 303.15 | 0.5
0.1398 | 282.15 | 0.077 | 303.15 | 0.6
0.1398 | 282.15 | 0.077 | 303.15 | 0.7
0.1398 | 282.15 | 0.077 | 303.15 | 0.8
0.1398 | 282.15 | 0.077 | 303.15 | 0.9
0.1398 | 282.15 | 0.077 | 303.15 | 1
0.1398 | 282.15 | 0.09437 | 283.65 | 0.15
0.1398 | 282.15 | 0.09437 | 283.65 | 0.2
0.1398 | 282.15 | 0.09437 | 283.65 | 0.3
0.1398 | 282.15 | 0.09437 | 283.65 | 0.4
0.1398 | 282.15 | 0.09437 | 283.65 | 0.5
0.1398 | 282.15 | 0.09437 | 283.65 | 0.6
0.1398 | 282.15 | 0.09437 | 283.65 | 0.7
0.1398 | 282.15 | 0.09437 | 283.65 | 0.8
0.1398 | 282.15 | 0.09437 | 283.65 | 0.9
0.1398 | 282.15 | 0.09437 | 283.65 | 1
0.1398 | 282.15 | 0.09437 | 284.15 | 0.15
0.1398 | 282.15 | 0.09437 | 284.15 | 0.2
0.1398 | 282.15 | 0.09437 | 284.15 | 0.3
0.1398 | 282.15 | 0.09437 | 284.15 | 0.4
0.1398 | 282.15 | 0.09437 | 284.15 | 0.5
0.1398 | 282.15 | 0.09437 | 284.15 | 0.6
0.1398 | 282.15 | 0.09437 | 284.15 | 0.7
0.1398 | 282.15 | 0.09437 | 284.15 | 0.8
0.1398 | 282.15 | 0.09437 | 284.15 | 0.9
0.1398 | 282.15 | 0.09437 | 284.15 | 1
0.1398 | 282.15 | 0.09437 | 284.65 | 0.15
0.1398 | 282.15 | 0.09437 | 284.65 | 0.2
0.1398 | 282.15 | 0.09437 | 284.65 | 0.3
0.1398 | 282.15 | 0.09437 | 284.65 | 0.4
0.1398 | 282.15 | 0.09437 | 284.65 | 0.5
0.1398 | 282.15 | 0.09437 | 284.65 | 0.6
0.1398 | 282.15 | 0.09437 | 284.65 | 0.7
0.1398 | 282.15 | 0.09437 | 284.65 | 0.8
0.1398 | 282.15 | 0.09437 | 284.65 | 0.9
0.1398 | 282.15 | 0.09437 | 284.65 | 1
0.1398 | 282.15 | 0.09437 | 285.15 | 0.15
0.1398 | 282.15 | 0.09437 | 285.15 | 0.2
0.1398 | 282.15 | 0.09437 | 285.15 | 0.3
0.1398 | 282.15 | 0.09437 | 285.15 | 0.4
0.1398 | 282.15 | 0.09437 | 285.15 | 0.5
0.1398 | 282.15 | 0.09437 | 285.15 | 0.6
0.1398 | 282.15 | 0.09437 | 285.15 | 0.7
0.1398 | 282.15 | 0.09437 | 285.15 | 0.8
0.1398 | 282.15 | 0.09437 | 285.15 | 0.9
0.1398 | 282.15 | 0.09437 | 285.15 | 1
0.1398 | 282.15 | 0.09437 | 285.65 | 0.15
0.1398 | 282.15 | 0.09437 | 285.65 | 0.2
0.1398 | 282.15 | 0.09437 | 285.65 | 0.3
0.1398 | 282.15 | 0.09437 | 285.65 | 0.4
0.1398 | 282.15 | 0.09437 | 285.65 | 0.5
0.1398 | 282.15 | 0.09437 | 285.65 | 0.6
0.1398 | 282.15 | 0.09437 | 285.65 | 0.7
0.1398 | 282.15 | 0.09437 | 285.65 | 0.8
0.1398 | 282.15 | 0.09437 | 285.65 | 0.9
0.1398 | 282.15 | 0.09437 | 285.65 | 1
0.1398 | 282.15 | 0.09437 | 286.15 | 0.15
0.1398 | 282.15 | 0.09437 | 286.15 | 0.2
0.1398 | 282.15 | 0.09437 | 286.15 | 0.3
0.1398 | 282.15 | 0.09437 | 286.15 | 0.4
0.1398 | 282.15 | 0.09437 | 286.15 | 0.5
0.1398 | 282.15 | 0.09437 | 286.15 | 0.6
0.1398 | 282.15 | 0.09437 | 286.15 | 0.7
0.1398 | 282.15 | 0.09437 | 286.15 | 0.8
0.1398 | 282.15 | 0.09437 | 286.15 | 0.9
0.1398 | 282.15 | 0.09437 | 286.15 | 1
0.1398 | 282.15 | 0.09437 | 286.65 | 0.15
0.1398 | 282.15 | 0.09437 | 286.65 | 0.2
0.1398 | 282.15 | 0.09437 | 286.65 | 0.3
0.1398 | 282.15 | 0.09437 | 286.65 | 0.4
0.1398 | 282.15 | 0.09437 | 286.65 | 0.5
0.1398 | 282.15 | 0.09437 | 286.65 | 0.6
0.1398 | 282.15 | 0.09437 | 286.65 | 0.7
0.1398 | 282.15 | 0.09437 | 286.65 | 0.8
0.1398 | 282.15 | 0.09437 | 286.65 | 0.9
0.1398 | 282.15 | 0.09437 | 286.65 | 1
0.1398 | 282.15 | 0.09437 | 287.15 | 0.15
0.1398 | 282.15 | 0.09437 | 287.15 | 0.2
0.1398 | 282.15 | 0.09437 | 287.15 | 0.3
0.1398 | 282.15 | 0.09437 | 287.15 | 0.4
0.1398 | 282.15 | 0.09437 | 287.15 | 0.5
0.1398 | 282.15 | 0.09437 | 287.15 | 0.6
0.1398 | 282.15 | 0.09437 | 287.15 | 0.7
0.1398 | 282.15 | 0.09437 | 287.15 | 0.8
0.1398 | 282.15 | 0.09437 | 287.15 | 0.9
0.1398 | 282.15 | 0.09437 | 287.15 | 1
0.1398 | 282.15 | 0.09437 | 287.65 | 0.15
0.1398 | 282.15 | 0.09437 | 287.65 | 0.2
0.1398 | 282.15 | 0.09437 | 287.65 | 0.3
0.1398 | 282.15 | 0.09437 | 287.65 | 0.4
0.1398 | 282.15 | 0.09437 | 287.65 | 0.5
0.1398 | 282.15 | 0.09437 | 287.65 | 0.6
0.1398 | 282.15 | 0.09437 | 287.65 | 0.7
0.1398 | 282.15 | 0.09437 | 287.65 | 0.8
0.1398 | 282.15 | 0.09437 | 287.65 | 0.9
0.1398 | 282.15 | 0.09437 | 287.65 | 1
0.1398 | 282.15 | 0.09437 | 288.15 | 0.15
0.1398 | 282.15 | 0.09437 | 288.15 | 0.2
0.1398 | 282.15 | 0.09437 | 288.15 | 0.3
0.1398 | 282.15 | 0.09437 | 288.15 | 0.4
0.1398 | 282.15 | 0.09437 | 288.15 | 0.5
0.1398 | 282.15 | 0.09437 | 288.15 | 0.6
0.1398 | 282.15 | 0.09437 | 288.15 | 0.7
0.1398 | 282.15 | 0.09437 | 288.15 | 0.8
0.1398 | 282.15 | 0.09437 | 288.15 | 0.9
0.1398 | 282.15 | 0.09437 | 288.15 | 1
0.1398 | 282.15 | 0.09437 | 288.65 | 0.15
0.1398 | 282.15 | 0.09437 | 288.65 | 0.2
0.1398 | 282.15 | 0.09437 | 288.65 | 0.3
0.1398 | 282.15 | 0.09437 | 288.65 | 0.4
0.1398 | 282.15 | 0.09437 | 288.65 | 0.5
0.1398 | 282.15 | 0.09437 | 288.65 | 0.6
0.1398 | 282.15 | 0.09437 | 288.65 | 0.7
0.1398 | 282.15 | 0.09437 | 288.65 | 0.8
0.1398 | 282.15 | 0.09437 | 288.65 | 0.9
0.1398 | 282.15 | 0.09437 | 288.65 | 1
0.1398 | 282.15 | 0.09437 | 289.15 | 0.15
0.1398 | 282.15 | 0.09437 | 289.15 | 0.2
0.1398 | 282.15 | 0.09437 | 289.15 | 0.3
0.1398 | 282.15 | 0.09437 | 289.15 | 0.4
0.1398 | 282.15 | 0.09437 | 289.15 | 0.5
0.1398 | 282.15 | 0.09437 | 289.15 | 0.6
0.1398 | 282.15 | 0.09437 | 289.15 | 0.7
0.1398 | 282.15 | 0.09437 | 289.15 | 0.8
0.1398 | 282.15 | 0.09437 | 289.15 | 0.9
0.1398 | 282.15 | 0.09437 | 289.15 | 1
0.1398 | 282.15 | 0.09437 | 289.65 | 0.15
0.1398 | 282.15 | 0.09437 | 289.65 | 0.2
0.1398 | 282.15 | 0.09437 | 289.65 | 0.3
0.1398 | 282.15 | 0.09437 | 289.65 | 0.4
0.1398 | 282.15 | 0.09437 | 289.65 | 0.5
0.1398 | 282.15 | 0.09437 | 289.65 | 0.6
0.1398 | 282.15 | 0.09437 | 289.65 | 0.7
0.1398 | 282.15 | 0.09437 | 289.65 | 0.8
0.1398 | 282.15 | 0.09437 | 289.65 | 0.9
0.1398 | 282.15 | 0.09437 | 289.65 | 1
0.1398 | 282.15 | 0.09437 | 290.15 | 0.15
0.1398 | 282.15 | 0.09437 | 290.15 | 0.2
0.1398 | 282.15 | 0.09437 | 290.15 | 0.3
0.1398 | 282.15 | 0.09437 | 290.15 | 0.4
0.1398 | 282.15 | 0.09437 | 290.15 | 0.5
0.1398 | 282.15 | 0.09437 | 290.15 | 0.6
0.1398 | 282.15 | 0.09437 | 290.15 | 0.7
0.1398 | 282.15 | 0.09437 | 290.15 | 0.8
0.1398 | 282.15 | 0.09437 | 290.15 | 0.9
0.1398 | 282.15 | 0.09437 | 290.15 | 1
0.1398 | 282.15 | 0.09437 | 290.65 | 0.15
0.1398 | 282.15 | 0.09437 | 290.65 | 0.2
0.1398 | 282.15 | 0.09437 | 290.65 | 0.3
0.1398 | 282.15 | 0.09437 | 290.65 | 0.4
0.1398 | 282.15 | 0.09437 | 290.65 | 0.5
0.1398 | 282.15 | 0.09437 | 290.65 | 0.6
0.1398 | 282.15 | 0.09437 | 290.65 | 0.7
0.1398 | 282.15 | 0.09437 | 290.65 | 0.8
0.1398 | 282.15 | 0.09437 | 290.65 | 0.9
0.1398 | 282.15 | 0.09437 | 290.65 | 1
0.1398 | 282.15 | 0.09437 | 291.15 | 0.15
0.1398 | 282.15 | 0.09437 | 291.15 | 0.2
0.1398 | 282.15 | 0.09437 | 291.15 | 0.3
0.1398 | 282.15 | 0.09437 | 291.15 | 0.4
0.1398 | 282.15 | 0.09437 | 291.15 | 0.5
0.1398 | 282.15 | 0.09437 | 291.15 | 0.6
0.1398 | 282.15 | 0.09437 | 291.15 | 0.7
0.1398 | 282.15 | 0.09437 | 291.15 | 0.8
0.1398 | 282.15 | 0.09437 | 291.15 | 0.9
0.1398 | 282.15 | 0.09437 | 291.15 | 1
0.1398 | 282.15 | 0.09437 | 294.15 | 0.15
0.1398 | 282.15 | 0.09437 | 294.15 | 0.2
0.1398 | 282.15 | 0.09437 | 294.15 | 0.3
0.1398 | 282.15 | 0.09437 | 294.15 | 0.4
0.1398 | 282.15 | 0.09437 | 294.15 | 0.5
0.1398 | 282.15 | 0.09437 | 294.15 | 0.6
0.1398 | 282.15 | 0.09437 | 294.15 | 0.7
0.1398 | 282.15 | 0.09437 | 294.15 | 0.8
0.1398 | 282.15 | 0.09437 | 294.15 | 0.9
0.1398 | 282.15 | 0.09437 | 294.15 | 1
0.1398 | 282.15 | 0.09437 | 297.15 | 0.15
0.1398 | 282.15 | 0.09437 | 297.15 | 0.2
0.1398 | 282.15 | 0.09437 | 297.15 | 0.3
0.1398 | 282.15 | 0.09437 | 297.15 | 0.4
0.1398 | 282.15 | 0.09437 | 297.15 | 0.5
0.1398 | 282.15 | 0.09437 | 297.15 | 0.6
0.1398 | 282.15 | 0.09437 | 297.15 | 0.7
0.1398 | 282.15 | 0.09437 | 297.15 | 0.8
0.1398 | 282.15 | 0.09437 | 297.15 | 0.9
0.1398 | 282.15 | 0.09437 | 297.15 | 1
0.1398 | 282.15 | 0.09437 | 300.15 | 0.15
0.1398 | 282.15 | 0.09437 | 300.15 | 0.2
0.1398 | 282.15 | 0.09437 | 300.15 | 0.3
0.1398 | 282.15 | 0.09437 | 300.15 | 0.4
0.1398 | 282.15 | 0.09437 | 300.15 | 0.5
0.1398 | 282.15 | 0.09437 | 300.15 | 0.6
0.1398 | 282.15 | 0.09437 | 300.15 | 0.7
0.1398 | 282.15 | 0.09437 | 300.15 | 0.8
0.1398 | 282.15 | 0.09437 | 300.15 | 0.9
0.1398 | 282.15 | 0.09437 | 300.15 | 1
0.1398 | 282.15 | 0.09437 | 303.15 | 0.15
0.1398 | 282.15 | 0.09437 | 303.15 | 0.2
0.1398 | 282.15 | 0.09437 | 303.15 | 0.3
0.1398 | 282.15 | 0.09437 | 303.15 | 0.4
0.1398 | 282.15 | 0.09437 | 303.15 | 0.5
0.1398 | 282.15 | 0.09437 | 303.15 | 0.6
0.1398 | 282.15 | 0.09437 | 303.15 | 0.7
0.1398 | 282.15 | 0.09437 | 303.15 | 0.8
0.1398 | 282.15 | 0.09437 | 303.15 | 0.9
0.1398 | 282.15 | 0.09437 | 303.15 | 1
0.1398 | 282.15 | 0.09644 | 283.65 | 0.15
0.1398 | 282.15 | 0.09644 | 283.65 | 0.2
0.1398 | 282.15 | 0.09644 | 283.65 | 0.3
0.1398 | 282.15 | 0.09644 | 283.65 | 0.4
0.1398 | 282.15 | 0.09644 | 283.65 | 0.5
0.1398 | 282.15 | 0.09644 | 283.65 | 0.6
0.1398 | 282.15 | 0.09644 | 283.65 | 0.7
0.1398 | 282.15 | 0.09644 | 283.65 | 0.8
0.1398 | 282.15 | 0.09644 | 283.65 | 0.9
0.1398 | 282.15 | 0.09644 | 283.65 | 1
0.1398 | 282.15 | 0.09644 | 284.15 | 0.15
0.1398 | 282.15 | 0.09644 | 284.15 | 0.2
0.1398 | 282.15 | 0.09644 | 284.15 | 0.3
0.1398 | 282.15 | 0.09644 | 284.15 | 0.4
0.1398 | 282.15 | 0.09644 | 284.15 | 0.5
0.1398 | 282.15 | 0.09644 | 284.15 | 0.6
0.1398 | 282.15 | 0.09644 | 284.15 | 0.7
0.1398 | 282.15 | 0.09644 | 284.15 | 0.8
0.1398 | 282.15 | 0.09644 | 284.15 | 0.9
0.1398 | 282.15 | 0.09644 | 284.15 | 1
0.1398 | 282.15 | 0.09644 | 284.65 | 0.15
0.1398 | 282.15 | 0.09644 | 284.65 | 0.2
0.1398 | 282.15 | 0.09644 | 284.65 | 0.3
0.1398 | 282.15 | 0.09644 | 284.65 | 0.4
0.1398 | 282.15 | 0.09644 | 284.65 | 0.5
0.1398 | 282.15 | 0.09644 | 284.65 | 0.6
0.1398 | 282.15 | 0.09644 | 284.65 | 0.7
0.1398 | 282.15 | 0.09644 | 284.65 | 0.8
0.1398 | 282.15 | 0.09644 | 284.65 | 0.9
0.1398 | 282.15 | 0.09644 | 284.65 | 1
0.1398 | 282.15 | 0.09644 | 285.15 | 0.15
0.1398 | 282.15 | 0.09644 | 285.15 | 0.2
0.1398 | 282.15 | 0.09644 | 285.15 | 0.3
0.1398 | 282.15 | 0.09644 | 285.15 | 0.4
0.1398 | 282.15 | 0.09644 | 285.15 | 0.5
0.1398 | 282.15 | 0.09644 | 285.15 | 0.6
0.1398 | 282.15 | 0.09644 | 285.15 | 0.7
0.1398 | 282.15 | 0.09644 | 285.15 | 0.8
0.1398 | 282.15 | 0.09644 | 285.15 | 0.9
0.1398 | 282.15 | 0.09644 | 285.15 | 1
0.1398 | 282.15 | 0.09644 | 285.65 | 0.15
0.1398 | 282.15 | 0.09644 | 285.65 | 0.2
0.1398 | 282.15 | 0.09644 | 285.65 | 0.3
0.1398 | 282.15 | 0.09644 | 285.65 | 0.4
0.1398 | 282.15 | 0.09644 | 285.65 | 0.5
0.1398 | 282.15 | 0.09644 | 285.65 | 0.6
0.1398 | 282.15 | 0.09644 | 285.65 | 0.7
0.1398 | 282.15 | 0.09644 | 285.65 | 0.8
0.1398 | 282.15 | 0.09644 | 285.65 | 0.9
0.1398 | 282.15 | 0.09644 | 285.65 | 1
0.1398 | 282.15 | 0.09644 | 286.15 | 0.15
0.1398 | 282.15 | 0.09644 | 286.15 | 0.2
0.1398 | 282.15 | 0.09644 | 286.15 | 0.3
0.1398 | 282.15 | 0.09644 | 286.15 | 0.4
0.1398 | 282.15 | 0.09644 | 286.15 | 0.5
0.1398 | 282.15 | 0.09644 | 286.15 | 0.6
0.1398 | 282.15 | 0.09644 | 286.15 | 0.7
0.1398 | 282.15 | 0.09644 | 286.15 | 0.8
0.1398 | 282.15 | 0.09644 | 286.15 | 0.9
0.1398 | 282.15 | 0.09644 | 286.15 | 1
0.1398 | 282.15 | 0.09644 | 286.65 | 0.15
0.1398 | 282.15 | 0.09644 | 286.65 | 0.2
0.1398 | 282.15 | 0.09644 | 286.65 | 0.3
0.1398 | 282.15 | 0.09644 | 286.65 | 0.4
0.1398 | 282.15 | 0.09644 | 286.65 | 0.5
0.1398 | 282.15 | 0.09644 | 286.65 | 0.6
0.1398 | 282.15 | 0.09644 | 286.65 | 0.7
0.1398 | 282.15 | 0.09644 | 286.65 | 0.8
0.1398 | 282.15 | 0.09644 | 286.65 | 0.9
0.1398 | 282.15 | 0.09644 | 286.65 | 1
0.1398 | 282.15 | 0.09644 | 287.15 | 0.15
0.1398 | 282.15 | 0.09644 | 287.15 | 0.2
0.1398 | 282.15 | 0.09644 | 287.15 | 0.3
0.1398 | 282.15 | 0.09644 | 287.15 | 0.4
0.1398 | 282.15 | 0.09644 | 287.15 | 0.5
0.1398 | 282.15 | 0.09644 | 287.15 | 0.6
0.1398 | 282.15 | 0.09644 | 287.15 | 0.7
0.1398 | 282.15 | 0.09644 | 287.15 | 0.8
0.1398 | 282.15 | 0.09644 | 287.15 | 0.9
0.1398 | 282.15 | 0.09644 | 287.15 | 1
0.1398 | 282.15 | 0.09644 | 287.65 | 0.15
0.1398 | 282.15 | 0.09644 | 287.65 | 0.2
0.1398 | 282.15 | 0.09644 | 287.65 | 0.3
0.1398 | 282.15 | 0.09644 | 287.65 | 0.4
0.1398 | 282.15 | 0.09644 | 287.65 | 0.5
0.1398 | 282.15 | 0.09644 | 287.65 | 0.6
0.1398 | 282.15 | 0.09644 | 287.65 | 0.7
0.1398 | 282.15 | 0.09644 | 287.65 | 0.8
0.1398 | 282.15 | 0.09644 | 287.65 | 0.9
0.1398 | 282.15 | 0.09644 | 287.65 | 1
0.1398 | 282.15 | 0.09644 | 288.15 | 0.15
0.1398 | 282.15 | 0.09644 | 288.15 | 0.2
0.1398 | 282.15 | 0.09644 | 288.15 | 0.3
0.1398 | 282.15 | 0.09644 | 288.15 | 0.4
0.1398 | 282.15 | 0.09644 | 288.15 | 0.5
0.1398 | 282.15 | 0.09644 | 288.15 | 0.6
0.1398 | 282.15 | 0.09644 | 288.15 | 0.7
0.1398 | 282.15 | 0.09644 | 288.15 | 0.8
0.1398 | 282.15 | 0.09644 | 288.15 | 0.9
0.1398 | 282.15 | 0.09644 | 288.15 | 1
0.1398 | 282.15 | 0.09644 | 288.65 | 0.15
0.1398 | 282.15 | 0.09644 | 288.65 | 0.2
0.1398 | 282.15 | 0.09644 | 288.65 | 0.3
0.1398 | 282.15 | 0.09644 | 288.65 | 0.4
0.1398 | 282.15 | 0.09644 | 288.65 | 0.5
0.1398 | 282.15 | 0.09644 | 288.65 | 0.6
0.1398 | 282.15 | 0.09644 | 288.65 | 0.7
0.1398 | 282.15 | 0.09644 | 288.65 | 0.8
0.1398 | 282.15 | 0.09644 | 288.65 | 0.9
0.1398 | 282.15 | 0.09644 | 288.65 | 1
0.1398 | 282.15 | 0.09644 | 289.15 | 0.15
0.1398 | 282.15 | 0.09644 | 289.15 | 0.2
0.1398 | 282.15 | 0.09644 | 289.15 | 0.3
0.1398 | 282.15 | 0.09644 | 289.15 | 0.4
0.1398 | 282.15 | 0.09644 | 289.15 | 0.5
0.1398 | 282.15 | 0.09644 | 289.15 | 0.6
0.1398 | 282.15 | 0.09644 | 289.15 | 0.7
0.1398 | 282.15 | 0.09644 | 289.15 | 0.8
0.1398 | 282.15 | 0.09644 | 289.15 | 0.9
0.1398 | 282.15 | 0.09644 | 289.15 | 1
0.1398 | 282.15 | 0.09644 | 289.65 | 0.15
0.1398 | 282.15 | 0.09644 | 289.65 | 0.2
0.1398 | 282.15 | 0.09644 | 289.65 | 0.3
0.1398 | 282.15 | 0.09644 | 289.65 | 0.4
0.1398 | 282.15 | 0.09644 | 289.65 | 0.5
0.1398 | 282.15 | 0.09644 | 289.65 | 0.6
0.1398 | 282.15 | 0.09644 | 289.65 | 0.7
0.1398 | 282.15 | 0.09644 | 289.65 | 0.8
0.1398 | 282.15 | 0.09644 | 289.65 | 0.9
0.1398 | 282.15 | 0.09644 | 289.65 | 1
0.1398 | 282.15 | 0.09644 | 290.15 | 0.15
0.1398 | 282.15 | 0.09644 | 290.15 | 0.2
0.1398 | 282.15 | 0.09644 | 290.15 | 0.3
0.1398 | 282.15 | 0.09644 | 290.15 | 0.4
0.1398 | 282.15 | 0.09644 | 290.15 | 0.5
0.1398 | 282.15 | 0.09644 | 290.15 | 0.6
0.1398 | 282.15 | 0.09644 | 290.15 | 0.7
0.1398 | 282.15 | 0.09644 | 290.15 | 0.8
0.1398 | 282.15 | 0.09644 | 290.15 | 0.9
0.1398 | 282.15 | 0.09644 | 290.15 | 1
0.1398 | 282.15 | 0.09644 | 290.65 | 0.15
0.1398 | 282.15 | 0.09644 | 290.65 | 0.2
0.1398 | 282.15 | 0.09644 | 290.65 | 0.3
0.1398 | 282.15 | 0.09644 | 290.65 | 0.4
0.1398 | 282.15 | 0.09644 | 290.65 | 0.5
0.1398 | 282.15 | 0.09644 | 290.65 | 0.6
0.1398 | 282.15 | 0.09644 | 290.65 | 0.7
0.1398 | 282.15 | 0.09644 | 290.65 | 0.8
0.1398 | 282.15 | 0.09644 | 290.65 | 0.9
0.1398 | 282.15 | 0.09644 | 290.65 | 1
0.1398 | 282.15 | 0.09644 | 291.15 | 0.15
0.1398 | 282.15 | 0.09644 | 291.15 | 0.2
0.1398 | 282.15 | 0.09644 | 291.15 | 0.3
0.1398 | 282.15 | 0.09644 | 291.15 | 0.4
0.1398 | 282.15 | 0.09644 | 291.15 | 0.5
0.1398 | 282.15 | 0.09644 | 291.15 | 0.6
0.1398 | 282.15 | 0.09644 | 291.15 | 0.7
0.1398 | 282.15 | 0.09644 | 291.15 | 0.8
0.1398 | 282.15 | 0.09644 | 291.15 | 0.9
0.1398 | 282.15 | 0.09644 | 291.15 | 1
0.1398 | 282.15 | 0.09644 | 294.15 | 0.15
0.1398 | 282.15 | 0.09644 | 294.15 | 0.2
0.1398 | 282.15 | 0.09644 | 294.15 | 0.3
0.1398 | 282.15 | 0.09644 | 294.15 | 0.4
0.1398 | 282.15 | 0.09644 | 294.15 | 0.5
0.1398 | 282.15 | 0.09644 | 294.15 | 0.6
0.1398 | 282.15 | 0.09644 | 294.15 | 0.7
0.1398 | 282.15 | 0.09644 | 294.15 | 0.8
0.1398 | 282.15 | 0.09644 | 294.15 | 0.9
0.1398 | 282.15 | 0.09644 | 294.15 | 1
0.1398 | 282.15 | 0.09644 | 297.15 | 0.15
0.1398 | 282.15 | 0.09644 | 297.15 | 0.2
0.1398 | 282.15 | 0.09644 | 297.15 | 0.3
0.1398 | 282.15 | 0.09644 | 297.15 | 0.4
0.1398 | 282.15 | 0.09644 | 297.15 | 0.5
0.1398 | 282.15 | 0.09644 | 297.15 | 0.6
0.1398 | 282.15 | 0.09644 | 297.15 | 0.7
0.1398 | 282.15 | 0.09644 | 297.15 | 0.8
0.1398 | 282.15 | 0.09644 | 297.15 | 0.9
0.1398 | 282.15 | 0.09644 | 297.15 | 1
0.1398 | 282.15 | 0.09644 | 300.15 | 0.15
0.1398 | 282.15 | 0.09644 | 300.15 | 0.2
0.1398 | 282.15 | 0.09644 | 300.15 | 0.3
0.1398 | 282.15 | 0.09644 | 300.15 | 0.4
0.1398 | 282.15 | 0.09644 | 300.15 | 0.5
0.1398 | 282.15 | 0.09644 | 300.15 | 0.6
0.1398 | 282.15 | 0.09644 | 300.15 | 0.7
0.1398 | 282.15 | 0.09644 | 300.15 | 0.8
0.1398 | 282.15 | 0.09644 | 300.15 | 0.9
0.1398 | 282.15 | 0.09644 | 300.15 | 1
0.1398 | 282.15 | 0.09644 | 303.15 | 0.15
0.1398 | 282.15 | 0.09644 | 303.15 | 0.2
0.1398 | 282.15 | 0.09644 | 303.15 | 0.3
0.1398 | 282.15 | 0.09644 | 303.15 | 0.4
0.1398 | 282.15 | 0.09644 | 303.15 | 0.5
0.1398 | 282.15 | 0.09644 | 303.15 | 0.6
0.1398 | 282.15 | 0.09644 | 303.15 | 0.7
0.1398 | 282.15 | 0.09644 | 303.15 | 0.8
0.1398 | 282.15 | 0.09644 | 303.15 | 0.9
0.1398 | 282.15 | 0.09644 | 303.15 | 1
0.1398 | 282.15 | 0.09737 | 283.65 | 0.15
0.1398 | 282.15 | 0.09737 | 283.65 | 0.2
0.1398 | 282.15 | 0.09737 | 283.65 | 0.3
0.1398 | 282.15 | 0.09737 | 283.65 | 0.4
0.1398 | 282.15 | 0.09737 | 283.65 | 0.5
0.1398 | 282.15 | 0.09737 | 283.65 | 0.6
0.1398 | 282.15 | 0.09737 | 283.65 | 0.7
0.1398 | 282.15 | 0.09737 | 283.65 | 0.8
0.1398 | 282.15 | 0.09737 | 283.65 | 0.9
0.1398 | 282.15 | 0.09737 | 283.65 | 1
0.1398 | 282.15 | 0.09737 | 284.15 | 0.15
0.1398 | 282.15 | 0.09737 | 284.15 | 0.2
0.1398 | 282.15 | 0.09737 | 284.15 | 0.3
0.1398 | 282.15 | 0.09737 | 284.15 | 0.4
0.1398 | 282.15 | 0.09737 | 284.15 | 0.5
0.1398 | 282.15 | 0.09737 | 284.15 | 0.6
0.1398 | 282.15 | 0.09737 | 284.15 | 0.7
0.1398 | 282.15 | 0.09737 | 284.15 | 0.8
0.1398 | 282.15 | 0.09737 | 284.15 | 0.9
0.1398 | 282.15 | 0.09737 | 284.15 | 1
0.1398 | 282.15 | 0.09737 | 284.65 | 0.15
0.1398 | 282.15 | 0.09737 | 284.65 | 0.2
0.1398 | 282.15 | 0.09737 | 284.65 | 0.3
0.1398 | 282.15 | 0.09737 | 284.65 | 0.4
0.1398 | 282.15 | 0.09737 | 284.65 | 0.5
0.1398 | 282.15 | 0.09737 | 284.65 | 0.6
0.1398 | 282.15 | 0.09737 | 284.65 | 0.7
0.1398 | 282.15 | 0.09737 | 284.65 | 0.8
0.1398 | 282.15 | 0.09737 | 284.65 | 0.9
0.1398 | 282.15 | 0.09737 | 284.65 | 1
0.1398 | 282.15 | 0.09737 | 285.15 | 0.15
0.1398 | 282.15 | 0.09737 | 285.15 | 0.2
0.1398 | 282.15 | 0.09737 | 285.15 | 0.3
0.1398 | 282.15 | 0.09737 | 285.15 | 0.4
0.1398 | 282.15 | 0.09737 | 285.15 | 0.5
0.1398 | 282.15 | 0.09737 | 285.15 | 0.6
0.1398 | 282.15 | 0.09737 | 285.15 | 0.7
0.1398 | 282.15 | 0.09737 | 285.15 | 0.8
0.1398 | 282.15 | 0.09737 | 285.15 | 0.9
0.1398 | 282.15 | 0.09737 | 285.15 | 1
0.1398 | 282.15 | 0.09737 | 285.65 | 0.15
0.1398 | 282.15 | 0.09737 | 285.65 | 0.2
0.1398 | 282.15 | 0.09737 | 285.65 | 0.3
0.1398 | 282.15 | 0.09737 | 285.65 | 0.4
0.1398 | 282.15 | 0.09737 | 285.65 | 0.5
0.1398 | 282.15 | 0.09737 | 285.65 | 0.6
0.1398 | 282.15 | 0.09737 | 285.65 | 0.7
0.1398 | 282.15 | 0.09737 | 285.65 | 0.8
0.1398 | 282.15 | 0.09737 | 285.65 | 0.9
0.1398 | 282.15 | 0.09737 | 285.65 | 1
0.1398 | 282.15 | 0.09737 | 286.15 | 0.15
0.1398 | 282.15 | 0.09737 | 286.15 | 0.2
0.1398 | 282.15 | 0.09737 | 286.15 | 0.3
0.1398 | 282.15 | 0.09737 | 286.15 | 0.4
0.1398 | 282.15 | 0.09737 | 286.15 | 0.5
0.1398 | 282.15 | 0.09737 | 286.15 | 0.6
0.1398 | 282.15 | 0.09737 | 286.15 | 0.7
0.1398 | 282.15 | 0.09737 | 286.15 | 0.8
0.1398 | 282.15 | 0.09737 | 286.15 | 0.9
0.1398 | 282.15 | 0.09737 | 286.15 | 1
0.1398 | 282.15 | 0.09737 | 286.65 | 0.15
0.1398 | 282.15 | 0.09737 | 286.65 | 0.2
0.1398 | 282.15 | 0.09737 | 286.65 | 0.3
0.1398 | 282.15 | 0.09737 | 286.65 | 0.4
0.1398 | 282.15 | 0.09737 | 286.65 | 0.5
0.1398 | 282.15 | 0.09737 | 286.65 | 0.6
0.1398 | 282.15 | 0.09737 | 286.65 | 0.7
0.1398 | 282.15 | 0.09737 | 286.65 | 0.8
0.1398 | 282.15 | 0.09737 | 286.65 | 0.9
0.1398 | 282.15 | 0.09737 | 286.65 | 1
0.1398 | 282.15 | 0.09737 | 287.15 | 0.15
0.1398 | 282.15 | 0.09737 | 287.15 | 0.2
0.1398 | 282.15 | 0.09737 | 287.15 | 0.3
0.1398 | 282.15 | 0.09737 | 287.15 | 0.4
0.1398 | 282.15 | 0.09737 | 287.15 | 0.5
0.1398 | 282.15 | 0.09737 | 287.15 | 0.6
0.1398 | 282.15 | 0.09737 | 287.15 | 0.7
0.1398 | 282.15 | 0.09737 | 287.15 | 0.8
0.1398 | 282.15 | 0.09737 | 287.15 | 0.9
0.1398 | 282.15 | 0.09737 | 287.15 | 1
0.1398 | 282.15 | 0.09737 | 287.65 | 0.15
0.1398 | 282.15 | 0.09737 | 287.65 | 0.2
0.1398 | 282.15 | 0.09737 | 287.65 | 0.3
0.1398 | 282.15 | 0.09737 | 287.65 | 0.4
0.1398 | 282.15 | 0.09737 | 287.65 | 0.5
0.1398 | 282.15 | 0.09737 | 287.65 | 0.6
0.1398 | 282.15 | 0.09737 | 287.65 | 0.7
0.1398 | 282.15 | 0.09737 | 287.65 | 0.8
0.1398 | 282.15 | 0.09737 | 287.65 | 0.9
0.1398 | 282.15 | 0.09737 | 287.65 | 1
0.1398 | 282.15 | 0.09737 | 288.15 | 0.15
0.1398 | 282.15 | 0.09737 | 288.15 | 0.2
0.1398 | 282.15 | 0.09737 | 288.15 | 0.3
0.1398 | 282.15 | 0.09737 | 288.15 | 0.4
0.1398 | 282.15 | 0.09737 | 288.15 | 0.5
0.1398 | 282.15 | 0.09737 | 288.15 | 0.6
0.1398 | 282.15 | 0.09737 | 288.15 | 0.7
0.1398 | 282.15 | 0.09737 | 288.15 | 0.8
0.1398 | 282.15 | 0.09737 | 288.15 | 0.9
0.1398 | 282.15 | 0.09737 | 288.15 | 1
0.1398 | 282.15 | 0.09737 | 288.65 | 0.15
0.1398 | 282.15 | 0.09737 | 288.65 | 0.2
0.1398 | 282.15 | 0.09737 | 288.65 | 0.3
0.1398 | 282.15 | 0.09737 | 288.65 | 0.4
0.1398 | 282.15 | 0.09737 | 288.65 | 0.5
0.1398 | 282.15 | 0.09737 | 288.65 | 0.6
0.1398 | 282.15 | 0.09737 | 288.65 | 0.7
0.1398 | 282.15 | 0.09737 | 288.65 | 0.8
0.1398 | 282.15 | 0.09737 | 288.65 | 0.9
0.1398 | 282.15 | 0.09737 | 288.65 | 1
0.1398 | 282.15 | 0.09737 | 289.15 | 0.15
0.1398 | 282.15 | 0.09737 | 289.15 | 0.2
0.1398 | 282.15 | 0.09737 | 289.15 | 0.3
0.1398 | 282.15 | 0.09737 | 289.15 | 0.4
0.1398 | 282.15 | 0.09737 | 289.15 | 0.5
0.1398 | 282.15 | 0.09737 | 289.15 | 0.6
0.1398 | 282.15 | 0.09737 | 289.15 | 0.7
0.1398 | 282.15 | 0.09737 | 289.15 | 0.8
0.1398 | 282.15 | 0.09737 | 289.15 | 0.9
0.1398 | 282.15 | 0.09737 | 289.15 | 1
0.1398 | 282.15 | 0.09737 | 289.65 | 0.15
0.1398 | 282.15 | 0.09737 | 289.65 | 0.2
0.1398 | 282.15 | 0.09737 | 289.65 | 0.3
0.1398 | 282.15 | 0.09737 | 289.65 | 0.4
0.1398 | 282.15 | 0.09737 | 289.65 | 0.5
0.1398 | 282.15 | 0.09737 | 289.65 | 0.6
0.1398 | 282.15 | 0.09737 | 289.65 | 0.7
0.1398 | 282.15 | 0.09737 | 289.65 | 0.8
0.1398 | 282.15 | 0.09737 | 289.65 | 0.9
0.1398 | 282.15 | 0.09737 | 289.65 | 1
0.1398 | 282.15 | 0.09737 | 290.15 | 0.15
0.1398 | 282.15 | 0.09737 | 290.15 | 0.2
0.1398 | 282.15 | 0.09737 | 290.15 | 0.3
0.1398 | 282.15 | 0.09737 | 290.15 | 0.4
0.1398 | 282.15 | 0.09737 | 290.15 | 0.5
0.1398 | 282.15 | 0.09737 | 290.15 | 0.6
0.1398 | 282.15 | 0.09737 | 290.15 | 0.7
0.1398 | 282.15 | 0.09737 | 290.15 | 0.8
0.1398 | 282.15 | 0.09737 | 290.15 | 0.9
0.1398 | 282.15 | 0.09737 | 290.15 | 1
0.1398 | 282.15 | 0.09737 | 290.65 | 0.15
0.1398 | 282.15 | 0.09737 | 290.65 | 0.2
0.1398 | 282.15 | 0.09737 | 290.65 | 0.3
0.1398 | 282.15 | 0.09737 | 290.65 | 0.4
0.1398 | 282.15 | 0.09737 | 290.65 | 0.5
0.1398 | 282.15 | 0.09737 | 290.65 | 0.6
0.1398 | 282.15 | 0.09737 | 290.65 | 0.7
0.1398 | 282.15 | 0.09737 | 290.65 | 0.8
0.1398 | 282.15 | 0.09737 | 290.65 | 0.9
0.1398 | 282.15 | 0.09737 | 290.65 | 1
0.1398 | 282.15 | 0.09737 | 291.15 | 0.15
0.1398 | 282.15 | 0.09737 | 291.15 | 0.2
0.1398 | 282.15 | 0.09737 | 291.15 | 0.3
0.1398 | 282.15 | 0.09737 | 291.15 | 0.4
0.1398 | 282.15 | 0.09737 | 291.15 | 0.5
0.1398 | 282.15 | 0.09737 | 291.15 | 0.6
0.1398 | 282.15 | 0.09737 | 291.15 | 0.7
0.1398 | 282.15 | 0.09737 | 291.15 | 0.8
0.1398 | 282.15 | 0.09737 | 291.15 | 0.9
0.1398 | 282.15 | 0.09737 | 291.15 | 1
0.1398 | 282.15 | 0.09737 | 294.15 | 0.15
0.1398 | 282.15 | 0.09737 | 294.15 | 0.2
0.1398 | 282.15 | 0.09737 | 294.15 | 0.3
0.1398 | 282.15 | 0.09737 | 294.15 | 0.4
0.1398 | 282.15 | 0.09737 | 294.15 | 0.5
0.1398 | 282.15 | 0.09737 | 294.15 | 0.6
0.1398 | 282.15 | 0.09737 | 294.15 | 0.7
0.1398 | 282.15 | 0.09737 | 294.15 | 0.8
0.1398 | 282.15 | 0.09737 | 294.15 | 0.9
0.1398 | 282.15 | 0.09737 | 294.15 | 1
0.1398 | 282.15 | 0.09737 | 297.15 | 0.15
0.1398 | 282.15 | 0.09737 | 297.15 | 0.2
0.1398 | 282.15 | 0.09737 | 297.15 | 0.3
0.1398 | 282.15 | 0.09737 | 297.15 | 0.4
0.1398 | 282.15 | 0.09737 | 297.15 | 0.5
0.1398 | 282.15 | 0.09737 | 297.15 | 0.6
0.1398 | 282.15 | 0.09737 | 297.15 | 0.7
0.1398 | 282.15 | 0.09737 | 297.15 | 0.8
0.1398 | 282.15 | 0.09737 | 297.15 | 0.9
0.1398 | 282.15 | 0.09737 | 297.15 | 1
0.1398 | 282.15 | 0.09737 | 300.15 | 0.15
0.1398 | 282.15 | 0.09737 | 300.15 | 0.2
0.1398 | 282.15 | 0.09737 | 300.15 | 0.3
0.1398 | 282.15 | 0.09737 | 300.15 | 0.4
0.1398 | 282.15 | 0.09737 | 300.15 | 0.5
0.1398 | 282.15 | 0.09737 | 300.15 | 0.6
0.1398 | 282.15 | 0.09737 | 300.15 | 0.7
0.1398 | 282.15 | 0.09737 | 300.15 | 0.8
0.1398 | 282.15 | 0.09737 | 300.15 | 0.9
0.1398 | 282.15 | 0.09737 | 300.15 | 1
0.1398 | 282.15 | 0.09737 | 303.15 | 0.15
0.1398 | 282.15 | 0.09737 | 303.15 | 0.2
0.1398 | 282.15 | 0.09737 | 303.15 | 0.3
0.1398 | 282.15 | 0.09737 | 303.15 | 0.4
0.1398 | 282.15 | 0.09737 | 303.15 | 0.5
0.1398 | 282.15 | 0.09737 | 303.15 | 0.6
0.1398 | 282.15 | 0.09737 | 303.15 | 0.7
0.1398 | 282.15 | 0.09737 | 303.15 | 0.8
0.1398 | 282.15 | 0.09737 | 303.15 | 0.9
0.1398 | 282.15 | 0.09737 | 303.15 | 1
0.1398 | 282.15 | 0.115 | 283.65 | 0.15
0.1398 | 282.15 | 0.115 | 283.65 | 0.2
0.1398 | 282.15 | 0.115 | 283.65 | 0.3
0.1398 | 282.15 | 0.115 | 283.65 | 0.4
0.1398 | 282.15 | 0.115 | 283.65 | 0.5
0.1398 | 282.15 | 0.115 | 283.65 | 0.6
0.1398 | 282.15 | 0.115 | 283.65 | 0.7
0.1398 | 282.15 | 0.115 | 283.65 | 0.8
0.1398 | 282.15 | 0.115 | 283.65 | 0.9
0.1398 | 282.15 | 0.115 | 283.65 | 1
0.1398 | 282.15 | 0.115 | 284.15 | 0.15
0.1398 | 282.15 | 0.115 | 284.15 | 0.2
0.1398 | 282.15 | 0.115 | 284.15 | 0.3
0.1398 | 282.15 | 0.115 | 284.15 | 0.4
0.1398 | 282.15 | 0.115 | 284.15 | 0.5
0.1398 | 282.15 | 0.115 | 284.15 | 0.6
0.1398 | 282.15 | 0.115 | 284.15 | 0.7
0.1398 | 282.15 | 0.115 | 284.15 | 0.8
0.1398 | 282.15 | 0.115 | 284.15 | 0.9
0.1398 | 282.15 | 0.115 | 284.15 | 1
0.1398 | 282.15 | 0.115 | 284.65 | 0.15
0.1398 | 282.15 | 0.115 | 284.65 | 0.2
0.1398 | 282.15 | 0.115 | 284.65 | 0.3
0.1398 | 282.15 | 0.115 | 284.65 | 0.4
0.1398 | 282.15 | 0.115 | 284.65 | 0.5
0.1398 | 282.15 | 0.115 | 284.65 | 0.6
0.1398 | 282.15 | 0.115 | 284.65 | 0.7
0.1398 | 282.15 | 0.115 | 284.65 | 0.8
0.1398 | 282.15 | 0.115 | 284.65 | 0.9
0.1398 | 282.15 | 0.115 | 284.65 | 1
0.1398 | 282.15 | 0.115 | 285.15 | 0.15
0.1398 | 282.15 | 0.115 | 285.15 | 0.2
0.1398 | 282.15 | 0.115 | 285.15 | 0.3
0.1398 | 282.15 | 0.115 | 285.15 | 0.4
0.1398 | 282.15 | 0.115 | 285.15 | 0.5
0.1398 | 282.15 | 0.115 | 285.15 | 0.6
0.1398 | 282.15 | 0.115 | 285.15 | 0.7
0.1398 | 282.15 | 0.115 | 285.15 | 0.8
0.1398 | 282.15 | 0.115 | 285.15 | 0.9
0.1398 | 282.15 | 0.115 | 285.15 | 1
0.1398 | 282.15 | 0.115 | 285.65 | 0.15
0.1398 | 282.15 | 0.115 | 285.65 | 0.2
0.1398 | 282.15 | 0.115 | 285.65 | 0.3
0.1398 | 282.15 | 0.115 | 285.65 | 0.4
0.1398 | 282.15 | 0.115 | 285.65 | 0.5
0.1398 | 282.15 | 0.115 | 285.65 | 0.6
0.1398 | 282.15 | 0.115 | 285.65 | 0.7
0.1398 | 282.15 | 0.115 | 285.65 | 0.8
0.1398 | 282.15 | 0.115 | 285.65 | 0.9
0.1398 | 282.15 | 0.115 | 285.65 | 1
0.1398 | 282.15 | 0.115 | 286.15 | 0.15
0.1398 | 282.15 | 0.115 | 286.15 | 0.2
0.1398 | 282.15 | 0.115 | 286.15 | 0.3
0.1398 | 282.15 | 0.115 | 286.15 | 0.4
0.1398 | 282.15 | 0.115 | 286.15 | 0.5
0.1398 | 282.15 | 0.115 | 286.15 | 0.6
0.1398 | 282.15 | 0.115 | 286.15 | 0.7
0.1398 | 282.15 | 0.115 | 286.15 | 0.8
0.1398 | 282.15 | 0.115 | 286.15 | 0.9
0.1398 | 282.15 | 0.115 | 286.15 | 1
0.1398 | 282.15 | 0.115 | 286.65 | 0.15
0.1398 | 282.15 | 0.115 | 286.65 | 0.2
0.1398 | 282.15 | 0.115 | 286.65 | 0.3
0.1398 | 282.15 | 0.115 | 286.65 | 0.4
0.1398 | 282.15 | 0.115 | 286.65 | 0.5
0.1398 | 282.15 | 0.115 | 286.65 | 0.6
0.1398 | 282.15 | 0.115 | 286.65 | 0.7
0.1398 | 282.15 | 0.115 | 286.65 | 0.8
0.1398 | 282.15 | 0.115 | 286.65 | 0.9
0.1398 | 282.15 | 0.115 | 286.65 | 1
0.1398 | 282.15 | 0.115 | 287.15 | 0.15
0.1398 | 282.15 | 0.115 | 287.15 | 0.2
0.1398 | 282.15 | 0.115 | 287.15 | 0.3
0.1398 | 282.15 | 0.115 | 287.15 | 0.4
0.1398 | 282.15 | 0.115 | 287.15 | 0.5
0.1398 | 282.15 | 0.115 | 287.15 | 0.6
0.1398 | 282.15 | 0.115 | 287.15 | 0.7
0.1398 | 282.15 | 0.115 | 287.15 | 0.8
0.1398 | 282.15 | 0.115 | 287.15 | 0.9
0.1398 | 282.15 | 0.115 | 287.15 | 1
0.1398 | 282.15 | 0.115 | 287.65 | 0.15
0.1398 | 282.15 | 0.115 | 287.65 | 0.2
0.1398 | 282.15 | 0.115 | 287.65 | 0.3
0.1398 | 282.15 | 0.115 | 287.65 | 0.4
0.1398 | 282.15 | 0.115 | 287.65 | 0.5
0.1398 | 282.15 | 0.115 | 287.65 | 0.6
0.1398 | 282.15 | 0.115 | 287.65 | 0.7
0.1398 | 282.15 | 0.115 | 287.65 | 0.8
0.1398 | 282.15 | 0.115 | 287.65 | 0.9
0.1398 | 282.15 | 0.115 | 287.65 | 1
0.1398 | 282.15 | 0.115 | 288.15 | 0.15
0.1398 | 282.15 | 0.115 | 288.15 | 0.2
0.1398 | 282.15 | 0.115 | 288.15 | 0.3
0.1398 | 282.15 | 0.115 | 288.15 | 0.4
0.1398 | 282.15 | 0.115 | 288.15 | 0.5
0.1398 | 282.15 | 0.115 | 288.15 | 0.6
0.1398 | 282.15 | 0.115 | 288.15 | 0.7
0.1398 | 282.15 | 0.115 | 288.15 | 0.8
0.1398 | 282.15 | 0.115 | 288.15 | 0.9
0.1398 | 282.15 | 0.115 | 288.15 | 1
0.1398 | 282.15 | 0.115 | 288.65 | 0.15
0.1398 | 282.15 | 0.115 | 288.65 | 0.2
0.1398 | 282.15 | 0.115 | 288.65 | 0.3
0.1398 | 282.15 | 0.115 | 288.65 | 0.4
0.1398 | 282.15 | 0.115 | 288.65 | 0.5
0.1398 | 282.15 | 0.115 | 288.65 | 0.6
0.1398 | 282.15 | 0.115 | 288.65 | 0.7
0.1398 | 282.15 | 0.115 | 288.65 | 0.8
0.1398 | 282.15 | 0.115 | 288.65 | 0.9
0.1398 | 282.15 | 0.115 | 288.65 | 1
0.1398 | 282.15 | 0.115 | 289.15 | 0.15
0.1398 | 282.15 | 0.115 | 289.15 | 0.2
0.1398 | 282.15 | 0.115 | 289.15 | 0.3
0.1398 | 282.15 | 0.115 | 289.15 | 0.4
0.1398 | 282.15 | 0.115 | 289.15 | 0.5
0.1398 | 282.15 | 0.115 | 289.15 | 0.6
0.1398 | 282.15 | 0.115 | 289.15 | 0.7
0.1398 | 282.15 | 0.115 | 289.15 | 0.8
0.1398 | 282.15 | 0.115 | 289.15 | 0.9
0.1398 | 282.15 | 0.115 | 289.15 | 1
0.1398 | 282.15 | 0.115 | 289.65 | 0.15
0.1398 | 282.15 | 0.115 | 289.65 | 0.2
0.1398 | 282.15 | 0.115 | 289.65 | 0.3
0.1398 | 282.15 | 0.115 | 289.65 | 0.4
0.1398 | 282.15 | 0.115 | 289.65 | 0.5
0.1398 | 282.15 | 0.115 | 289.65 | 0.6
0.1398 | 282.15 | 0.115 | 289.65 | 0.7
0.1398 | 282.15 | 0.115 | 289.65 | 0.8
0.1398 | 282.15 | 0.115 | 289.65 | 0.9
0.1398 | 282.15 | 0.115 | 289.65 | 1
0.1398 | 282.15 | 0.115 | 290.15 | 0.15
0.1398 | 282.15 | 0.115 | 290.15 | 0.2
0.1398 | 282.15 | 0.115 | 290.15 | 0.3
0.1398 | 282.15 | 0.115 | 290.15 | 0.4
0.1398 | 282.15 | 0.115 | 290.15 | 0.5
0.1398 | 282.15 | 0.115 | 290.15 | 0.6
0.1398 | 282.15 | 0.115 | 290.15 | 0.7
0.1398 | 282.15 | 0.115 | 290.15 | 0.8
0.1398 | 282.15 | 0.115 | 290.15 | 0.9
0.1398 | 282.15 | 0.115 | 290.15 | 1
0.1398 | 282.15 | 0.115 | 290.65 | 0.15
0.1398 | 282.15 | 0.115 | 290.65 | 0.2
0.1398 | 282.15 | 0.115 | 290.65 | 0.3
0.1398 | 282.15 | 0.115 | 290.65 | 0.4
0.1398 | 282.15 | 0.115 | 290.65 | 0.5
0.1398 | 282.15 | 0.115 | 290.65 | 0.6
0.1398 | 282.15 | 0.115 | 290.65 | 0.7
0.1398 | 282.15 | 0.115 | 290.65 | 0.8
0.1398 | 282.15 | 0.115 | 290.65 | 0.9
0.1398 | 282.15 | 0.115 | 290.65 | 1
0.1398 | 282.15 | 0.115 | 291.15 | 0.15
0.1398 | 282.15 | 0.115 | 291.15 | 0.2
0.1398 | 282.15 | 0.115 | 291.15 | 0.3
0.1398 | 282.15 | 0.115 | 291.15 | 0.4
0.1398 | 282.15 | 0.115 | 291.15 | 0.5
0.1398 | 282.15 | 0.115 | 291.15 | 0.6
0.1398 | 282.15 | 0.115 | 291.15 | 0.7
0.1398 | 282.15 | 0.115 | 291.15 | 0.8
0.1398 | 282.15 | 0.115 | 291.15 | 0.9
0.1398 | 282.15 | 0.115 | 291.15 | 1
0.1398 | 282.15 | 0.115 | 294.15 | 0.15
0.1398 | 282.15 | 0.115 | 294.15 | 0.2
0.1398 | 282.15 | 0.115 | 294.15 | 0.3
0.1398 | 282.15 | 0.115 | 294.15 | 0.4
0.1398 | 282.15 | 0.115 | 294.15 | 0.5
0.1398 | 282.15 | 0.115 | 294.15 | 0.6
0.1398 | 282.15 | 0.115 | 294.15 | 0.7
0.1398 | 282.15 | 0.115 | 294.15 | 0.8
0.1398 | 282.15 | 0.115 | 294.15 | 0.9
0.1398 | 282.15 | 0.115 | 294.15 | 1
0.1398 | 282.15 | 0.115 | 297.15 | 0.15
0.1398 | 282.15 | 0.115 | 297.15 | 0.2
0.1398 | 282.15 | 0.115 | 297.15 | 0.3
0.1398 | 282.15 | 0.115 | 297.15 | 0.4
0.1398 | 282.15 | 0.115 | 297.15 | 0.5
0.1398 | 282.15 | 0.115 | 297.15 | 0.6
0.1398 | 282.15 | 0.115 | 297.15 | 0.7
0.1398 | 282.15 | 0.115 | 297.15 | 0.8
0.1398 | 282.15 | 0.115 | 297.15 | 0.9
0.1398 | 282.15 | 0.115 | 297.15 | 1
0.1398 | 282.15 | 0.115 | 300.15 | 0.15
0.1398 | 282.15 | 0.115 | 300.15 | 0.2
0.1398 | 282.15 | 0.115 | 300.15 | 0.3
0.1398 | 282.15 | 0.115 | 300.15 | 0.4
0.1398 | 282.15 | 0.115 | 300.15 | 0.5
0.1398 | 282.15 | 0.115 | 300.15 | 0.6
0.1398 | 282.15 | 0.115 | 300.15 | 0.7
0.1398 | 282.15 | 0.115 | 300.15 | 0.8
0.1398 | 282.15 | 0.115 | 300.15 | 0.9
0.1398 | 282.15 | 0.115 | 300.15 | 1
0.1398 | 282.15 | 0.115 | 303.15 | 0.15
0.1398 | 282.15 | 0.115 | 303.15 | 0.2
0.1398 | 282.15 | 0.115 | 303.15 | 0.3
0.1398 | 282.15 | 0.115 | 303.15 | 0.4
0.1398 | 282.15 | 0.115 | 303.15 | 0.5
0.1398 | 282.15 | 0.115 | 303.15 | 0.6
0.1398 | 282.15 | 0.115 | 303.15 | 0.7
0.1398 | 282.15 | 0.115 | 303.15 | 0.8
0.1398 | 282.15 | 0.115 | 303.15 | 0.9
0.1398 | 282.15 | 0.115 | 303.15 | 1

## performance_map_standby
ASHRAE205.RS_instance.RS0001.performance.performance_map_standby.grid_variables
grid_variables | lookup_variables
chiller_environment_dry_bulb_temperature | input_power
K | W