## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'C': 0.0-75.0 ton, 4.69 COP, 5.86 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 34ea7160-77c8-4643-a1ff-6b72fe5da2fa |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'C' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| maximum | 2 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.0056508 | 277.0389 | 0.0074401 | 285.9278 | 1 | 7020.5001 | 33321.1319 | 40341.632 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074401 | 285.9278 | 2 | 10322.6457 | 66642.2638 | 76964.9095 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074401 | 285.9278 | 3 | 15222.8395 | 99963.3957 | 115186.2352 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074401 | 285.9278 | 4 | 21721.0815 | 133284.5276 | 155005.6092 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074401 | 295.0019 | 1 | 7837.0222 | 31768.5818 | 39605.604 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074401 | 295.0019 | 2 | 11523.2252 | 63537.1636 | 75060.3888 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074401 | 295.0019 | 3 | 16993.338 | 95305.7454 | 112299.0834 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074401 | 295.0019 | 4 | 24247.3607 | 127074.3273 | 151321.6879 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074401 | 304.0759 | 1 | 8992.9782 | 29265.8685 | 38258.8467 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074401 | 304.0759 | 2 | 13222.8938 | 58531.737 | 71754.6308 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074401 | 304.0759 | 3 | 19499.8449 | 87797.6055 | 107297.4504 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074401 | 304.0759 | 4 | 27823.8315 | 117063.474 | 144887.3055 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074401 | 313.15 | 1 | 10130.9757 | 25812.992 | 35943.9677 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074401 | 313.15 | 2 | 14896.1571 | 51625.9839 | 66522.141 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074401 | 313.15 | 3 | 21967.4118 | 77438.9759 | 99406.3877 | 0 | 0 | NORMAL
0.0056508 | 277.0389 | 0.0074401 | 313.15 | 4 | 31344.7398 | 103251.9678 | 134596.7076 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 285.9278 | 1 | 7128.3375 | 37498.651 | 44626.9885 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 285.9278 | 2 | 10481.2053 | 74997.3019 | 85478.5072 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 285.9278 | 3 | 15456.6678 | 112495.9529 | 127952.6207 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 285.9278 | 4 | 22054.7252 | 149994.6039 | 172049.329 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 295.0019 | 1 | 7990.649 | 35969.3702 | 43960.0192 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 295.0019 | 2 | 11749.1115 | 71938.7404 | 83687.8519 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 295.0019 | 3 | 17326.4533 | 107908.1105 | 125234.5638 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 295.0019 | 4 | 24722.6744 | 143877.4807 | 168600.1551 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 304.0759 | 1 | 9337.0872 | 33489.9262 | 42827.0134 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 304.0759 | 2 | 13728.8571 | 66979.8523 | 80708.7095 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 304.0759 | 3 | 20245.9907 | 100469.7785 | 120715.7692 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 304.0759 | 4 | 28888.4878 | 133959.7047 | 162848.1925 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 313.15 | 1 | 10823.2168 | 30060.3189 | 40883.5357 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 313.15 | 2 | 15913.999 | 60120.6379 | 76034.6368 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 313.15 | 3 | 23468.4265 | 90180.9568 | 113649.3833 | 0 | 0 | NORMAL
0.0056508 | 280.9278 | 0.0074401 | 313.15 | 4 | 33486.4994 | 120241.2757 | 153727.7751 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 285.9278 | 1 | 7221.4325 | 39564.9794 | 46786.4119 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 285.9278 | 2 | 10618.0882 | 79129.9587 | 89748.0469 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 285.9278 | 3 | 15658.5295 | 118694.9381 | 134353.4676 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 285.9278 | 4 | 22342.7565 | 158259.9175 | 180602.6739 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 295.0019 | 1 | 8016.4849 | 38058.9679 | 46075.4528 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 295.0019 | 2 | 11787.0995 | 76117.9358 | 87905.0352 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 295.0019 | 3 | 17382.4743 | 114176.9036 | 131559.3779 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 295.0019 | 4 | 24802.6093 | 152235.8715 | 177038.4808 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 304.0759 | 1 | 9375.6911 | 35602.7932 | 44978.4843 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 304.0759 | 2 | 13785.6187 | 71205.5863 | 84991.205 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 304.0759 | 3 | 20329.6972 | 106808.3795 | 127138.0767 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 304.0759 | 4 | 29007.9265 | 142411.1727 | 171419.0992 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 313.15 | 1 | 10967.573 | 32196.4552 | 43164.0282 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 313.15 | 2 | 16126.2542 | 64392.9105 | 80519.1647 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 313.15 | 3 | 23781.44 | 96589.3657 | 120370.8058 | 0 | 0 | NORMAL
0.0056508 | 284.8167 | 0.0074401 | 313.15 | 4 | 33933.1304 | 128785.8209 | 162718.9514 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 285.9278 | 1 | 7428.4807 | 39520.1171 | 46948.5978 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 285.9278 | 2 | 10922.523 | 79040.2342 | 89962.7572 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 285.9278 | 3 | 16107.4805 | 118560.3513 | 134667.8318 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 285.9278 | 4 | 22983.3532 | 158080.4684 | 181063.8216 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 295.0019 | 1 | 8069.1089 | 38037.3749 | 46106.4838 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 295.0019 | 2 | 11864.4756 | 76074.7498 | 87939.2254 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 295.0019 | 3 | 17496.5811 | 114112.1248 | 131608.7058 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 295.0019 | 4 | 24965.4254 | 152149.4997 | 177114.925 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 304.0759 | 1 | 9289.2526 | 35604.4695 | 44893.7221 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 304.0759 | 2 | 13658.5231 | 71208.939 | 84867.4621 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 304.0759 | 3 | 20142.2689 | 106813.4085 | 126955.6774 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 304.0759 | 4 | 28740.4899 | 142417.878 | 171158.3679 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 313.15 | 1 | 10770.3904 | 32221.4009 | 42991.7913 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 313.15 | 2 | 15836.3254 | 64442.8018 | 80279.1271 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 313.15 | 3 | 23353.881 | 96664.2026 | 120018.0837 | 0 | 0 | NORMAL
0.0056508 | 288.7056 | 0.0074401 | 313.15 | 4 | 33323.0574 | 128885.6035 | 162208.6609 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.0056508 | 277.0389 | 15000
0.0056508 | 280.9278 | 15000
0.0056508 | 284.8167 | 15000
0.0056508 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.0074401 | 285.9278 | 15000
0.0074401 | 295.0019 | 15000
0.0074401 | 304.0759 | 15000
0.0074401 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser