## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'J': 400.0+ ton, 6.28 COP, 7.03 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | c4ab8d90-d2f7-4a29-9d33-0cdf4141ced3 |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'J' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.88889 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Minimum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.067809 | 277.0389 | 0.085306 | 285.9278 | 1 | 68750.7573 | 401365.947 | 470116.7043 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085306 | 285.9278 | 2 | 95869.7905 | 802731.8941 | 898601.6845 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085306 | 285.9278 | 3 | 139103.9832 | 1204097.8411 | 1343201.8242 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085306 | 285.9278 | 4 | 198453.3354 | 1605463.7881 | 1803917.1235 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085306 | 295.0019 | 1 | 79013.4974 | 374998.9009 | 454012.3982 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085306 | 295.0019 | 2 | 110180.7126 | 749997.8018 | 860178.5144 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085306 | 295.0019 | 3 | 159868.671 | 1124996.7026 | 1284865.3737 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085306 | 295.0019 | 4 | 228077.3725 | 1499995.6035 | 1728072.9761 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085306 | 304.0759 | 1 | 79564.5964 | 341790.6795 | 421355.2759 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085306 | 304.0759 | 2 | 110949.1951 | 683581.359 | 794530.5541 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085306 | 304.0759 | 3 | 160983.7144 | 1025372.0385 | 1186355.7529 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085306 | 304.0759 | 4 | 229668.1542 | 1367162.718 | 1596830.8722 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085306 | 313.15 | 1 | 71677.0154 | 301741.2829 | 373418.2983 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085306 | 313.15 | 2 | 99950.3237 | 603482.5658 | 703432.8895 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085306 | 313.15 | 3 | 145024.7056 | 905223.8487 | 1050248.5543 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.085306 | 313.15 | 4 | 206900.1612 | 1206965.1316 | 1413865.2928 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 285.9278 | 1 | 71152.1878 | 452239.8437 | 523392.0315 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 285.9278 | 2 | 99218.4756 | 904479.6874 | 1003698.163 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 285.9278 | 3 | 143962.8176 | 1356719.5311 | 1500682.3488 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 285.9278 | 4 | 205385.2138 | 1808959.3748 | 2014344.5887 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 295.0019 | 1 | 85402.1612 | 432434.7412 | 517836.9023 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 295.0019 | 2 | 119089.4125 | 864869.4823 | 983958.8948 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 295.0019 | 3 | 172794.9081 | 1297304.2235 | 1470099.1316 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 295.0019 | 4 | 246518.6479 | 1729738.9646 | 1976257.6125 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 304.0759 | 1 | 89404.5002 | 405788.4634 | 495192.9636 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 304.0759 | 2 | 124670.4915 | 811576.9267 | 936247.4182 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 304.0759 | 3 | 180892.8742 | 1217365.3901 | 1398258.2643 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 304.0759 | 4 | 258071.6484 | 1623153.8534 | 1881225.5018 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 313.15 | 1 | 84075.731 | 372301.0103 | 456376.7413 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 313.15 | 2 | 117239.7662 | 744602.0207 | 861841.7869 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 313.15 | 3 | 170111.1308 | 1116903.031 | 1287014.1618 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.085306 | 313.15 | 4 | 242689.8246 | 1489204.0414 | 1731893.866 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 285.9278 | 1 | 70836.8962 | 472669.5134 | 543506.4095 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 285.9278 | 2 | 98778.8158 | 945339.0267 | 1044117.8426 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 285.9278 | 3 | 143324.8854 | 1418008.5401 | 1561333.4255 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 285.9278 | 4 | 204475.1049 | 1890678.0535 | 2095153.1584 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 295.0019 | 1 | 87645.4253 | 459426.3544 | 547071.7797 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 295.0019 | 2 | 122217.5418 | 918852.7088 | 1041070.2506 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 295.0019 | 3 | 177333.7231 | 1378279.0632 | 1555612.7863 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 295.0019 | 4 | 252993.9691 | 1837705.4176 | 2090699.3867 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 304.0759 | 1 | 94173.0392 | 439342.0202 | 533515.0594 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 304.0759 | 2 | 131320.0012 | 878684.0404 | 1010004.0416 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 304.0759 | 3 | 190541.099 | 1318026.0606 | 1508567.1596 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 304.0759 | 4 | 271836.3326 | 1757368.0808 | 2029204.4134 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 313.15 | 1 | 90979.8291 | 412416.5108 | 503396.3399 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 313.15 | 2 | 126867.2157 | 824833.0215 | 951700.2372 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 313.15 | 3 | 184080.2504 | 1237249.5323 | 1421329.7827 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.085306 | 313.15 | 4 | 262618.9332 | 1649666.0431 | 1912284.9763 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 285.9278 | 1 | 68884.7656 | 462654.956 | 531539.7216 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 285.9278 | 2 | 96056.6589 | 925309.912 | 1021366.5709 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 285.9278 | 3 | 139375.1232 | 1387964.868 | 1527339.9912 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 285.9278 | 4 | 198840.1585 | 1850619.8241 | 2049459.9826 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 295.0019 | 1 | 86882.7205 | 455973.7406 | 542856.4611 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 295.0019 | 2 | 121153.9848 | 911947.4813 | 1033101.4661 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 295.0019 | 3 | 175790.5361 | 1367921.2219 | 1543711.758 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 295.0019 | 4 | 250792.3743 | 1823894.9625 | 2074687.3368 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 304.0759 | 1 | 95069.1919 | 442451.35 | 537520.5419 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 304.0759 | 2 | 132569.6452 | 884902.7 | 1017472.3453 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 304.0759 | 3 | 192354.2923 | 1327354.05 | 1519708.3423 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 304.0759 | 4 | 274423.133 | 1769805.4 | 2044228.5331 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 313.15 | 1 | 93647.8361 | 422087.7842 | 515735.6203 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 313.15 | 2 | 130587.6296 | 844175.5683 | 974763.1979 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 313.15 | 3 | 189478.4513 | 1266263.3525 | 1455741.8038 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.085306 | 313.15 | 4 | 270320.3013 | 1688351.1367 | 1958671.4379 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.067809 | 277.0389 | 15000
0.067809 | 280.9278 | 15000
0.067809 | 284.8167 | 15000
0.067809 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.085306 | 285.9278 | 15000
0.085306 | 295.0019 | 15000
0.085306 | 304.0759 | 15000
0.085306 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser