## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'N': 75.0-150.0 ton, 4.69 COP, 7.18 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 31a7f511-95b5-4a62-8ae9-d86c5dc63418 |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'N' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Minimum scaling factor
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.016952 | 277.0389 | 0.02232 | 285.9278 | 1 | 14692.4835 | 100049.4035 | 114741.887 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.02232 | 285.9278 | 2 | 24392.7426 | 200098.8071 | 224491.5496 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.02232 | 285.9278 | 3 | 41040.7118 | 300148.2106 | 341188.9224 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.02232 | 285.9278 | 4 | 64636.3913 | 400197.6142 | 464834.0054 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.02232 | 295.0019 | 1 | 16529.6541 | 95242.3311 | 111771.9852 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.02232 | 295.0019 | 2 | 27442.8484 | 190484.6622 | 217927.5106 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.02232 | 295.0019 | 3 | 46172.5052 | 285726.9933 | 331899.4985 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.02232 | 295.0019 | 4 | 72718.6245 | 380969.3244 | 453687.9489 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.02232 | 304.0759 | 1 | 18932.7393 | 87943.1163 | 106875.8555 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.02232 | 304.0759 | 2 | 31432.4964 | 175886.2325 | 207318.7289 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.02232 | 304.0759 | 3 | 52885.0753 | 263829.3488 | 316714.4241 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.02232 | 304.0759 | 4 | 83290.476 | 351772.465 | 435062.941 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.02232 | 313.15 | 1 | 21260.6478 | 78151.759 | 99412.4068 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.02232 | 313.15 | 2 | 35297.3348 | 156303.518 | 191600.8528 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.02232 | 313.15 | 3 | 59387.6536 | 234455.277 | 293842.9306 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.02232 | 313.15 | 4 | 93531.6042 | 312607.036 | 406138.6402 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 285.9278 | 1 | 14921.5992 | 112396.5566 | 127318.1558 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 285.9278 | 2 | 24773.1248 | 224793.1132 | 249566.238 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 285.9278 | 3 | 41680.7037 | 337189.6698 | 378870.3735 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 285.9278 | 4 | 65644.3359 | 449586.2265 | 515230.5623 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 295.0019 | 1 | 16877.2395 | 107669.7633 | 124547.0028 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 295.0019 | 2 | 28019.9164 | 215339.5265 | 243359.4429 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 295.0019 | 3 | 47143.4202 | 323009.2898 | 370152.71 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 295.0019 | 4 | 74247.7511 | 430679.0531 | 504926.8041 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 304.0759 | 1 | 19665.3068 | 100450.8275 | 120116.1343 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 304.0759 | 2 | 32648.719 | 200901.655 | 233550.3741 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 304.0759 | 3 | 54931.366 | 301352.4826 | 356283.8485 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 304.0759 | 4 | 86513.2476 | 401803.3101 | 488316.5577 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 313.15 | 1 | 22668.5892 | 90739.7494 | 113408.3385 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 313.15 | 2 | 37634.826 | 181479.4987 | 219114.3247 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 313.15 | 3 | 63320.4751 | 272219.2481 | 335539.7232 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.02232 | 313.15 | 4 | 99725.5365 | 362958.9975 | 462684.5339 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 285.9278 | 1 | 15112.5962 | 118529.8084 | 133642.4046 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 285.9278 | 2 | 25090.2217 | 237059.6168 | 262149.8385 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 285.9278 | 3 | 42214.2183 | 355589.4252 | 397803.6435 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 285.9278 | 4 | 66484.586 | 474119.2336 | 540603.8195 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 295.0019 | 1 | 16943.7936 | 113883.2941 | 130827.0877 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 295.0019 | 2 | 28130.4106 | 227766.5883 | 255896.9989 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 295.0019 | 3 | 47329.3265 | 341649.8824 | 388979.2089 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 295.0019 | 4 | 74540.5411 | 455533.1766 | 530073.7177 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 304.0759 | 1 | 19757.6521 | 106744.6375 | 126502.2896 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 304.0759 | 2 | 32802.0325 | 213489.275 | 246291.3075 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 304.0759 | 3 | 55189.3153 | 320233.9125 | 375423.2278 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 304.0759 | 4 | 86919.5007 | 426978.55 | 513898.0507 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 313.15 | 1 | 22960.8394 | 97113.8384 | 120074.6779 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 313.15 | 2 | 38120.0255 | 194227.6769 | 232347.7023 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 313.15 | 3 | 64136.8216 | 291341.5153 | 355478.337 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.02232 | 313.15 | 4 | 101011.228 | 388455.3538 | 489466.5818 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 285.9278 | 1 | 15526.0689 | 118449.1589 | 133975.2278 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 285.9278 | 2 | 25776.6771 | 236898.3178 | 262674.9948 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 285.9278 | 3 | 43369.1772 | 355347.4767 | 398716.6539 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 285.9278 | 4 | 68303.5694 | 473796.6356 | 542100.2049 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 295.0019 | 1 | 17042.5543 | 113882.9237 | 130925.4781 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 295.0019 | 2 | 28294.3752 | 227765.8475 | 256060.2227 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 295.0019 | 3 | 47605.1963 | 341648.7712 | 389253.9675 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 295.0019 | 4 | 74975.0177 | 455531.695 | 530506.7126 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 304.0759 | 1 | 19575.6572 | 106824.5462 | 126400.2033 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 304.0759 | 2 | 32499.881 | 213649.0924 | 246148.9734 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 304.0759 | 3 | 54680.9465 | 320473.6386 | 375154.585 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 304.0759 | 4 | 86118.8536 | 427298.1847 | 513417.0383 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 313.15 | 1 | 22555.9244 | 97274.0262 | 119829.9507 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 313.15 | 2 | 37447.7778 | 194548.0524 | 231995.8303 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 313.15 | 3 | 63005.7672 | 291822.0787 | 354827.8459 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.02232 | 313.15 | 4 | 99229.8925 | 389096.1049 | 488325.9973 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.016952 | 277.0389 | 15000
0.016952 | 280.9278 | 15000
0.016952 | 284.8167 | 15000
0.016952 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.02232 | 285.9278 | 15000
0.02232 | 295.0019 | 15000
0.02232 | 304.0759 | 15000
0.02232 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser