## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'R': 0.0-150.0 ton, 5.06 COP, 7.99 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | cf701e04-f088-4e64-8412-092d8f614182 |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'R' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| maximum | 2 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.011302 | 277.0389 | 0.014688 | 285.9278 | 1 | 6629.8169 | 67122.1555 | 73751.9725 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014688 | 285.9278 | 2 | 14585.2657 | 134244.3111 | 148829.5768 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014688 | 285.9278 | 3 | 27046.5411 | 201366.4666 | 228413.0078 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014688 | 285.9278 | 4 | 44013.6431 | 268488.6222 | 312502.2653 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014688 | 295.0019 | 1 | 7327.756 | 63238.0877 | 70565.8437 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014688 | 295.0019 | 2 | 16120.6967 | 126476.1755 | 142596.8722 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014688 | 295.0019 | 3 | 29893.8048 | 189714.2632 | 219608.0679 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014688 | 295.0019 | 4 | 48647.0801 | 252952.3509 | 301599.431 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014688 | 304.0759 | 1 | 7503.7029 | 59495.187 | 66998.8899 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014688 | 304.0759 | 2 | 16507.7712 | 118990.374 | 135498.1452 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014688 | 304.0759 | 3 | 30611.5857 | 178485.5611 | 209097.1468 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014688 | 304.0759 | 4 | 49815.1465 | 237980.7481 | 287795.8946 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014688 | 313.15 | 1 | 7238.9824 | 55893.4534 | 63132.4358 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014688 | 313.15 | 2 | 15925.3993 | 111786.9068 | 127712.3061 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014688 | 313.15 | 3 | 29531.6502 | 167680.3602 | 197212.0104 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014688 | 313.15 | 4 | 48057.7352 | 223573.8137 | 271631.5489 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 285.9278 | 1 | 6668.4585 | 73346.8557 | 80015.3142 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 285.9278 | 2 | 14670.2753 | 146693.7114 | 161363.9867 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 285.9278 | 3 | 27204.1807 | 220040.5671 | 247244.7478 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 285.9278 | 4 | 44270.1747 | 293387.4228 | 337657.5974 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 295.0019 | 1 | 7586.4062 | 70226.021 | 77812.4272 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 295.0019 | 2 | 16689.7142 | 140452.0421 | 157141.7562 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 295.0019 | 3 | 30948.9761 | 210678.0631 | 241627.0392 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 295.0019 | 4 | 50364.1919 | 280904.0841 | 331268.276 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 304.0759 | 1 | 7954.1676 | 67246.3535 | 75200.5211 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 304.0759 | 2 | 17498.771 | 134492.7069 | 151991.478 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 304.0759 | 3 | 32449.2703 | 201739.0604 | 234188.3307 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 304.0759 | 4 | 52805.6654 | 268985.4139 | 321791.0793 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 313.15 | 1 | 7837.3728 | 64407.853 | 72245.2258 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 313.15 | 2 | 17241.8281 | 128815.7061 | 146057.5342 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 313.15 | 3 | 31972.802 | 193223.5591 | 225196.3611 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014688 | 313.15 | 4 | 52030.2944 | 257631.4121 | 309661.7065 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 285.9278 | 1 | 6595.1484 | 76019.3304 | 82614.4788 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 285.9278 | 2 | 14508.9966 | 152038.6609 | 166547.6575 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 285.9278 | 3 | 26905.1096 | 228057.9913 | 254963.1009 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 285.9278 | 4 | 43783.4873 | 304077.3218 | 347860.8091 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 295.0019 | 1 | 7651.7047 | 73661.7289 | 81313.4336 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 295.0019 | 2 | 16833.3676 | 147323.4579 | 164156.8255 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 295.0019 | 3 | 31215.3634 | 220985.1868 | 252200.5502 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 295.0019 | 4 | 50797.6919 | 294646.9158 | 345444.6077 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 304.0759 | 1 | 8154.7824 | 71445.2945 | 79600.0769 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 304.0759 | 2 | 17940.1135 | 142890.5891 | 160830.7025 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 304.0759 | 3 | 33267.6843 | 214335.8836 | 247603.568 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 304.0759 | 4 | 54137.495 | 285781.1782 | 339918.6732 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 313.15 | 1 | 8154.3165 | 69370.0272 | 77524.3437 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 313.15 | 2 | 17939.0885 | 138740.0545 | 156679.143 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 313.15 | 3 | 33265.7837 | 208110.0817 | 241375.8654 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014688 | 313.15 | 4 | 54134.402 | 277480.109 | 331614.511 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 285.9278 | 1 | 6483.8492 | 75139.5798 | 81623.429 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 285.9278 | 2 | 14264.1441 | 150279.1596 | 164543.3037 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 285.9278 | 3 | 26451.0614 | 225418.7395 | 251869.8008 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 285.9278 | 4 | 43044.6011 | 300558.3193 | 343602.9204 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 295.0019 | 1 | 7605.9855 | 73545.2115 | 81151.197 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 295.0019 | 2 | 16732.7878 | 147090.4229 | 163823.2107 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 295.0019 | 3 | 31028.8507 | 220635.6344 | 251664.4851 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 295.0019 | 4 | 50494.1743 | 294180.8459 | 344675.0202 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 304.0759 | 1 | 8196.2524 | 72092.0102 | 80288.2626 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 304.0759 | 2 | 18031.3454 | 144184.0204 | 162215.3658 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 304.0759 | 3 | 33436.8624 | 216276.0307 | 249712.8931 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 304.0759 | 4 | 54412.8035 | 288368.0409 | 342780.8444 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 313.15 | 1 | 8288.8899 | 70779.9761 | 79068.866 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 313.15 | 2 | 18235.1433 | 141559.9522 | 159795.0955 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 313.15 | 3 | 33814.7801 | 212339.9282 | 246154.7084 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014688 | 313.15 | 4 | 55027.8003 | 283119.9043 | 338147.7046 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.011302 | 277.0389 | 15000
0.011302 | 280.9278 | 15000
0.011302 | 284.8167 | 15000
0.011302 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.014688 | 285.9278 | 15000
0.014688 | 295.0019 | 15000
0.014688 | 304.0759 | 15000
0.014688 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser