## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'I': 300.0-400.0 ton, 6.28 COP, 6.76 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 8be8f696-3f57-4201-b9d2-f0b17617cc50 |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'I' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.85714 | -
| maximum | 1.1429 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Minimum scaling factor
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.052741 | 277.0389 | 0.066349 | 285.9278 | 1 | 62725.1904 | 335171.6098 | 397896.8002 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066349 | 285.9278 | 2 | 88817.5704 | 670343.2197 | 759160.7901 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066349 | 285.9278 | 3 | 129187.6487 | 1005514.8295 | 1134702.4782 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066349 | 285.9278 | 4 | 183835.4251 | 1340686.4394 | 1524521.8644 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066349 | 295.0019 | 1 | 65241.5757 | 302451.1426 | 367692.7183 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066349 | 295.0019 | 2 | 92380.7199 | 604902.2852 | 697283.0051 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066349 | 295.0019 | 3 | 134370.3495 | 907353.4279 | 1041723.7774 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066349 | 295.0019 | 4 | 191210.4646 | 1209804.5705 | 1401015.0351 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066349 | 304.0759 | 1 | 64170.4623 | 279967.1006 | 344137.5629 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066349 | 304.0759 | 2 | 90864.0456 | 559934.2011 | 650798.2467 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066349 | 304.0759 | 3 | 132164.3042 | 839901.3017 | 972065.6058 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066349 | 304.0759 | 4 | 188071.2381 | 1119868.4022 | 1307939.6403 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066349 | 313.15 | 1 | 60942.7419 | 267719.4836 | 328662.2255 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066349 | 313.15 | 2 | 86293.6603 | 535438.9673 | 621732.6276 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066349 | 313.15 | 3 | 125516.5505 | 803158.4509 | 928675.0014 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066349 | 313.15 | 4 | 178611.4126 | 1070877.9346 | 1249489.3471 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 285.9278 | 1 | 61513.9198 | 358720.6769 | 420234.5966 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 285.9278 | 2 | 87102.4364 | 717441.3537 | 804543.7901 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 285.9278 | 3 | 126692.938 | 1076162.0306 | 1202854.9686 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 285.9278 | 4 | 180285.4248 | 1434882.7074 | 1615168.1322 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 295.0019 | 1 | 66451.6131 | 331201.6746 | 397653.2877 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 295.0019 | 2 | 94094.1078 | 662403.3492 | 756497.457 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 295.0019 | 3 | 136862.5204 | 993605.0238 | 1130467.5442 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 295.0019 | 4 | 194756.8507 | 1324806.6984 | 1519563.5492 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 304.0759 | 1 | 67406.6423 | 313919.0975 | 381325.7399 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 304.0759 | 2 | 95446.4095 | 627838.195 | 723284.6045 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 304.0759 | 3 | 138829.481 | 941757.2925 | 1080586.7736 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 304.0759 | 4 | 197555.8571 | 1255676.39 | 1453232.2471 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 313.15 | 1 | 65592.9034 | 306872.9456 | 372465.849 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 313.15 | 2 | 92878.1927 | 613745.8911 | 706624.0839 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 313.15 | 3 | 135093.9377 | 920618.8367 | 1055712.7745 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066349 | 313.15 | 4 | 192240.1385 | 1227491.7823 | 1419731.9208 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 285.9278 | 1 | 58940.6498 | 371584.4797 | 430525.1295 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 285.9278 | 2 | 83458.7393 | 743168.9594 | 826627.6987 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 285.9278 | 3 | 121393.0784 | 1114753.4391 | 1236146.5175 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 285.9278 | 4 | 172743.6671 | 1486337.9188 | 1659081.5859 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 295.0019 | 1 | 65790.3211 | 349266.9424 | 415057.2635 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 295.0019 | 2 | 93157.7321 | 698533.8848 | 791691.6169 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 295.0019 | 3 | 135500.5355 | 1047800.8273 | 1183301.3628 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 295.0019 | 4 | 192818.7315 | 1397067.7697 | 1589886.5012 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 304.0759 | 1 | 68464.1259 | 337185.8303 | 405649.9562 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 304.0759 | 2 | 96943.7842 | 674371.6606 | 771315.4448 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 304.0759 | 3 | 141007.4547 | 1011557.4909 | 1152564.9456 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 304.0759 | 4 | 200655.1372 | 1348743.3212 | 1549398.4584 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 313.15 | 1 | 67958.9644 | 335341.1433 | 403300.1077 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 313.15 | 2 | 96228.486 | 670682.2867 | 766910.7727 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 313.15 | 3 | 139967.0333 | 1006023.43 | 1145990.4633 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066349 | 313.15 | 4 | 199174.6063 | 1341364.5734 | 1540539.1797 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 285.9278 | 1 | 55525.745 | 373763.0184 | 429288.7634 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 285.9278 | 2 | 78623.3049 | 747526.0368 | 826149.3417 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 285.9278 | 3 | 114359.8034 | 1121289.0551 | 1235648.8585 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 285.9278 | 4 | 162735.2404 | 1495052.0735 | 1657787.3139 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 295.0019 | 1 | 63802.8337 | 356646.9461 | 420449.7798 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 295.0019 | 2 | 90343.4911 | 713293.8922 | 803637.3832 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 295.0019 | 3 | 131407.1431 | 1069940.8382 | 1201347.9813 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 295.0019 | 4 | 186993.7897 | 1426587.7843 | 1613581.574 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 304.0759 | 1 | 67912.8163 | 349767.2989 | 417680.1153 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 304.0759 | 2 | 96163.1413 | 699534.5979 | 795697.7392 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 304.0759 | 3 | 139871.9877 | 1049301.8968 | 1189173.8845 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 304.0759 | 4 | 199039.3553 | 1399069.1957 | 1598108.5511 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 313.15 | 1 | 68635.5974 | 353124.0769 | 421759.6744 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 313.15 | 2 | 97186.5844 | 706248.1539 | 803434.7383 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 313.15 | 3 | 141360.6144 | 1059372.2308 | 1200732.8452 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066349 | 313.15 | 4 | 201157.6872 | 1412496.3078 | 1613653.995 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.052741 | 277.0389 | 15000
0.052741 | 280.9278 | 15000
0.052741 | 284.8167 | 15000
0.052741 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.066349 | 285.9278 | 15000
0.066349 | 295.0019 | 15000
0.066349 | 304.0759 | 15000
0.066349 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser