## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'S': 150.0-300.0 ton, 5.54 COP, 8.79 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | c5542f64-1d0c-482b-975a-2176bcc4fa57 |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'S' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Minimum scaling factor
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.033905 | 277.0389 | 0.043438 | 285.9278 | 1 | 17848.4869 | 203945.2164 | 221793.7033 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043438 | 285.9278 | 2 | 39512.2112 | 407890.4329 | 447402.6441 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043438 | 285.9278 | 3 | 72639.8046 | 611835.6493 | 684475.4539 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043438 | 285.9278 | 4 | 117231.2671 | 815780.8657 | 933012.1328 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043438 | 295.0019 | 1 | 20286.8684 | 191187.4551 | 211474.3236 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043438 | 295.0019 | 2 | 44910.1953 | 382374.9103 | 427285.1055 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043438 | 295.0019 | 3 | 82563.5344 | 573562.3654 | 656125.8998 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043438 | 295.0019 | 4 | 133246.8859 | 764749.8205 | 897996.7064 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043438 | 304.0759 | 1 | 20105.4736 | 174064.3725 | 194169.8461 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043438 | 304.0759 | 2 | 44508.6312 | 348128.745 | 392637.3762 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043438 | 304.0759 | 3 | 81825.2934 | 522193.1175 | 604018.4109 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043438 | 304.0759 | 4 | 132055.4602 | 696257.49 | 828312.9502 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043438 | 313.15 | 1 | 17653.7252 | 152575.9685 | 170229.6937 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043438 | 313.15 | 2 | 39081.0562 | 305151.937 | 344232.9932 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043438 | 313.15 | 3 | 71847.1632 | 457727.9055 | 529575.0687 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043438 | 313.15 | 4 | 115952.0462 | 610303.8741 | 726255.9202 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 285.9278 | 1 | 17590.605 | 222081.568 | 239672.173 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 285.9278 | 2 | 38941.3234 | 444163.136 | 483104.4594 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 285.9278 | 3 | 71590.2764 | 666244.7041 | 737834.9804 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 285.9278 | 4 | 115537.464 | 888326.2721 | 1003863.7361 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 295.0019 | 1 | 21135.1236 | 214273.1876 | 235408.3112 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 295.0019 | 2 | 46788.0261 | 428546.3751 | 475334.4012 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 295.0019 | 3 | 86015.765 | 642819.5627 | 728835.3277 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 295.0019 | 4 | 138818.3403 | 857092.7503 | 995911.0906 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 304.0759 | 1 | 22002.0093 | 202099.4858 | 224101.495 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 304.0759 | 2 | 48707.1001 | 404198.9716 | 452906.0717 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 304.0759 | 3 | 89543.8176 | 606298.4574 | 695842.275 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 304.0759 | 4 | 144512.1619 | 808397.9431 | 952910.105 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 313.15 | 1 | 20393.1855 | 185560.4627 | 205953.6481 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 313.15 | 2 | 45145.5553 | 371120.9253 | 416266.4807 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 313.15 | 3 | 82996.2237 | 556681.388 | 639677.6117 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043438 | 313.15 | 4 | 133945.1905 | 742241.8506 | 876187.0411 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 285.9278 | 1 | 16800.9232 | 229100.5112 | 245901.4344 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 285.9278 | 2 | 37193.1599 | 458201.0225 | 495394.1823 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 285.9278 | 3 | 68376.428 | 687301.5337 | 755677.9617 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 285.9278 | 4 | 110350.7276 | 916402.0449 | 1026752.7726 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 295.0019 | 1 | 21175.6437 | 226241.5116 | 247417.1554 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 295.0019 | 2 | 46877.7277 | 452483.0233 | 499360.751 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 295.0019 | 3 | 86180.6737 | 678724.5349 | 764905.2086 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 295.0019 | 4 | 139084.4817 | 904966.0465 | 1044050.5282 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 304.0759 | 1 | 22923.0259 | 219017.1907 | 241940.2166 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 304.0759 | 2 | 50746.007 | 438034.3814 | 488780.3884 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 304.0759 | 3 | 93292.1727 | 657051.5721 | 750343.7448 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 304.0759 | 4 | 150561.523 | 876068.7628 | 1026630.2859 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 313.15 | 1 | 22097.4941 | 207427.5484 | 229525.0425 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 313.15 | 2 | 48918.4803 | 414855.0969 | 463773.5772 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 313.15 | 3 | 89932.422 | 622282.6453 | 712215.0673 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043438 | 313.15 | 4 | 145139.3192 | 829710.1937 | 974849.5129 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 285.9278 | 1 | 15726.6043 | 225002.0461 | 240728.6504 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 285.9278 | 2 | 34814.879 | 450004.0921 | 484818.9712 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 285.9278 | 3 | 64004.1631 | 675006.1382 | 739010.3013 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 285.9278 | 4 | 103294.4565 | 900008.1843 | 1003302.6407 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 295.0019 | 1 | 20663.9012 | 227092.4273 | 247756.3285 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 295.0019 | 2 | 45744.8542 | 454184.8546 | 499929.7088 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 295.0019 | 3 | 84097.9831 | 681277.282 | 765375.265 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 295.0019 | 4 | 135723.2879 | 908369.7093 | 1044092.9972 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 304.0759 | 1 | 23132.3057 | 224817.4872 | 247949.7929 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 304.0759 | 2 | 51209.3016 | 449634.9745 | 500844.2761 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 304.0759 | 3 | 94143.9001 | 674452.4617 | 768596.3618 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 304.0759 | 4 | 151936.101 | 899269.949 | 1051206.05 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 313.15 | 1 | 23038.743 | 218177.2258 | 241215.9689 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 313.15 | 2 | 51002.1767 | 436354.4517 | 487356.6283 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 313.15 | 3 | 93763.1187 | 654531.6775 | 748294.7962 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043438 | 313.15 | 4 | 151321.5691 | 872708.9033 | 1024030.4724 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.033905 | 277.0389 | 15000
0.033905 | 280.9278 | 15000
0.033905 | 284.8167 | 15000
0.033905 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.043438 | 285.9278 | 15000
0.043438 | 295.0019 | 15000
0.043438 | 304.0759 | 15000
0.043438 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser