## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'Z': 0.0-150.0 ton, 5.00 COP, 5.25 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 72b4c3bc-531b-4cfd-bfe5-588063d984f5 |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'Z' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| maximum | 2 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.011302 | 277.0389 | 0.014718 | 285.9278 | 1 | 16274.4003 | 67133.4534 | 83407.8537 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014718 | 285.9278 | 2 | 22851.1495 | 134266.9069 | 157118.0563 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014718 | 285.9278 | 3 | 32303.8599 | 201400.3603 | 233704.2202 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014718 | 285.9278 | 4 | 44632.5315 | 268533.8137 | 313166.3452 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014718 | 295.0019 | 1 | 17971.9745 | 63235.6235 | 81207.598 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014718 | 295.0019 | 2 | 25234.741 | 126471.247 | 151705.988 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014718 | 295.0019 | 3 | 35673.4587 | 189706.8705 | 225380.3292 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014718 | 295.0019 | 4 | 49288.1276 | 252942.4939 | 302230.6216 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014718 | 304.0759 | 1 | 18402.8316 | 59511.5377 | 77914.3693 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014718 | 304.0759 | 2 | 25839.7145 | 119023.0753 | 144862.7898 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014718 | 304.0759 | 3 | 36528.6883 | 178534.613 | 215063.3013 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014718 | 304.0759 | 4 | 50469.753 | 238046.1507 | 288515.9037 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014718 | 313.15 | 1 | 17767.2961 | 55961.196 | 73728.4921 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014718 | 313.15 | 2 | 24947.3488 | 111922.392 | 136869.7408 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014718 | 313.15 | 3 | 35267.1825 | 167883.588 | 203150.7705 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.014718 | 313.15 | 4 | 48726.7974 | 223844.784 | 272571.5813 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 285.9278 | 1 | 16384.8173 | 73386.5041 | 89771.3214 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 285.9278 | 2 | 23006.1878 | 146773.0083 | 169779.196 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 285.9278 | 3 | 32523.032 | 220159.5124 | 252682.5444 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 285.9278 | 4 | 44935.35 | 293546.0166 | 338481.3666 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 295.0019 | 1 | 18621.4694 | 70249.5804 | 88871.0499 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 295.0019 | 2 | 26146.7074 | 140499.1608 | 166645.8682 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 295.0019 | 3 | 36962.6732 | 210748.7413 | 247711.4145 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 295.0019 | 4 | 51069.367 | 280998.3217 | 332067.6887 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 304.0759 | 1 | 19521.2182 | 67286.4008 | 86807.6191 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 304.0759 | 2 | 27410.0593 | 134572.8017 | 161982.8609 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 304.0759 | 3 | 38748.629 | 201859.2025 | 240607.8315 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 304.0759 | 4 | 53536.9275 | 269145.6033 | 322682.5308 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 313.15 | 1 | 19246.1336 | 64496.9654 | 83743.099 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 313.15 | 2 | 27023.8085 | 128993.9307 | 156017.7392 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 313.15 | 3 | 38202.6 | 193490.8961 | 231693.4961 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.014718 | 313.15 | 4 | 52782.5082 | 257987.8615 | 310770.3696 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 285.9278 | 1 | 16214.2411 | 76085.3349 | 92299.5761 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 285.9278 | 2 | 22766.679 | 152170.6699 | 174937.3489 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 285.9278 | 3 | 32184.447 | 228256.0048 | 260440.4519 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 285.9278 | 4 | 44467.5451 | 304341.3398 | 348808.8849 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 295.0019 | 1 | 18791.0862 | 73709.3174 | 92500.4036 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 295.0019 | 2 | 26384.869 | 147418.6349 | 173803.5039 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 295.0019 | 3 | 37299.3539 | 221127.9523 | 258427.3062 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 295.0019 | 4 | 51534.5408 | 294837.2698 | 346371.8106 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 304.0759 | 1 | 20022.0456 | 71507.0441 | 91529.0897 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 304.0759 | 2 | 28113.279 | 143014.0882 | 171127.3672 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 304.0759 | 3 | 39742.7459 | 214521.1322 | 254263.8781 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 304.0759 | 4 | 54910.4461 | 286028.1763 | 340938.6224 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 313.15 | 1 | 20030.9348 | 69478.5148 | 89509.4496 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 313.15 | 2 | 28125.7605 | 138957.0297 | 167082.7902 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 313.15 | 3 | 39760.3905 | 208435.5445 | 248195.9351 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.014718 | 313.15 | 4 | 54934.8248 | 277914.0594 | 332848.8841 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 285.9278 | 1 | 15943.8054 | 75229.9459 | 91173.7512 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 285.9278 | 2 | 22386.9558 | 150459.8917 | 172846.8475 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 285.9278 | 3 | 31647.6457 | 225689.8376 | 257337.4833 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 285.9278 | 4 | 43725.8751 | 300919.7834 | 344645.6586 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 295.0019 | 1 | 18682.2597 | 73614.8346 | 92297.0943 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 295.0019 | 2 | 26232.064 | 147229.6692 | 173461.7332 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 295.0019 | 3 | 37083.3389 | 220844.5037 | 257927.8426 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 295.0019 | 4 | 51236.0844 | 294459.3383 | 345695.4227 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 304.0759 | 1 | 20127.0502 | 72173.4674 | 92300.5177 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 304.0759 | 2 | 28260.7178 | 144346.9349 | 172607.6527 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 304.0759 | 3 | 39951.1748 | 216520.4023 | 256471.5771 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 304.0759 | 4 | 55198.4213 | 288693.8697 | 343892.2911 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 313.15 | 1 | 20363.7377 | 70905.8444 | 91269.5822 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 313.15 | 2 | 28593.0546 | 141811.6889 | 170404.7434 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 313.15 | 3 | 40420.9875 | 212717.5333 | 253138.5208 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.014718 | 313.15 | 4 | 55847.5367 | 283623.3777 | 339470.9144 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.011302 | 277.0389 | 15000
0.011302 | 280.9278 | 15000
0.011302 | 284.8167 | 15000
0.011302 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.014718 | 285.9278 | 15000
0.014718 | 295.0019 | 15000
0.014718 | 304.0759 | 15000
0.014718 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser