## RS0004
RS0004: Air-to-Air Direct Expansion Refrigerant System
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| schema_version | 2.0.0 |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0004 |  | ✓
| description | DX System with two-stage cooling |  | ✓
| id | 123e4567-e89b-12d3-a456-426614174000 |  | ✓
| data_timestamp | 2022-04-10T00:00Z |  | ✓
| data_version | 1 |  | ✓
| data_source | Heat Pump Design Model by Oak Ridge National Laboratory
| disclaimer | Example data not to be used for simulation
| notes | An example representation that applies a two-stage residential air conditioner having a SEER of 16.0.
description
description.product_information
| outdoor_unit_manufacturer | ABC HVAC
| outdoor_unit_model_number | DX AB12
| indoor_unit_manufacturer | ABC HVAC
| indoor_unit_model_number | DX AB12
| refrigerant | R-410A
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | DISCRETE |  | ✓
| cycling_degradation_coefficient | 0.1 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: The version of the schema the data complies with
Note on B5: Data model name
Note on B6: Schema name or identifier
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Outdoor unit manufacturer name
Note on B17: Outdoor unit model number
Note on B18: Indoor unit manufacturer name
Note on B19: Indoor unit model number
Note on B20: Refrigerant used
Note on B21: Type of compressor
Note on A22: Data group containing performance information
Note on B23: Method used to control different speeds of the compressor
Note on B24: Cycling degradation coefficient (C~D~) as described in AHRI 210/240
Note on A25: Data group describing cooling performance over a range of conditions
Note on A26: Data group describing standby performance

## performance_map_cooling
performance.performance_map_cooling
grid_variables | [5 empty] | lookup_variables
outdoor_coil_entering_dry_bulb_temperature | indoor_coil_entering_relative_humidity | indoor_coil_entering_dry_bulb_temperature | indoor_coil_air_mass_flow_rate | compressor_sequence_number | ambient_absolute_air_pressure | gross_total_capacity | gross_sensible_capacity | gross_power | operation_state
K | - | K | kg/s | - | Pa | W | W | W | -
285.928 | 0.05 | 288.706 | 0.5 | 1 | 57226.51 | 8882.415 | 8880.15 | 2169.513 | NORMAL
285.928 | 0.05 | 288.706 | 0.5 | 1 | 79289.74 | 9041.7937 | 9021.0699 | 2023.103 | NORMAL
285.928 | 0.05 | 288.706 | 0.5 | 1 | 101352.97 | 9126.8171 | 9097.9672 | 1946.7541 | NORMAL
285.928 | 0.05 | 288.706 | 0.5 | 1 | 106868.78 | 9121.483 | 9119.2756 | 1935.7017 | NORMAL
285.928 | 0.05 | 288.706 | 0.5 | 2 | 57226.51 | 10799.3259 | 10781.3342 | 2895.62 | NORMAL
285.928 | 0.05 | 288.706 | 0.5 | 2 | 79289.74 | 10978.8687 | 10972.3582 | 2684.535 | NORMAL
285.928 | 0.05 | 288.706 | 0.5 | 2 | 101352.97 | 11066.0023 | 11060.0156 | 2575.3636 | NORMAL
285.928 | 0.05 | 288.706 | 0.5 | 2 | 106868.78 | 11062.0457 | 11060.2979 | 2555.8452 | NORMAL
285.928 | 0.05 | 288.706 | 0.8 | 1 | 57226.51 | 10253.9859 | 10217.3177 | 2189.719 | NORMAL
285.928 | 0.05 | 288.706 | 0.8 | 1 | 79289.74 | 10487.0457 | 10483.0502 | 2011.739 | NORMAL
285.928 | 0.05 | 288.706 | 0.8 | 1 | 101352.97 | 10615.6213 | 10591.577 | 1916.404 | NORMAL
285.928 | 0.05 | 288.706 | 0.8 | 1 | 106868.78 | 10638.306 | 10634.3485 | 1899.646 | NORMAL
285.928 | 0.05 | 288.706 | 0.8 | 2 | 57226.51 | 12696.4537 | 12692.5559 | 3038.304 | NORMAL
285.928 | 0.05 | 288.706 | 0.8 | 2 | 79289.74 | 12983.4994 | 12979.6303 | 2783.327 | NORMAL
285.928 | 0.05 | 288.706 | 0.8 | 2 | 101352.97 | 13137.6319 | 13133.7826 | 2651.635 | NORMAL
285.928 | 0.05 | 288.706 | 0.8 | 2 | 106868.78 | 13148.2415 | 13144.4417 | 2628.781 | NORMAL
285.928 | 0.05 | 288.706 | 1.11 | 1 | 57226.51 | 11044.7538 | 10959.157 | 2203.06 | NORMAL
285.928 | 0.05 | 288.706 | 1.11 | 1 | 79289.74 | 11327.1981 | 11321.9196 | 2007.239 | NORMAL
285.928 | 0.05 | 288.706 | 1.11 | 1 | 101352.97 | 11487.1629 | 11481.8674 | 1901.034 | NORMAL
285.928 | 0.05 | 288.706 | 1.11 | 1 | 106868.78 | 11516.2661 | 11510.9571 | 1881.946 | NORMAL
285.928 | 0.05 | 288.706 | 1.11 | 2 | 57226.51 | 13811.3716 | 13805.8471 | 3124.89 | NORMAL
285.928 | 0.05 | 288.706 | 1.11 | 2 | 79289.74 | 14174.8828 | 14169.3687 | 2843.525 | NORMAL
285.928 | 0.05 | 288.706 | 1.11 | 2 | 101352.97 | 14372.3036 | 14366.526 | 2698.949 | NORMAL
285.928 | 0.05 | 288.706 | 1.11 | 2 | 106868.78 | 14407.2392 | 14401.7644 | 2673.456 | NORMAL
285.928 | 0.05 | 288.706 | 1.42 | 1 | 57226.51 | 11570.9848 | 11564.8753 | 2212.88 | NORMAL
285.928 | 0.05 | 288.706 | 1.42 | 1 | 79289.74 | 11892.1747 | 11885.9432 | 2004.77 | NORMAL
285.928 | 0.05 | 288.706 | 1.42 | 1 | 101352.97 | 12075.762 | 12069.4947 | 1891.426 | NORMAL
285.928 | 0.05 | 288.706 | 1.42 | 1 | 106868.78 | 12109.9941 | 12101.6503 | 1870.648 | NORMAL
285.928 | 0.05 | 288.706 | 1.42 | 2 | 57226.51 | 14554.7773 | 14548.0529 | 3184.02 | NORMAL
285.928 | 0.05 | 288.706 | 1.42 | 2 | 79289.74 | 14991.1782 | 14984.3722 | 2885.6 | NORMAL
285.928 | 0.05 | 288.706 | 1.42 | 2 | 101352.97 | 15224.1794 | 15217.3437 | 2732.427 | NORMAL
285.928 | 0.05 | 288.706 | 1.42 | 2 | 106868.78 | 15266.1196 | 15259.2804 | 2705.444 | NORMAL
285.928 | 0.05 | 291.483 | 0.5 | 1 | 57226.51 | 9430.0996 | 9413.0029 | 2177.153 | NORMAL
285.928 | 0.05 | 291.483 | 0.5 | 1 | 79289.74 | 9609.5838 | 9606.6049 | 2017.414 | NORMAL
285.928 | 0.05 | 291.483 | 0.5 | 1 | 101352.97 | 9704.1911 | 9691.76 | 1934.499 | NORMAL
285.928 | 0.05 | 291.483 | 0.5 | 1 | 106868.78 | 9705.1876 | 9702.2566 | 1920.6072 | NORMAL
285.928 | 0.05 | 291.483 | 0.5 | 2 | 57226.51 | 11408.646 | 11406.1132 | 2943.336 | NORMAL
285.928 | 0.05 | 291.483 | 0.5 | 2 | 79289.74 | 11608.177 | 11605.7277 | 2715.376 | NORMAL
285.928 | 0.05 | 291.483 | 0.5 | 2 | 101352.97 | 11705.2169 | 11702.7939 | 2598.7013 | NORMAL
285.928 | 0.05 | 291.483 | 0.5 | 2 | 106868.78 | 11705.6272 | 11703.251 | 2577.5041 | NORMAL
285.928 | 0.05 | 291.483 | 0.8 | 1 | 57226.51 | 10932.7374 | 10927.5334 | 2201.121 | NORMAL
285.928 | 0.05 | 291.483 | 0.8 | 1 | 79289.74 | 11188.3939 | 11183.1689 | 2007.914 | NORMAL
285.928 | 0.05 | 291.483 | 0.8 | 1 | 101352.97 | 11331.9754 | 11326.7513 | 1903.701 | NORMAL
285.928 | 0.05 | 291.483 | 0.8 | 1 | 106868.78 | 11357.9132 | 11352.6886 | 1885.122 | NORMAL
285.928 | 0.05 | 291.483 | 0.8 | 2 | 57226.51 | 13449.2673 | 13418.3878 | 3096.51 | NORMAL
285.928 | 0.05 | 291.483 | 0.8 | 2 | 79289.74 | 13770.1641 | 13755.1684 | 2822.927 | NORMAL
285.928 | 0.05 | 291.483 | 0.8 | 2 | 101352.97 | 13939.1559 | 13934.0681 | 2682.255 | NORMAL
285.928 | 0.05 | 291.483 | 0.8 | 2 | 106868.78 | 13968.9918 | 13963.9769 | 2657.458 | NORMAL
285.928 | 0.05 | 291.483 | 1.11 | 1 | 57226.51 | 11796.3658 | 11789.5829 | 2217.26 | NORMAL
285.928 | 0.05 | 291.483 | 1.11 | 1 | 79289.74 | 12111.2544 | 12104.3994 | 2003.963 | NORMAL
285.928 | 0.05 | 291.483 | 1.11 | 1 | 101352.97 | 12290.5334 | 12283.6507 | 1887.932 | NORMAL
285.928 | 0.05 | 291.483 | 1.11 | 1 | 106868.78 | 12322.4795 | 12315.5912 | 1866.985 | NORMAL
285.928 | 0.05 | 291.483 | 1.11 | 2 | 57226.51 | 14647.9191 | 14640.7709 | 3191.48 | NORMAL
285.928 | 0.05 | 291.483 | 1.11 | 2 | 79289.74 | 15064.2439 | 15057.0431 | 2889.356 | NORMAL
285.928 | 0.05 | 291.483 | 1.11 | 2 | 101352.97 | 15285.1114 | 15277.8968 | 2734.791 | NORMAL
285.928 | 0.05 | 291.483 | 1.11 | 2 | 106868.78 | 15324.9414 | 15317.7233 | 2707.655 | NORMAL
285.928 | 0.05 | 291.483 | 1.42 | 1 | 57226.51 | 12372.3329 | 12361.3092 | 2229.17 | NORMAL
285.928 | 0.05 | 291.483 | 1.42 | 1 | 79289.74 | 12733.7925 | 12725.732 | 2002.24 | NORMAL
285.928 | 0.05 | 291.483 | 1.42 | 1 | 101352.97 | 12941.0317 | 12932.9047 | 1877.541 | NORMAL
285.928 | 0.05 | 291.483 | 1.42 | 1 | 106868.78 | 12979.6893 | 12971.5511 | 1857.666 | NORMAL
285.928 | 0.05 | 291.483 | 1.42 | 2 | 57226.51 | 15457.7667 | 15449.0176 | 3257.53 | NORMAL
285.928 | 0.05 | 291.483 | 1.42 | 2 | 79289.74 | 15948.7984 | 15939.9627 | 2936.71 | NORMAL
285.928 | 0.05 | 291.483 | 1.42 | 2 | 101352.97 | 16211.6354 | 16202.7514 | 2771.892 | NORMAL
285.928 | 0.05 | 291.483 | 1.42 | 2 | 106868.78 | 16259.1149 | 16250.2211 | 2743.289 | NORMAL
285.928 | 0.05 | 294.26 | 0.5 | 1 | 57226.51 | 9994.0211 | 9978.1806 | 2185.595 | NORMAL
285.928 | 0.05 | 294.26 | 0.5 | 1 | 79289.74 | 10188.4818 | 10165.2521 | 2013.617 | NORMAL
285.928 | 0.05 | 294.26 | 0.5 | 1 | 101352.97 | 10289.83 | 10257.9315 | 1922.635 | NORMAL
285.928 | 0.05 | 294.26 | 0.5 | 1 | 106868.78 | 10307.6495 | 10303.846 | 1906.9642 | NORMAL
285.928 | 0.05 | 294.26 | 0.5 | 2 | 57226.51 | 12031.3599 | 12028.0392 | 2987.723 | NORMAL
285.928 | 0.05 | 294.26 | 0.5 | 2 | 79289.74 | 12245.3986 | 12214.9565 | 2746.72 | NORMAL
285.928 | 0.05 | 294.26 | 0.5 | 2 | 101352.97 | 12358.4115 | 12331.3589 | 2622.3741 | NORMAL
285.928 | 0.05 | 294.26 | 0.5 | 2 | 106868.78 | 12356.5065 | 12353.3185 | 2600.1419 | NORMAL
285.928 | 0.05 | 294.26 | 0.8 | 1 | 57226.51 | 11625.1465 | 11618.5086 | 2213.892 | NORMAL
285.928 | 0.05 | 294.26 | 0.8 | 1 | 79289.74 | 11907.1512 | 11900.4951 | 2004.683 | NORMAL
285.928 | 0.05 | 294.26 | 0.8 | 1 | 101352.97 | 12065.8851 | 12059.2127 | 1891.589 | NORMAL
285.928 | 0.05 | 294.26 | 0.8 | 1 | 106868.78 | 12095.8382 | 12089.1734 | 1870.909 | NORMAL
285.928 | 0.05 | 294.26 | 0.8 | 2 | 57226.51 | 14217.5264 | 14208.2281 | 3157.062 | NORMAL
285.928 | 0.05 | 294.26 | 0.8 | 2 | 79289.74 | 14574.0035 | 14522.1201 | 2864.004 | NORMAL
285.928 | 0.05 | 294.26 | 0.8 | 2 | 101352.97 | 14761.9871 | 14755.4328 | 2714.123 | NORMAL
285.928 | 0.05 | 294.26 | 0.8 | 2 | 106868.78 | 14795.5451 | 14789.0055 | 2687.841 | NORMAL
285.928 | 0.05 | 294.26 | 1.11 | 1 | 57226.51 | 12564.9472 | 12542.6822 | 2233.32 | NORMAL
285.928 | 0.05 | 294.26 | 1.11 | 1 | 79289.74 | 12915.2989 | 12906.594 | 2001.82 | NORMAL
285.928 | 0.05 | 294.26 | 1.11 | 1 | 101352.97 | 13115.7093 | 13106.9611 | 1874.955 | NORMAL
285.928 | 0.05 | 294.26 | 1.11 | 1 | 106868.78 | 13152.9894 | 13144.2296 | 1852.227 | NORMAL
285.928 | 0.05 | 294.26 | 1.11 | 2 | 57226.51 | 15503.9859 | 15490.637 | 3261.38 | NORMAL
285.928 | 0.05 | 294.26 | 1.11 | 2 | 79289.74 | 15969.578 | 15960.3954 | 2937.814 | NORMAL
285.928 | 0.05 | 294.26 | 1.11 | 2 | 101352.97 | 16216.8523 | 16207.6573 | 2772.083 | NORMAL
285.928 | 0.05 | 294.26 | 1.11 | 2 | 106868.78 | 16260.9027 | 16251.699 | 2743.359 | NORMAL
285.928 | 0.05 | 294.26 | 1.42 | 1 | 57226.51 | 13193.5815 | 13157.2463 | 2247.74 | NORMAL
285.928 | 0.05 | 294.26 | 1.42 | 1 | 79289.74 | 13597.5381 | 13573.1713 | 2000.81 | NORMAL
285.928 | 0.05 | 294.26 | 1.42 | 1 | 101352.97 | 13827.8136 | 13817.5119 | 1865.119 | NORMAL
285.928 | 0.05 | 294.26 | 1.42 | 1 | 106868.78 | 13870.721 | 13860.4012 | 1840.712 | NORMAL
285.928 | 0.05 | 294.26 | 1.42 | 2 | 57226.51 | 16372.9191 | 16355.8422 | 3334.68 | NORMAL
285.928 | 0.05 | 294.26 | 1.42 | 2 | 79289.74 | 16925.4103 | 16914.2057 | 2989.66 | NORMAL
285.928 | 0.05 | 294.26 | 1.42 | 2 | 101352.97 | 17219.3728 | 17208.0941 | 2814.109 | NORMAL
285.928 | 0.05 | 294.26 | 1.42 | 2 | 106868.78 | 17272.5674 | 17261.2884 | 2782.964 | NORMAL
285.928 | 0.05 | 297.037 | 0.5 | 1 | 57226.51 | 10569.7245 | 10564.8201 | 2194.893 | NORMAL
285.928 | 0.05 | 297.037 | 0.5 | 1 | 79289.74 | 10777.1102 | 10772.2174 | 2010.095 | NORMAL
285.928 | 0.05 | 297.037 | 0.5 | 1 | 101352.97 | 10889.83 | 10884.984 | 1911.566 | NORMAL
285.928 | 0.05 | 297.037 | 0.5 | 1 | 106868.78 | 10911.5768 | 10906.7321 | 1893.8177 | NORMAL
285.928 | 0.05 | 297.037 | 0.5 | 2 | 57226.51 | 12659.789 | 12655.4973 | 3035.483 | NORMAL
285.928 | 0.05 | 297.037 | 0.5 | 2 | 79289.74 | 12898.9449 | 12878.9386 | 2779.177 | NORMAL
285.928 | 0.05 | 297.037 | 0.5 | 2 | 101352.97 | 13023.6518 | 13019.5103 | 2647.365 | NORMAL
285.928 | 0.05 | 297.037 | 0.5 | 2 | 106868.78 | 13030.0703 | 13025.9659 | 2624.4408 | NORMAL
285.928 | 0.05 | 297.037 | 0.8 | 1 | 57226.51 | 12331.1841 | 12317.1142 | 2228.212 | NORMAL
285.928 | 0.05 | 297.037 | 0.8 | 1 | 79289.74 | 12641.3834 | 12633.04 | 2002.408 | NORMAL
285.928 | 0.05 | 297.037 | 0.8 | 1 | 101352.97 | 12817.8488 | 12809.4915 | 1879.268 | NORMAL
285.928 | 0.05 | 297.037 | 0.8 | 1 | 106868.78 | 12849.8242 | 12841.4718 | 1857.526 | NORMAL
285.928 | 0.05 | 297.037 | 0.8 | 2 | 57226.51 | 14996.2485 | 14982.6319 | 3219.611 | NORMAL
285.928 | 0.05 | 297.037 | 0.8 | 2 | 79289.74 | 15391.1196 | 15382.8546 | 2906.435 | NORMAL
285.928 | 0.05 | 297.037 | 0.8 | 2 | 101352.97 | 15599.2673 | 15591.0153 | 2747.302 | NORMAL
285.928 | 0.05 | 297.037 | 0.8 | 2 | 106868.78 | 15636.9578 | 15628.7171 | 2719.417 | NORMAL
285.928 | 0.05 | 297.037 | 1.11 | 1 | 57226.51 | 13349.0621 | 13338.3295 | 2251.5 | NORMAL
285.928 | 0.05 | 297.037 | 1.11 | 1 | 79289.74 | 13739.6835 | 13728.8291 | 2001.788 | NORMAL
285.928 | 0.05 | 297.037 | 1.11 | 1 | 101352.97 | 13960.3458 | 13949.4289 | 1863.277 | NORMAL
285.928 | 0.05 | 297.037 | 1.11 | 1 | 106868.78 | 14001.8464 | 13990.911 | 1838.734 | NORMAL
285.928 | 0.05 | 297.037 | 1.11 | 2 | 57226.51 | 16371.1313 | 16359.7206 | 3334.55 | NORMAL
285.928 | 0.05 | 297.037 | 1.11 | 2 | 79289.74 | 16890.2989 | 16878.8135 | 2987.737 | NORMAL
285.928 | 0.05 | 297.037 | 1.11 | 2 | 101352.97 | 17165.2696 | 17153.7689 | 2811.886 | NORMAL
285.928 | 0.05 | 297.037 | 1.11 | 2 | 106868.78 | 17214.4783 | 17202.9618 | 2780.653 | NORMAL
285.928 | 0.05 | 297.037 | 1.42 | 1 | 57226.51 | 14032.4443 | 14019.9274 | 2268.72 | NORMAL
285.928 | 0.05 | 297.037 | 1.42 | 1 | 79289.74 | 14483.2063 | 14470.4756 | 2002.19 | NORMAL
285.928 | 0.05 | 297.037 | 1.42 | 1 | 101352.97 | 14738.7163 | 14725.8641 | 1853.533 | NORMAL
285.928 | 0.05 | 297.037 | 1.42 | 1 | 106868.78 | 14786.6647 | 14773.7855 | 1827.203 | NORMAL
285.928 | 0.05 | 297.037 | 1.42 | 2 | 57226.51 | 17301.4947 | 17287.7054 | 3415.27 | NORMAL
285.928 | 0.05 | 297.037 | 1.42 | 2 | 79289.74 | 17918.1125 | 17904.1543 | 3045.12 | NORMAL
285.928 | 0.05 | 297.037 | 1.42 | 2 | 101352.97 | 18247.2743 | 18233.2239 | 2857.917 | NORMAL
285.928 | 0.05 | 297.037 | 1.42 | 2 | 106868.78 | 18305.9496 | 18291.8723 | 2824.787 | NORMAL
285.928 | 0.05 | 299.814 | 0.5 | 1 | 57226.51 | 11154.3376 | 11148.225 | 2205.16 | NORMAL
285.928 | 0.05 | 299.814 | 0.5 | 1 | 79289.74 | 11378.8101 | 11372.7452 | 2006.977 | NORMAL
285.928 | 0.05 | 299.814 | 0.5 | 1 | 101352.97 | 11503.4291 | 11497.4013 | 1900.769 | NORMAL
285.928 | 0.05 | 299.814 | 0.5 | 1 | 106868.78 | 11526.2309 | 11520.2027 | 1881.6971 | NORMAL
285.928 | 0.05 | 299.814 | 0.5 | 2 | 57226.51 | 13293.5815 | 13284.2893 | 3087.364 | NORMAL
285.928 | 0.05 | 299.814 | 0.5 | 2 | 79289.74 | 13553.5756 | 13534.4922 | 2811.995 | NORMAL
285.928 | 0.05 | 299.814 | 0.5 | 2 | 101352.97 | 13688.6284 | 13676.9109 | 2672.687 | NORMAL
285.928 | 0.05 | 299.814 | 0.5 | 2 | 106868.78 | 13712.8957 | 13707.7259 | 2648.1169 | NORMAL
285.928 | 0.05 | 299.814 | 0.8 | 1 | 57226.51 | 13049.2966 | 13039.066 | 2244.288 | NORMAL
285.928 | 0.05 | 299.814 | 0.8 | 1 | 79289.74 | 13391.1489 | 13380.8779 | 2000.945 | NORMAL
285.928 | 0.05 | 299.814 | 0.8 | 1 | 101352.97 | 13584.7011 | 13574.4174 | 1868.27 | NORMAL
285.928 | 0.05 | 299.814 | 0.8 | 1 | 106868.78 | 13620.7796 | 13610.4823 | 1844.633 | NORMAL
285.928 | 0.05 | 299.814 | 0.8 | 2 | 57226.51 | 15783.646 | 15773.3708 | 3284.742 | NORMAL
285.928 | 0.05 | 299.814 | 0.8 | 2 | 79289.74 | 16220.4279 | 16210.1928 | 2951.298 | NORMAL
285.928 | 0.05 | 299.814 | 0.8 | 2 | 101352.97 | 16450.8793 | 16440.6797 | 2781.568 | NORMAL
285.928 | 0.05 | 299.814 | 0.8 | 2 | 106868.78 | 16491.7644 | 16481.5724 | 2752.303 | NORMAL
285.928 | 0.05 | 299.814 | 1.11 | 1 | 57226.51 | 14149.5018 | 14136.3286 | 2271.78 | NORMAL
285.928 | 0.05 | 299.814 | 1.11 | 1 | 79289.74 | 14581.8288 | 14568.4865 | 2002.325 | NORMAL
285.928 | 0.05 | 299.814 | 1.11 | 1 | 101352.97 | 14824.1501 | 14810.7194 | 1852.52 | NORMAL
285.928 | 0.05 | 299.814 | 1.11 | 1 | 106868.78 | 14869.8417 | 14856.3994 | 1826.04 | NORMAL
285.928 | 0.05 | 299.814 | 1.11 | 2 | 57226.51 | 17250.1465 | 17236.1222 | 3410.76 | NORMAL
285.928 | 0.05 | 299.814 | 1.11 | 2 | 79289.74 | 17825.2345 | 17811.1169 | 3039.806 | NORMAL
285.928 | 0.05 | 299.814 | 1.11 | 2 | 101352.97 | 18130.1876 | 18116.0279 | 2852.868 | NORMAL
285.928 | 0.05 | 299.814 | 1.11 | 2 | 106868.78 | 18185.2579 | 18171.0916 | 2819.801 | NORMAL
285.928 | 0.05 | 299.814 | 1.42 | 1 | 57226.51 | 14887.544 | 14872.1949 | 2292.3 | NORMAL
285.928 | 0.05 | 299.814 | 1.42 | 1 | 79289.74 | 15389.5956 | 15373.9597 | 2004.31 | NORMAL
285.928 | 0.05 | 299.814 | 1.42 | 1 | 101352.97 | 15671.8347 | 15656.0532 | 1844.469 | NORMAL
285.928 | 0.05 | 299.814 | 1.42 | 1 | 106868.78 | 15723.7397 | 15707.9217 | 1814.712 | NORMAL
285.928 | 0.05 | 299.814 | 1.42 | 2 | 57226.51 | 18240.7386 | 18211.1521 | 3499.67 | NORMAL
285.928 | 0.05 | 299.814 | 1.42 | 2 | 79289.74 | 18927.0516 | 18904.1877 | 3103.1 | NORMAL
285.928 | 0.05 | 299.814 | 1.42 | 2 | 101352.97 | 19292.6436 | 19275.396 | 2903.847 | NORMAL
285.928 | 0.05 | 299.814 | 1.42 | 2 | 106868.78 | 19358.3529 | 19341.0852 | 2868.652 | NORMAL
285.928 | 0.05 | 302.591 | 0.5 | 1 | 57226.51 | 11748.3587 | 11740.8868 | 2216.437 | NORMAL
285.928 | 0.05 | 302.591 | 0.5 | 1 | 79289.74 | 11991.7057 | 11984.2949 | 2004.372 | NORMAL
285.928 | 0.05 | 302.591 | 0.5 | 1 | 101352.97 | 12126.3189 | 12118.9461 | 1890.62 | NORMAL
285.928 | 0.05 | 302.591 | 0.5 | 1 | 106868.78 | 12151.612 | 12144.2481 | 1869.8859 | NORMAL
285.928 | 0.05 | 302.591 | 0.5 | 2 | 57226.51 | 13939.7714 | 13933.0942 | 3134.972 | NORMAL
285.928 | 0.05 | 302.591 | 0.5 | 2 | 79289.74 | 14222.1278 | 14190.2987 | 2845.987 | NORMAL
285.928 | 0.05 | 302.591 | 0.5 | 2 | 101352.97 | 14369.2263 | 14362.7457 | 2698.877 | NORMAL
285.928 | 0.05 | 302.591 | 0.5 | 2 | 106868.78 | 14395.8089 | 14389.4172 | 2673.051 | NORMAL
285.928 | 0.05 | 302.591 | 0.8 | 1 | 57226.51 | 13780.9203 | 13768.5037 | 2262.167 | NORMAL
285.928 | 0.05 | 302.591 | 0.8 | 1 | 79289.74 | 14156.9461 | 14144.4738 | 2001.88 | NORMAL
285.928 | 0.05 | 302.591 | 0.8 | 1 | 101352.97 | 14366.9695 | 14354.4703 | 1858.008 | NORMAL
285.928 | 0.05 | 302.591 | 0.8 | 1 | 106868.78 | 14406.5944 | 14394.0894 | 1832.678 | NORMAL
285.928 | 0.05 | 302.591 | 0.8 | 2 | 57226.51 | 16581.272 | 16568.7531 | 3352.404 | NORMAL
285.928 | 0.05 | 302.591 | 0.8 | 2 | 79289.74 | 17061.8699 | 17049.3976 | 2997.186 | NORMAL
285.928 | 0.05 | 302.591 | 0.8 | 2 | 101352.97 | 17314.2732 | 17301.8415 | 2818.114 | NORMAL
285.928 | 0.05 | 302.591 | 0.8 | 2 | 106868.78 | 17359.8476 | 17347.4179 | 2786.445 | NORMAL
285.928 | 0.05 | 302.591 | 1.11 | 1 | 57226.51 | 14964.6249 | 14948.6576 | 2294.53 | NORMAL
285.928 | 0.05 | 302.591 | 1.11 | 1 | 79289.74 | 15441.0317 | 15424.8494 | 2004.482 | NORMAL
285.928 | 0.05 | 302.591 | 1.11 | 1 | 101352.97 | 15707.7081 | 15691.4349 | 1844.116 | NORMAL
285.928 | 0.05 | 302.591 | 1.11 | 1 | 106868.78 | 15757.034 | 15740.7255 | 1814.34 | NORMAL
285.928 | 0.05 | 302.591 | 1.11 | 2 | 57226.51 | 18137.456 | 18120.4612 | 3490.32 | NORMAL
285.928 | 0.05 | 302.591 | 1.11 | 2 | 79289.74 | 18774.0035 | 18756.8816 | 3094.201 | NORMAL
285.928 | 0.05 | 302.591 | 1.11 | 2 | 101352.97 | 19110.8734 | 19093.6927 | 2895.765 | NORMAL
285.928 | 0.05 | 302.591 | 1.11 | 2 | 106868.78 | 19171.3072 | 19154.1105 | 2860.759 | NORMAL
285.928 | 0.05 | 302.591 | 1.42 | 1 | 57226.51 | 15758.4994 | 15737.6982 | 2318.67 | NORMAL
285.928 | 0.05 | 302.591 | 1.42 | 1 | 79289.74 | 16315.211 | 16296.2691 | 2008.19 | NORMAL
285.928 | 0.05 | 302.591 | 1.42 | 1 | 101352.97 | 16625.5275 | 16596.1835 | 1835.719 | NORMAL
285.928 | 0.05 | 302.591 | 1.42 | 1 | 106868.78 | 16682.5909 | 16663.4226 | 1803.476 | NORMAL
285.928 | 0.05 | 302.591 | 1.42 | 2 | 57226.51 | 19188.8042 | 19168.3873 | 3588.3 | NORMAL
285.928 | 0.05 | 302.591 | 1.42 | 2 | 79289.74 | 19950.9379 | 19930.1889 | 3163.94 | NORMAL
285.928 | 0.05 | 302.591 | 1.42 | 2 | 101352.97 | 20356.5651 | 20335.6792 | 2952.326 | NORMAL
285.928 | 0.05 | 302.591 | 1.42 | 2 | 106868.78 | 20428.1946 | 20407.2761 | 2914.687 | NORMAL
285.928 | 0.05 | 305.368 | 0.5 | 1 | 57226.51 | 12353.6049 | 12344.5868 | 2228.811 | NORMAL
285.928 | 0.05 | 305.368 | 0.5 | 1 | 79289.74 | 12614.0973 | 12605.1539 | 2002.45 | NORMAL
285.928 | 0.05 | 305.368 | 0.5 | 1 | 101352.97 | 12760.4631 | 12751.569 | 1880.089 | NORMAL
285.928 | 0.05 | 305.368 | 0.5 | 1 | 106868.78 | 12787.0164 | 12778.1294 | 1858.6216 | NORMAL
285.928 | 0.05 | 305.368 | 0.5 | 2 | 57226.51 | 14591.8523 | 14583.7246 | 3186.746 | NORMAL
285.928 | 0.05 | 305.368 | 0.5 | 2 | 79289.74 | 14899.1501 | 14891.179 | 2880.848 | NORMAL
285.928 | 0.05 | 305.368 | 0.5 | 2 | 101352.97 | 15058.5287 | 15050.6531 | 2725.911 | NORMAL
285.928 | 0.05 | 305.368 | 0.5 | 2 | 106868.78 | 15087.4854 | 15079.6248 | 2698.7928 | NORMAL
285.928 | 0.05 | 305.368 | 0.8 | 1 | 57226.51 | 14524.7069 | 14509.8191 | 2281.955 | NORMAL
285.928 | 0.05 | 305.368 | 0.8 | 1 | 79289.74 | 14935.9613 | 14920.9955 | 2003.065 | NORMAL
285.928 | 0.05 | 305.368 | 0.8 | 1 | 101352.97 | 15164.3904 | 15149.3928 | 1849.729 | NORMAL
285.928 | 0.05 | 305.368 | 0.8 | 1 | 106868.78 | 15207.3564 | 15192.3619 | 1821.428 | NORMAL
285.928 | 0.05 | 305.368 | 0.8 | 2 | 57226.51 | 17385.9613 | 17370.9051 | 3422.768 | NORMAL
285.928 | 0.05 | 305.368 | 0.8 | 2 | 79289.74 | 17914.0094 | 17899.0154 | 3044.883 | NORMAL
285.928 | 0.05 | 305.368 | 0.8 | 2 | 101352.97 | 18190.5334 | 18175.5626 | 2855.435 | NORMAL
285.928 | 0.05 | 305.368 | 0.8 | 2 | 106868.78 | 18240.0352 | 18225.0783 | 2822.101 | NORMAL
285.928 | 0.05 | 305.368 | 1.11 | 1 | 57226.51 | 15792.966 | 15752.8677 | 2319.7 | NORMAL
285.928 | 0.05 | 305.368 | 1.11 | 1 | 79289.74 | 16317.4678 | 16298.0826 | 2008.217 | NORMAL
285.928 | 0.05 | 305.368 | 1.11 | 1 | 101352.97 | 16609.2907 | 16589.7748 | 1835.863 | NORMAL
285.928 | 0.05 | 305.368 | 1.11 | 1 | 106868.78 | 16662.6612 | 16643.1326 | 1803.659 | NORMAL
285.928 | 0.05 | 305.368 | 1.11 | 2 | 57226.51 | 19032.5615 | 19012.2157 | 3573.49 | NORMAL
285.928 | 0.05 | 305.368 | 1.11 | 2 | 79289.74 | 19736.1665 | 19715.6409 | 3151.001 | NORMAL
285.928 | 0.05 | 305.368 | 1.11 | 2 | 101352.97 | 20106.0668 | 20085.4782 | 2940.809 | NORMAL
285.928 | 0.05 | 305.368 | 1.11 | 2 | 106868.78 | 20172.4502 | 20151.8339 | 2903.553 | NORMAL
285.928 | 0.05 | 305.368 | 1.42 | 1 | 57226.51 | 16644.49 | 16574.2336 | 2347.99 | NORMAL
285.928 | 0.05 | 305.368 | 1.42 | 1 | 79289.74 | 17258.6753 | 17235.9801 | 2014.22 | NORMAL
285.928 | 0.05 | 305.368 | 1.42 | 1 | 101352.97 | 17599.2966 | 17576.3647 | 1828.606 | NORMAL
285.928 | 0.05 | 305.368 | 1.42 | 1 | 106868.78 | 17660.9613 | 17638.0021 | 1793.424 | NORMAL
285.928 | 0.05 | 305.368 | 1.42 | 2 | 57226.51 | 20146.5416 | 20102.8639 | 3680.56 | NORMAL
285.928 | 0.05 | 305.368 | 1.42 | 2 | 79289.74 | 20989.3904 | 20964.5809 | 3227.75 | NORMAL
285.928 | 0.05 | 305.368 | 1.42 | 2 | 101352.97 | 21436.0785 | 21411.0626 | 3003.107 | NORMAL
285.928 | 0.05 | 305.368 | 1.42 | 2 | 106868.78 | 21514.9473 | 21489.9038 | 2962.969 | NORMAL
285.928 | 0.15 | 288.706 | 0.5 | 1 | 57226.51 | 8891.2661 | 8884.9978 | 2169.643 | NORMAL
285.928 | 0.15 | 288.706 | 0.5 | 1 | 79289.74 | 9048.0363 | 9027.1173 | 2023.033 | NORMAL
285.928 | 0.15 | 288.706 | 0.5 | 1 | 101352.97 | 9130.0703 | 9127.8426 | 1946.6818 | NORMAL
285.928 | 0.15 | 288.706 | 0.5 | 1 | 106868.78 | 9129.6893 | 9127.4982 | 1935.4993 | NORMAL
285.928 | 0.15 | 288.706 | 0.5 | 2 | 57226.51 | 10813.5698 | 10811.7206 | 2897.558 | NORMAL
285.928 | 0.15 | 288.706 | 0.5 | 2 | 79289.74 | 10985.9613 | 10978.9303 | 2684.903 | NORMAL
285.928 | 0.15 | 288.706 | 0.5 | 2 | 101352.97 | 11073.9742 | 11056.134 | 2575.6421 | NORMAL
285.928 | 0.15 | 288.706 | 0.5 | 2 | 106868.78 | 11069.9883 | 11068.2282 | 2556.0239 | NORMAL
285.928 | 0.15 | 288.706 | 0.8 | 1 | 57226.51 | 10264.5369 | 10260.544 | 2189.882 | NORMAL
285.928 | 0.15 | 288.706 | 0.8 | 1 | 79289.74 | 10493.7866 | 10489.7885 | 2011.707 | NORMAL
285.928 | 0.15 | 288.706 | 0.8 | 1 | 101352.97 | 10621.0141 | 10617.0099 | 1916.322 | NORMAL
285.928 | 0.15 | 288.706 | 0.8 | 1 | 106868.78 | 10643.4935 | 10639.4916 | 1899.515 | NORMAL
285.928 | 0.15 | 288.706 | 0.8 | 2 | 57226.51 | 12707.6202 | 12687.3642 | 3039.131 | NORMAL
285.928 | 0.15 | 288.706 | 0.8 | 2 | 79289.74 | 12992.0868 | 12988.2151 | 2783.765 | NORMAL
285.928 | 0.15 | 288.706 | 0.8 | 2 | 101352.97 | 13141.9695 | 13138.1058 | 2651.783 | NORMAL
285.928 | 0.15 | 288.706 | 0.8 | 2 | 106868.78 | 13167.8488 | 13164.0564 | 2628.568 | NORMAL
285.928 | 0.15 | 288.706 | 1.11 | 1 | 57226.51 | 11052.2861 | 11047.0583 | 2203.19 | NORMAL
285.928 | 0.15 | 288.706 | 1.11 | 1 | 79289.74 | 11333.0012 | 11327.7313 | 2007.211 | NORMAL
285.928 | 0.15 | 288.706 | 1.11 | 1 | 101352.97 | 11491.8523 | 11486.5545 | 1900.952 | NORMAL
285.928 | 0.15 | 288.706 | 1.11 | 1 | 106868.78 | 11520.6038 | 11515.3043 | 1881.872 | NORMAL
285.928 | 0.15 | 288.706 | 1.11 | 2 | 57226.51 | 13816.2954 | 13810.7827 | 3125.28 | NORMAL
285.928 | 0.15 | 288.706 | 1.11 | 2 | 79289.74 | 14183.177 | 14177.6598 | 2843.952 | NORMAL
285.928 | 0.15 | 288.706 | 1.11 | 2 | 101352.97 | 14379.1911 | 14373.6695 | 2699.198 | NORMAL
285.928 | 0.15 | 288.706 | 1.11 | 2 | 106868.78 | 14413.5991 | 14408.0642 | 2673.689 | NORMAL
285.928 | 0.15 | 288.706 | 1.42 | 1 | 57226.51 | 11577.5205 | 11571.396 | 2213.01 | NORMAL
285.928 | 0.15 | 288.706 | 1.42 | 1 | 79289.74 | 11897.2743 | 11891.0521 | 2004.76 | NORMAL
285.928 | 0.15 | 288.706 | 1.42 | 1 | 101352.97 | 12079.9824 | 12073.725 | 1891.36 | NORMAL
285.928 | 0.15 | 288.706 | 1.42 | 1 | 106868.78 | 12113.9214 | 12107.6464 | 1870.582 | NORMAL
285.928 | 0.15 | 288.706 | 1.42 | 2 | 57226.51 | 14564.1559 | 14544.5526 | 3184.79 | NORMAL
285.928 | 0.15 | 288.706 | 1.42 | 2 | 79289.74 | 14998.5639 | 14991.7545 | 2885.98 | NORMAL
285.928 | 0.15 | 288.706 | 1.42 | 2 | 101352.97 | 15230.2755 | 15223.4371 | 2732.658 | NORMAL
285.928 | 0.15 | 288.706 | 1.42 | 2 | 106868.78 | 15271.864 | 15265.0222 | 2705.65 | NORMAL
285.928 | 0.15 | 291.483 | 0.5 | 1 | 57226.51 | 9446.3365 | 9443.3325 | 2177.314 | NORMAL
285.928 | 0.15 | 291.483 | 0.5 | 1 | 79289.74 | 9617.4385 | 9607.9172 | 2017.362 | NORMAL
285.928 | 0.15 | 291.483 | 0.5 | 1 | 101352.97 | 9708.0305 | 9676.7609 | 1934.397 | NORMAL
285.928 | 0.15 | 291.483 | 0.5 | 1 | 106868.78 | 9722.9484 | 9720.0121 | 1920.2331 | NORMAL
285.928 | 0.15 | 291.483 | 0.5 | 2 | 57226.51 | 11428.6049 | 11426.0678 | 2942.511 | NORMAL
285.928 | 0.15 | 291.483 | 0.5 | 2 | 79289.74 | 11558.4701 | 11555.985 | 2714.368 | NORMAL
285.928 | 0.15 | 291.483 | 0.5 | 2 | 101352.97 | 11675.8792 | 11673.4507 | 2597.6395 | NORMAL
285.928 | 0.15 | 291.483 | 0.5 | 2 | 106868.78 | 11697.7139 | 11695.3159 | 2577.2291 | NORMAL
285.928 | 0.15 | 291.483 | 0.8 | 1 | 57226.51 | 10944.3142 | 10939.1047 | 2201.328 | NORMAL
285.928 | 0.15 | 291.483 | 0.8 | 1 | 79289.74 | 11197.245 | 11192.0271 | 2007.871 | NORMAL
285.928 | 0.15 | 291.483 | 0.8 | 1 | 101352.97 | 11339.1266 | 11333.8993 | 1903.577 | NORMAL
285.928 | 0.15 | 291.483 | 0.8 | 1 | 106868.78 | 11364.8007 | 11359.5729 | 1884.913 | NORMAL
285.928 | 0.15 | 291.483 | 0.8 | 2 | 57226.51 | 13466.6471 | 13461.5029 | 3097.858 | NORMAL
285.928 | 0.15 | 291.483 | 0.8 | 2 | 79289.74 | 13782.4736 | 13777.3603 | 2823.547 | NORMAL
285.928 | 0.15 | 291.483 | 0.8 | 2 | 101352.97 | 13949.1794 | 13944.0879 | 2682.631 | NORMAL
285.928 | 0.15 | 291.483 | 0.8 | 2 | 106868.78 | 13978.3705 | 13973.2823 | 2657.798 | NORMAL
285.928 | 0.15 | 291.483 | 1.11 | 1 | 57226.51 | 11806.2134 | 11799.4366 | 2217.45 | NORMAL
285.928 | 0.15 | 291.483 | 1.11 | 1 | 79289.74 | 12118.728 | 12111.8809 | 2003.935 | NORMAL
285.928 | 0.15 | 291.483 | 1.11 | 1 | 101352.97 | 12296.7468 | 12289.8729 | 1887.836 | NORMAL
285.928 | 0.15 | 291.483 | 1.11 | 1 | 106868.78 | 12328.3705 | 12321.4789 | 1866.86 | NORMAL
285.928 | 0.15 | 291.483 | 1.11 | 2 | 57226.51 | 14661.6647 | 14654.4805 | 3192.59 | NORMAL
285.928 | 0.15 | 291.483 | 1.11 | 2 | 79289.74 | 15075 | 15067.7941 | 2889.915 | NORMAL
285.928 | 0.15 | 291.483 | 1.11 | 2 | 101352.97 | 15293.9039 | 15286.6851 | 2735.139 | NORMAL
285.928 | 0.15 | 291.483 | 1.11 | 2 | 106868.78 | 15333.2356 | 15326.029 | 2707.963 | NORMAL
285.928 | 0.15 | 291.483 | 1.42 | 1 | 57226.51 | 12380.9789 | 12373.0551 | 2229.35 | NORMAL
285.928 | 0.15 | 291.483 | 1.42 | 1 | 79289.74 | 12740.592 | 12732.5527 | 2002.23 | NORMAL
285.928 | 0.15 | 291.483 | 1.42 | 1 | 101352.97 | 12946.5123 | 12938.4078 | 1877.457 | NORMAL
285.928 | 0.15 | 291.483 | 1.42 | 1 | 106868.78 | 12984.9355 | 12976.807 | 1857.511 | NORMAL
285.928 | 0.15 | 291.483 | 1.42 | 2 | 57226.51 | 15469.9003 | 15461.1599 | 3258.53 | NORMAL
285.928 | 0.15 | 291.483 | 1.42 | 2 | 79289.74 | 15958.3822 | 15949.5572 | 2937.22 | NORMAL
285.928 | 0.15 | 291.483 | 1.42 | 2 | 101352.97 | 16219.5193 | 16210.6473 | 2772.212 | NORMAL
285.928 | 0.15 | 291.483 | 1.42 | 2 | 106868.78 | 16266.5592 | 16257.6777 | 2743.578 | NORMAL
285.928 | 0.15 | 294.26 | 0.5 | 1 | 57226.51 | 10014.1266 | 10010.2211 | 2185.854 | NORMAL
285.928 | 0.15 | 294.26 | 0.5 | 1 | 79289.74 | 10200.0586 | 10196.1928 | 2013.551 | NORMAL
285.928 | 0.15 | 294.26 | 0.5 | 1 | 101352.97 | 10300.4982 | 10296.6562 | 1922.436 | NORMAL
285.928 | 0.15 | 294.26 | 0.5 | 1 | 106868.78 | 10317.6729 | 10313.8451 | 1906.7428 | NORMAL
285.928 | 0.15 | 294.26 | 0.5 | 2 | 57226.51 | 11974.2966 | 11971.0156 | 2983.414 | NORMAL
285.928 | 0.15 | 294.26 | 0.5 | 2 | 79289.74 | 12207.7081 | 12204.4364 | 2744.817 | NORMAL
285.928 | 0.15 | 294.26 | 0.5 | 2 | 101352.97 | 12336.1079 | 12332.8758 | 2621.5689 | NORMAL
285.928 | 0.15 | 294.26 | 0.5 | 2 | 106868.78 | 12341.442 | 12338.2826 | 2599.5589 | NORMAL
285.928 | 0.15 | 294.26 | 0.8 | 1 | 57226.51 | 11640.1231 | 11633.2903 | 2214.181 | NORMAL
285.928 | 0.15 | 294.26 | 0.8 | 1 | 79289.74 | 11918.6108 | 11911.9483 | 2004.637 | NORMAL
285.928 | 0.15 | 294.26 | 0.8 | 1 | 101352.97 | 12075.1758 | 12068.5104 | 1891.438 | NORMAL
285.928 | 0.15 | 294.26 | 0.8 | 1 | 106868.78 | 12104.5428 | 12097.8732 | 1870.757 | NORMAL
285.928 | 0.15 | 294.26 | 0.8 | 2 | 57226.51 | 14237.8371 | 14231.2307 | 3158.642 | NORMAL
285.928 | 0.15 | 294.26 | 0.8 | 2 | 79289.74 | 14589.7128 | 14583.1328 | 2864.794 | NORMAL
285.928 | 0.15 | 294.26 | 0.8 | 2 | 101352.97 | 14774.7948 | 14768.2496 | 2714.616 | NORMAL
285.928 | 0.15 | 294.26 | 0.8 | 2 | 106868.78 | 14807.5616 | 14801.0166 | 2688.282 | NORMAL
285.928 | 0.15 | 294.26 | 1.11 | 1 | 57226.51 | 12577.6964 | 12569.1058 | 2233.59 | NORMAL
285.928 | 0.15 | 294.26 | 1.11 | 1 | 79289.74 | 12925.2052 | 12916.5065 | 2001.797 | NORMAL
285.928 | 0.15 | 294.26 | 1.11 | 1 | 101352.97 | 13123.7691 | 13115.0286 | 1874.842 | NORMAL
285.928 | 0.15 | 294.26 | 1.11 | 1 | 106868.78 | 13160.5803 | 13151.8285 | 1852.093 | NORMAL
285.928 | 0.15 | 294.26 | 1.11 | 2 | 57226.51 | 15521.6002 | 15512.4735 | 3262.85 | NORMAL
285.928 | 0.15 | 294.26 | 1.11 | 2 | 79289.74 | 15983.4115 | 15974.237 | 2938.562 | NORMAL
285.928 | 0.15 | 294.26 | 1.11 | 2 | 101352.97 | 16227.6084 | 16218.4074 | 2772.554 | NORMAL
285.928 | 0.15 | 294.26 | 1.11 | 2 | 106868.78 | 16271.5709 | 16262.3775 | 2743.77 | NORMAL
285.928 | 0.15 | 294.26 | 1.42 | 1 | 57226.51 | 13204.7186 | 13194.683 | 2248 | NORMAL
285.928 | 0.15 | 294.26 | 1.42 | 1 | 79289.74 | 13606.2427 | 13596.038 | 2000.78 | NORMAL
285.928 | 0.15 | 294.26 | 1.42 | 1 | 101352.97 | 13834.9062 | 13824.613 | 1865.006 | NORMAL
285.928 | 0.15 | 294.26 | 1.42 | 1 | 106868.78 | 13877.4326 | 13867.1217 | 1840.602 | NORMAL
285.928 | 0.15 | 294.26 | 1.42 | 2 | 57226.51 | 16388.4818 | 16365.1446 | 3336.01 | NORMAL
285.928 | 0.15 | 294.26 | 1.42 | 2 | 79289.74 | 16937.7198 | 16926.524 | 2990.34 | NORMAL
285.928 | 0.15 | 294.26 | 1.42 | 2 | 101352.97 | 17229.5428 | 17218.2747 | 2814.525 | NORMAL
285.928 | 0.15 | 294.26 | 1.42 | 2 | 106868.78 | 17282.1219 | 17270.8367 | 2783.339 | NORMAL
285.928 | 0.15 | 297.037 | 0.5 | 1 | 57226.51 | 10593.4056 | 10588.4691 | 2195.279 | NORMAL
285.928 | 0.15 | 297.037 | 0.5 | 1 | 79289.74 | 10794.0797 | 10789.19 | 2009.983 | NORMAL
285.928 | 0.15 | 297.037 | 0.5 | 1 | 101352.97 | 10903.3705 | 10898.5076 | 1911.365 | NORMAL
285.928 | 0.15 | 297.037 | 0.5 | 1 | 106868.78 | 10924.3552 | 10919.5048 | 1893.5949 | NORMAL
285.928 | 0.15 | 297.037 | 0.5 | 2 | 57226.51 | 12597.9191 | 12593.6862 | 3030.791 | NORMAL
285.928 | 0.15 | 297.037 | 0.5 | 2 | 79289.74 | 12877.7843 | 12873.5733 | 2778.338 | NORMAL
285.928 | 0.15 | 297.037 | 0.5 | 2 | 101352.97 | 13028.7515 | 13007.0195 | 2647.742 | NORMAL
285.928 | 0.15 | 297.037 | 0.5 | 2 | 106868.78 | 13025.4396 | 13021.2845 | 2623.1335 | NORMAL
285.928 | 0.15 | 297.037 | 0.8 | 1 | 57226.51 | 12350.381 | 12342.0692 | 2228.618 | NORMAL
285.928 | 0.15 | 297.037 | 0.8 | 1 | 79289.74 | 12657.034 | 12648.693 | 2002.803 | NORMAL
285.928 | 0.15 | 297.037 | 0.8 | 1 | 101352.97 | 12829.8359 | 12821.4837 | 1879.08 | NORMAL
285.928 | 0.15 | 297.037 | 0.8 | 1 | 106868.78 | 12861.1079 | 12852.761 | 1857.334 | NORMAL
285.928 | 0.15 | 297.037 | 0.8 | 2 | 57226.51 | 15022.1571 | 15013.8348 | 3221.702 | NORMAL
285.928 | 0.15 | 297.037 | 0.8 | 2 | 79289.74 | 15411.1958 | 15402.92 | 2907.477 | NORMAL
285.928 | 0.15 | 297.037 | 0.8 | 2 | 101352.97 | 15615.3869 | 15607.1419 | 2747.928 | NORMAL
285.928 | 0.15 | 297.037 | 0.8 | 2 | 106868.78 | 15652.3447 | 15644.0959 | 2719.99 | NORMAL
285.928 | 0.15 | 297.037 | 1.11 | 1 | 57226.51 | 13365.5334 | 13354.8142 | 2251.89 | NORMAL
285.928 | 0.15 | 297.037 | 1.11 | 1 | 79289.74 | 13752.5205 | 13741.6698 | 2001.778 | NORMAL
285.928 | 0.15 | 297.037 | 1.11 | 1 | 101352.97 | 13970.8089 | 13959.8977 | 1863.14 | NORMAL
285.928 | 0.15 | 297.037 | 1.11 | 1 | 106868.78 | 14011.694 | 14000.7649 | 1838.578 | NORMAL
285.928 | 0.15 | 297.037 | 1.11 | 2 | 57226.51 | 16393.8746 | 16382.4808 | 3336.41 | NORMAL
285.928 | 0.15 | 297.037 | 1.11 | 2 | 79289.74 | 16908.0012 | 16896.5206 | 2988.718 | NORMAL
285.928 | 0.15 | 297.037 | 1.11 | 2 | 101352.97 | 17179.3376 | 17167.8447 | 2812.437 | NORMAL
285.928 | 0.15 | 297.037 | 1.11 | 2 | 106868.78 | 17228.136 | 17216.6276 | 2781.193 | NORMAL
285.928 | 0.15 | 297.037 | 1.42 | 1 | 57226.51 | 14046.8347 | 14034.3471 | 2269.1 | NORMAL
285.928 | 0.15 | 297.037 | 1.42 | 1 | 79289.74 | 14494.5487 | 14481.8369 | 2002.19 | NORMAL
285.928 | 0.15 | 297.037 | 1.42 | 1 | 101352.97 | 14748.007 | 14735.1763 | 1853.433 | NORMAL
285.928 | 0.15 | 297.037 | 1.42 | 1 | 106868.78 | 14795.3986 | 14777.6441 | 1827.069 | NORMAL
285.928 | 0.15 | 297.037 | 1.42 | 2 | 57226.51 | 17321.1606 | 17307.4076 | 3416.98 | NORMAL
285.928 | 0.15 | 297.037 | 1.42 | 2 | 79289.74 | 17934.2028 | 17920.25 | 3046.02 | NORMAL
285.928 | 0.15 | 297.037 | 1.42 | 2 | 101352.97 | 18259.6718 | 18245.6301 | 2858.411 | NORMAL
285.928 | 0.15 | 297.037 | 1.42 | 2 | 106868.78 | 18318.2005 | 18304.1321 | 2825.29 | NORMAL
285.928 | 0.15 | 299.814 | 0.5 | 1 | 57226.51 | 11184.5838 | 11178.4547 | 2205.523 | NORMAL
285.928 | 0.15 | 299.814 | 0.5 | 1 | 79289.74 | 11400.4689 | 11394.4039 | 2006.83 | NORMAL
285.928 | 0.15 | 299.814 | 0.5 | 1 | 101352.97 | 11520.721 | 11514.6841 | 1900.456 | NORMAL
285.928 | 0.15 | 299.814 | 0.5 | 1 | 106868.78 | 11542.2333 | 11536.2082 | 1881.3993 | NORMAL
285.928 | 0.15 | 299.814 | 0.5 | 2 | 57226.51 | 13261.9285 | 13256.5574 | 3083.009 | NORMAL
285.928 | 0.15 | 299.814 | 0.5 | 2 | 79289.74 | 13601.5533 | 13510.2733 | 2814.49 | NORMAL
285.928 | 0.15 | 299.814 | 0.5 | 2 | 101352.97 | 13762.8371 | 13620.0476 | 2675.624 | NORMAL
285.928 | 0.15 | 299.814 | 0.5 | 2 | 106868.78 | 13746.8933 | 13674.9833 | 2649.1258 | NORMAL
285.928 | 0.15 | 299.814 | 0.8 | 1 | 57226.51 | 13074.238 | 13064.0139 | 2244.859 | NORMAL
285.928 | 0.15 | 299.814 | 0.8 | 1 | 79289.74 | 13410.0235 | 13399.7648 | 2000.896 | NORMAL
285.928 | 0.15 | 299.814 | 0.8 | 1 | 101352.97 | 13600.1465 | 13589.8648 | 1868.074 | NORMAL
285.928 | 0.15 | 299.814 | 0.8 | 1 | 106868.78 | 13635.1993 | 13624.9184 | 1844.402 | NORMAL
285.928 | 0.15 | 299.814 | 0.8 | 2 | 57226.51 | 15816.3247 | 15806.0283 | 3287.464 | NORMAL
285.928 | 0.15 | 299.814 | 0.8 | 2 | 79289.74 | 16245.7503 | 16235.5155 | 2952.661 | NORMAL
285.928 | 0.15 | 299.814 | 0.8 | 2 | 101352.97 | 16470.8382 | 16460.6263 | 2782.417 | NORMAL
285.928 | 0.15 | 299.814 | 0.8 | 2 | 106868.78 | 16511.1372 | 16500.9333 | 2753.057 | NORMAL
285.928 | 0.15 | 299.814 | 1.11 | 1 | 57226.51 | 14170.5158 | 14157.3798 | 2272.35 | NORMAL
285.928 | 0.15 | 299.814 | 1.11 | 1 | 79289.74 | 14598.2415 | 14584.9279 | 2002.361 | NORMAL
285.928 | 0.15 | 299.814 | 1.11 | 1 | 101352.97 | 14837.6026 | 14824.2042 | 1852.364 | NORMAL
285.928 | 0.15 | 299.814 | 1.11 | 1 | 106868.78 | 14882.4736 | 14869.0496 | 1825.865 | NORMAL
285.928 | 0.15 | 299.814 | 1.11 | 2 | 57226.51 | 17278.2825 | 17264.2699 | 3413.31 | NORMAL
285.928 | 0.15 | 299.814 | 1.11 | 2 | 79289.74 | 17847.5967 | 17833.4971 | 3041.065 | NORMAL
285.928 | 0.15 | 299.814 | 1.11 | 2 | 101352.97 | 18148.1829 | 18134.0273 | 2853.601 | NORMAL
285.928 | 0.15 | 299.814 | 1.11 | 2 | 106868.78 | 18202.5205 | 18188.359 | 2820.492 | NORMAL
285.928 | 0.15 | 299.814 | 1.42 | 1 | 57226.51 | 14905.891 | 14871.4137 | 2292.83 | NORMAL
285.928 | 0.15 | 299.814 | 1.42 | 1 | 79289.74 | 15404.1032 | 15388.5142 | 2004.35 | NORMAL
285.928 | 0.15 | 299.814 | 1.42 | 1 | 101352.97 | 15683.646 | 15665.5313 | 1844.341 | NORMAL
285.928 | 0.15 | 299.814 | 1.42 | 1 | 106868.78 | 15735.3165 | 15719.534 | 1814.58 | NORMAL
285.928 | 0.15 | 299.814 | 1.42 | 2 | 57226.51 | 18265.5334 | 18248.6743 | 3501.93 | NORMAL
285.928 | 0.15 | 299.814 | 1.42 | 2 | 79289.74 | 18946.9812 | 18926.4427 | 3104.27 | NORMAL
285.928 | 0.15 | 299.814 | 1.42 | 2 | 101352.97 | 19309.1735 | 19291.9497 | 2904.588 | NORMAL
285.928 | 0.15 | 299.814 | 1.42 | 2 | 106868.78 | 19373.857 | 19356.5949 | 2869.297 | NORMAL
285.928 | 0.15 | 302.591 | 0.5 | 1 | 57226.51 | 11786.9871 | 11779.4906 | 2217.042 | NORMAL
285.928 | 0.15 | 302.591 | 0.5 | 1 | 79289.74 | 12018.4935 | 12011.0661 | 2004.252 | NORMAL
285.928 | 0.15 | 302.591 | 0.5 | 1 | 101352.97 | 12148.3587 | 12140.9725 | 1890.253 | NORMAL
285.928 | 0.15 | 302.591 | 0.5 | 1 | 106868.78 | 12171.2778 | 12163.9021 | 1869.7429 | NORMAL
285.928 | 0.15 | 302.591 | 0.5 | 2 | 57226.51 | 13993.8453 | 13951.22 | 3138.872 | NORMAL
285.928 | 0.15 | 302.591 | 0.5 | 2 | 79289.74 | 14361.7233 | 14100.699 | 2853.408 | NORMAL
285.928 | 0.15 | 302.591 | 0.5 | 2 | 101352.97 | 14527.8722 | 14226.6949 | 2704.928 | NORMAL
285.928 | 0.15 | 302.591 | 0.5 | 2 | 106868.78 | 14504.8359 | 14285.7113 | 2676.6702 | NORMAL
285.928 | 0.15 | 302.591 | 0.8 | 1 | 57226.51 | 13811.8992 | 13799.4961 | 2262.96 | NORMAL
285.928 | 0.15 | 302.591 | 0.8 | 1 | 79289.74 | 14180.9203 | 14168.4553 | 2001.899 | NORMAL
285.928 | 0.15 | 302.591 | 0.8 | 1 | 101352.97 | 14386.4302 | 14373.9428 | 1857.767 | NORMAL
285.928 | 0.15 | 302.591 | 0.8 | 1 | 106868.78 | 14425.0586 | 14412.5521 | 1832.414 | NORMAL
285.928 | 0.15 | 302.591 | 0.8 | 2 | 57226.51 | 16621.864 | 16607.6523 | 3355.885 | NORMAL
285.928 | 0.15 | 302.591 | 0.8 | 2 | 79289.74 | 17093.6401 | 17081.1617 | 2998.949 | NORMAL
285.928 | 0.15 | 302.591 | 0.8 | 2 | 101352.97 | 17340.2403 | 17327.79 | 2819.211 | NORMAL
285.928 | 0.15 | 302.591 | 0.8 | 2 | 106868.78 | 17384.2028 | 17371.7557 | 2787.419 | NORMAL
285.928 | 0.15 | 302.591 | 1.11 | 1 | 57226.51 | 14991.2368 | 14975.3161 | 2295.31 | NORMAL
285.928 | 0.15 | 302.591 | 1.11 | 1 | 79289.74 | 15462.3388 | 15446.1961 | 2004.583 | NORMAL
285.928 | 0.15 | 302.591 | 1.11 | 1 | 101352.97 | 15724.8828 | 15708.6232 | 1843.941 | NORMAL
285.928 | 0.15 | 302.591 | 1.11 | 1 | 106868.78 | 15773.1536 | 15756.8757 | 1814.131 | NORMAL
285.928 | 0.15 | 302.591 | 1.11 | 2 | 57226.51 | 18172.6846 | 18155.7114 | 3493.52 | NORMAL
285.928 | 0.15 | 302.591 | 1.11 | 2 | 79289.74 | 18802.1102 | 18785.0003 | 3095.846 | NORMAL
285.928 | 0.15 | 302.591 | 1.11 | 2 | 101352.97 | 19133.9977 | 19116.8345 | 2896.8 | NORMAL
285.928 | 0.15 | 302.591 | 1.11 | 2 | 106868.78 | 19193.0832 | 19175.9054 | 2861.678 | NORMAL
285.928 | 0.15 | 302.591 | 1.42 | 1 | 57226.51 | 15781.8582 | 15763.3303 | 2319.4 | NORMAL
285.928 | 0.15 | 302.591 | 1.42 | 1 | 79289.74 | 16333.8218 | 16314.9236 | 2008.3 | NORMAL
285.928 | 0.15 | 302.591 | 1.42 | 1 | 101352.97 | 16640.8851 | 16621.7814 | 1835.596 | NORMAL
285.928 | 0.15 | 302.591 | 1.42 | 1 | 106868.78 | 16696.9519 | 16677.8005 | 1803.318 | NORMAL
285.928 | 0.15 | 302.591 | 1.42 | 2 | 57226.51 | 19219.3435 | 19198.971 | 3591.16 | NORMAL
285.928 | 0.15 | 302.591 | 1.42 | 2 | 79289.74 | 19976.143 | 19955.4278 | 3165.47 | NORMAL
285.928 | 0.15 | 302.591 | 1.42 | 2 | 101352.97 | 20376.6706 | 20355.7845 | 2953.265 | NORMAL
285.928 | 0.15 | 302.591 | 1.42 | 2 | 106868.78 | 20447.8019 | 20426.9042 | 2915.54 | NORMAL
285.928 | 0.15 | 305.368 | 0.5 | 1 | 57226.51 | 12398.9156 | 12389.8768 | 2229.73 | NORMAL
285.928 | 0.15 | 305.368 | 0.5 | 1 | 79289.74 | 12648.3587 | 12639.4037 | 2002.352 | NORMAL
285.928 | 0.15 | 305.368 | 0.5 | 1 | 101352.97 | 12788.0715 | 12779.171 | 1879.666 | NORMAL
285.928 | 0.15 | 305.368 | 0.5 | 1 | 106868.78 | 12812.9836 | 12804.0914 | 1858.1739 | NORMAL
285.928 | 0.15 | 305.368 | 0.5 | 2 | 57226.51 | 14740.0352 | 14574.1066 | 3199.471 | NORMAL
285.928 | 0.15 | 305.368 | 0.5 | 2 | 79289.74 | 15143.8746 | 14783.5866 | 2893.863 | NORMAL
285.928 | 0.15 | 305.368 | 0.5 | 2 | 101352.97 | 15316.6471 | 14920.1144 | 2735.983 | NORMAL
285.928 | 0.15 | 305.368 | 0.5 | 2 | 106868.78 | 15290.0645 | 14972.2452 | 2705.8301 | NORMAL
285.928 | 0.15 | 305.368 | 0.8 | 1 | 57226.51 | 14563.6284 | 14544.2296 | 2283.048 | NORMAL
285.928 | 0.15 | 305.368 | 0.8 | 1 | 79289.74 | 14966.1782 | 14951.227 | 2003.134 | NORMAL
285.928 | 0.15 | 305.368 | 0.8 | 1 | 101352.97 | 15189.7128 | 15174.7205 | 1849.455 | NORMAL
285.928 | 0.15 | 305.368 | 0.8 | 1 | 106868.78 | 15230.1876 | 15215.2011 | 1821.096 | NORMAL
285.928 | 0.15 | 305.368 | 0.8 | 2 | 57226.51 | 17436.4595 | 17421.3944 | 3427.245 | NORMAL
285.928 | 0.15 | 305.368 | 0.8 | 2 | 79289.74 | 17953.6928 | 17938.6836 | 3047.149 | NORMAL
285.928 | 0.15 | 305.368 | 0.8 | 2 | 101352.97 | 18223.007 | 18208.0277 | 2856.85 | NORMAL
285.928 | 0.15 | 305.368 | 0.8 | 2 | 106868.78 | 18271.0434 | 18256.0794 | 2823.348 | NORMAL
285.928 | 0.15 | 305.368 | 1.11 | 1 | 57226.51 | 15826.4654 | 15807.4262 | 2320.77 | NORMAL
285.928 | 0.15 | 305.368 | 1.11 | 1 | 79289.74 | 16343.9332 | 16324.5983 | 2008.363 | NORMAL
285.928 | 0.15 | 305.368 | 1.11 | 1 | 101352.97 | 16630.9789 | 16611.4874 | 1835.69 | NORMAL
285.928 | 0.15 | 305.368 | 1.11 | 1 | 106868.78 | 16683.0598 | 16663.5573 | 1803.435 | NORMAL
285.928 | 0.15 | 305.368 | 1.11 | 2 | 57226.51 | 19076.524 | 19044.8379 | 3577.59 | NORMAL
285.928 | 0.15 | 305.368 | 1.11 | 2 | 79289.74 | 19771.1899 | 19750.6872 | 3153.117 | NORMAL
285.928 | 0.15 | 305.368 | 1.11 | 2 | 101352.97 | 20135.0527 | 20114.4747 | 2942.137 | NORMAL
285.928 | 0.15 | 305.368 | 1.11 | 2 | 106868.78 | 20199.7362 | 20179.1527 | 2904.749 | NORMAL
285.928 | 0.15 | 305.368 | 1.42 | 1 | 57226.51 | 16673.857 | 16651.7308 | 2349 | NORMAL
285.928 | 0.15 | 305.368 | 1.42 | 1 | 79289.74 | 17282.1512 | 17250.6804 | 2014.4 | NORMAL
285.928 | 0.15 | 305.368 | 1.42 | 1 | 101352.97 | 17618.6401 | 17595.7711 | 1828.484 | NORMAL
285.928 | 0.15 | 305.368 | 1.42 | 1 | 106868.78 | 17679.1618 | 17656.2496 | 1793.263 | NORMAL
285.928 | 0.15 | 305.368 | 1.42 | 2 | 57226.51 | 20185.2579 | 20160.9549 | 3684.37 | NORMAL
285.928 | 0.15 | 305.368 | 1.42 | 2 | 79289.74 | 21020.5744 | 20995.8122 | 3229.73 | NORMAL
285.928 | 0.15 | 305.368 | 1.42 | 2 | 101352.97 | 21461.2544 | 21436.295 | 3004.331 | NORMAL
285.928 | 0.15 | 305.368 | 1.42 | 2 | 106868.78 | 21539.5662 | 21514.5588 | 2964.071 | NORMAL
285.928 | 0.25 | 288.706 | 0.5 | 1 | 57226.51 | 8862.8077 | 8860.5477 | 2169.106 | NORMAL
285.928 | 0.25 | 288.706 | 0.5 | 1 | 79289.74 | 9037.3095 | 9025.073 | 2022.74 | NORMAL
285.928 | 0.25 | 288.706 | 0.5 | 1 | 101352.97 | 9136.9871 | 9077.7337 | 1946.609 | NORMAL
285.928 | 0.25 | 288.706 | 0.5 | 1 | 106868.78 | 9129.1032 | 9126.8939 | 1935.3718 | NORMAL
285.928 | 0.25 | 288.706 | 0.5 | 2 | 57226.51 | 11262.2802 | 10273.6772 | 2930.278 | NORMAL
285.928 | 0.25 | 288.706 | 0.5 | 2 | 79289.74 | 11392.7022 | 10482.8582 | 2704.642 | NORMAL
285.928 | 0.25 | 288.706 | 0.5 | 2 | 101352.97 | 11429.5721 | 10678.112 | 2588.4123 | NORMAL
285.928 | 0.25 | 288.706 | 0.5 | 2 | 106868.78 | 11403.1067 | 10832.7917 | 2567.2597 | NORMAL
285.928 | 0.25 | 288.706 | 0.8 | 1 | 57226.51 | 10273.4467 | 10269.4503 | 2190.007 | NORMAL
285.928 | 0.25 | 288.706 | 0.8 | 1 | 79289.74 | 10500.5569 | 10496.5562 | 2011.663 | NORMAL
285.928 | 0.25 | 288.706 | 0.8 | 1 | 101352.97 | 10626.4654 | 10622.4699 | 1916.227 | NORMAL
285.928 | 0.25 | 288.706 | 0.8 | 1 | 106868.78 | 10648.8863 | 10644.8823 | 1899.353 | NORMAL
285.928 | 0.25 | 288.706 | 0.8 | 2 | 57226.51 | 12561.0199 | 12557.2893 | 3028.078 | NORMAL
285.928 | 0.25 | 288.706 | 0.8 | 2 | 79289.74 | 12920.1934 | 12916.4207 | 2780.152 | NORMAL
285.928 | 0.25 | 288.706 | 0.8 | 2 | 101352.97 | 13111.2837 | 13107.4945 | 2651.082 | NORMAL
285.928 | 0.25 | 288.706 | 0.8 | 2 | 106868.78 | 13111.4302 | 13107.6542 | 2626.168 | NORMAL
285.928 | 0.25 | 288.706 | 1.11 | 1 | 57226.51 | 11059.8183 | 11044.976 | 2203.32 | NORMAL
285.928 | 0.25 | 288.706 | 1.11 | 1 | 79289.74 | 11338.8628 | 11328.3064 | 2007.166 | NORMAL
285.928 | 0.25 | 288.706 | 1.11 | 1 | 101352.97 | 11495.252 | 11489.9527 | 1901.196 | NORMAL
285.928 | 0.25 | 288.706 | 1.11 | 1 | 106868.78 | 11525.2638 | 11519.9621 | 1881.715 | NORMAL
285.928 | 0.25 | 288.706 | 1.11 | 2 | 57226.51 | 13826.993 | 13821.4898 | 3126.13 | NORMAL
285.928 | 0.25 | 288.706 | 1.11 | 2 | 79289.74 | 14191.5592 | 14186.0387 | 2844.382 | NORMAL
285.928 | 0.25 | 288.706 | 1.11 | 2 | 101352.97 | 14385.3751 | 14379.8512 | 2699.466 | NORMAL
285.928 | 0.25 | 288.706 | 1.11 | 2 | 106868.78 | 14420.1055 | 14414.5826 | 2673.924 | NORMAL
285.928 | 0.25 | 288.706 | 1.42 | 1 | 57226.51 | 11584.1149 | 11577.9985 | 2213.13 | NORMAL
285.928 | 0.25 | 288.706 | 1.42 | 1 | 79289.74 | 11902.374 | 11891.2334 | 2004.73 | NORMAL
285.928 | 0.25 | 288.706 | 1.42 | 1 | 101352.97 | 12083.7632 | 12077.5038 | 1891.3 | NORMAL
285.928 | 0.25 | 288.706 | 1.42 | 1 | 106868.78 | 12117.8488 | 12111.5838 | 1870.51 | NORMAL
285.928 | 0.25 | 288.706 | 1.42 | 2 | 57226.51 | 14573.5346 | 14566.8016 | 3185.54 | NORMAL
285.928 | 0.25 | 288.706 | 1.42 | 2 | 79289.74 | 15005.9789 | 14994.7094 | 2886.36 | NORMAL
285.928 | 0.25 | 288.706 | 1.42 | 2 | 101352.97 | 15236.4302 | 15229.5891 | 2732.886 | NORMAL
285.928 | 0.25 | 288.706 | 1.42 | 2 | 106868.78 | 15277.1395 | 15270.2954 | 2705.872 | NORMAL
285.928 | 0.25 | 291.483 | 0.5 | 1 | 57226.51 | 9443.6401 | 9440.6181 | 2177.509 | NORMAL
285.928 | 0.25 | 291.483 | 0.5 | 1 | 79289.74 | 9659.9648 | 9542.7895 | 2017.638 | NORMAL
285.928 | 0.25 | 291.483 | 0.5 | 1 | 101352.97 | 9762.6612 | 9620.8683 | 1933.401 | NORMAL
285.928 | 0.25 | 291.483 | 0.5 | 1 | 106868.78 | 9745.8675 | 9673.0172 | 1919.7306 | NORMAL
285.928 | 0.25 | 291.483 | 0.5 | 2 | 57226.51 | 12023.3294 | 10749.9025 | 2986.718 | NORMAL
285.928 | 0.25 | 291.483 | 0.5 | 2 | 79289.74 | 12158.7339 | 11016.0682 | 2742.437 | NORMAL
285.928 | 0.25 | 291.483 | 0.5 | 2 | 101352.97 | 12192.7022 | 11196.7779 | 2616.1822 | NORMAL
285.928 | 0.25 | 291.483 | 0.5 | 2 | 106868.78 | 12158.558 | 11380.6413 | 2593.4151 | NORMAL
285.928 | 0.25 | 291.483 | 0.8 | 1 | 57226.51 | 10955.9496 | 10949.0035 | 2201.506 | NORMAL
285.928 | 0.25 | 291.483 | 0.8 | 1 | 79289.74 | 11206.2427 | 11201.0206 | 2007.823 | NORMAL
285.928 | 0.25 | 291.483 | 0.8 | 1 | 101352.97 | 11346.3951 | 11341.1644 | 1903.441 | NORMAL
285.928 | 0.25 | 291.483 | 0.8 | 1 | 106868.78 | 11371.7468 | 11366.5271 | 1884.762 | NORMAL
285.928 | 0.25 | 291.483 | 0.8 | 2 | 57226.51 | 13333.8511 | 13328.9176 | 3088.933 | NORMAL
285.928 | 0.25 | 291.483 | 0.8 | 2 | 79289.74 | 13750.4689 | 13745.4225 | 2822.043 | NORMAL
285.928 | 0.25 | 291.483 | 0.8 | 2 | 101352.97 | 13960.9613 | 13955.8935 | 2683.588 | NORMAL
285.928 | 0.25 | 291.483 | 0.8 | 2 | 106868.78 | 13950.6448 | 13945.6226 | 2656.467 | NORMAL
285.928 | 0.25 | 291.483 | 1.11 | 1 | 57226.51 | 11816.1196 | 11799.0335 | 2217.63 | NORMAL
285.928 | 0.25 | 291.483 | 1.11 | 1 | 79289.74 | 12127.5498 | 12120.7099 | 2004.193 | NORMAL
285.928 | 0.25 | 291.483 | 1.11 | 1 | 101352.97 | 12302.9894 | 12296.1121 | 1887.737 | NORMAL
285.928 | 0.25 | 291.483 | 1.11 | 1 | 106868.78 | 12334.2907 | 12327.4082 | 1866.761 | NORMAL
285.928 | 0.25 | 291.483 | 1.11 | 2 | 57226.51 | 14675.4689 | 14668.2926 | 3193.7 | NORMAL
285.928 | 0.25 | 291.483 | 1.11 | 2 | 79289.74 | 15085.8148 | 15078.6038 | 2890.493 | NORMAL
285.928 | 0.25 | 291.483 | 1.11 | 2 | 101352.97 | 15302.7257 | 15295.5181 | 2735.483 | NORMAL
285.928 | 0.25 | 291.483 | 1.11 | 2 | 106868.78 | 15341.6471 | 15334.4366 | 2708.277 | NORMAL
285.928 | 0.25 | 291.483 | 1.42 | 1 | 57226.51 | 12389.5662 | 12370.2633 | 2229.54 | NORMAL
285.928 | 0.25 | 291.483 | 1.42 | 1 | 79289.74 | 12747.2743 | 12739.2435 | 2002.22 | NORMAL
285.928 | 0.25 | 291.483 | 1.42 | 1 | 101352.97 | 12951.993 | 12939.6109 | 1877.386 | NORMAL
285.928 | 0.25 | 291.483 | 1.42 | 1 | 106868.78 | 12988.8921 | 12980.7741 | 1854.977 | NORMAL
285.928 | 0.25 | 291.483 | 1.42 | 2 | 57226.51 | 15482.034 | 15454.3986 | 3259.54 | NORMAL
285.928 | 0.25 | 291.483 | 1.42 | 2 | 79289.74 | 15967.9953 | 15959.165 | 2937.73 | NORMAL
285.928 | 0.25 | 291.483 | 1.42 | 2 | 101352.97 | 16227.4033 | 16218.5431 | 2772.535 | NORMAL
285.928 | 0.25 | 291.483 | 1.42 | 2 | 106868.78 | 16274.0914 | 16265.2221 | 2743.871 | NORMAL
285.928 | 0.25 | 294.26 | 0.5 | 1 | 57226.51 | 10080.5979 | 9926.2639 | 2186.735 | NORMAL
285.928 | 0.25 | 294.26 | 0.5 | 1 | 79289.74 | 10304.3962 | 10036.0595 | 2013.127 | NORMAL
285.928 | 0.25 | 294.26 | 0.5 | 1 | 101352.97 | 10418.4642 | 10139.9787 | 1920.182 | NORMAL
285.928 | 0.25 | 294.26 | 0.5 | 1 | 106868.78 | 10396.2485 | 10203.6164 | 1904.9597 | NORMAL
285.928 | 0.25 | 294.26 | 0.5 | 2 | 57226.51 | 12806.4771 | 11249.9907 | 3046.735 | NORMAL
285.928 | 0.25 | 294.26 | 0.5 | 2 | 79289.74 | 12956.8288 | 11558.0225 | 2782.048 | NORMAL
285.928 | 0.25 | 294.26 | 0.5 | 2 | 101352.97 | 12989.1852 | 11758.1222 | 2646.173 | NORMAL
285.928 | 0.25 | 294.26 | 0.5 | 2 | 106868.78 | 12950.5276 | 11824.7382 | 2620.8864 | NORMAL
285.928 | 0.25 | 294.26 | 0.8 | 1 | 57226.51 | 11655.041 | 11648.3977 | 2214.453 | NORMAL
285.928 | 0.25 | 294.26 | 0.8 | 1 | 79289.74 | 11930.891 | 11924.2335 | 2004.825 | NORMAL
285.928 | 0.25 | 294.26 | 0.8 | 1 | 101352.97 | 12084.6131 | 12077.9424 | 1891.275 | NORMAL
285.928 | 0.25 | 294.26 | 0.8 | 1 | 106868.78 | 12113.306 | 12106.6316 | 1870.592 | NORMAL
285.928 | 0.25 | 294.26 | 0.8 | 2 | 57226.51 | 14151.5533 | 14145.171 | 3152.14 | NORMAL
285.928 | 0.25 | 294.26 | 0.8 | 2 | 79289.74 | 14612.1629 | 14605.6605 | 2866.378 | NORMAL
285.928 | 0.25 | 294.26 | 0.8 | 2 | 101352.97 | 14844.1969 | 14837.6655 | 2717.83 | NORMAL
285.928 | 0.25 | 294.26 | 0.8 | 2 | 106868.78 | 14834.2321 | 14827.7644 | 2689.44 | NORMAL
285.928 | 0.25 | 294.26 | 1.11 | 1 | 57226.51 | 12590.4748 | 12581.8881 | 2233.87 | NORMAL
285.928 | 0.25 | 294.26 | 1.11 | 1 | 79289.74 | 12936.0199 | 12927.3399 | 2002.218 | NORMAL
285.928 | 0.25 | 294.26 | 1.11 | 1 | 101352.97 | 13131.8875 | 13123.1547 | 1874.724 | NORMAL
285.928 | 0.25 | 294.26 | 1.11 | 1 | 106868.78 | 13168.3177 | 13159.5739 | 1851.963 | NORMAL
285.928 | 0.25 | 294.26 | 1.11 | 2 | 57226.51 | 15539.2439 | 15530.1223 | 3264.31 | NORMAL
285.928 | 0.25 | 294.26 | 1.11 | 2 | 79289.74 | 15997.2743 | 15988.1079 | 2939.305 | NORMAL
285.928 | 0.25 | 294.26 | 1.11 | 2 | 101352.97 | 16238.9801 | 16229.7888 | 2773.01 | NORMAL
285.928 | 0.25 | 294.26 | 1.11 | 2 | 106868.78 | 16282.415 | 16273.2154 | 2744.185 | NORMAL
285.928 | 0.25 | 294.26 | 1.42 | 1 | 57226.51 | 13215.8851 | 13205.101 | 2248.27 | NORMAL
285.928 | 0.25 | 294.26 | 1.42 | 1 | 79289.74 | 13615.4162 | 13604.5647 | 2001.82 | NORMAL
285.928 | 0.25 | 294.26 | 1.42 | 1 | 101352.97 | 13842.0574 | 13831.7728 | 1864.898 | NORMAL
285.928 | 0.25 | 294.26 | 1.42 | 1 | 106868.78 | 13884.2907 | 13873.9886 | 1840.491 | NORMAL
285.928 | 0.25 | 294.26 | 1.42 | 2 | 57226.51 | 16404.0152 | 16392.9753 | 3337.34 | NORMAL
285.928 | 0.25 | 294.26 | 1.42 | 2 | 79289.74 | 16950.0586 | 16938.8716 | 2991.02 | NORMAL
285.928 | 0.25 | 294.26 | 1.42 | 2 | 101352.97 | 17239.7128 | 17228.4552 | 2814.952 | NORMAL
285.928 | 0.25 | 294.26 | 1.42 | 2 | 106868.78 | 17291.8523 | 17280.578 | 2783.723 | NORMAL
285.928 | 0.25 | 297.037 | 0.5 | 1 | 57226.51 | 10744.6952 | 10514.8124 | 2197.44 | NORMAL
285.928 | 0.25 | 297.037 | 0.5 | 1 | 79289.74 | 10983.646 | 10641.9447 | 2009.216 | NORMAL
285.928 | 0.25 | 297.037 | 0.5 | 1 | 101352.97 | 11097.8605 | 10753.6271 | 1907.701 | NORMAL
285.928 | 0.25 | 297.037 | 0.5 | 1 | 106868.78 | 11074.2673 | 10808.1416 | 1890.529 | NORMAL
285.928 | 0.25 | 297.037 | 0.5 | 2 | 57226.51 | 13629.4549 | 11697.5342 | 3110.769 | NORMAL
285.928 | 0.25 | 297.037 | 0.5 | 2 | 79289.74 | 13794.3142 | 12067.2661 | 2824.26 | NORMAL
285.928 | 0.25 | 297.037 | 0.5 | 2 | 101352.97 | 13822.245 | 12299.9735 | 2678.022 | NORMAL
285.928 | 0.25 | 297.037 | 0.5 | 2 | 106868.78 | 13775.6448 | 12373.8627 | 2650.5412 | NORMAL
285.928 | 0.25 | 297.037 | 0.8 | 1 | 57226.51 | 12369.5193 | 12361.2194 | 2229.037 | NORMAL
285.928 | 0.25 | 297.037 | 0.8 | 1 | 79289.74 | 12671.8054 | 12663.48 | 2002.768 | NORMAL
285.928 | 0.25 | 297.037 | 0.8 | 1 | 101352.97 | 12841.7644 | 12833.4172 | 1878.868 | NORMAL
285.928 | 0.25 | 297.037 | 0.8 | 1 | 106868.78 | 12872.5967 | 12864.2424 | 1857.128 | NORMAL
285.928 | 0.25 | 297.037 | 0.8 | 2 | 57226.51 | 14982.0926 | 14973.9274 | 3218.164 | NORMAL
285.928 | 0.25 | 297.037 | 0.8 | 2 | 79289.74 | 15517.1454 | 15381.2772 | 2913.585 | NORMAL
285.928 | 0.25 | 297.037 | 0.8 | 2 | 101352.97 | 15762.5733 | 15531.4309 | 2754.135 | NORMAL
285.928 | 0.25 | 297.037 | 0.8 | 2 | 106868.78 | 15743.9039 | 15667.7663 | 2723.792 | NORMAL
285.928 | 0.25 | 297.037 | 1.11 | 1 | 57226.51 | 13382.0047 | 13371.3125 | 2252.3 | NORMAL
285.928 | 0.25 | 297.037 | 1.11 | 1 | 79289.74 | 13765.3576 | 13754.538 | 2001.777 | NORMAL
285.928 | 0.25 | 297.037 | 1.11 | 1 | 101352.97 | 13981.3013 | 13970.3959 | 1863.004 | NORMAL
285.928 | 0.25 | 297.037 | 1.11 | 1 | 106868.78 | 14021.7175 | 14010.8086 | 1838.415 | NORMAL
285.928 | 0.25 | 297.037 | 1.11 | 2 | 57226.51 | 16415.7386 | 16399.1751 | 3338.33 | NORMAL
285.928 | 0.25 | 297.037 | 1.11 | 2 | 79289.74 | 16925.7327 | 16914.274 | 2989.696 | NORMAL
285.928 | 0.25 | 297.037 | 1.11 | 2 | 101352.97 | 17167.2919 | 17155.8242 | 2813.019 | NORMAL
285.928 | 0.25 | 297.037 | 1.11 | 2 | 106868.78 | 17241.6178 | 17230.1177 | 2781.806 | NORMAL
285.928 | 0.25 | 297.037 | 1.42 | 1 | 57226.51 | 14061.1665 | 14048.7223 | 2269.47 | NORMAL
285.928 | 0.25 | 297.037 | 1.42 | 1 | 79289.74 | 14505.891 | 14493.1983 | 2002.21 | NORMAL
285.928 | 0.25 | 297.037 | 1.42 | 1 | 101352.97 | 14757.3271 | 14744.5177 | 1853.337 | NORMAL
285.928 | 0.25 | 297.037 | 1.42 | 1 | 106868.78 | 14804.279 | 14791.4437 | 1826.941 | NORMAL
285.928 | 0.25 | 297.037 | 1.42 | 2 | 57226.51 | 17341.0023 | 17327.2683 | 3418.7 | NORMAL
285.928 | 0.25 | 297.037 | 1.42 | 2 | 79289.74 | 17949.238 | 17935.3094 | 3046.89 | NORMAL
285.928 | 0.25 | 297.037 | 1.42 | 2 | 101352.97 | 18272.6846 | 18258.6512 | 2858.983 | NORMAL
285.928 | 0.25 | 297.037 | 1.42 | 2 | 106868.78 | 18330.7151 | 18316.6555 | 2825.799 | NORMAL
285.928 | 0.25 | 299.814 | 0.5 | 1 | 57226.51 | 11504.5135 | 10831.0393 | 2211.528 | NORMAL
285.928 | 0.25 | 299.814 | 0.5 | 1 | 79289.74 | 11745.0762 | 10983.6429 | 2005.602 | NORMAL
285.928 | 0.25 | 299.814 | 0.5 | 1 | 101352.97 | 11862.1043 | 11127.9706 | 1894.399 | NORMAL
285.928 | 0.25 | 299.814 | 0.5 | 1 | 106868.78 | 11827.374 | 11218.1933 | 1875.8285 | NORMAL
285.928 | 0.25 | 299.814 | 0.5 | 2 | 57226.51 | 14480.6565 | 12283.2458 | 3178.508 | NORMAL
285.928 | 0.25 | 299.814 | 0.5 | 2 | 79289.74 | 14670.5744 | 12523.1838 | 2869.193 | NORMAL
285.928 | 0.25 | 299.814 | 0.5 | 2 | 101352.97 | 14695.5744 | 12776.8468 | 2712.077 | NORMAL
285.928 | 0.25 | 299.814 | 0.5 | 2 | 106868.78 | 14639.9472 | 12879.5229 | 2682.2331 | NORMAL
285.928 | 0.25 | 299.814 | 0.8 | 1 | 57226.51 | 13098.4467 | 13088.2299 | 2245.447 | NORMAL
285.928 | 0.25 | 299.814 | 0.8 | 1 | 79289.74 | 13429.4549 | 13419.1948 | 2001.969 | NORMAL
285.928 | 0.25 | 299.814 | 0.8 | 1 | 101352.97 | 13615.4748 | 13605.1951 | 1867.851 | NORMAL
285.928 | 0.25 | 299.814 | 0.8 | 1 | 106868.78 | 13649.8828 | 13639.6044 | 1844.165 | NORMAL
285.928 | 0.25 | 299.814 | 0.8 | 2 | 57226.51 | 15982.6495 | 15820.4735 | 3301.453 | NORMAL
285.928 | 0.25 | 299.814 | 0.8 | 2 | 79289.74 | 16528.9566 | 16031.435 | 2967.604 | NORMAL
285.928 | 0.25 | 299.814 | 0.8 | 2 | 101352.97 | 16784.2614 | 16230.0787 | 2795.166 | NORMAL
285.928 | 0.25 | 299.814 | 0.8 | 2 | 106868.78 | 16765.2989 | 16355.8233 | 2763.504 | NORMAL
285.928 | 0.25 | 299.814 | 1.11 | 1 | 57226.51 | 14191.5299 | 14178.4169 | 2272.91 | NORMAL
285.928 | 0.25 | 299.814 | 1.11 | 1 | 79289.74 | 14614.7128 | 14601.4134 | 2002.385 | NORMAL
285.928 | 0.25 | 299.814 | 1.11 | 1 | 101352.97 | 14850.9379 | 14837.5423 | 1852.133 | NORMAL
285.928 | 0.25 | 299.814 | 1.11 | 1 | 106868.78 | 14895.3986 | 14881.9927 | 1825.678 | NORMAL
285.928 | 0.25 | 299.814 | 1.11 | 2 | 57226.51 | 17306.5358 | 17279.5722 | 3415.63 | NORMAL
285.928 | 0.25 | 299.814 | 1.11 | 2 | 79289.74 | 17504.1911 | 17490.7304 | 3024.877 | NORMAL
285.928 | 0.25 | 299.814 | 1.11 | 2 | 101352.97 | 17937.2802 | 17923.7375 | 2843.912 | NORMAL
285.928 | 0.25 | 299.814 | 1.11 | 2 | 106868.78 | 18003.3118 | 17989.5753 | 2812.345 | NORMAL
285.928 | 0.25 | 299.814 | 1.42 | 1 | 57226.51 | 14924.3552 | 14909.1025 | 2293.37 | NORMAL
285.928 | 0.25 | 299.814 | 1.42 | 1 | 79289.74 | 15418.6694 | 15384.3629 | 2004.4 | NORMAL
285.928 | 0.25 | 299.814 | 1.42 | 1 | 101352.97 | 15696.1313 | 15680.4038 | 1844.223 | NORMAL
285.928 | 0.25 | 299.814 | 1.42 | 1 | 106868.78 | 15746.8347 | 15731.0721 | 1814.453 | NORMAL
285.928 | 0.25 | 299.814 | 1.42 | 2 | 57226.51 | 18289.9473 | 18273.1388 | 3504.21 | NORMAL
285.928 | 0.25 | 299.814 | 1.42 | 2 | 79289.74 | 18966.9402 | 18949.851 | 3105.44 | NORMAL
285.928 | 0.25 | 299.814 | 1.42 | 2 | 101352.97 | 19325.7327 | 19308.5135 | 2905.339 | NORMAL
285.928 | 0.25 | 299.814 | 1.42 | 2 | 106868.78 | 19389.6835 | 19372.446 | 2869.964 | NORMAL
285.928 | 0.25 | 302.591 | 0.5 | 1 | 57226.51 | 12282.0926 | 11265.2827 | 2227.169 | NORMAL
285.928 | 0.25 | 302.591 | 0.5 | 1 | 79289.74 | 12540.0352 | 11433.6404 | 2003.431 | NORMAL
285.928 | 0.25 | 302.591 | 0.5 | 1 | 101352.97 | 12643.2005 | 11604.8903 | 1882 | NORMAL
285.928 | 0.25 | 302.591 | 0.5 | 1 | 106868.78 | 12597.2157 | 11708.5325 | 1861.9885 | NORMAL
285.928 | 0.25 | 302.591 | 0.5 | 2 | 57226.51 | 15463.218 | 12572.1529 | 3258.181 | NORMAL
285.928 | 0.25 | 302.591 | 0.5 | 2 | 79289.74 | 15587.1923 | 13119.3345 | 2917.582 | NORMAL
285.928 | 0.25 | 302.591 | 0.5 | 2 | 101352.97 | 15609.8769 | 13360.8058 | 2748.467 | NORMAL
285.928 | 0.25 | 302.591 | 0.5 | 2 | 106868.78 | 15546.2485 | 13358.425 | 2716.3022 | NORMAL
285.928 | 0.25 | 302.591 | 0.8 | 1 | 57226.51 | 13842.9367 | 13824.1657 | 2263.739 | NORMAL
285.928 | 0.25 | 302.591 | 0.8 | 1 | 79289.74 | 14204.9531 | 14192.4954 | 2001.917 | NORMAL
285.928 | 0.25 | 302.591 | 0.8 | 1 | 101352.97 | 14221.6588 | 14209.5562 | 1860.102 | NORMAL
285.928 | 0.25 | 302.591 | 0.8 | 1 | 106868.78 | 14451.993 | 14404.0702 | 1832.723 | NORMAL
285.928 | 0.25 | 302.591 | 0.8 | 2 | 57226.51 | 16932.8253 | 16447.3104 | 3384.429 | NORMAL
285.928 | 0.25 | 302.591 | 0.8 | 2 | 79289.74 | 17548.007 | 16678.398 | 3023.703 | NORMAL
285.928 | 0.25 | 302.591 | 0.8 | 2 | 101352.97 | 17818.7866 | 16912.3806 | 2838.067 | NORMAL
285.928 | 0.25 | 302.591 | 0.8 | 2 | 106868.78 | 17785.6389 | 17064.698 | 2804.209 | NORMAL
285.928 | 0.25 | 302.591 | 1.11 | 1 | 57226.51 | 15017.8488 | 15001.9749 | 2296.09 | NORMAL
285.928 | 0.25 | 302.591 | 1.11 | 1 | 79289.74 | 15483.3236 | 15457.358 | 2004.659 | NORMAL
285.928 | 0.25 | 302.591 | 1.11 | 1 | 101352.97 | 15742.0868 | 15725.8409 | 1843.779 | NORMAL
285.928 | 0.25 | 302.591 | 1.11 | 1 | 106868.78 | 15789.6249 | 15773.3615 | 1813.916 | NORMAL
285.928 | 0.25 | 302.591 | 1.11 | 2 | 57226.51 | 17711.2544 | 17695.6862 | 3452.13 | NORMAL
285.928 | 0.25 | 302.591 | 1.11 | 2 | 79289.74 | 18555.1876 | 18538.8776 | 3081.164 | NORMAL
285.928 | 0.25 | 302.591 | 1.11 | 2 | 101352.97 | 19009.3787 | 18992.7455 | 2890.433 | NORMAL
285.928 | 0.25 | 302.591 | 1.11 | 2 | 106868.78 | 19001.1137 | 18984.6207 | 2854.423 | NORMAL
285.928 | 0.25 | 302.591 | 1.42 | 1 | 57226.51 | 15805.3927 | 15786.9478 | 2320.13 | NORMAL
285.928 | 0.25 | 302.591 | 1.42 | 1 | 79289.74 | 16352.4033 | 16333.549 | 2008.4 | NORMAL
285.928 | 0.25 | 302.591 | 1.42 | 1 | 101352.97 | 16656.1841 | 16632.7488 | 1835.473 | NORMAL
285.928 | 0.25 | 302.591 | 1.42 | 1 | 106868.78 | 16711.6354 | 16692.534 | 1803.155 | NORMAL
285.928 | 0.25 | 302.591 | 1.42 | 2 | 57226.51 | 19250.381 | 19230.0719 | 3594.11 | NORMAL
285.928 | 0.25 | 302.591 | 1.42 | 2 | 79289.74 | 20001.3189 | 19980.6575 | 3167.01 | NORMAL
285.928 | 0.25 | 302.591 | 1.42 | 2 | 101352.97 | 20397.5088 | 20376.6625 | 2954.223 | NORMAL
285.928 | 0.25 | 302.591 | 1.42 | 2 | 106868.78 | 20467.8488 | 20446.9716 | 2916.416 | NORMAL
285.928 | 0.25 | 305.368 | 0.5 | 1 | 57226.51 | 13095.9261 | 11695.199 | 2245.395 | NORMAL
285.928 | 0.25 | 305.368 | 0.5 | 1 | 79289.74 | 13371.3951 | 11871.646 | 2002.218 | NORMAL
285.928 | 0.25 | 305.368 | 0.5 | 1 | 101352.97 | 13470.5744 | 12080.3303 | 1869.966 | NORMAL
285.928 | 0.25 | 305.368 | 0.5 | 1 | 106868.78 | 13416.5592 | 12194.9546 | 1847.6712 | NORMAL
285.928 | 0.25 | 305.368 | 0.5 | 2 | 57226.51 | 16438.8042 | 12961.2903 | 3341.451 | NORMAL
285.928 | 0.25 | 305.368 | 0.5 | 2 | 79289.74 | 16646.102 | 13438.3981 | 2974.453 | NORMAL
285.928 | 0.25 | 305.368 | 0.5 | 2 | 101352.97 | 16642.9367 | 13783.4971 | 2790.67 | NORMAL
285.928 | 0.25 | 305.368 | 0.5 | 2 | 106868.78 | 16535.932 | 13900.9643 | 2754.1965 | NORMAL
285.928 | 0.25 | 305.368 | 0.8 | 1 | 57226.51 | 14602.6964 | 14586.7356 | 2284.118 | NORMAL
285.928 | 0.25 | 305.368 | 0.8 | 1 | 79289.74 | 14670.6917 | 14656.4611 | 2002.103 | NORMAL
285.928 | 0.25 | 305.368 | 0.8 | 1 | 101352.97 | 15002.0223 | 14987.5603 | 1850.909 | NORMAL
285.928 | 0.25 | 305.368 | 0.8 | 1 | 106868.78 | 15022.7433 | 15008.2914 | 1823.775 | NORMAL
285.928 | 0.25 | 305.368 | 0.8 | 2 | 57226.51 | 17935.3751 | 17054.1743 | 3472.891 | NORMAL
285.928 | 0.25 | 305.368 | 0.8 | 2 | 79289.74 | 18607.4736 | 17321.6042 | 3084.041 | NORMAL
285.928 | 0.25 | 305.368 | 0.8 | 2 | 101352.97 | 18904.8945 | 17579.926 | 2886.987 | NORMAL
285.928 | 0.25 | 305.368 | 0.8 | 2 | 106868.78 | 18859.0563 | 17769.3423 | 2848.559 | NORMAL
285.928 | 0.25 | 305.368 | 1.11 | 1 | 57226.51 | 15860.0528 | 15841.0683 | 2321.86 | NORMAL
285.928 | 0.25 | 305.368 | 1.11 | 1 | 79289.74 | 16370.4865 | 16351.2021 | 2008.509 | NORMAL
285.928 | 0.25 | 305.368 | 1.11 | 1 | 101352.97 | 16652.7257 | 16633.2753 | 1835.513 | NORMAL
285.928 | 0.25 | 305.368 | 1.11 | 1 | 106868.78 | 16703.8687 | 16684.392 | 1803.209 | NORMAL
285.928 | 0.25 | 305.368 | 1.11 | 2 | 57226.51 | 18699.619 | 18680.7324 | 3543.38 | NORMAL
285.928 | 0.25 | 305.368 | 1.11 | 2 | 79289.74 | 19637.2216 | 19617.4076 | 3144.856 | NORMAL
285.928 | 0.25 | 305.368 | 1.11 | 2 | 101352.97 | 20122.714 | 20102.5108 | 2940.616 | NORMAL
285.928 | 0.25 | 305.368 | 1.11 | 2 | 106868.78 | 20110.6096 | 20090.5795 | 2902.12 | NORMAL
285.928 | 0.25 | 305.368 | 1.42 | 1 | 57226.51 | 16703.4584 | 16638.0309 | 2350.01 | NORMAL
285.928 | 0.25 | 305.368 | 1.42 | 1 | 79289.74 | 17305.6858 | 17283.1365 | 2014.59 | NORMAL
285.928 | 0.25 | 305.368 | 1.42 | 1 | 101352.97 | 17637.5733 | 17614.7503 | 1828.362 | NORMAL
285.928 | 0.25 | 305.368 | 1.42 | 1 | 106868.78 | 17697.6553 | 17669.0382 | 1793.097 | NORMAL
285.928 | 0.25 | 305.368 | 1.42 | 2 | 57226.51 | 20224.2966 | 20158.1025 | 3688.17 | NORMAL
285.928 | 0.25 | 305.368 | 1.42 | 2 | 79289.74 | 21052.2567 | 21027.5624 | 3231.73 | NORMAL
285.928 | 0.25 | 305.368 | 1.42 | 2 | 101352.97 | 21487.4267 | 21462.5013 | 3005.583 | NORMAL
285.928 | 0.25 | 305.368 | 1.42 | 2 | 106868.78 | 21564.6835 | 21539.7116 | 2965.206 | NORMAL
285.928 | 0.35 | 288.706 | 0.5 | 1 | 57226.51 | 9375.0879 | 8259.9493 | 2175.961 | NORMAL
285.928 | 0.35 | 288.706 | 0.5 | 1 | 79289.74 | 9486.4889 | 8452.8221 | 2018.825 | NORMAL
285.928 | 0.35 | 288.706 | 0.5 | 1 | 101352.97 | 9524.2673 | 8621.1763 | 1937.8046 | NORMAL
285.928 | 0.35 | 288.706 | 0.5 | 1 | 106868.78 | 9493.9039 | 8696.9286 | 1925.529 | NORMAL
285.928 | 0.35 | 288.706 | 0.5 | 2 | 57226.51 | 11952.5498 | 9546.9199 | 2981.913 | NORMAL
285.928 | 0.35 | 288.706 | 0.5 | 2 | 79289.74 | 11966.0903 | 9948.6553 | 2733.211 | NORMAL
285.928 | 0.35 | 288.706 | 0.5 | 2 | 101352.97 | 11921.4244 | 10217.4833 | 2606.2392 | NORMAL
285.928 | 0.35 | 288.706 | 0.5 | 2 | 106868.78 | 11871.8933 | 10284.4431 | 2583.2879 | NORMAL
285.928 | 0.35 | 288.706 | 0.8 | 1 | 57226.51 | 10184.9941 | 10181.1646 | 2188.322 | NORMAL
285.928 | 0.35 | 288.706 | 0.8 | 1 | 79289.74 | 10473.2708 | 10469.3433 | 2011.927 | NORMAL
285.928 | 0.35 | 288.706 | 0.8 | 1 | 101352.97 | 10629.9531 | 10625.9988 | 1916.575 | NORMAL
285.928 | 0.35 | 288.706 | 0.8 | 1 | 106868.78 | 10615.3869 | 10611.4592 | 1900.136 | NORMAL
285.928 | 0.35 | 288.706 | 0.8 | 2 | 57226.51 | 13222.3329 | 12090.9772 | 3078.275 | NORMAL
285.928 | 0.35 | 288.706 | 0.8 | 2 | 79289.74 | 13508.9097 | 12373.4589 | 2809.787 | NORMAL
285.928 | 0.35 | 288.706 | 0.8 | 2 | 101352.97 | 13625.2638 | 12621.4497 | 2670.302 | NORMAL
285.928 | 0.35 | 288.706 | 0.8 | 2 | 106868.78 | 13594.6366 | 12723.1388 | 2643.948 | NORMAL
285.928 | 0.35 | 288.706 | 1.11 | 1 | 57226.51 | 11067.204 | 11061.9913 | 2203.48 | NORMAL
285.928 | 0.35 | 288.706 | 1.11 | 1 | 79289.74 | 11344.6659 | 11339.402 | 2007.144 | NORMAL
285.928 | 0.35 | 288.706 | 1.11 | 1 | 101352.97 | 11499.9707 | 11494.6807 | 1901.118 | NORMAL
285.928 | 0.35 | 288.706 | 1.11 | 1 | 106868.78 | 11529.7773 | 11524.4736 | 1881.625 | NORMAL
285.928 | 0.35 | 288.706 | 1.11 | 2 | 57226.51 | 13882.034 | 13876.62 | 3129.98 | NORMAL
285.928 | 0.35 | 288.706 | 1.11 | 2 | 79289.74 | 14323.0363 | 14258.3822 | 2851.901 | NORMAL
285.928 | 0.35 | 288.706 | 1.11 | 2 | 101352.97 | 14555.6565 | 14462.0636 | 2706.178 | NORMAL
285.928 | 0.35 | 288.706 | 1.11 | 2 | 106868.78 | 14540.0059 | 14534.4807 | 2678.477 | NORMAL
285.928 | 0.35 | 288.706 | 1.42 | 1 | 57226.51 | 11590.6213 | 11584.5015 | 2213.27 | NORMAL
285.928 | 0.35 | 288.706 | 1.42 | 1 | 79289.74 | 11907.4736 | 11899.9124 | 2004.73 | NORMAL
285.928 | 0.35 | 288.706 | 1.42 | 1 | 101352.97 | 12087.925 | 12081.6755 | 1891.225 | NORMAL
285.928 | 0.35 | 288.706 | 1.42 | 1 | 106868.78 | 12121.8347 | 12115.5798 | 1870.434 | NORMAL
285.928 | 0.35 | 288.706 | 1.42 | 2 | 57226.51 | 14304.2497 | 14298.013 | 3165.1 | NORMAL
285.928 | 0.35 | 288.706 | 1.42 | 2 | 79289.74 | 14860.4044 | 14853.9105 | 2879.14 | NORMAL
285.928 | 0.35 | 288.706 | 1.42 | 2 | 101352.97 | 15169.6952 | 15163.0964 | 2730.829 | NORMAL
285.928 | 0.35 | 288.706 | 1.42 | 2 | 106868.78 | 15160.0528 | 15153.4885 | 2701.021 | NORMAL
285.928 | 0.35 | 291.483 | 0.5 | 1 | 57226.51 | 10064.5076 | 8618.1775 | 2186.605 | NORMAL
285.928 | 0.35 | 291.483 | 0.5 | 1 | 79289.74 | 10193.9332 | 8887.7539 | 2014.104 | NORMAL
285.928 | 0.35 | 291.483 | 0.5 | 1 | 101352.97 | 10226.8171 | 9092.4586 | 1923.807 | NORMAL
285.928 | 0.35 | 291.483 | 0.5 | 1 | 106868.78 | 10189.449 | 9178.941 | 1909.6427 | NORMAL
285.928 | 0.35 | 291.483 | 0.5 | 2 | 57226.51 | 12815.592 | 9955.1519 | 3047.567 | NORMAL
285.928 | 0.35 | 291.483 | 0.5 | 2 | 79289.74 | 12842.4678 | 10386.7182 | 2776.059 | NORMAL
285.928 | 0.35 | 291.483 | 0.5 | 2 | 101352.97 | 12778.0774 | 10639.6406 | 2637.8866 | NORMAL
285.928 | 0.35 | 291.483 | 0.5 | 2 | 106868.78 | 12719.7831 | 10750.5317 | 2612.6711 | NORMAL
285.928 | 0.35 | 291.483 | 0.8 | 1 | 57226.51 | 10895.8382 | 10890.739 | 2200.405 | NORMAL
285.928 | 0.35 | 291.483 | 0.8 | 1 | 79289.74 | 11209.408 | 11204.1956 | 2007.951 | NORMAL
285.928 | 0.35 | 291.483 | 0.8 | 1 | 101352.97 | 11392.2333 | 11332.5494 | 1902.723 | NORMAL
285.928 | 0.35 | 291.483 | 0.8 | 1 | 106868.78 | 11371.3072 | 11366.1105 | 1884.466 | NORMAL
285.928 | 0.35 | 291.483 | 0.8 | 2 | 57226.51 | 14114.9765 | 12788.5499 | 3148.746 | NORMAL
285.928 | 0.35 | 291.483 | 0.8 | 2 | 79289.74 | 14444.7538 | 13053.5651 | 2857.631 | NORMAL
285.928 | 0.35 | 291.483 | 0.8 | 2 | 101352.97 | 14573.007 | 13277.6707 | 2707.104 | NORMAL
285.928 | 0.35 | 291.483 | 0.8 | 2 | 106868.78 | 14535.7561 | 13370.8316 | 2678.374 | NORMAL
285.928 | 0.35 | 291.483 | 1.11 | 1 | 57226.51 | 11825.762 | 11818.9977 | 2217.86 | NORMAL
285.928 | 0.35 | 291.483 | 1.11 | 1 | 79289.74 | 12135.2286 | 12128.3965 | 2004.169 | NORMAL
285.928 | 0.35 | 291.483 | 1.11 | 1 | 101352.97 | 12309.2321 | 12302.3636 | 1887.633 | NORMAL
285.928 | 0.35 | 291.483 | 1.11 | 1 | 106868.78 | 12340.211 | 12332.918 | 1866.659 | NORMAL
285.928 | 0.35 | 291.483 | 1.11 | 2 | 57226.51 | 14777.2567 | 14770.0898 | 3202.83 | NORMAL
285.928 | 0.35 | 291.483 | 1.11 | 2 | 79289.74 | 15292.8488 | 14999.7002 | 2901.696 | NORMAL
285.928 | 0.35 | 291.483 | 1.11 | 2 | 101352.97 | 15544.6659 | 15199.3256 | 2745.072 | NORMAL
285.928 | 0.35 | 291.483 | 1.11 | 2 | 106868.78 | 15525.3224 | 15339.0185 | 2715.453 | NORMAL
285.928 | 0.35 | 291.483 | 1.42 | 1 | 57226.51 | 12398.0657 | 12390.1805 | 2229.74 | NORMAL
285.928 | 0.35 | 291.483 | 1.42 | 1 | 79289.74 | 12753.9859 | 12745.9509 | 2002.21 | NORMAL
285.928 | 0.35 | 291.483 | 1.42 | 1 | 101352.97 | 12957.4736 | 12949.3752 | 1877.307 | NORMAL
285.928 | 0.35 | 291.483 | 1.42 | 1 | 106868.78 | 12994.1969 | 12986.0886 | 1854.89 | NORMAL
285.928 | 0.35 | 291.483 | 1.42 | 2 | 57226.51 | 15298.0363 | 15289.806 | 3244.03 | NORMAL
285.928 | 0.35 | 291.483 | 1.42 | 2 | 79289.74 | 15837.1043 | 15828.5998 | 2929.97 | NORMAL
285.928 | 0.35 | 291.483 | 1.42 | 2 | 101352.97 | 16164.2145 | 16155.5829 | 2770.596 | NORMAL
285.928 | 0.35 | 291.483 | 1.42 | 2 | 106868.78 | 16162.6612 | 16154.095 | 2739.956 | NORMAL
285.928 | 0.35 | 294.26 | 0.5 | 1 | 57226.51 | 10780.51 | 9059.5525 | 2198.382 | NORMAL
285.928 | 0.35 | 294.26 | 0.5 | 1 | 79289.74 | 10933.0598 | 9409.2864 | 2009.78 | NORMAL
285.928 | 0.35 | 294.26 | 0.5 | 1 | 101352.97 | 10962.5733 | 9563.727 | 1910.032 | NORMAL
285.928 | 0.35 | 294.26 | 0.5 | 1 | 106868.78 | 10918.6694 | 9620.2649 | 1893.9447 | NORMAL
285.928 | 0.35 | 294.26 | 0.5 | 2 | 57226.51 | 13725.5569 | 10316.3756 | 3118.192 | NORMAL
285.928 | 0.35 | 294.26 | 0.5 | 2 | 79289.74 | 13756.0082 | 10834.7273 | 2821.938 | NORMAL
285.928 | 0.35 | 294.26 | 0.5 | 2 | 101352.97 | 13672.7726 | 11155.1366 | 2671.913 | NORMAL
285.928 | 0.35 | 294.26 | 0.5 | 2 | 106868.78 | 13608.1184 | 11209.6875 | 2644.4422 | NORMAL
285.928 | 0.35 | 294.26 | 0.8 | 1 | 57226.51 | 11745.3986 | 11639.9249 | 2216.42 | NORMAL
285.928 | 0.35 | 294.26 | 0.8 | 1 | 79289.74 | 12090.1817 | 11760.555 | 2004.515 | NORMAL
285.928 | 0.35 | 294.26 | 0.8 | 1 | 101352.97 | 12267.7902 | 11901.0078 | 1889.178 | NORMAL
285.928 | 0.35 | 294.26 | 0.8 | 1 | 106868.78 | 12230.7444 | 12023.6535 | 1868.161 | NORMAL
285.928 | 0.35 | 294.26 | 0.8 | 2 | 57226.51 | 15016.1782 | 13217.0749 | 3221.738 | NORMAL
285.928 | 0.35 | 294.26 | 0.8 | 2 | 79289.74 | 15419.2556 | 13601.2328 | 2908.474 | NORMAL
285.928 | 0.35 | 294.26 | 0.8 | 2 | 101352.97 | 15559.027 | 13927.8653 | 2746.309 | NORMAL
285.928 | 0.35 | 294.26 | 0.8 | 2 | 106868.78 | 15515.6213 | 14138.2841 | 2715.143 | NORMAL
285.928 | 0.35 | 294.26 | 1.11 | 1 | 57226.51 | 12603.1653 | 12594.5951 | 2234.17 | NORMAL
285.928 | 0.35 | 294.26 | 1.11 | 1 | 79289.74 | 12721.6295 | 12713.2969 | 2002.551 | NORMAL
285.928 | 0.35 | 294.26 | 1.11 | 1 | 101352.97 | 12968.0832 | 12959.6929 | 1877.114 | NORMAL
285.928 | 0.35 | 294.26 | 1.11 | 1 | 106868.78 | 13175.1465 | 13166.3982 | 1852.252 | NORMAL
285.928 | 0.35 | 294.26 | 1.11 | 2 | 57226.51 | 15825 | 15449.8684 | 3288.57 | NORMAL
285.928 | 0.35 | 294.26 | 1.11 | 2 | 79289.74 | 16375.1172 | 15643.0512 | 2959.617 | NORMAL
285.928 | 0.35 | 294.26 | 1.11 | 2 | 101352.97 | 16652.7257 | 15867.966 | 2789.706 | NORMAL
285.928 | 0.35 | 294.26 | 1.11 | 2 | 106868.78 | 16620.3693 | 16045.7699 | 2756.282 | NORMAL
285.928 | 0.35 | 294.26 | 1.42 | 1 | 57226.51 | 13226.9343 | 13216.9348 | 2248.56 | NORMAL
285.928 | 0.35 | 294.26 | 1.42 | 1 | 79289.74 | 13624.4431 | 13614.2793 | 2001.82 | NORMAL
285.928 | 0.35 | 294.26 | 1.42 | 1 | 101352.97 | 13849.2087 | 13835.0963 | 1864.797 | NORMAL
285.928 | 0.35 | 294.26 | 1.42 | 1 | 106868.78 | 13891.1489 | 13880.8555 | 1840.392 | NORMAL
285.928 | 0.35 | 294.26 | 1.42 | 2 | 57226.51 | 16286.4595 | 16275.9059 | 3327.49 | NORMAL
285.928 | 0.35 | 294.26 | 1.42 | 2 | 79289.74 | 16973.6225 | 16962.6236 | 2991.99 | NORMAL
285.928 | 0.35 | 294.26 | 1.42 | 2 | 101352.97 | 17342.5264 | 17331.3578 | 2819.021 | NORMAL
285.928 | 0.35 | 294.26 | 1.42 | 2 | 106868.78 | 17323.6518 | 17312.5647 | 2785.419 | NORMAL
285.928 | 0.35 | 297.037 | 0.5 | 1 | 57226.51 | 11659.6717 | 9369.6656 | 2214.448 | NORMAL
285.928 | 0.35 | 297.037 | 0.5 | 1 | 79289.74 | 11775.1172 | 9667.7834 | 2005.821 | NORMAL
285.928 | 0.35 | 297.037 | 0.5 | 1 | 101352.97 | 11796.9519 | 9923.7729 | 1896.062 | NORMAL
285.928 | 0.35 | 297.037 | 0.5 | 1 | 106868.78 | 11711.0199 | 9985.2138 | 1877.9996 | NORMAL
285.928 | 0.35 | 297.037 | 0.5 | 2 | 57226.51 | 14678.1946 | 10632.0622 | 3193.963 | NORMAL
285.928 | 0.35 | 297.037 | 0.5 | 2 | 79289.74 | 14722.1571 | 11189.973 | 2871.595 | NORMAL
285.928 | 0.35 | 297.037 | 0.5 | 2 | 101352.97 | 14626.524 | 11575.4019 | 2708.695 | NORMAL
285.928 | 0.35 | 297.037 | 0.5 | 2 | 106868.78 | 14550.0879 | 11627.1062 | 2678.9244 | NORMAL
285.928 | 0.35 | 297.037 | 0.8 | 1 | 57226.51 | 12593.5229 | 12193.0992 | 2233.908 | NORMAL
285.928 | 0.35 | 297.037 | 0.8 | 1 | 79289.74 | 12958.1184 | 12290.1015 | 2002.13 | NORMAL
285.928 | 0.35 | 297.037 | 0.8 | 1 | 101352.97 | 13146.9519 | 12457.4995 | 1874.652 | NORMAL
285.928 | 0.35 | 297.037 | 0.8 | 1 | 106868.78 | 13105.7444 | 12615.3668 | 1852.708 | NORMAL
285.928 | 0.35 | 297.037 | 0.8 | 2 | 57226.51 | 16130.6565 | 13685.5716 | 3314.46 | NORMAL
285.928 | 0.35 | 297.037 | 0.8 | 2 | 79289.74 | 16531.7995 | 14097.8723 | 2968.222 | NORMAL
285.928 | 0.35 | 297.037 | 0.8 | 2 | 101352.97 | 16678.6635 | 14473.8276 | 2792.133 | NORMAL
285.928 | 0.35 | 297.037 | 0.8 | 2 | 106868.78 | 16609.6424 | 14624.8566 | 2755.753 | NORMAL
285.928 | 0.35 | 297.037 | 1.11 | 1 | 57226.51 | 13080.5979 | 13070.6566 | 2244.98 | NORMAL
285.928 | 0.35 | 297.037 | 1.11 | 1 | 79289.74 | 13590.1524 | 13579.7695 | 2002.073 | NORMAL
285.928 | 0.35 | 297.037 | 1.11 | 1 | 101352.97 | 13877.1102 | 13866.5358 | 1865.077 | NORMAL
285.928 | 0.35 | 297.037 | 1.11 | 1 | 106868.78 | 13847.7433 | 13837.2605 | 1840.745 | NORMAL
285.928 | 0.35 | 297.037 | 1.11 | 2 | 57226.51 | 16849.238 | 16079.3458 | 3376.07 | NORMAL
285.928 | 0.35 | 297.037 | 1.11 | 2 | 79289.74 | 17476.3482 | 16325.5132 | 3020.125 | NORMAL
285.928 | 0.35 | 297.037 | 1.11 | 2 | 101352.97 | 17767.2333 | 16609.2361 | 2835.677 | NORMAL
285.928 | 0.35 | 297.037 | 1.11 | 2 | 106868.78 | 17732.7374 | 16818.0828 | 2801.975 | NORMAL
285.928 | 0.35 | 297.037 | 1.42 | 1 | 57226.51 | 14075.5862 | 14063.1715 | 2269.85 | NORMAL
285.928 | 0.35 | 297.037 | 1.42 | 1 | 79289.74 | 14517.2333 | 14504.5743 | 2002.23 | NORMAL
285.928 | 0.35 | 297.037 | 1.42 | 1 | 101352.97 | 14766.6471 | 14753.8592 | 1853.237 | NORMAL
285.928 | 0.35 | 297.037 | 1.42 | 1 | 106868.78 | 14813.218 | 14800.3898 | 1826.822 | NORMAL
285.928 | 0.35 | 297.037 | 1.42 | 2 | 57226.51 | 17313.9508 | 17300.6363 | 3417.74 | NORMAL
285.928 | 0.35 | 297.037 | 1.42 | 2 | 79289.74 | 18085.8441 | 18071.9361 | 3054.1 | NORMAL
285.928 | 0.35 | 297.037 | 1.42 | 2 | 101352.97 | 18484.3787 | 18406.3191 | 2868.631 | NORMAL
285.928 | 0.35 | 297.037 | 1.42 | 2 | 106868.78 | 18467.4385 | 18453.4401 | 2832.083 | NORMAL
285.928 | 0.35 | 299.814 | 0.5 | 1 | 57226.51 | 12512.9543 | 9708.5635 | 2232.134 | NORMAL
285.928 | 0.35 | 299.814 | 0.5 | 1 | 79289.74 | 12648.4467 | 10035.8468 | 2003.2 | NORMAL
285.928 | 0.35 | 299.814 | 0.5 | 1 | 101352.97 | 12649.8828 | 10324.8976 | 1881.814 | NORMAL
285.928 | 0.35 | 299.814 | 0.5 | 1 | 106868.78 | 12580.422 | 10387.4029 | 1862.2667 | NORMAL
285.928 | 0.35 | 299.814 | 0.5 | 2 | 57226.51 | 15760.6975 | 10929.9334 | 3283.549 | NORMAL
285.928 | 0.35 | 299.814 | 0.5 | 2 | 79289.74 | 15720.1641 | 11520.9624 | 2924.598 | NORMAL
285.928 | 0.35 | 299.814 | 0.5 | 2 | 101352.97 | 15627.9601 | 11956.8898 | 2748.348 | NORMAL
285.928 | 0.35 | 299.814 | 0.5 | 2 | 106868.78 | 15540.7679 | 11970.5096 | 2716.1192 | NORMAL
285.928 | 0.35 | 299.814 | 0.8 | 1 | 57226.51 | 13471.8933 | 12723.5835 | 2254.458 | NORMAL
285.928 | 0.35 | 299.814 | 0.8 | 1 | 79289.74 | 13871.4244 | 12816.78 | 2000.83 | NORMAL
285.928 | 0.35 | 299.814 | 0.8 | 1 | 101352.97 | 14072.1571 | 13039.5141 | 1861.965 | NORMAL
285.928 | 0.35 | 299.814 | 0.8 | 1 | 106868.78 | 14022.7139 | 13201.2073 | 1837.907 | NORMAL
285.928 | 0.35 | 299.814 | 0.8 | 2 | 57226.51 | 17193.6108 | 14193.3601 | 3406.286 | NORMAL
285.928 | 0.35 | 299.814 | 0.8 | 2 | 79289.74 | 17646.6295 | 14617.6915 | 3029.308 | NORMAL
285.928 | 0.35 | 299.814 | 0.8 | 2 | 101352.97 | 17802.0516 | 15039.7428 | 2839.437 | NORMAL
285.928 | 0.35 | 299.814 | 0.8 | 2 | 106868.78 | 17731.1254 | 15222.2244 | 2802.006 | NORMAL
285.928 | 0.35 | 299.814 | 1.11 | 1 | 57226.51 | 13963.9801 | 13951.608 | 2266.82 | NORMAL
285.928 | 0.35 | 299.814 | 1.11 | 1 | 79289.74 | 14514.5956 | 14501.663 | 2001.661 | NORMAL
285.928 | 0.35 | 299.814 | 1.11 | 1 | 101352.97 | 14831.8288 | 14818.6582 | 1853.001 | NORMAL
285.928 | 0.35 | 299.814 | 1.11 | 1 | 106868.78 | 14799.3259 | 14786.2729 | 1827.634 | NORMAL
285.928 | 0.35 | 299.814 | 1.11 | 2 | 57226.51 | 17917.1747 | 16798.7667 | 3470.99 | NORMAL
285.928 | 0.35 | 299.814 | 1.11 | 2 | 79289.74 | 18613.9215 | 17019.9369 | 3085.139 | NORMAL
285.928 | 0.35 | 299.814 | 1.11 | 2 | 101352.97 | 18936.6647 | 17338.9783 | 2888.523 | NORMAL
285.928 | 0.35 | 299.814 | 1.11 | 2 | 106868.78 | 18895.6624 | 17553.1444 | 2850.032 | NORMAL
285.928 | 0.35 | 299.814 | 1.42 | 1 | 57226.51 | 14942.585 | 14927.3734 | 2293.92 | NORMAL
285.928 | 0.35 | 299.814 | 1.42 | 1 | 79289.74 | 15433.3236 | 15417.7976 | 2004.45 | NORMAL
285.928 | 0.35 | 299.814 | 1.42 | 1 | 101352.97 | 15696.102 | 15680.3902 | 1844.148 | NORMAL
285.928 | 0.35 | 299.814 | 1.42 | 1 | 106868.78 | 15758.7339 | 15743.0067 | 1814.404 | NORMAL
285.928 | 0.35 | 299.814 | 1.42 | 2 | 57226.51 | 18381.4478 | 18364.9413 | 3513.87 | NORMAL
285.928 | 0.35 | 299.814 | 1.42 | 2 | 79289.74 | 19245.8968 | 18997.7402 | 3121.55 | NORMAL
285.928 | 0.35 | 299.814 | 1.42 | 2 | 101352.97 | 19678.8101 | 19252.2916 | 2921.571 | NORMAL
285.928 | 0.35 | 299.814 | 1.42 | 2 | 106868.78 | 19654.8652 | 19517.969 | 2882.311 | NORMAL
285.928 | 0.35 | 302.591 | 0.5 | 1 | 57226.51 | 13422.5674 | 10062.1337 | 2253.167 | NORMAL
285.928 | 0.35 | 302.591 | 0.5 | 1 | 79289.74 | 13573.7691 | 10383.051 | 2002.105 | NORMAL
285.928 | 0.35 | 302.591 | 0.5 | 1 | 101352.97 | 13569.4314 | 10709.7552 | 1869.174 | NORMAL
285.928 | 0.35 | 302.591 | 0.5 | 1 | 106868.78 | 13483.5287 | 10733.0102 | 1846.6064 | NORMAL
285.928 | 0.35 | 302.591 | 0.5 | 2 | 57226.51 | 16867.2919 | 11177.4821 | 3377.737 | NORMAL
285.928 | 0.35 | 302.591 | 0.5 | 2 | 79289.74 | 16910.6682 | 11845.5341 | 2988.532 | NORMAL
285.928 | 0.35 | 302.591 | 0.5 | 2 | 101352.97 | 16763.1301 | 12324.0186 | 2794.278 | NORMAL
285.928 | 0.35 | 302.591 | 0.5 | 2 | 106868.78 | 16653.8101 | 12341.8722 | 2758.7819 | NORMAL
285.928 | 0.35 | 302.591 | 0.8 | 1 | 57226.51 | 14380.2169 | 13201.2548 | 2277.982 | NORMAL
285.928 | 0.35 | 302.591 | 0.8 | 1 | 79289.74 | 14841.6471 | 13365.6899 | 2002.946 | NORMAL
285.928 | 0.35 | 302.591 | 0.8 | 1 | 101352.97 | 15048.3001 | 13589.8189 | 1850.046 | NORMAL
285.928 | 0.35 | 302.591 | 0.8 | 1 | 106868.78 | 14988.5405 | 13781.828 | 1823.682 | NORMAL
285.928 | 0.35 | 302.591 | 0.8 | 2 | 57226.51 | 18285.7562 | 14665.0119 | 3505.908 | NORMAL
285.928 | 0.35 | 302.591 | 0.8 | 2 | 79289.74 | 18819.7831 | 15104.852 | 3096.086 | NORMAL
285.928 | 0.35 | 302.591 | 0.8 | 2 | 101352.97 | 18993.347 | 15573.7468 | 2891.406 | NORMAL
285.928 | 0.35 | 302.591 | 0.8 | 2 | 106868.78 | 18911.0492 | 15798.4796 | 2850.716 | NORMAL
285.928 | 0.35 | 302.591 | 1.11 | 1 | 57226.51 | 14888.2474 | 14873.0613 | 2292.19 | NORMAL
285.928 | 0.35 | 302.591 | 1.11 | 1 | 79289.74 | 15492.2333 | 15476.3073 | 2003.969 | NORMAL
285.928 | 0.35 | 302.591 | 1.11 | 1 | 101352.97 | 15831.6823 | 15815.4707 | 1841.313 | NORMAL
285.928 | 0.35 | 302.591 | 1.11 | 1 | 106868.78 | 15795.7796 | 15779.7311 | 1814.848 | NORMAL
285.928 | 0.35 | 302.591 | 1.11 | 2 | 57226.51 | 19000.1465 | 17378.864 | 3572.93 | NORMAL
285.928 | 0.35 | 302.591 | 1.11 | 2 | 79289.74 | 19801.7292 | 17716.1517 | 3155.054 | NORMAL
285.928 | 0.35 | 302.591 | 1.11 | 2 | 101352.97 | 20164.2732 | 18049.424 | 2944.044 | NORMAL
285.928 | 0.35 | 302.591 | 1.11 | 2 | 106868.78 | 20110.9906 | 18268.844 | 2902.153 | NORMAL
285.928 | 0.35 | 302.591 | 1.42 | 1 | 57226.51 | 15828.3412 | 15809.9803 | 2320.92 | NORMAL
285.928 | 0.35 | 302.591 | 1.42 | 1 | 79289.74 | 15929.2497 | 15911.6797 | 2006.63 | NORMAL
285.928 | 0.35 | 302.591 | 1.42 | 1 | 101352.97 | 16319.5193 | 16301.4536 | 1837.218 | NORMAL
285.928 | 0.35 | 302.591 | 1.42 | 1 | 106868.78 | 16318.2298 | 16300.296 | 1808.45 | NORMAL
285.928 | 0.35 | 302.591 | 1.42 | 2 | 57226.51 | 19474.9414 | 19454.7264 | 3617.21 | NORMAL
285.928 | 0.35 | 302.591 | 1.42 | 2 | 79289.74 | 20442.2333 | 19810.6705 | 3193.47 | NORMAL
285.928 | 0.35 | 302.591 | 1.42 | 2 | 101352.97 | 20921.7468 | 20083.4961 | 2978.884 | NORMAL
285.928 | 0.35 | 302.591 | 1.42 | 2 | 106868.78 | 20891.7644 | 20357.9589 | 2936.725 | NORMAL
285.928 | 0.35 | 305.368 | 0.5 | 1 | 57226.51 | 14376.3189 | 10325.9923 | 2277.742 | NORMAL
285.928 | 0.35 | 305.368 | 0.5 | 1 | 79289.74 | 14555.5979 | 10731.1582 | 2002.852 | NORMAL
285.928 | 0.35 | 305.368 | 0.5 | 1 | 101352.97 | 14541.0317 | 11076.8199 | 1856.845 | NORMAL
285.928 | 0.35 | 305.368 | 0.5 | 1 | 106868.78 | 14440.6799 | 11052.6509 | 1831.736 | NORMAL
285.928 | 0.35 | 305.368 | 0.5 | 2 | 57226.51 | 18017.7608 | 11390.7924 | 3480.529 | NORMAL
285.928 | 0.35 | 305.368 | 0.5 | 2 | 79289.74 | 18101.7585 | 12136.324 | 3055.148 | NORMAL
285.928 | 0.35 | 305.368 | 0.5 | 2 | 101352.97 | 17936.1665 | 12659.9561 | 2843.745 | NORMAL
285.928 | 0.35 | 305.368 | 0.5 | 2 | 106868.78 | 17807.8839 | 12673.8532 | 2805.0992 | NORMAL
285.928 | 0.35 | 305.368 | 0.8 | 1 | 57226.51 | 15338.8042 | 13782.5598 | 2305.614 | NORMAL
285.928 | 0.35 | 305.368 | 0.8 | 1 | 79289.74 | 15854.9531 | 13873.7499 | 2006.549 | NORMAL
285.928 | 0.35 | 305.368 | 0.8 | 1 | 101352.97 | 16083.2063 | 14126.0892 | 1841.021 | NORMAL
285.928 | 0.35 | 305.368 | 0.8 | 1 | 106868.78 | 16014.6542 | 14339.7936 | 1812.195 | NORMAL
285.928 | 0.35 | 305.368 | 0.8 | 2 | 57226.51 | 19420.8089 | 15130.4026 | 3613.181 | NORMAL
285.928 | 0.35 | 305.368 | 0.8 | 2 | 79289.74 | 20043.5522 | 15615.8112 | 3168.853 | NORMAL
285.928 | 0.35 | 305.368 | 0.8 | 2 | 101352.97 | 20244.2263 | 16111.2663 | 2948.667 | NORMAL
285.928 | 0.35 | 305.368 | 0.8 | 2 | 106868.78 | 20150.1465 | 16332.8222 | 2903.956 | NORMAL
285.928 | 0.35 | 305.368 | 1.11 | 1 | 57226.51 | 15842.3798 | 15823.9393 | 2321.33 | NORMAL
285.928 | 0.35 | 305.368 | 1.11 | 1 | 79289.74 | 16515.8265 | 16469.6317 | 2008.387 | NORMAL
285.928 | 0.35 | 305.368 | 1.11 | 1 | 101352.97 | 16883.4115 | 16593.3882 | 1832.663 | NORMAL
285.928 | 0.35 | 305.368 | 1.11 | 1 | 106868.78 | 16840.2696 | 16790.0856 | 1803.312 | NORMAL
285.928 | 0.35 | 305.368 | 1.11 | 2 | 57226.51 | 20138.1008 | 17932.8378 | 3682.02 | NORMAL
285.928 | 0.35 | 305.368 | 1.11 | 2 | 79289.74 | 21033.646 | 18328.2984 | 3230.804 | NORMAL
285.928 | 0.35 | 305.368 | 1.11 | 2 | 101352.97 | 21440.1231 | 18762.8949 | 3004.103 | NORMAL
285.928 | 0.35 | 305.368 | 1.11 | 2 | 106868.78 | 21378.6635 | 18998.9617 | 2958.801 | NORMAL
285.928 | 0.35 | 305.368 | 1.42 | 1 | 57226.51 | 16158.8511 | 16138.8303 | 2331.53 | NORMAL
285.928 | 0.35 | 305.368 | 1.42 | 1 | 79289.74 | 16959.8769 | 16938.6092 | 2012.04 | NORMAL
285.928 | 0.35 | 305.368 | 1.42 | 1 | 101352.97 | 17387.3681 | 17365.4948 | 1829.551 | NORMAL
285.928 | 0.35 | 305.368 | 1.42 | 1 | 106868.78 | 17362.837 | 17341.1682 | 1795.872 | NORMAL
285.928 | 0.35 | 305.368 | 1.42 | 2 | 57226.51 | 20582.8839 | 20395.2298 | 3728.18 | NORMAL
285.928 | 0.35 | 305.368 | 1.42 | 2 | 79289.74 | 21680.9789 | 20571.9318 | 3270.85 | NORMAL
285.928 | 0.35 | 305.368 | 1.42 | 2 | 101352.97 | 22212.2216 | 20898.2132 | 3040.727 | NORMAL
285.928 | 0.35 | 305.368 | 1.42 | 2 | 106868.78 | 22176.5533 | 21239.3057 | 2995.59 | NORMAL
285.928 | 0.45 | 288.706 | 0.5 | 1 | 57226.51 | 9909.5252 | 7560.2047 | 2183.965 | NORMAL
285.928 | 0.45 | 288.706 | 0.5 | 1 | 79289.74 | 9951.9637 | 7915.0057 | 2015.657 | NORMAL
285.928 | 0.45 | 288.706 | 0.5 | 1 | 101352.97 | 9923.0657 | 8150.1314 | 1929.879 | NORMAL
285.928 | 0.45 | 288.706 | 0.5 | 1 | 106868.78 | 9876.0258 | 8208.7156 | 1916.4929 | NORMAL
285.928 | 0.45 | 288.706 | 0.5 | 2 | 57226.51 | 12629.1618 | 8817.3398 | 3033.155 | NORMAL
285.928 | 0.45 | 288.706 | 0.5 | 2 | 79289.74 | 12547.6553 | 9324.9783 | 2762.005 | NORMAL
285.928 | 0.45 | 288.706 | 0.5 | 2 | 101352.97 | 12415.2989 | 9659.624 | 2624.6955 | NORMAL
285.928 | 0.45 | 288.706 | 0.5 | 2 | 106868.78 | 12346.1606 | 9740.4911 | 2599.7839 | NORMAL
285.928 | 0.45 | 288.706 | 0.8 | 1 | 57226.51 | 10696.8054 | 9662.5527 | 2196.935 | NORMAL
285.928 | 0.45 | 288.706 | 0.8 | 1 | 79289.74 | 10931.5944 | 9980.7096 | 2009.45 | NORMAL
285.928 | 0.45 | 288.706 | 0.8 | 1 | 101352.97 | 11037.3681 | 10259.5979 | 1908.796 | NORMAL
285.928 | 0.45 | 288.706 | 0.8 | 1 | 106868.78 | 11006.0082 | 10366.5371 | 1891.965 | NORMAL
285.928 | 0.45 | 288.706 | 0.8 | 2 | 57226.51 | 13886.6061 | 11120.5608 | 3131.214 | NORMAL
285.928 | 0.45 | 288.706 | 0.8 | 2 | 79289.74 | 14103.2532 | 11490.8089 | 2839.986 | NORMAL
285.928 | 0.45 | 288.706 | 0.8 | 2 | 101352.97 | 14153.1946 | 11881.6069 | 2690.793 | NORMAL
285.928 | 0.45 | 288.706 | 0.8 | 2 | 106868.78 | 14100 | 12026.6655 | 2662.36 | NORMAL
285.928 | 0.45 | 288.706 | 1.11 | 1 | 57226.51 | 11178.2825 | 11137.0123 | 2205.42 | NORMAL
285.928 | 0.45 | 288.706 | 1.11 | 1 | 79289.74 | 11514.2145 | 11205.6566 | 2006.497 | NORMAL
285.928 | 0.45 | 288.706 | 1.11 | 1 | 101352.97 | 11654.4549 | 11351.812 | 1898.394 | NORMAL
285.928 | 0.45 | 288.706 | 1.11 | 1 | 106868.78 | 11592.2919 | 11562.407 | 1880.055 | NORMAL
285.928 | 0.45 | 288.706 | 1.11 | 2 | 57226.51 | 14519.2849 | 12858.2787 | 3181.68 | NORMAL
285.928 | 0.45 | 288.706 | 1.11 | 2 | 79289.74 | 14917.8781 | 13316.5035 | 2882.175 | NORMAL
285.928 | 0.45 | 288.706 | 1.11 | 2 | 101352.97 | 15082.3857 | 13736.2677 | 2727.11 | NORMAL
285.928 | 0.45 | 288.706 | 1.11 | 2 | 106868.78 | 15043.6694 | 13920.8551 | 2697.273 | NORMAL
285.928 | 0.45 | 288.706 | 1.42 | 1 | 57226.51 | 11463.1301 | 11457.3183 | 2210.67 | NORMAL
285.928 | 0.45 | 288.706 | 1.42 | 1 | 79289.74 | 11855.041 | 11848.995 | 2005.12 | NORMAL
285.928 | 0.45 | 288.706 | 1.42 | 1 | 101352.97 | 12079.1325 | 12072.9842 | 1891.39 | NORMAL
285.928 | 0.45 | 288.706 | 1.42 | 1 | 106868.78 | 12052.9601 | 12046.8613 | 1871.879 | NORMAL
285.928 | 0.45 | 288.706 | 1.42 | 2 | 57226.51 | 14917.0574 | 14311.9172 | 3213.08 | NORMAL
285.928 | 0.45 | 288.706 | 1.42 | 2 | 79289.74 | 15438.8628 | 14500.0873 | 2909.14 | NORMAL
285.928 | 0.45 | 288.706 | 1.42 | 2 | 101352.97 | 15681.3013 | 14777.4938 | 2750.296 | NORMAL
285.928 | 0.45 | 288.706 | 1.42 | 2 | 106868.78 | 15652.1395 | 14984.2471 | 2719.287 | NORMAL
285.928 | 0.45 | 291.483 | 0.5 | 1 | 57226.51 | 10679.8066 | 7800.7123 | 2196.642 | NORMAL
285.928 | 0.45 | 291.483 | 0.5 | 1 | 79289.74 | 10734.0563 | 8252.1707 | 2010.783 | NORMAL
285.928 | 0.45 | 291.483 | 0.5 | 1 | 101352.97 | 10697.8312 | 8514.5429 | 1915.154 | NORMAL
285.928 | 0.45 | 291.483 | 0.5 | 1 | 106868.78 | 10642.7022 | 8558.1055 | 1899.5752 | NORMAL
285.928 | 0.45 | 291.483 | 0.5 | 2 | 57226.51 | 13595.1348 | 9035.4626 | 3107.941 | NORMAL
285.928 | 0.45 | 291.483 | 0.5 | 2 | 79289.74 | 13514.3318 | 9687.4649 | 2810.365 | NORMAL
285.928 | 0.45 | 291.483 | 0.5 | 2 | 101352.97 | 13361.0199 | 10088.3584 | 2660.37 | NORMAL
285.928 | 0.45 | 291.483 | 0.5 | 2 | 106868.78 | 13281.1254 | 10137.9744 | 2632.7173 | NORMAL
285.928 | 0.45 | 291.483 | 0.8 | 1 | 57226.51 | 11598.388 | 10024.8695 | 2213.142 | NORMAL
285.928 | 0.45 | 291.483 | 0.8 | 1 | 79289.74 | 11831.7409 | 10247.1159 | 2005.256 | NORMAL
285.928 | 0.45 | 291.483 | 0.8 | 1 | 101352.97 | 11936.2251 | 10479.1223 | 1893.207 | NORMAL
285.928 | 0.45 | 291.483 | 0.8 | 1 | 106868.78 | 11896.5416 | 10617.0329 | 1874.326 | NORMAL
285.928 | 0.45 | 291.483 | 0.8 | 2 | 57226.51 | 14862.3388 | 11545.9714 | 3209.624 | NORMAL
285.928 | 0.45 | 291.483 | 0.8 | 2 | 79289.74 | 15131.6237 | 12251.3191 | 2893.143 | NORMAL
285.928 | 0.45 | 291.483 | 0.8 | 2 | 101352.97 | 15192.0868 | 12561.2275 | 2731.707 | NORMAL
285.928 | 0.45 | 291.483 | 0.8 | 2 | 106868.78 | 15130.041 | 12568.7974 | 2700.563 | NORMAL
285.928 | 0.45 | 291.483 | 1.11 | 1 | 57226.51 | 12041.0903 | 11727.8654 | 2222.17 | NORMAL
285.928 | 0.45 | 291.483 | 1.11 | 1 | 79289.74 | 12406.7116 | 11832.9384 | 2004.041 | NORMAL
285.928 | 0.45 | 291.483 | 1.11 | 1 | 101352.97 | 12596.3072 | 11991.7474 | 1883.106 | NORMAL
285.928 | 0.45 | 291.483 | 1.11 | 1 | 106868.78 | 12556.3013 | 12150.4942 | 1862.79 | NORMAL
285.928 | 0.45 | 291.483 | 1.11 | 2 | 57226.51 | 15615.2696 | 13330.2092 | 3271.36 | NORMAL
285.928 | 0.45 | 291.483 | 1.11 | 2 | 79289.74 | 16046.1313 | 13744.1854 | 2941.88 | NORMAL
285.928 | 0.45 | 291.483 | 1.11 | 2 | 101352.97 | 16140.5041 | 14172.444 | 2769.595 | NORMAL
285.928 | 0.45 | 291.483 | 1.11 | 2 | 106868.78 | 16111.3423 | 14358.9438 | 2738.132 | NORMAL
285.928 | 0.45 | 291.483 | 1.42 | 1 | 57226.51 | 12333.6753 | 12326.0654 | 2228.31 | NORMAL
285.928 | 0.45 | 291.483 | 1.42 | 1 | 79289.74 | 12771.3951 | 12763.4768 | 2002.49 | NORMAL
285.928 | 0.45 | 291.483 | 1.42 | 1 | 101352.97 | 13018.6694 | 13010.6108 | 1876.247 | NORMAL
285.928 | 0.45 | 291.483 | 1.42 | 1 | 106868.78 | 12994.3142 | 12986.3357 | 1855.467 | NORMAL
285.928 | 0.45 | 291.483 | 1.42 | 2 | 57226.51 | 16052.9601 | 14896.8581 | 3308.14 | NORMAL
285.928 | 0.45 | 291.483 | 1.42 | 2 | 79289.74 | 16612.8664 | 15173.5608 | 2971.25 | NORMAL
285.928 | 0.45 | 291.483 | 1.42 | 2 | 101352.97 | 16874.3845 | 15461.2223 | 2798.384 | NORMAL
285.928 | 0.45 | 291.483 | 1.42 | 2 | 106868.78 | 16842.2626 | 15700.2898 | 2766.395 | NORMAL
285.928 | 0.45 | 294.26 | 0.5 | 1 | 57226.51 | 11592.9074 | 8087.5484 | 2213.19 | NORMAL
285.928 | 0.45 | 294.26 | 0.5 | 1 | 79289.74 | 11621.8054 | 8543.8865 | 2006.548 | NORMAL
285.928 | 0.45 | 294.26 | 0.5 | 1 | 101352.97 | 11504.5135 | 8830.3584 | 1900.69 | NORMAL
285.928 | 0.45 | 294.26 | 0.5 | 1 | 106868.78 | 11443.347 | 8824.7316 | 1882.8038 | NORMAL
285.928 | 0.45 | 294.26 | 0.5 | 2 | 57226.51 | 14607.9426 | 9119.1396 | 3188.576 | NORMAL
285.928 | 0.45 | 294.26 | 0.5 | 2 | 79289.74 | 14538.8921 | 9926.385 | 2862.716 | NORMAL
285.928 | 0.45 | 294.26 | 0.5 | 2 | 101352.97 | 14359.9062 | 10420.9983 | 2698.164 | NORMAL
285.928 | 0.45 | 294.26 | 0.5 | 2 | 106868.78 | 14268.3177 | 10514.5659 | 2668.5381 | NORMAL
285.928 | 0.45 | 294.26 | 0.8 | 1 | 57226.51 | 12493.0246 | 10409.9627 | 2231.714 | NORMAL
285.928 | 0.45 | 294.26 | 0.8 | 1 | 79289.74 | 12760.1407 | 10711.9339 | 2003.011 | NORMAL
285.928 | 0.45 | 294.26 | 0.8 | 1 | 101352.97 | 12865.9144 | 10982.0358 | 1878.666 | NORMAL
285.928 | 0.45 | 294.26 | 0.8 | 1 | 106868.78 | 12812.6905 | 11138.0847 | 1859.191 | NORMAL
285.928 | 0.45 | 294.26 | 0.8 | 2 | 57226.51 | 16023.6518 | 11883.9734 | 3305.853 | NORMAL
285.928 | 0.45 | 294.26 | 0.8 | 2 | 79289.74 | 16306.8875 | 12485.2705 | 2955.987 | NORMAL
285.928 | 0.45 | 294.26 | 0.8 | 2 | 101352.97 | 16268.9625 | 12943.2124 | 2774.829 | NORMAL
285.928 | 0.45 | 294.26 | 0.8 | 2 | 106868.78 | 16193.7573 | 13096.6203 | 2741.242 | NORMAL
285.928 | 0.45 | 294.26 | 1.11 | 1 | 57226.51 | 12951.2896 | 12279.7652 | 2242.03 | NORMAL
285.928 | 0.45 | 294.26 | 1.11 | 1 | 79289.74 | 13347.8898 | 12370.5173 | 2001.282 | NORMAL
285.928 | 0.45 | 294.26 | 1.11 | 1 | 101352.97 | 13559.8769 | 12614.0484 | 1869.631 | NORMAL
285.928 | 0.45 | 294.26 | 1.11 | 1 | 106868.78 | 13511.6354 | 12786.8037 | 1846.057 | NORMAL
285.928 | 0.45 | 294.26 | 1.11 | 2 | 57226.51 | 16719.6366 | 13829.2963 | 3364.86 | NORMAL
285.928 | 0.45 | 294.26 | 1.11 | 2 | 79289.74 | 17215.7679 | 14296.2835 | 3005.715 | NORMAL
285.928 | 0.45 | 294.26 | 1.11 | 2 | 101352.97 | 17405.3927 | 14757.8236 | 2822.307 | NORMAL
285.928 | 0.45 | 294.26 | 1.11 | 2 | 106868.78 | 17344.4607 | 14974.3749 | 2786.259 | NORMAL
285.928 | 0.45 | 294.26 | 1.42 | 1 | 57226.51 | 13246.3951 | 13236.6325 | 2249.03 | NORMAL
285.928 | 0.45 | 294.26 | 1.42 | 1 | 79289.74 | 13730.3634 | 13720.1892 | 2000.94 | NORMAL
285.928 | 0.45 | 294.26 | 1.42 | 1 | 101352.97 | 14006.0375 | 13936.2034 | 1863.506 | NORMAL
285.928 | 0.45 | 294.26 | 1.42 | 1 | 106868.78 | 13972.0106 | 13961.7691 | 1840.196 | NORMAL
285.928 | 0.45 | 294.26 | 1.42 | 2 | 57226.51 | 17155.7444 | 15471.4621 | 3403.23 | NORMAL
285.928 | 0.45 | 294.26 | 1.42 | 2 | 79289.74 | 17794.9883 | 15827.4854 | 3038.24 | NORMAL
285.928 | 0.45 | 294.26 | 1.42 | 2 | 101352.97 | 18086.0785 | 16198.3441 | 2851.268 | NORMAL
285.928 | 0.45 | 294.26 | 1.42 | 2 | 106868.78 | 18042.1747 | 16452.5508 | 2814.427 | NORMAL
285.928 | 0.45 | 297.037 | 0.5 | 1 | 57226.51 | 12519.1383 | 8296.12 | 2232.31 | NORMAL
285.928 | 0.45 | 297.037 | 0.5 | 1 | 79289.74 | 12550.9086 | 8804.0105 | 2003.222 | NORMAL
285.928 | 0.45 | 297.037 | 0.5 | 1 | 101352.97 | 12472.3036 | 9162.1168 | 1885.073 | NORMAL
285.928 | 0.45 | 297.037 | 0.5 | 1 | 106868.78 | 12384.1149 | 9161.632 | 1865.9834 | NORMAL
285.928 | 0.45 | 297.037 | 0.5 | 2 | 57226.51 | 15781.9461 | 9295.1243 | 3283.922 | NORMAL
285.928 | 0.45 | 297.037 | 0.5 | 2 | 79289.74 | 15615.2989 | 10074.8503 | 2918.88 | NORMAL
285.928 | 0.45 | 297.037 | 0.5 | 2 | 101352.97 | 15428.2532 | 10670.0719 | 2740.09 | NORMAL
285.928 | 0.45 | 297.037 | 0.5 | 2 | 106868.78 | 15321.7761 | 10816.7602 | 2707.834 | NORMAL
285.928 | 0.45 | 297.037 | 0.8 | 1 | 57226.51 | 13430.7737 | 10819.4956 | 2253.374 | NORMAL
285.928 | 0.45 | 297.037 | 0.8 | 1 | 79289.74 | 13739.83 | 11127.3662 | 2002.002 | NORMAL
285.928 | 0.45 | 297.037 | 0.8 | 1 | 101352.97 | 13850.3224 | 11458.1224 | 1864.797 | NORMAL
285.928 | 0.45 | 297.037 | 0.8 | 1 | 106868.78 | 13783.4994 | 11631.3025 | 1841.758 | NORMAL
285.928 | 0.45 | 297.037 | 0.8 | 2 | 57226.51 | 17169.5487 | 12261.8564 | 3404.311 | NORMAL
285.928 | 0.45 | 297.037 | 0.8 | 2 | 79289.74 | 17501.1723 | 12898.0665 | 3021.626 | NORMAL
285.928 | 0.45 | 297.037 | 0.8 | 2 | 101352.97 | 17549.5018 | 13408.574 | 2828.856 | NORMAL
285.928 | 0.45 | 297.037 | 0.8 | 2 | 106868.78 | 17456.9168 | 13592.0078 | 2790.899 | NORMAL
285.928 | 0.45 | 297.037 | 1.11 | 1 | 57226.51 | 13894.8124 | 12789.2995 | 2264.94 | NORMAL
285.928 | 0.45 | 297.037 | 1.11 | 1 | 79289.74 | 14344.8417 | 12906.6279 | 2001.055 | NORMAL
285.928 | 0.45 | 297.037 | 1.11 | 1 | 101352.97 | 14572.6553 | 13179.3929 | 1855.732 | NORMAL
285.928 | 0.45 | 297.037 | 1.11 | 1 | 106868.78 | 14517.7315 | 13405.6443 | 1830.667 | NORMAL
285.928 | 0.45 | 297.037 | 1.11 | 2 | 57226.51 | 17858.5873 | 14355.9647 | 3466.13 | NORMAL
285.928 | 0.45 | 297.037 | 1.11 | 2 | 79289.74 | 18435.4631 | 14838.9623 | 3075.146 | NORMAL
285.928 | 0.45 | 297.037 | 1.11 | 2 | 101352.97 | 18650.9379 | 15312.1589 | 2876.119 | NORMAL
285.928 | 0.45 | 297.037 | 1.11 | 2 | 106868.78 | 18578.8687 | 15596.5144 | 2836.68 | NORMAL
285.928 | 0.45 | 297.037 | 1.42 | 1 | 57226.51 | 14200.1758 | 14187.8501 | 2273.17 | NORMAL
285.928 | 0.45 | 297.037 | 1.42 | 1 | 79289.74 | 14744.871 | 14476.9715 | 2002.5 | NORMAL
285.928 | 0.45 | 297.037 | 1.42 | 1 | 101352.97 | 15043.0832 | 14645.5698 | 1851.526 | NORMAL
285.928 | 0.45 | 297.037 | 1.42 | 1 | 106868.78 | 14992.5264 | 14846.1693 | 1823.818 | NORMAL
285.928 | 0.45 | 297.037 | 1.42 | 2 | 57226.51 | 18293.347 | 16126.5001 | 3505.92 | NORMAL
285.928 | 0.45 | 297.037 | 1.42 | 2 | 79289.74 | 19025.4396 | 16448.6341 | 3109.07 | NORMAL
285.928 | 0.45 | 297.037 | 1.42 | 2 | 101352.97 | 19356.8582 | 16910.1126 | 2907.127 | NORMAL
285.928 | 0.45 | 297.037 | 1.42 | 2 | 106868.78 | 19301.9343 | 17207.5394 | 2867.137 | NORMAL
285.928 | 0.45 | 299.814 | 0.5 | 1 | 57226.51 | 13486.1958 | 8519.3647 | 2254.743 | NORMAL
285.928 | 0.45 | 299.814 | 0.5 | 1 | 79289.74 | 13538.5991 | 9046.7627 | 2001.757 | NORMAL
285.928 | 0.45 | 299.814 | 0.5 | 1 | 101352.97 | 13445.0176 | 9442.772 | 1871.037 | NORMAL
285.928 | 0.45 | 299.814 | 0.5 | 1 | 106868.78 | 13342.2333 | 9432.5186 | 1848.7642 | NORMAL
285.928 | 0.45 | 299.814 | 0.5 | 2 | 57226.51 | 16959.7011 | 9344.1678 | 3385.263 | NORMAL
285.928 | 0.45 | 299.814 | 0.5 | 2 | 79289.74 | 16877.0223 | 10306.9325 | 2986.362 | NORMAL
285.928 | 0.45 | 299.814 | 0.5 | 2 | 101352.97 | 16634.3787 | 10955.801 | 2788.818 | NORMAL
285.928 | 0.45 | 299.814 | 0.5 | 2 | 106868.78 | 16448.7397 | 11091.8951 | 2750.8404 | NORMAL
285.928 | 0.45 | 299.814 | 0.8 | 1 | 57226.51 | 14412.6026 | 11225.6158 | 2278.795 | NORMAL
285.928 | 0.45 | 299.814 | 0.8 | 1 | 79289.74 | 14769.2556 | 11542.4538 | 2003.014 | NORMAL
285.928 | 0.45 | 299.814 | 0.8 | 1 | 101352.97 | 14887.4854 | 11898.6291 | 1851.823 | NORMAL
285.928 | 0.45 | 299.814 | 0.8 | 1 | 106868.78 | 14809.8476 | 12123.6671 | 1826.414 | NORMAL
285.928 | 0.45 | 299.814 | 0.8 | 2 | 57226.51 | 18346.5123 | 12649.2231 | 3510.801 | NORMAL
285.928 | 0.45 | 299.814 | 0.8 | 2 | 79289.74 | 18754.5428 | 13281.5171 | 3092.939 | NORMAL
285.928 | 0.45 | 299.814 | 0.8 | 2 | 101352.97 | 18816.8523 | 13885.087 | 2883.931 | NORMAL
285.928 | 0.45 | 299.814 | 0.8 | 2 | 106868.78 | 18710.17 | 13964.5412 | 2842.217 | NORMAL
285.928 | 0.45 | 299.814 | 1.11 | 1 | 57226.51 | 14878.517 | 13290.5626 | 2291.9 | NORMAL
285.928 | 0.45 | 299.814 | 1.11 | 1 | 79289.74 | 15395.1641 | 13461.0697 | 2004.121 | NORMAL
285.928 | 0.45 | 299.814 | 1.11 | 1 | 101352.97 | 15637.5146 | 13744.9375 | 1843.67 | NORMAL
285.928 | 0.45 | 299.814 | 1.11 | 1 | 106868.78 | 15573.2122 | 13992.4066 | 1816.102 | NORMAL
285.928 | 0.45 | 299.814 | 1.11 | 2 | 57226.51 | 19028.4584 | 14889.5403 | 3574.72 | NORMAL
285.928 | 0.45 | 299.814 | 1.11 | 2 | 79289.74 | 19703.4291 | 15341.7598 | 3149.767 | NORMAL
285.928 | 0.45 | 299.814 | 1.11 | 2 | 101352.97 | 19951.524 | 15900.6065 | 2934.693 | NORMAL
285.928 | 0.45 | 299.814 | 1.11 | 2 | 106868.78 | 19869.2849 | 16179.3997 | 2891.506 | NORMAL
285.928 | 0.45 | 299.814 | 1.42 | 1 | 57226.51 | 15178.7515 | 15034.4926 | 2300.8 | NORMAL
285.928 | 0.45 | 299.814 | 1.42 | 1 | 79289.74 | 15799.0328 | 15120.7172 | 2006.25 | NORMAL
285.928 | 0.45 | 299.814 | 1.42 | 1 | 101352.97 | 16119.0211 | 15287.1345 | 1839.27 | NORMAL
285.928 | 0.45 | 299.814 | 1.42 | 1 | 106868.78 | 16065.592 | 15578.3869 | 1809.761 | NORMAL
285.928 | 0.45 | 299.814 | 1.42 | 2 | 57226.51 | 19459.0856 | 16726.7965 | 3615.92 | NORMAL
285.928 | 0.45 | 299.814 | 1.42 | 2 | 79289.74 | 20299.6776 | 17039.3464 | 3185.38 | NORMAL
285.928 | 0.45 | 299.814 | 1.42 | 2 | 101352.97 | 20675.2638 | 17561.3623 | 2967.792 | NORMAL
285.928 | 0.45 | 299.814 | 1.42 | 2 | 106868.78 | 20611.5768 | 17906.3898 | 2923.931 | NORMAL
285.928 | 0.45 | 302.591 | 0.5 | 1 | 57226.51 | 14511.0199 | 8636.6834 | 2281.465 | NORMAL
285.928 | 0.45 | 302.591 | 0.5 | 1 | 79289.74 | 14588.9801 | 9255.0155 | 2002.191 | NORMAL
285.928 | 0.45 | 302.591 | 0.5 | 1 | 101352.97 | 14478.8394 | 9713.5927 | 1856.439 | NORMAL
285.928 | 0.45 | 302.591 | 0.5 | 1 | 106868.78 | 14364.5956 | 9692.2236 | 1832.9476 | NORMAL
285.928 | 0.45 | 302.591 | 0.5 | 2 | 57226.51 | 18191.5592 | 9306.1104 | 3496.067 | NORMAL
285.928 | 0.45 | 302.591 | 0.5 | 2 | 79289.74 | 18154.8652 | 10421.3465 | 3057.931 | NORMAL
285.928 | 0.45 | 302.591 | 0.5 | 2 | 101352.97 | 17885.1407 | 11147.057 | 2841.669 | NORMAL
285.928 | 0.45 | 302.591 | 0.5 | 2 | 106868.78 | 17730.6858 | 11377.1605 | 2801.8847 | NORMAL
285.928 | 0.45 | 302.591 | 0.8 | 1 | 57226.51 | 15442.3212 | 11644.2051 | 2308.627 | NORMAL
285.928 | 0.45 | 302.591 | 0.8 | 1 | 79289.74 | 15846.9519 | 11933.5472 | 2005.207 | NORMAL
285.928 | 0.45 | 302.591 | 0.8 | 1 | 101352.97 | 15990.1524 | 12359.0926 | 1841.784 | NORMAL
285.928 | 0.45 | 302.591 | 0.8 | 1 | 106868.78 | 15894.4021 | 12580.2603 | 1811.903 | NORMAL
285.928 | 0.45 | 302.591 | 0.8 | 2 | 57226.51 | 19565.1524 | 13046.0632 | 3626.194 | NORMAL
285.928 | 0.45 | 302.591 | 0.8 | 2 | 79289.74 | 20068.7573 | 13669.3925 | 3170.907 | NORMAL
285.928 | 0.45 | 302.591 | 0.8 | 2 | 101352.97 | 20146.3365 | 14321.8694 | 2941.045 | NORMAL
285.928 | 0.45 | 302.591 | 0.8 | 2 | 106868.78 | 20033.3529 | 14289.6904 | 2898.668 | NORMAL
285.928 | 0.45 | 302.591 | 1.11 | 1 | 57226.51 | 15916.4713 | 13858.949 | 2323.77 | NORMAL
285.928 | 0.45 | 302.591 | 1.11 | 1 | 79289.74 | 16492.4678 | 13957.5755 | 2009.258 | NORMAL
285.928 | 0.45 | 302.591 | 1.11 | 1 | 101352.97 | 16757.6202 | 14300.7855 | 1832.949 | NORMAL
285.928 | 0.45 | 302.591 | 1.11 | 1 | 106868.78 | 16682.5322 | 14588.5408 | 1802.513 | NORMAL
285.928 | 0.45 | 302.591 | 1.11 | 2 | 57226.51 | 20234.789 | 15372.956 | 3691.97 | NORMAL
285.928 | 0.45 | 302.591 | 1.11 | 2 | 79289.74 | 21017.1161 | 15865.7789 | 3228.652 | NORMAL
285.928 | 0.45 | 302.591 | 1.11 | 2 | 101352.97 | 21314.9765 | 16430.7989 | 2998.666 | NORMAL
285.928 | 0.45 | 302.591 | 1.11 | 2 | 106868.78 | 21222.0985 | 16741.2434 | 2951.406 | NORMAL
285.928 | 0.45 | 302.591 | 1.42 | 1 | 57226.51 | 16205.1583 | 15747.7353 | 2332.99 | NORMAL
285.928 | 0.45 | 302.591 | 1.42 | 1 | 79289.74 | 16894.109 | 15695.5058 | 2010.61 | NORMAL
285.928 | 0.45 | 302.591 | 1.42 | 1 | 101352.97 | 17251.9343 | 15945.7386 | 1829.464 | NORMAL
285.928 | 0.45 | 302.591 | 1.42 | 1 | 106868.78 | 17196.864 | 16295.3356 | 1799.392 | NORMAL
285.928 | 0.45 | 302.591 | 1.42 | 2 | 57226.51 | 20657.3564 | 17376.5964 | 3734.4 | NORMAL
285.928 | 0.45 | 302.591 | 1.42 | 2 | 79289.74 | 21623.007 | 17676.2244 | 3268.11 | NORMAL
285.928 | 0.45 | 302.591 | 1.42 | 2 | 101352.97 | 22050.8793 | 18238.0617 | 3033.725 | NORMAL
285.928 | 0.45 | 302.591 | 1.42 | 2 | 106868.78 | 21980.4513 | 18554.7321 | 2986.102 | NORMAL
285.928 | 0.45 | 305.368 | 0.5 | 1 | 57226.51 | 15594.6659 | 8667.5465 | 2313.535 | NORMAL
285.928 | 0.45 | 305.368 | 0.5 | 1 | 79289.74 | 15701.3189 | 9398.5112 | 2005.335 | NORMAL
285.928 | 0.45 | 305.368 | 0.5 | 1 | 101352.97 | 15585.0528 | 9915.5067 | 1844.013 | NORMAL
285.928 | 0.45 | 305.368 | 0.5 | 1 | 106868.78 | 15454.4842 | 9941.916 | 1817.682 | NORMAL
285.928 | 0.45 | 305.368 | 0.5 | 2 | 57226.51 | 19470.6331 | 9204.3913 | 3617.045 | NORMAL
285.928 | 0.45 | 305.368 | 0.5 | 2 | 79289.74 | 19506.7995 | 10478.5455 | 3136.584 | NORMAL
285.928 | 0.45 | 305.368 | 0.5 | 2 | 101352.97 | 19224.9121 | 11298.5577 | 2900.086 | NORMAL
285.928 | 0.45 | 305.368 | 0.5 | 2 | 106868.78 | 19050.1758 | 11574.6011 | 2856.4678 | NORMAL
285.928 | 0.45 | 305.368 | 0.8 | 1 | 57226.51 | 16522.8312 | 12061.7329 | 2343.824 | NORMAL
285.928 | 0.45 | 305.368 | 0.8 | 1 | 79289.74 | 16982.9133 | 12321.647 | 2011.032 | NORMAL
285.928 | 0.45 | 305.368 | 0.8 | 1 | 101352.97 | 17149.1501 | 12748.2494 | 1832.457 | NORMAL
285.928 | 0.45 | 305.368 | 0.8 | 1 | 106868.78 | 17037.2509 | 13004.9084 | 1798.548 | NORMAL
285.928 | 0.45 | 305.368 | 0.8 | 2 | 57226.51 | 20818.4349 | 13286.1586 | 3750.817 | NORMAL
285.928 | 0.45 | 305.368 | 0.8 | 2 | 79289.74 | 21440.0352 | 14057.1805 | 3255.731 | NORMAL
285.928 | 0.45 | 305.368 | 0.8 | 2 | 101352.97 | 21550.0879 | 14647.056 | 3006.528 | NORMAL
285.928 | 0.45 | 305.368 | 0.8 | 2 | 106868.78 | 21424.9121 | 14578.0244 | 2960.682 | NORMAL
285.928 | 0.45 | 305.368 | 1.11 | 1 | 57226.51 | 16973.388 | 14453.3152 | 2359.4 | NORMAL
285.928 | 0.45 | 305.368 | 1.11 | 1 | 79289.74 | 17630.2755 | 14479.7982 | 2015.844 | NORMAL
285.928 | 0.45 | 305.368 | 1.11 | 1 | 101352.97 | 17938.9215 | 14849.3548 | 1827.139 | NORMAL
285.928 | 0.45 | 305.368 | 1.11 | 1 | 106868.78 | 17856.3306 | 15145.2753 | 1793.542 | NORMAL
285.928 | 0.45 | 305.368 | 1.11 | 2 | 57226.51 | 21470.8968 | 15767.4752 | 3818.18 | NORMAL
285.928 | 0.45 | 305.368 | 1.11 | 2 | 79289.74 | 22387.0457 | 16377.3552 | 3316.013 | NORMAL
285.928 | 0.45 | 305.368 | 1.11 | 2 | 101352.97 | 22738.2474 | 16972.0097 | 3068.724 | NORMAL
285.928 | 0.45 | 305.368 | 1.11 | 2 | 106868.78 | 22636.1665 | 17271.5761 | 3017.087 | NORMAL
285.928 | 0.45 | 305.368 | 1.42 | 1 | 57226.51 | 17269.6659 | 16340.2125 | 2370.17 | NORMAL
285.928 | 0.45 | 305.368 | 1.42 | 1 | 79289.74 | 18041.6178 | 16344.4068 | 2018.98 | NORMAL
285.928 | 0.45 | 305.368 | 1.42 | 1 | 101352.97 | 18445.3107 | 16582.8323 | 1824.287 | NORMAL
285.928 | 0.45 | 305.368 | 1.42 | 1 | 106868.78 | 18374.7362 | 16989.961 | 1789.651 | NORMAL
285.928 | 0.45 | 305.368 | 1.42 | 2 | 57226.51 | 21882.0926 | 17949.9462 | 3861.73 | NORMAL
285.928 | 0.45 | 305.368 | 1.42 | 2 | 79289.74 | 22990.6213 | 18262.5771 | 3357.79 | NORMAL
285.928 | 0.45 | 305.368 | 1.42 | 2 | 101352.97 | 23482.3564 | 18873.803 | 3105.931 | NORMAL
285.928 | 0.45 | 305.368 | 1.42 | 2 | 106868.78 | 23404.8066 | 19227.4699 | 3053.936 | NORMAL
285.928 | 0.55 | 288.706 | 0.5 | 1 | 57226.51 | 10429.279 | 6682.8943 | 2192.408 | NORMAL
285.928 | 0.55 | 288.706 | 0.5 | 1 | 79289.74 | 10407.034 | 7251.767 | 2012.7 | NORMAL
285.928 | 0.55 | 288.706 | 0.5 | 1 | 101352.97 | 10323.3001 | 7611.5343 | 1921.889 | NORMAL
285.928 | 0.55 | 288.706 | 0.5 | 1 | 106868.78 | 10259.3787 | 7658.7082 | 1908.0294 | NORMAL
285.928 | 0.55 | 288.706 | 0.5 | 2 | 57226.51 | 13291.5299 | 7867.8812 | 3084.347 | NORMAL
285.928 | 0.55 | 288.706 | 0.5 | 2 | 79289.74 | 13123.7691 | 8640.6108 | 2790.778 | NORMAL
285.928 | 0.55 | 288.706 | 0.5 | 2 | 101352.97 | 12913.0715 | 9106.75 | 2643.135 | NORMAL
285.928 | 0.55 | 288.706 | 0.5 | 2 | 106868.78 | 12824.1501 | 9234.6192 | 2616.3549 | NORMAL
285.928 | 0.55 | 288.706 | 0.8 | 1 | 57226.51 | 11293.9332 | 8551.0547 | 2207.5 | NORMAL
285.928 | 0.55 | 288.706 | 0.8 | 1 | 79289.74 | 11448.0363 | 8930.6017 | 2006.745 | NORMAL
285.928 | 0.55 | 288.706 | 0.8 | 1 | 101352.97 | 11442.2333 | 9289.6517 | 1901.525 | NORMAL
285.928 | 0.55 | 288.706 | 0.8 | 1 | 106868.78 | 11401.9637 | 9385.1843 | 1883.889 | NORMAL
285.928 | 0.55 | 288.706 | 0.8 | 2 | 57226.51 | 14538.7456 | 9979.9038 | 3183.128 | NORMAL
285.928 | 0.55 | 288.706 | 0.8 | 2 | 79289.74 | 14699.2966 | 10669.1464 | 2871.001 | NORMAL
285.928 | 0.55 | 288.706 | 0.8 | 2 | 101352.97 | 14683.3529 | 11155.413 | 2711.544 | NORMAL
285.928 | 0.55 | 288.706 | 0.8 | 2 | 106868.78 | 14609.8183 | 11236.3382 | 2681.076 | NORMAL
285.928 | 0.55 | 288.706 | 1.11 | 1 | 57226.51 | 11721.2485 | 9900.4581 | 2215.69 | NORMAL
285.928 | 0.55 | 288.706 | 1.11 | 1 | 79289.74 | 11997.8898 | 10160.8329 | 2005.428 | NORMAL
285.928 | 0.55 | 288.706 | 1.11 | 1 | 101352.97 | 12119.2849 | 10447.9264 | 1890.993 | NORMAL
285.928 | 0.55 | 288.706 | 1.11 | 1 | 106868.78 | 12064.9472 | 10645.1322 | 1871.679 | NORMAL
285.928 | 0.55 | 288.706 | 1.11 | 2 | 57226.51 | 15230.1876 | 11531.2776 | 3239.22 | NORMAL
285.928 | 0.55 | 288.706 | 1.11 | 2 | 79289.74 | 15508.3236 | 12113.5825 | 2913.387 | NORMAL
285.928 | 0.55 | 288.706 | 1.11 | 2 | 101352.97 | 15614.8007 | 12595.3042 | 2748.413 | NORMAL
285.928 | 0.55 | 288.706 | 1.11 | 2 | 106868.78 | 15556.4771 | 12826.7354 | 2716.567 | NORMAL
285.928 | 0.55 | 288.706 | 1.42 | 1 | 57226.51 | 11991.2954 | 11076.0598 | 2221.06 | NORMAL
285.928 | 0.55 | 288.706 | 1.42 | 1 | 79289.74 | 12340.0645 | 11211.1337 | 2004.2 | NORMAL
285.928 | 0.55 | 288.706 | 1.42 | 1 | 101352.97 | 12519.5487 | 11432.8769 | 1884.206 | NORMAL
285.928 | 0.55 | 288.706 | 1.42 | 1 | 106868.78 | 12476.2896 | 11634.2523 | 1864.375 | NORMAL
285.928 | 0.55 | 288.706 | 1.42 | 2 | 57226.51 | 15661.9578 | 12707.1885 | 3274.68 | NORMAL
285.928 | 0.55 | 288.706 | 1.42 | 2 | 79289.74 | 16112.1923 | 13207.2768 | 2945.53 | NORMAL
285.928 | 0.55 | 288.706 | 1.42 | 2 | 101352.97 | 16191.2954 | 13753.8254 | 2774.054 | NORMAL
285.928 | 0.55 | 288.706 | 1.42 | 2 | 106868.78 | 16152.5205 | 13994.8184 | 2739.516 | NORMAL
285.928 | 0.55 | 291.483 | 0.5 | 1 | 57226.51 | 11358.8804 | 6869.4533 | 2208.684 | NORMAL
285.928 | 0.55 | 291.483 | 0.5 | 1 | 79289.74 | 11246.6588 | 7408.5116 | 2008.142 | NORMAL
285.928 | 0.55 | 291.483 | 0.5 | 1 | 101352.97 | 11169.4021 | 7846.9518 | 1906.531 | NORMAL
285.928 | 0.55 | 291.483 | 0.5 | 1 | 106868.78 | 11092.9953 | 7919.8995 | 1890.3454 | NORMAL
285.928 | 0.55 | 291.483 | 0.5 | 2 | 57226.51 | 14349.8242 | 7926.2976 | 3167.812 | NORMAL
285.928 | 0.55 | 291.483 | 0.5 | 2 | 79289.74 | 14186.694 | 8872.9117 | 2844.603 | NORMAL
285.928 | 0.55 | 291.483 | 0.5 | 2 | 101352.97 | 13946.5416 | 9429.7868 | 2682.369 | NORMAL
285.928 | 0.55 | 291.483 | 0.5 | 2 | 106868.78 | 13842.0574 | 9561.1935 | 2652.8814 | NORMAL
285.928 | 0.55 | 291.483 | 0.8 | 1 | 57226.51 | 12230.7737 | 8902.927 | 2226.024 | NORMAL
285.928 | 0.55 | 291.483 | 0.8 | 1 | 79289.74 | 12411.0492 | 9290.2909 | 2003.337 | NORMAL
285.928 | 0.55 | 291.483 | 0.8 | 1 | 101352.97 | 12459.1735 | 9676.5417 | 1885.928 | NORMAL
285.928 | 0.55 | 291.483 | 0.8 | 1 | 106868.78 | 12389.068 | 9821.5699 | 1866.12 | NORMAL
285.928 | 0.55 | 291.483 | 0.8 | 2 | 57226.51 | 15729.7773 | 10238.1188 | 3280.654 | NORMAL
285.928 | 0.55 | 291.483 | 0.8 | 2 | 79289.74 | 15803.136 | 10974.6616 | 2929.035 | NORMAL
285.928 | 0.55 | 291.483 | 0.8 | 2 | 101352.97 | 15811.9285 | 11524.8877 | 2756.661 | NORMAL
285.928 | 0.55 | 291.483 | 0.8 | 2 | 106868.78 | 15723.6811 | 11534.295 | 2722.971 | NORMAL
285.928 | 0.55 | 291.483 | 1.11 | 1 | 57226.51 | 12666.061 | 10351.769 | 2235.47 | NORMAL
285.928 | 0.55 | 291.483 | 1.11 | 1 | 79289.74 | 12975.4689 | 10600.1926 | 2002.13 | NORMAL
285.928 | 0.55 | 291.483 | 1.11 | 1 | 101352.97 | 13116.442 | 10941.1194 | 1875.734 | NORMAL
285.928 | 0.55 | 291.483 | 1.11 | 1 | 106868.78 | 13058.3236 | 11175.3655 | 1854.221 | NORMAL
285.928 | 0.55 | 291.483 | 1.11 | 2 | 57226.51 | 16398.857 | 11967.6234 | 3337.43 | NORMAL
285.928 | 0.55 | 291.483 | 1.11 | 2 | 79289.74 | 16775.3517 | 12536.9417 | 2981.821 | NORMAL
285.928 | 0.55 | 291.483 | 1.11 | 2 | 101352.97 | 16877.7843 | 13080.536 | 2800.222 | NORMAL
285.928 | 0.55 | 291.483 | 1.11 | 2 | 106868.78 | 16808.5873 | 13315.225 | 2765.08 | NORMAL
285.928 | 0.55 | 291.483 | 1.42 | 1 | 57226.51 | 12941.2661 | 11561.2354 | 2241.66 | NORMAL
285.928 | 0.55 | 291.483 | 1.42 | 1 | 79289.74 | 13338.5111 | 11779.3859 | 2002.14 | NORMAL
285.928 | 0.55 | 291.483 | 1.42 | 1 | 101352.97 | 13536.1958 | 12051.3834 | 1869.792 | NORMAL
285.928 | 0.55 | 291.483 | 1.42 | 1 | 106868.78 | 13486.2251 | 12288.1223 | 1847.201 | NORMAL
285.928 | 0.55 | 291.483 | 1.42 | 2 | 57226.51 | 16815.1817 | 13233.4808 | 3373.51 | NORMAL
285.928 | 0.55 | 291.483 | 1.42 | 2 | 79289.74 | 17330.5393 | 13737.4679 | 3012.35 | NORMAL
285.928 | 0.55 | 291.483 | 1.42 | 2 | 101352.97 | 17534.32 | 14261.0482 | 2827.634 | NORMAL
285.928 | 0.55 | 291.483 | 1.42 | 2 | 106868.78 | 17467.5264 | 14541.9603 | 2789.632 | NORMAL
285.928 | 0.55 | 294.26 | 0.5 | 1 | 57226.51 | 12324.8828 | 6946.7476 | 2228.189 | NORMAL
285.928 | 0.55 | 294.26 | 0.5 | 1 | 79289.74 | 12269.9003 | 7645.1172 | 2004.239 | NORMAL
285.928 | 0.55 | 294.26 | 0.5 | 1 | 101352.97 | 12136.1079 | 8102.2719 | 1890.385 | NORMAL
285.928 | 0.55 | 294.26 | 0.5 | 1 | 106868.78 | 12036.9578 | 8177.7888 | 1871.8165 | NORMAL
285.928 | 0.55 | 294.26 | 0.5 | 2 | 57226.51 | 15552.7843 | 7960.1327 | 3265.934 | NORMAL
285.928 | 0.55 | 294.26 | 0.5 | 2 | 79289.74 | 15316.2954 | 8994.4792 | 2903.266 | NORMAL
285.928 | 0.55 | 294.26 | 0.5 | 2 | 101352.97 | 15052.1688 | 9678.6198 | 2725.323 | NORMAL
285.928 | 0.55 | 294.26 | 0.5 | 2 | 106868.78 | 14930.2755 | 9820.5231 | 2692.9863 | NORMAL
285.928 | 0.55 | 294.26 | 0.8 | 1 | 57226.51 | 13211.9871 | 9259.238 | 2248.061 | NORMAL
285.928 | 0.55 | 294.26 | 0.8 | 1 | 79289.74 | 13427.4033 | 9650.221 | 2002.071 | NORMAL
285.928 | 0.55 | 294.26 | 0.8 | 1 | 101352.97 | 13471.9812 | 10054.0588 | 1869.866 | NORMAL
285.928 | 0.55 | 294.26 | 0.8 | 1 | 106868.78 | 13395.4572 | 10159.9587 | 1848.836 | NORMAL
285.928 | 0.55 | 294.26 | 0.8 | 2 | 57226.51 | 16915.2696 | 10473.4613 | 3382.178 | NORMAL
285.928 | 0.55 | 294.26 | 0.8 | 2 | 79289.74 | 17137.6026 | 11285.6254 | 3001.43 | NORMAL
285.928 | 0.55 | 294.26 | 0.8 | 2 | 101352.97 | 17100.7327 | 11888.5662 | 2809.223 | NORMAL
285.928 | 0.55 | 294.26 | 0.8 | 2 | 106868.78 | 16990.8265 | 11884.6414 | 2772.185 | NORMAL
285.928 | 0.55 | 294.26 | 1.11 | 1 | 57226.51 | 13653.6635 | 10812.3362 | 2258.81 | NORMAL
285.928 | 0.55 | 294.26 | 1.11 | 1 | 79289.74 | 14010.1993 | 11063.35 | 2001.257 | NORMAL
285.928 | 0.55 | 294.26 | 1.11 | 1 | 101352.97 | 14167.2919 | 11429.8169 | 1862.022 | NORMAL
285.928 | 0.55 | 294.26 | 1.11 | 1 | 106868.78 | 14098.5639 | 11680.6461 | 1837.896 | NORMAL
285.928 | 0.55 | 294.26 | 1.11 | 2 | 57226.51 | 17588.3353 | 12356.5091 | 3441.86 | NORMAL
285.928 | 0.55 | 294.26 | 1.11 | 2 | 79289.74 | 18043.0246 | 12990.7432 | 3052.739 | NORMAL
285.928 | 0.55 | 294.26 | 1.11 | 2 | 101352.97 | 18169.0211 | 13551.5461 | 2854.997 | NORMAL
285.928 | 0.55 | 294.26 | 1.11 | 2 | 106868.78 | 18080.0117 | 13816.5822 | 2815.936 | NORMAL
285.928 | 0.55 | 294.26 | 1.42 | 1 | 57226.51 | 13932.5322 | 12046.7779 | 2265.8 | NORMAL
285.928 | 0.55 | 294.26 | 1.42 | 1 | 79289.74 | 14382.9132 | 12205.5703 | 2001.31 | NORMAL
285.928 | 0.55 | 294.26 | 1.42 | 1 | 101352.97 | 14606.3306 | 12604.2409 | 1856.501 | NORMAL
285.928 | 0.55 | 294.26 | 1.42 | 1 | 106868.78 | 14547.4209 | 12892.1571 | 1831.347 | NORMAL
285.928 | 0.55 | 294.26 | 1.42 | 2 | 57226.51 | 18002.7257 | 13765.8202 | 3479.43 | NORMAL
285.928 | 0.55 | 294.26 | 1.42 | 2 | 79289.74 | 18610.6096 | 14263.9715 | 3085.11 | NORMAL
285.928 | 0.55 | 294.26 | 1.42 | 2 | 101352.97 | 18847.6846 | 14840.0261 | 2884.515 | NORMAL
285.928 | 0.55 | 294.26 | 1.42 | 2 | 106868.78 | 18770.252 | 15116.5286 | 2842.339 | NORMAL
285.928 | 0.55 | 297.037 | 0.5 | 1 | 57226.51 | 13343.9918 | 6958.7182 | 2251.42 | NORMAL
285.928 | 0.55 | 297.037 | 0.5 | 1 | 79289.74 | 13302.7843 | 7752.9292 | 2002.299 | NORMAL
285.928 | 0.55 | 297.037 | 0.5 | 1 | 101352.97 | 13149.8828 | 8282.4142 | 1875.192 | NORMAL
285.928 | 0.55 | 297.037 | 0.5 | 1 | 106868.78 | 13039.3318 | 8413.9027 | 1854.7139 | NORMAL
285.928 | 0.55 | 297.037 | 0.5 | 2 | 57226.51 | 16792.3505 | 7962.6304 | 3371.333 | NORMAL
285.928 | 0.55 | 297.037 | 0.5 | 2 | 79289.74 | 16614.1852 | 9137.3367 | 2972.168 | NORMAL
285.928 | 0.55 | 297.037 | 0.5 | 2 | 101352.97 | 16212.5146 | 9886.667 | 2773.711 | NORMAL
285.928 | 0.55 | 297.037 | 0.5 | 2 | 106868.78 | 16092.7902 | 10031.3603 | 2737.1956 | NORMAL
285.928 | 0.55 | 297.037 | 0.8 | 1 | 57226.51 | 14246.2192 | 9544.5537 | 2274.22 | NORMAL
285.928 | 0.55 | 297.037 | 0.8 | 1 | 79289.74 | 14505.3341 | 10004.3144 | 2002.411 | NORMAL
285.928 | 0.55 | 297.037 | 0.8 | 1 | 101352.97 | 14554.66 | 10428.2975 | 1855.794 | NORMAL
285.928 | 0.55 | 297.037 | 0.8 | 1 | 106868.78 | 14465.8851 | 10462.1332 | 1832.817 | NORMAL
285.928 | 0.55 | 297.037 | 0.8 | 2 | 57226.51 | 18153.7222 | 10592.0252 | 3493.141 | NORMAL
285.928 | 0.55 | 297.037 | 0.8 | 2 | 79289.74 | 18452.9015 | 11513.5218 | 3075.563 | NORMAL
285.928 | 0.55 | 297.037 | 0.8 | 2 | 101352.97 | 18424.3552 | 12154.6577 | 2865.7 | NORMAL
285.928 | 0.55 | 297.037 | 0.8 | 2 | 106868.78 | 18301.5827 | 12197.895 | 2825.108 | NORMAL
285.928 | 0.55 | 297.037 | 1.11 | 1 | 57226.51 | 14696.1313 | 11217.3954 | 2286.84 | NORMAL
285.928 | 0.55 | 297.037 | 1.11 | 1 | 79289.74 | 15103.6928 | 11513.7414 | 2002.205 | NORMAL
285.928 | 0.55 | 297.037 | 1.11 | 1 | 101352.97 | 15276.0551 | 11887.765 | 1847.693 | NORMAL
285.928 | 0.55 | 297.037 | 1.11 | 1 | 106868.78 | 15201.0551 | 12163.3979 | 1822.697 | NORMAL
285.928 | 0.55 | 297.037 | 1.11 | 2 | 57226.51 | 18821.483 | 12725.4682 | 3555.23 | NORMAL
285.928 | 0.55 | 297.037 | 1.11 | 2 | 79289.74 | 19374.3552 | 13416.2954 | 3130.254 | NORMAL
285.928 | 0.55 | 297.037 | 1.11 | 2 | 101352.97 | 19529.3963 | 14032.8672 | 2915.382 | NORMAL
285.928 | 0.55 | 297.037 | 1.11 | 2 | 106868.78 | 19428.2825 | 14303.5096 | 2872.331 | NORMAL
285.928 | 0.55 | 297.037 | 1.42 | 1 | 57226.51 | 14977.5498 | 12629.0251 | 2295 | NORMAL
285.928 | 0.55 | 297.037 | 1.42 | 1 | 79289.74 | 15485.6682 | 12756.1024 | 2003.5 | NORMAL
285.928 | 0.55 | 297.037 | 1.42 | 1 | 101352.97 | 15737.075 | 13139.3088 | 1844.724 | NORMAL
285.928 | 0.55 | 297.037 | 1.42 | 1 | 106868.78 | 15668.9039 | 13461.9388 | 1816.79 | NORMAL
285.928 | 0.55 | 297.037 | 1.42 | 2 | 57226.51 | 19230.4513 | 14267.0334 | 3594.19 | NORMAL
285.928 | 0.55 | 297.037 | 1.42 | 2 | 79289.74 | 19949.0035 | 14786.2014 | 3164.35 | NORMAL
285.928 | 0.55 | 297.037 | 1.42 | 2 | 101352.97 | 20227.0223 | 15377.2296 | 2946.936 | NORMAL
285.928 | 0.55 | 297.037 | 1.42 | 2 | 106868.78 | 20142.4091 | 15722.7214 | 2903.107 | NORMAL
285.928 | 0.55 | 299.814 | 0.5 | 1 | 57226.51 | 14418.1418 | 6897.4516 | 2278.868 | NORMAL
285.928 | 0.55 | 299.814 | 0.5 | 1 | 79289.74 | 14398.5639 | 7828.4272 | 2002.265 | NORMAL
285.928 | 0.55 | 299.814 | 0.5 | 1 | 101352.97 | 14228.8101 | 8436.105 | 1860.805 | NORMAL
285.928 | 0.55 | 299.814 | 0.5 | 1 | 106868.78 | 14101.8171 | 8620.9485 | 1838.1126 | NORMAL
285.928 | 0.55 | 299.814 | 0.5 | 2 | 57226.51 | 18082.1219 | 7937.0389 | 3486.329 | NORMAL
285.928 | 0.55 | 299.814 | 0.5 | 2 | 79289.74 | 17950.0879 | 9234.692 | 3046.418 | NORMAL
285.928 | 0.55 | 299.814 | 0.5 | 2 | 101352.97 | 17595.8675 | 10062.8655 | 2829.681 | NORMAL
285.928 | 0.55 | 299.814 | 0.5 | 2 | 106868.78 | 17423.857 | 10248.2422 | 2789.3473 | NORMAL
285.928 | 0.55 | 299.814 | 0.8 | 1 | 57226.51 | 15318.6987 | 9731.3106 | 2304.817 | NORMAL
285.928 | 0.55 | 299.814 | 0.8 | 1 | 79289.74 | 15636.4009 | 10316.3188 | 2005.348 | NORMAL
285.928 | 0.55 | 299.814 | 0.8 | 1 | 101352.97 | 15699.9414 | 10781.9504 | 1844.507 | NORMAL
285.928 | 0.55 | 299.814 | 0.8 | 1 | 106868.78 | 15591.0903 | 10713.4644 | 1815.968 | NORMAL
285.928 | 0.55 | 299.814 | 0.8 | 2 | 57226.51 | 19432.1512 | 10607.9919 | 3613.43 | NORMAL
285.928 | 0.55 | 299.814 | 0.8 | 2 | 79289.74 | 19826.4947 | 11623.6989 | 3156.168 | NORMAL
285.928 | 0.55 | 299.814 | 0.8 | 2 | 101352.97 | 19814.5662 | 12346.8327 | 2925.757 | NORMAL
285.928 | 0.55 | 299.814 | 0.8 | 2 | 106868.78 | 19679.9531 | 12478.8418 | 2883.147 | NORMAL
285.928 | 0.55 | 299.814 | 1.11 | 1 | 57226.51 | 15771.9519 | 11584.6564 | 2319.16 | NORMAL
285.928 | 0.55 | 299.814 | 1.11 | 1 | 79289.74 | 16246.7761 | 11944.9385 | 2006.134 | NORMAL
285.928 | 0.55 | 299.814 | 1.11 | 1 | 101352.97 | 16443.4642 | 12379.4785 | 1836.025 | NORMAL
285.928 | 0.55 | 299.814 | 1.11 | 1 | 106868.78 | 16353.4584 | 12649.858 | 1806.699 | NORMAL
285.928 | 0.55 | 299.814 | 1.11 | 2 | 57226.51 | 20076.7292 | 13072.9221 | 3676.35 | NORMAL
285.928 | 0.55 | 299.814 | 1.11 | 2 | 79289.74 | 20756.3013 | 13765.8489 | 3214.316 | NORMAL
285.928 | 0.55 | 299.814 | 1.11 | 2 | 101352.97 | 20951.231 | 14518.784 | 2981.235 | NORMAL
285.928 | 0.55 | 299.814 | 1.11 | 2 | 106868.78 | 20838.9508 | 14619.8368 | 2933.875 | NORMAL
285.928 | 0.55 | 299.814 | 1.42 | 1 | 57226.51 | 16054.1911 | 13133.8374 | 2328.27 | NORMAL
285.928 | 0.55 | 299.814 | 1.42 | 1 | 79289.74 | 16635.4045 | 13253.3269 | 2008.48 | NORMAL
285.928 | 0.55 | 299.814 | 1.42 | 1 | 101352.97 | 16914.1852 | 13690.8828 | 1832.307 | NORMAL
285.928 | 0.55 | 299.814 | 1.42 | 1 | 106868.78 | 16836.9871 | 13992.6307 | 1801.358 | NORMAL
285.928 | 0.55 | 299.814 | 1.42 | 2 | 57226.51 | 20484.9355 | 14688.6616 | 3717.46 | NORMAL
285.928 | 0.55 | 299.814 | 1.42 | 2 | 79289.74 | 21333.4408 | 15265.2502 | 3250.12 | NORMAL
285.928 | 0.55 | 299.814 | 1.42 | 2 | 101352.97 | 21663.5111 | 15949.0452 | 3014.892 | NORMAL
285.928 | 0.55 | 299.814 | 1.42 | 2 | 106868.78 | 21569.6073 | 16287.2105 | 2966.794 | NORMAL
285.928 | 0.55 | 302.591 | 0.5 | 1 | 57226.51 | 15540.4748 | 6760.1842 | 2312.04 | NORMAL
285.928 | 0.55 | 302.591 | 0.5 | 1 | 79289.74 | 15564.8007 | 7837.4531 | 2005.251 | NORMAL
285.928 | 0.55 | 302.591 | 0.5 | 1 | 101352.97 | 15384.7304 | 8541.5715 | 1847.636 | NORMAL
285.928 | 0.55 | 302.591 | 0.5 | 1 | 106868.78 | 15239.8007 | 8806.5932 | 1822.326 | NORMAL
285.928 | 0.55 | 302.591 | 0.5 | 2 | 57226.51 | 19425.0293 | 7873.4694 | 3612.398 | NORMAL
285.928 | 0.55 | 302.591 | 0.5 | 2 | 79289.74 | 19369.6659 | 9290.8539 | 3128.635 | NORMAL
285.928 | 0.55 | 302.591 | 0.5 | 2 | 101352.97 | 18996.864 | 10202.2848 | 2890.326 | NORMAL
285.928 | 0.55 | 302.591 | 0.5 | 2 | 106868.78 | 18801.6999 | 10407.1169 | 2845.7803 | NORMAL
285.928 | 0.55 | 302.591 | 0.8 | 1 | 57226.51 | 16446.3365 | 9771.9526 | 2341.262 | NORMAL
285.928 | 0.55 | 302.591 | 0.8 | 1 | 79289.74 | 16827.2567 | 10571.0341 | 2011.569 | NORMAL
285.928 | 0.55 | 302.591 | 0.8 | 1 | 101352.97 | 16909.4666 | 10999.1346 | 1833.916 | NORMAL
285.928 | 0.55 | 302.591 | 0.8 | 1 | 106868.78 | 16787.1336 | 10916.5891 | 1801.631 | NORMAL
285.928 | 0.55 | 302.591 | 0.8 | 2 | 57226.51 | 20736.4889 | 10530.2586 | 3743.367 | NORMAL
285.928 | 0.55 | 302.591 | 0.8 | 2 | 79289.74 | 21264.3611 | 11668.4141 | 3244.754 | NORMAL
285.928 | 0.55 | 302.591 | 0.8 | 2 | 101352.97 | 21284.4959 | 12459.9439 | 2993.781 | NORMAL
285.928 | 0.55 | 302.591 | 0.8 | 2 | 106868.78 | 21135.7855 | 12742.2367 | 2947.137 | NORMAL
285.928 | 0.55 | 302.591 | 1.11 | 1 | 57226.51 | 16890.7679 | 12049.5022 | 2356.75 | NORMAL
285.928 | 0.55 | 302.591 | 1.11 | 1 | 79289.74 | 17450.5275 | 12271.5949 | 2015.734 | NORMAL
285.928 | 0.55 | 302.591 | 1.11 | 1 | 101352.97 | 17671.1606 | 12816.3096 | 1826.489 | NORMAL
285.928 | 0.55 | 302.591 | 1.11 | 1 | 106868.78 | 17570.721 | 13162.8069 | 1793.662 | NORMAL
285.928 | 0.55 | 302.591 | 1.11 | 2 | 57226.51 | 21370.9555 | 13549.1858 | 3808.07 | NORMAL
285.928 | 0.55 | 302.591 | 1.11 | 2 | 79289.74 | 22194.7538 | 14130.2678 | 3306.125 | NORMAL
285.928 | 0.55 | 302.591 | 1.11 | 2 | 101352.97 | 22443.1418 | 14888.8925 | 3053.898 | NORMAL
285.928 | 0.55 | 302.591 | 1.11 | 2 | 106868.78 | 22319.4314 | 14879.9632 | 3001.612 | NORMAL
285.928 | 0.55 | 302.591 | 1.42 | 1 | 57226.51 | 17162.5147 | 13579.4965 | 2366.11 | NORMAL
285.928 | 0.55 | 302.591 | 1.42 | 1 | 79289.74 | 17837.544 | 13773.4915 | 2017.1 | NORMAL
285.928 | 0.55 | 302.591 | 1.42 | 1 | 101352.97 | 18153.1653 | 14207.0302 | 1823.581 | NORMAL
285.928 | 0.55 | 302.591 | 1.42 | 1 | 106868.78 | 18066.2368 | 14555.8044 | 1789.064 | NORMAL
285.928 | 0.55 | 302.591 | 1.42 | 2 | 57226.51 | 21769.0504 | 15210.8845 | 3850.62 | NORMAL
285.928 | 0.55 | 302.591 | 1.42 | 2 | 79289.74 | 22768.8746 | 15679.1252 | 3343.46 | NORMAL
285.928 | 0.55 | 302.591 | 1.42 | 2 | 101352.97 | 23163.1888 | 16442.4359 | 3089.551 | NORMAL
285.928 | 0.55 | 302.591 | 1.42 | 2 | 106868.78 | 23061.782 | 16886.2288 | 3036.691 | NORMAL
285.928 | 0.55 | 305.368 | 0.5 | 1 | 57226.51 | 16713.1888 | 6539.5198 | 2350.86 | NORMAL
285.928 | 0.55 | 305.368 | 0.5 | 1 | 79289.74 | 16799.0621 | 7786.4325 | 2011.33 | NORMAL
285.928 | 0.55 | 305.368 | 0.5 | 1 | 101352.97 | 16617.3212 | 8600.9925 | 1836.034 | NORMAL
285.928 | 0.55 | 305.368 | 0.5 | 1 | 106868.78 | 16454.4549 | 8885.2082 | 1807.868 | NORMAL
285.928 | 0.55 | 305.368 | 0.5 | 2 | 57226.51 | 20807.7374 | 7794.1623 | 3751.183 | NORMAL
285.928 | 0.55 | 305.368 | 0.5 | 2 | 79289.74 | 20867.0867 | 9320.952 | 3219.779 | NORMAL
285.928 | 0.55 | 305.368 | 0.5 | 2 | 101352.97 | 20490.7972 | 10316.2558 | 2958.179 | NORMAL
285.928 | 0.55 | 305.368 | 0.5 | 2 | 106868.78 | 20272.4795 | 10531.3301 | 2908.728 | NORMAL
285.928 | 0.55 | 305.368 | 0.8 | 1 | 57226.51 | 17609.4959 | 9800.3184 | 2382.979 | NORMAL
285.928 | 0.55 | 305.368 | 0.8 | 1 | 79289.74 | 18077.9308 | 10743.4612 | 2021.264 | NORMAL
285.928 | 0.55 | 305.368 | 0.8 | 1 | 101352.97 | 18184.9062 | 11238.6721 | 1826.08 | NORMAL
285.928 | 0.55 | 305.368 | 0.8 | 1 | 106868.78 | 18047.0105 | 11092.1619 | 1788.92 | NORMAL
285.928 | 0.55 | 305.368 | 0.8 | 2 | 57226.51 | 22080.8324 | 10294.3049 | 3883.86 | NORMAL
285.928 | 0.55 | 305.368 | 0.8 | 2 | 79289.74 | 22759.8183 | 11626.7394 | 3341.363 | NORMAL
285.928 | 0.55 | 305.368 | 0.8 | 2 | 101352.97 | 22827.7257 | 12511.671 | 3068.788 | NORMAL
285.928 | 0.55 | 305.368 | 0.8 | 2 | 106868.78 | 22666.442 | 13001.7204 | 3018.558 | NORMAL
285.928 | 0.55 | 305.368 | 1.11 | 1 | 57226.51 | 18037.3095 | 12486.111 | 2399.08 | NORMAL
285.928 | 0.55 | 305.368 | 1.11 | 1 | 79289.74 | 18704.1618 | 12686.0042 | 2027.397 | NORMAL
285.928 | 0.55 | 305.368 | 1.11 | 1 | 101352.97 | 18956.8875 | 13216.8746 | 1818.372 | NORMAL
285.928 | 0.55 | 305.368 | 1.11 | 1 | 106868.78 | 18846.0141 | 13586.28 | 1782.213 | NORMAL
285.928 | 0.55 | 305.368 | 1.11 | 2 | 57226.51 | 22688.4525 | 13809.7577 | 3949.73 | NORMAL
285.928 | 0.55 | 305.368 | 1.11 | 2 | 79289.74 | 23685.0235 | 14535.7594 | 3406.477 | NORMAL
285.928 | 0.55 | 305.368 | 1.11 | 2 | 101352.97 | 23999.2673 | 15270.9498 | 3134.089 | NORMAL
285.928 | 0.55 | 305.368 | 1.11 | 2 | 106868.78 | 23867.1161 | 15125.4745 | 3076.024 | NORMAL
285.928 | 0.55 | 305.368 | 1.42 | 1 | 57226.51 | 18313.7163 | 14189.7787 | 2410.01 | NORMAL
285.928 | 0.55 | 305.368 | 1.42 | 1 | 79289.74 | 19091.5006 | 14247.8533 | 2028.9 | NORMAL
285.928 | 0.55 | 305.368 | 1.42 | 1 | 101352.97 | 19446.3365 | 14753.8966 | 1816.609 | NORMAL
285.928 | 0.55 | 305.368 | 1.42 | 1 | 106868.78 | 19346.4244 | 15149.3337 | 1778.961 | NORMAL
285.928 | 0.55 | 305.368 | 1.42 | 2 | 57226.51 | 23075.1172 | 15780.1958 | 3989.16 | NORMAL
285.928 | 0.55 | 305.368 | 1.42 | 2 | 79289.74 | 24253.3705 | 16127.5212 | 3440.87 | NORMAL
285.928 | 0.55 | 305.368 | 1.42 | 2 | 101352.97 | 24723.4467 | 16900.7503 | 3171.691 | NORMAL
285.928 | 0.55 | 305.368 | 1.42 | 2 | 106868.78 | 24616.061 | 17347.3074 | 3113.357 | NORMAL
285.928 | 0.65 | 288.706 | 0.5 | 1 | 57226.51 | 10976.905 | 5831.5796 | 2201.826 | NORMAL
285.928 | 0.65 | 288.706 | 0.5 | 1 | 79289.74 | 10862.2509 | 6544.5062 | 2010.023 | NORMAL
285.928 | 0.65 | 288.706 | 0.5 | 1 | 101352.97 | 10724.2966 | 7036.0287 | 1914.602 | NORMAL
285.928 | 0.65 | 288.706 | 0.5 | 1 | 106868.78 | 10644.0504 | 7125.4467 | 1899.5177 | NORMAL
285.928 | 0.65 | 288.706 | 0.5 | 2 | 57226.51 | 13937.8957 | 7187.2013 | 3135.011 | NORMAL
285.928 | 0.65 | 288.706 | 0.5 | 2 | 79289.74 | 13698.0657 | 8054.942 | 2819.673 | NORMAL
285.928 | 0.65 | 288.706 | 0.5 | 2 | 101352.97 | 13413.1008 | 8601.285 | 2662.367 | NORMAL
285.928 | 0.65 | 288.706 | 0.5 | 2 | 106868.78 | 13304.2497 | 8729.8894 | 2633.5641 | NORMAL
285.928 | 0.65 | 288.706 | 0.8 | 1 | 57226.51 | 11842.0574 | 7455.2738 | 2218.215 | NORMAL
285.928 | 0.65 | 288.706 | 0.8 | 1 | 79289.74 | 11948.3294 | 8042.8746 | 2005.254 | NORMAL
285.928 | 0.65 | 288.706 | 0.8 | 1 | 101352.97 | 11937.9836 | 8472.0766 | 1893.62 | NORMAL
285.928 | 0.65 | 288.706 | 0.8 | 1 | 106868.78 | 11873.388 | 8483.2627 | 1874.949 | NORMAL
285.928 | 0.65 | 288.706 | 0.8 | 2 | 57226.51 | 15252.2274 | 8424.339 | 3241.053 | NORMAL
285.928 | 0.65 | 288.706 | 0.8 | 2 | 79289.74 | 15287.0457 | 9373.9094 | 2901.695 | NORMAL
285.928 | 0.65 | 288.706 | 0.8 | 2 | 101352.97 | 15213.8042 | 10088.9734 | 2732.315 | NORMAL
285.928 | 0.65 | 288.706 | 0.8 | 2 | 106868.78 | 15120.1055 | 10313.0157 | 2700.093 | NORMAL
285.928 | 0.65 | 288.706 | 1.11 | 1 | 57226.51 | 12258.7339 | 8760.1157 | 2226.86 | NORMAL
285.928 | 0.65 | 288.706 | 1.11 | 1 | 79289.74 | 12487.6026 | 9113.5772 | 2003.487 | NORMAL
285.928 | 0.65 | 288.706 | 1.11 | 1 | 101352.97 | 12565.9144 | 9530.8565 | 1883.486 | NORMAL
285.928 | 0.65 | 288.706 | 1.11 | 1 | 106868.78 | 12499.3845 | 9759.9069 | 1863.873 | NORMAL
285.928 | 0.65 | 288.706 | 1.11 | 2 | 57226.51 | 15915.1817 | 10148.2042 | 3295.97 | NORMAL
285.928 | 0.65 | 288.706 | 1.11 | 2 | 79289.74 | 16196.5123 | 10986.1267 | 2950.017 | NORMAL
285.928 | 0.65 | 288.706 | 1.11 | 2 | 101352.97 | 16134.5545 | 11535.7224 | 2768.801 | NORMAL
285.928 | 0.65 | 288.706 | 1.11 | 2 | 106868.78 | 16070.6624 | 11533.1591 | 2736.369 | NORMAL
285.928 | 0.65 | 288.706 | 1.42 | 1 | 57226.51 | 12516.7644 | 9625.4794 | 2232.02 | NORMAL
285.928 | 0.65 | 288.706 | 1.42 | 1 | 79289.74 | 12826.1137 | 9936.7494 | 2002.66 | NORMAL
285.928 | 0.65 | 288.706 | 1.42 | 1 | 101352.97 | 12962.8077 | 10364.0111 | 1877.551 | NORMAL
285.928 | 0.65 | 288.706 | 1.42 | 1 | 106868.78 | 12904.1911 | 10653.1324 | 1856.791 | NORMAL
285.928 | 0.65 | 288.706 | 1.42 | 2 | 57226.51 | 16316.823 | 11356.8515 | 3329.84 | NORMAL
285.928 | 0.65 | 288.706 | 1.42 | 2 | 79289.74 | 16722.9191 | 11948.1912 | 2978.73 | NORMAL
285.928 | 0.65 | 288.706 | 1.42 | 2 | 101352.97 | 16846.4537 | 12579.0111 | 2798.72 | NORMAL
285.928 | 0.65 | 288.706 | 1.42 | 2 | 106868.78 | 16777.1395 | 12867.9486 | 2762.465 | NORMAL
285.928 | 0.65 | 291.483 | 0.5 | 1 | 57226.51 | 11980.2755 | 5876.2892 | 2220.626 | NORMAL
285.928 | 0.65 | 291.483 | 0.5 | 1 | 79289.74 | 11865.3576 | 6683.8864 | 2005.54 | NORMAL
285.928 | 0.65 | 291.483 | 0.5 | 1 | 101352.97 | 11672.0106 | 7244.4551 | 1897.482 | NORMAL
285.928 | 0.65 | 291.483 | 0.5 | 1 | 106868.78 | 11535.9613 | 7309.0351 | 1881.5567 | NORMAL
285.928 | 0.65 | 291.483 | 0.5 | 2 | 57226.51 | 15085.2286 | 7245.556 | 3231.877 | NORMAL
285.928 | 0.65 | 291.483 | 0.5 | 2 | 79289.74 | 14856.0668 | 8200.9946 | 2878.747 | NORMAL
285.928 | 0.65 | 291.483 | 0.5 | 2 | 101352.97 | 14537.3974 | 8871.127 | 2705.205 | NORMAL
285.928 | 0.65 | 291.483 | 0.5 | 2 | 106868.78 | 14408.4115 | 8976.0513 | 2673.6275 | NORMAL
285.928 | 0.65 | 291.483 | 0.8 | 1 | 57226.51 | 12851.2896 | 7660.7308 | 2239.783 | NORMAL
285.928 | 0.65 | 291.483 | 0.8 | 1 | 79289.74 | 12983.7925 | 8268.8711 | 2002.604 | NORMAL
285.928 | 0.65 | 291.483 | 0.8 | 1 | 101352.97 | 12974.3552 | 8752.7855 | 1877.606 | NORMAL
285.928 | 0.65 | 291.483 | 0.8 | 1 | 106868.78 | 12888.218 | 8732.2059 | 1857.24 | NORMAL
285.928 | 0.65 | 291.483 | 0.8 | 2 | 57226.51 | 16491.6764 | 8359.3174 | 3344.899 | NORMAL
285.928 | 0.65 | 291.483 | 0.8 | 2 | 79289.74 | 16611.6061 | 9557.8364 | 2972.481 | NORMAL
285.928 | 0.65 | 291.483 | 0.8 | 2 | 101352.97 | 16499.9414 | 10326.9338 | 2784.224 | NORMAL
285.928 | 0.65 | 291.483 | 0.8 | 2 | 106868.78 | 16307.7667 | 10543.9986 | 2748.039 | NORMAL
285.928 | 0.65 | 291.483 | 1.11 | 1 | 57226.51 | 13276.0258 | 9068.0301 | 2249.84 | NORMAL
285.928 | 0.65 | 291.483 | 1.11 | 1 | 79289.74 | 13548.3001 | 9528.1401 | 2002.054 | NORMAL
285.928 | 0.65 | 291.483 | 1.11 | 1 | 101352.97 | 13637.075 | 9945.1643 | 1868.43 | NORMAL
285.928 | 0.65 | 291.483 | 1.11 | 1 | 106868.78 | 13560.5217 | 10135.5407 | 1845.885 | NORMAL
285.928 | 0.65 | 291.483 | 1.11 | 2 | 57226.51 | 17145.5744 | 10329.9 | 3401.45 | NORMAL
285.928 | 0.65 | 291.483 | 1.11 | 2 | 79289.74 | 17490.2989 | 11234.5612 | 3020.942 | NORMAL
285.928 | 0.65 | 291.483 | 1.11 | 2 | 101352.97 | 17539.2438 | 11901.5521 | 2827.84 | NORMAL
285.928 | 0.65 | 291.483 | 1.11 | 2 | 106868.78 | 17437.0457 | 11887.4269 | 2788.385 | NORMAL
285.928 | 0.65 | 291.483 | 1.42 | 1 | 57226.51 | 13538.3353 | 10032.0148 | 2255.73 | NORMAL
285.928 | 0.65 | 291.483 | 1.42 | 1 | 79289.74 | 13900.1758 | 10329.6933 | 2001.79 | NORMAL
285.928 | 0.65 | 291.483 | 1.42 | 1 | 101352.97 | 14054.5721 | 10808.5141 | 1862.918 | NORMAL
285.928 | 0.65 | 291.483 | 1.42 | 1 | 106868.78 | 13986.5182 | 11110.3865 | 1839.212 | NORMAL
285.928 | 0.65 | 291.483 | 1.42 | 2 | 57226.51 | 17544.6366 | 11683.5525 | 3437.15 | NORMAL
285.928 | 0.65 | 291.483 | 1.42 | 2 | 79289.74 | 18038.9215 | 12431.7392 | 3052.22 | NORMAL
285.928 | 0.65 | 291.483 | 1.42 | 2 | 101352.97 | 18193.2298 | 13059.3368 | 2855.772 | NORMAL
285.928 | 0.65 | 291.483 | 1.42 | 2 | 106868.78 | 18104.4842 | 13324.2124 | 2816.92 | NORMAL
285.928 | 0.65 | 294.26 | 0.5 | 1 | 57226.51 | 13023.9742 | 5871.416 | 2243.309 | NORMAL
285.928 | 0.65 | 294.26 | 0.5 | 1 | 79289.74 | 12916.8816 | 6784.6308 | 2002.66 | NORMAL
285.928 | 0.65 | 294.26 | 0.5 | 1 | 101352.97 | 12716.7644 | 7400.3557 | 1881.29 | NORMAL
285.928 | 0.65 | 294.26 | 0.5 | 1 | 106868.78 | 12597.5381 | 7514.6078 | 1862.1757 | NORMAL
285.928 | 0.65 | 294.26 | 0.5 | 2 | 57226.51 | 16431.9168 | 7291.9424 | 3339.784 | NORMAL
285.928 | 0.65 | 294.26 | 0.5 | 2 | 79289.74 | 16167.4384 | 8315.431 | 2948 | NORMAL
285.928 | 0.65 | 294.26 | 0.5 | 2 | 101352.97 | 15739.5369 | 9014.2532 | 2753.325 | NORMAL
285.928 | 0.65 | 294.26 | 0.5 | 2 | 106868.78 | 15590.592 | 9138.94 | 2717.8299 | NORMAL
285.928 | 0.65 | 294.26 | 0.8 | 1 | 57226.51 | 13910.3751 | 7656.2288 | 2265.742 | NORMAL
285.928 | 0.65 | 294.26 | 0.8 | 1 | 79289.74 | 14083.4701 | 8441.0405 | 2001.973 | NORMAL
285.928 | 0.65 | 294.26 | 0.8 | 1 | 101352.97 | 14075.7034 | 8982.3257 | 1862.683 | NORMAL
285.928 | 0.65 | 294.26 | 0.8 | 1 | 106868.78 | 13976.1137 | 8967.997 | 1839.641 | NORMAL
285.928 | 0.65 | 294.26 | 0.8 | 2 | 57226.51 | 17766.7644 | 8210.7858 | 3458.101 | NORMAL
285.928 | 0.65 | 294.26 | 0.8 | 2 | 79289.74 | 17956.2427 | 9568.4149 | 3046.508 | NORMAL
285.928 | 0.65 | 294.26 | 0.8 | 2 | 101352.97 | 17856.8875 | 10454.6898 | 2841.184 | NORMAL
285.928 | 0.65 | 294.26 | 0.8 | 2 | 106868.78 | 17722.0399 | 10833.483 | 2801.344 | NORMAL
285.928 | 0.65 | 294.26 | 1.11 | 1 | 57226.51 | 14339.9179 | 9382.7947 | 2277.07 | NORMAL
285.928 | 0.65 | 294.26 | 1.11 | 1 | 79289.74 | 14666.442 | 9811.395 | 2002.933 | NORMAL
285.928 | 0.65 | 294.26 | 1.11 | 1 | 101352.97 | 14770.9554 | 10374.543 | 1854.615 | NORMAL
285.928 | 0.65 | 294.26 | 1.11 | 1 | 106868.78 | 14682.0926 | 10398.3425 | 1829.228 | NORMAL
285.928 | 0.65 | 294.26 | 1.11 | 2 | 57226.51 | 18413.9508 | 10577.1759 | 3515.99 | NORMAL
285.928 | 0.65 | 294.26 | 1.11 | 2 | 79289.74 | 18853.898 | 11488.9056 | 3097.798 | NORMAL
285.928 | 0.65 | 294.26 | 1.11 | 2 | 101352.97 | 18930.2169 | 12201.6038 | 2888.087 | NORMAL
285.928 | 0.65 | 294.26 | 1.11 | 2 | 106868.78 | 18814.6835 | 12151.3881 | 2846.359 | NORMAL
285.928 | 0.65 | 294.26 | 1.42 | 1 | 57226.51 | 14606.7995 | 10516.9103 | 2284.42 | NORMAL
285.928 | 0.65 | 294.26 | 1.42 | 1 | 79289.74 | 15028.2825 | 10792.9218 | 2003.99 | NORMAL
285.928 | 0.65 | 294.26 | 1.42 | 1 | 101352.97 | 15206.7409 | 11259.7553 | 1849.555 | NORMAL
285.928 | 0.65 | 294.26 | 1.42 | 1 | 106868.78 | 15127.7843 | 11563.2547 | 1823.005 | NORMAL
285.928 | 0.65 | 294.26 | 1.42 | 2 | 57226.51 | 18809.5838 | 12052.8239 | 3552.77 | NORMAL
285.928 | 0.65 | 294.26 | 1.42 | 2 | 79289.74 | 19413.6284 | 12772.6532 | 3132.09 | NORMAL
285.928 | 0.65 | 294.26 | 1.42 | 2 | 101352.97 | 19605.6858 | 13541.6472 | 2918.34 | NORMAL
285.928 | 0.65 | 294.26 | 1.42 | 2 | 106868.78 | 19505.7151 | 13632.6613 | 2875.515 | NORMAL
285.928 | 0.65 | 297.037 | 0.5 | 1 | 57226.51 | 14132.1512 | 5864.3623 | 2270.877 | NORMAL
285.928 | 0.65 | 297.037 | 0.5 | 1 | 79289.74 | 14041.7937 | 6866.7039 | 2000.994 | NORMAL
285.928 | 0.65 | 297.037 | 0.5 | 1 | 101352.97 | 13821.7761 | 7536.9592 | 1864.982 | NORMAL
285.928 | 0.65 | 297.037 | 0.5 | 1 | 106868.78 | 13686.782 | 7664.2831 | 1843.8633 | NORMAL
285.928 | 0.65 | 297.037 | 0.5 | 2 | 57226.51 | 17771.1899 | 7303.3548 | 3458.376 | NORMAL
285.928 | 0.65 | 297.037 | 0.5 | 2 | 79289.74 | 17538.6284 | 8402.7744 | 3023.41 | NORMAL
285.928 | 0.65 | 297.037 | 0.5 | 2 | 101352.97 | 17115.592 | 9183.7303 | 2809.74 | NORMAL
285.928 | 0.65 | 297.037 | 0.5 | 2 | 106868.78 | 16933.4701 | 9300.2682 | 2769.7772 | NORMAL
285.928 | 0.65 | 297.037 | 0.8 | 1 | 57226.51 | 15023.095 | 7594.1294 | 2296.71 | NORMAL
285.928 | 0.65 | 297.037 | 0.8 | 1 | 79289.74 | 15250.2931 | 8481.298 | 2004.039 | NORMAL
285.928 | 0.65 | 297.037 | 0.8 | 1 | 101352.97 | 15251.0551 | 9107.6403 | 1849.004 | NORMAL
285.928 | 0.65 | 297.037 | 0.8 | 1 | 106868.78 | 15136.8406 | 9194.2683 | 1823.28 | NORMAL
285.928 | 0.65 | 297.037 | 0.8 | 2 | 57226.51 | 19091.5592 | 7949.8207 | 3579.292 | NORMAL
285.928 | 0.65 | 297.037 | 0.8 | 2 | 79289.74 | 19378.3705 | 9470.2872 | 3129.138 | NORMAL
285.928 | 0.65 | 297.037 | 0.8 | 2 | 101352.97 | 19292.9953 | 10509.3576 | 2903.904 | NORMAL
285.928 | 0.65 | 297.037 | 0.8 | 2 | 106868.78 | 19141.2661 | 10935.2905 | 2860.043 | NORMAL
285.928 | 0.65 | 297.037 | 1.11 | 1 | 57226.51 | 15453.1067 | 9600.8143 | 2309.34 | NORMAL
285.928 | 0.65 | 297.037 | 1.11 | 1 | 79289.74 | 15847.0985 | 10106.6931 | 2007.528 | NORMAL
285.928 | 0.65 | 297.037 | 1.11 | 1 | 101352.97 | 15973.2708 | 10688.5301 | 1842.877 | NORMAL
285.928 | 0.65 | 297.037 | 1.11 | 1 | 106868.78 | 15872.5088 | 10642.2314 | 1813.839 | NORMAL
285.928 | 0.65 | 297.037 | 1.11 | 2 | 57226.51 | 19726.1137 | 10549.861 | 3640.3 | NORMAL
285.928 | 0.65 | 297.037 | 1.11 | 2 | 79289.74 | 20284.2321 | 11600.9377 | 3182.775 | NORMAL
285.928 | 0.65 | 297.037 | 1.11 | 2 | 101352.97 | 20397.3916 | 12307.6433 | 2954.649 | NORMAL
285.928 | 0.65 | 297.037 | 1.11 | 2 | 106868.78 | 20269.6073 | 12408.6684 | 2908.69 | NORMAL
285.928 | 0.65 | 297.037 | 1.42 | 1 | 57226.51 | 15720.8382 | 10794.9179 | 2317.6 | NORMAL
285.928 | 0.65 | 297.037 | 1.42 | 1 | 79289.74 | 16217.204 | 11204.7257 | 2008.87 | NORMAL
285.928 | 0.65 | 297.037 | 1.42 | 1 | 101352.97 | 16424.7655 | 11720.9098 | 1838.56 | NORMAL
285.928 | 0.65 | 297.037 | 1.42 | 1 | 106868.78 | 16335.1407 | 12088.9515 | 1808.284 | NORMAL
285.928 | 0.65 | 297.037 | 1.42 | 2 | 57226.51 | 20115.5041 | 12450.0487 | 3678.41 | NORMAL
285.928 | 0.65 | 297.037 | 1.42 | 2 | 79289.74 | 20848.7104 | 13060.4245 | 3219.5 | NORMAL
285.928 | 0.65 | 297.037 | 1.42 | 2 | 101352.97 | 21088.9508 | 13935.6208 | 2987.093 | NORMAL
285.928 | 0.65 | 297.037 | 1.42 | 2 | 106868.78 | 20978.9273 | 13876.8262 | 2940.182 | NORMAL
285.928 | 0.65 | 299.814 | 0.5 | 1 | 57226.51 | 15285.7855 | 5847.0881 | 2303.423 | NORMAL
285.928 | 0.65 | 299.814 | 0.5 | 1 | 79289.74 | 15237.075 | 6944.1446 | 2002.716 | NORMAL
285.928 | 0.65 | 299.814 | 0.5 | 1 | 101352.97 | 15004.8652 | 7665.7455 | 1850.59 | NORMAL
285.928 | 0.65 | 299.814 | 0.5 | 1 | 106868.78 | 14849.9414 | 7780.3595 | 1826.918 | NORMAL
285.928 | 0.65 | 299.814 | 0.5 | 2 | 57226.51 | 19163.9801 | 7244.5211 | 3586.373 | NORMAL
285.928 | 0.65 | 299.814 | 0.5 | 2 | 79289.74 | 18997.6846 | 8418.9569 | 3107.108 | NORMAL
285.928 | 0.65 | 299.814 | 0.5 | 2 | 101352.97 | 18548.9449 | 9273.916 | 2870.988 | NORMAL
285.928 | 0.65 | 299.814 | 0.5 | 2 | 106868.78 | 18343.4642 | 9403.245 | 2826.6744 | NORMAL
285.928 | 0.65 | 299.814 | 0.8 | 1 | 57226.51 | 16176.4361 | 7479.3046 | 2332.756 | NORMAL
285.928 | 0.65 | 299.814 | 0.8 | 1 | 79289.74 | 16473.9449 | 8490.5888 | 2009.233 | NORMAL
285.928 | 0.65 | 299.814 | 0.8 | 1 | 101352.97 | 16491.6764 | 9170.8563 | 1837.157 | NORMAL
285.928 | 0.65 | 299.814 | 0.8 | 1 | 106868.78 | 16363.8921 | 9404.1979 | 1808.564 | NORMAL
285.928 | 0.65 | 299.814 | 0.8 | 2 | 57226.51 | 20447.0399 | 7509.2367 | 3711.529 | NORMAL
285.928 | 0.65 | 299.814 | 0.8 | 2 | 79289.74 | 20860.6096 | 9315.7433 | 3219.153 | NORMAL
285.928 | 0.65 | 299.814 | 0.8 | 2 | 101352.97 | 20806.3013 | 10484.857 | 2973.184 | NORMAL
285.928 | 0.65 | 299.814 | 0.8 | 2 | 106868.78 | 20635.1114 | 10957.306 | 2924.683 | NORMAL
285.928 | 0.65 | 299.814 | 1.11 | 1 | 57226.51 | 16603.6049 | 9595.8874 | 2347.02 | NORMAL
285.928 | 0.65 | 299.814 | 1.11 | 1 | 79289.74 | 17076.0551 | 10450.8019 | 2011.834 | NORMAL
285.928 | 0.65 | 299.814 | 1.11 | 1 | 101352.97 | 17236.4595 | 10995.9994 | 1833.365 | NORMAL
285.928 | 0.65 | 299.814 | 1.11 | 1 | 106868.78 | 17124.0328 | 10857.9554 | 1800.467 | NORMAL
285.928 | 0.65 | 299.814 | 1.11 | 2 | 57226.51 | 21061.9871 | 10411.888 | 3773.91 | NORMAL
285.928 | 0.65 | 299.814 | 1.11 | 2 | 79289.74 | 21766.6764 | 11610.4105 | 3275.504 | NORMAL
285.928 | 0.65 | 299.814 | 1.11 | 2 | 101352.97 | 21931.5065 | 12403.2977 | 3027.552 | NORMAL
285.928 | 0.65 | 299.814 | 1.11 | 2 | 106868.78 | 21792.2626 | 12645.5052 | 2977.095 | NORMAL
285.928 | 0.65 | 299.814 | 1.42 | 1 | 57226.51 | 16869.8124 | 11243.4601 | 2355.97 | NORMAL
285.928 | 0.65 | 299.814 | 1.42 | 1 | 79289.74 | 17457.3857 | 11544.5517 | 2017.49 | NORMAL
285.928 | 0.65 | 299.814 | 1.42 | 1 | 101352.97 | 17699.7948 | 12157.6882 | 1829.864 | NORMAL
285.928 | 0.65 | 299.814 | 1.42 | 1 | 106868.78 | 17599.5018 | 12550.7855 | 1795.793 | NORMAL
285.928 | 0.65 | 299.814 | 1.42 | 2 | 57226.51 | 21440.9144 | 12431.5494 | 3813 | NORMAL
285.928 | 0.65 | 299.814 | 1.42 | 2 | 79289.74 | 22323.857 | 13468.0499 | 3312.62 | NORMAL
285.928 | 0.65 | 299.814 | 1.42 | 2 | 101352.97 | 22633.1184 | 14239.3548 | 3062.339 | NORMAL
285.928 | 0.65 | 299.814 | 1.42 | 2 | 106868.78 | 22514.5076 | 14110.5174 | 3010.825 | NORMAL
285.928 | 0.65 | 302.591 | 0.5 | 1 | 57226.51 | 16497.8312 | 5863.9066 | 2341.709 | NORMAL
285.928 | 0.65 | 302.591 | 0.5 | 1 | 79289.74 | 16509.2907 | 7004.5289 | 2008.093 | NORMAL
285.928 | 0.65 | 302.591 | 0.5 | 1 | 101352.97 | 16272.1571 | 7780.7109 | 1837.556 | NORMAL
285.928 | 0.65 | 302.591 | 0.5 | 1 | 106868.78 | 16098.007 | 7867.418 | 1811.205 | NORMAL
285.928 | 0.65 | 302.591 | 0.5 | 2 | 57226.51 | 20604.9238 | 7190.2118 | 3727.632 | NORMAL
285.928 | 0.65 | 302.591 | 0.5 | 2 | 79289.74 | 20543.0539 | 8406.5874 | 3199.966 | NORMAL
285.928 | 0.65 | 302.591 | 0.5 | 2 | 101352.97 | 20084.8183 | 9325.2606 | 2939.767 | NORMAL
285.928 | 0.65 | 302.591 | 0.5 | 2 | 106868.78 | 19855.3927 | 9466.1578 | 2890.404 | NORMAL
285.928 | 0.65 | 302.591 | 0.8 | 1 | 57226.51 | 17368.728 | 7156.9928 | 2373.503 | NORMAL
285.928 | 0.65 | 302.591 | 0.8 | 1 | 79289.74 | 17761.1958 | 8431.1686 | 2018.876 | NORMAL
285.928 | 0.65 | 302.591 | 0.8 | 1 | 101352.97 | 17803.7222 | 9173.4925 | 1827.724 | NORMAL
285.928 | 0.65 | 302.591 | 0.8 | 1 | 106868.78 | 17662.163 | 9618.9729 | 1795.997 | NORMAL
285.928 | 0.65 | 302.591 | 0.8 | 2 | 57226.51 | 21835.2872 | 6924.4281 | 3854.389 | NORMAL
285.928 | 0.65 | 302.591 | 0.8 | 2 | 79289.74 | 22409.9941 | 9042.6567 | 3318.612 | NORMAL
285.928 | 0.65 | 302.591 | 0.8 | 2 | 101352.97 | 22402.1102 | 10426.6589 | 3049.824 | NORMAL
285.928 | 0.65 | 302.591 | 0.8 | 2 | 106868.78 | 22217.8488 | 10874.1262 | 2996.718 | NORMAL
285.928 | 0.65 | 302.591 | 1.11 | 1 | 57226.51 | 17795.7503 | 9684.1626 | 2390.61 | NORMAL
285.928 | 0.65 | 302.591 | 1.11 | 1 | 79289.74 | 18367.8195 | 10636.345 | 2022.135 | NORMAL
285.928 | 0.65 | 302.591 | 1.11 | 1 | 101352.97 | 18560.1407 | 11147.369 | 1821.608 | NORMAL
285.928 | 0.65 | 302.591 | 1.11 | 1 | 106868.78 | 18440.8851 | 10998.8446 | 1789.567 | NORMAL
285.928 | 0.65 | 302.591 | 1.11 | 2 | 57226.51 | 22422.2157 | 10077.0146 | 3921.54 | NORMAL
285.928 | 0.65 | 302.591 | 1.11 | 2 | 79289.74 | 23301.524 | 11492.6379 | 3377.133 | NORMAL
285.928 | 0.65 | 302.591 | 1.11 | 2 | 101352.97 | 23537.1923 | 12378.3271 | 3108.29 | NORMAL
285.928 | 0.65 | 302.591 | 1.11 | 2 | 106868.78 | 23387.2216 | 12887.622 | 3052.557 | NORMAL
285.928 | 0.65 | 302.591 | 1.42 | 1 | 57226.51 | 18059.4373 | 11825.0848 | 2400.26 | NORMAL
285.928 | 0.65 | 302.591 | 1.42 | 1 | 79289.74 | 18748.5053 | 11928.7927 | 2025.76 | NORMAL
285.928 | 0.65 | 302.591 | 1.42 | 1 | 101352.97 | 19036.782 | 12490.6609 | 1820.248 | NORMAL
285.928 | 0.65 | 302.591 | 1.42 | 1 | 106868.78 | 18925.4982 | 12927.213 | 1786.862 | NORMAL
285.928 | 0.65 | 302.591 | 1.42 | 2 | 57226.51 | 22787.8077 | 12551.7068 | 3961.93 | NORMAL
285.928 | 0.65 | 302.591 | 1.42 | 2 | 79289.74 | 23854.4256 | 13734.3764 | 3414.79 | NORMAL
285.928 | 0.65 | 302.591 | 1.42 | 2 | 101352.97 | 24244.2556 | 14384.4562 | 3142.937 | NORMAL
285.928 | 0.65 | 302.591 | 1.42 | 2 | 106868.78 | 24117.8781 | 14256.5842 | 3088.548 | NORMAL
285.928 | 0.65 | 305.368 | 0.5 | 1 | 57226.51 | 17752.9895 | 5963.6552 | 2387.217 | NORMAL
285.928 | 0.65 | 305.368 | 0.5 | 1 | 79289.74 | 17854.5135 | 7103.4182 | 2017.893 | NORMAL
285.928 | 0.65 | 305.368 | 0.5 | 1 | 101352.97 | 17621.8933 | 7835.8039 | 1827.132 | NORMAL
285.928 | 0.65 | 305.368 | 0.5 | 1 | 106868.78 | 17427.4619 | 7920.8686 | 1797.437 | NORMAL
285.928 | 0.65 | 305.368 | 0.5 | 2 | 57226.51 | 22077.1688 | 7157.661 | 3883.509 | NORMAL
285.928 | 0.65 | 305.368 | 0.5 | 2 | 79289.74 | 22168.2298 | 8369.3713 | 3303.459 | NORMAL
285.928 | 0.65 | 305.368 | 0.5 | 2 | 101352.97 | 21720.6331 | 9338.5907 | 3017.325 | NORMAL
285.928 | 0.65 | 305.368 | 0.5 | 2 | 106868.78 | 21467.7315 | 9488.5441 | 2962.055 | NORMAL
285.928 | 0.65 | 305.368 | 0.8 | 1 | 57226.51 | 18603.0481 | 6771.4909 | 2421.245 | NORMAL
285.928 | 0.65 | 305.368 | 0.8 | 1 | 79289.74 | 19107.7667 | 8245.5937 | 2032.702 | NORMAL
285.928 | 0.65 | 305.368 | 0.8 | 1 | 101352.97 | 19182.9719 | 9084.5184 | 1821.058 | NORMAL
285.928 | 0.65 | 305.368 | 0.8 | 1 | 106868.78 | 19021.3365 | 9686.977 | 1781.655 | NORMAL
285.928 | 0.65 | 305.368 | 0.8 | 2 | 57226.51 | 23242.0281 | 6216.1502 | 4011.344 | NORMAL
285.928 | 0.65 | 305.368 | 0.8 | 2 | 79289.74 | 24018.6401 | 8614.5014 | 3427.429 | NORMAL
285.928 | 0.65 | 305.368 | 0.8 | 2 | 101352.97 | 24077.0809 | 10286.9569 | 3134.883 | NORMAL
285.928 | 0.65 | 305.368 | 0.8 | 2 | 106868.78 | 23878.6049 | 10742.3874 | 3076.392 | NORMAL
285.928 | 0.65 | 305.368 | 1.11 | 1 | 57226.51 | 19023.1536 | 9537.5053 | 2440.82 | NORMAL
285.928 | 0.65 | 305.368 | 1.11 | 1 | 79289.74 | 19713.306 | 10823.1767 | 2035.412 | NORMAL
285.928 | 0.65 | 305.368 | 1.11 | 1 | 101352.97 | 19944.578 | 11319.0665 | 1814.331 | NORMAL
285.928 | 0.65 | 305.368 | 1.11 | 1 | 106868.78 | 19808.4408 | 11073.8692 | 1776.406 | NORMAL
285.928 | 0.65 | 305.368 | 1.11 | 2 | 57226.51 | 23803.9273 | 9856.6588 | 4077.56 | NORMAL
285.928 | 0.65 | 305.368 | 1.11 | 2 | 79289.74 | 24888.9215 | 11312.4379 | 3486.373 | NORMAL
285.928 | 0.65 | 305.368 | 1.11 | 2 | 101352.97 | 25208.6166 | 12242.2874 | 3193.792 | NORMAL
285.928 | 0.65 | 305.368 | 1.11 | 2 | 106868.78 | 25051.0551 | 13120.6655 | 3135.584 | NORMAL
285.928 | 0.65 | 305.368 | 1.42 | 1 | 57226.51 | 19282.1805 | 12062.7393 | 2451.7 | NORMAL
285.928 | 0.65 | 305.368 | 1.42 | 1 | 79289.74 | 20095.1934 | 12320.9258 | 2041.17 | NORMAL
285.928 | 0.65 | 305.368 | 1.42 | 1 | 101352.97 | 20420.4279 | 12855.7416 | 1813.435 | NORMAL
285.928 | 0.65 | 305.368 | 1.42 | 1 | 106868.78 | 20294.6659 | 13292.1538 | 1774.395 | NORMAL
285.928 | 0.65 | 305.368 | 1.42 | 2 | 57226.51 | 24149.238 | 12294.4978 | 4116.93 | NORMAL
285.928 | 0.65 | 305.368 | 1.42 | 2 | 79289.74 | 25431.5944 | 13955.1296 | 3525.31 | NORMAL
285.928 | 0.65 | 305.368 | 1.42 | 2 | 101352.97 | 25913.3939 | 14512.5371 | 3232.072 | NORMAL
285.928 | 0.65 | 305.368 | 1.42 | 2 | 106868.78 | 25780.9496 | 14303.6318 | 3173.931 | NORMAL
285.928 | 0.75 | 288.706 | 0.5 | 1 | 57226.51 | 11532.1512 | 5269.4089 | 2211.897 | NORMAL
285.928 | 0.75 | 288.706 | 0.5 | 1 | 79289.74 | 11305.3927 | 5978.9361 | 2007.69 | NORMAL
285.928 | 0.75 | 288.706 | 0.5 | 1 | 101352.97 | 11130.7737 | 6519.8952 | 1907.201 | NORMAL
285.928 | 0.75 | 288.706 | 0.5 | 1 | 106868.78 | 11034.2614 | 6600.7724 | 1891.2898 | NORMAL
285.928 | 0.75 | 288.706 | 0.5 | 2 | 57226.51 | 14577.7843 | 6464.7663 | 3186.114 | NORMAL
285.928 | 0.75 | 288.706 | 0.5 | 2 | 79289.74 | 14269.7538 | 7471.3292 | 2848.804 | NORMAL
285.928 | 0.75 | 288.706 | 0.5 | 2 | 101352.97 | 13911.0786 | 8131.9992 | 2681.394 | NORMAL
285.928 | 0.75 | 288.706 | 0.5 | 2 | 106868.78 | 13779.4549 | 8234.4093 | 2650.585 | NORMAL
285.928 | 0.75 | 288.706 | 0.8 | 1 | 57226.51 | 12370.5158 | 5821.8122 | 2228.991 | NORMAL
285.928 | 0.75 | 288.706 | 0.8 | 1 | 79289.74 | 12435.9027 | 6798.0862 | 2003.697 | NORMAL
285.928 | 0.75 | 288.706 | 0.8 | 1 | 101352.97 | 12381.6237 | 7451.5211 | 1886.476 | NORMAL
285.928 | 0.75 | 288.706 | 0.8 | 1 | 106868.78 | 12289.7714 | 7641.0916 | 1867.656 | NORMAL
285.928 | 0.75 | 288.706 | 0.8 | 2 | 57226.51 | 15928.6928 | 7166.9401 | 3296.985 | NORMAL
285.928 | 0.75 | 288.706 | 0.8 | 2 | 79289.74 | 15895.5451 | 8403.9906 | 2934.304 | NORMAL
285.928 | 0.75 | 288.706 | 0.8 | 2 | 101352.97 | 15753.5756 | 9224.8528 | 2753.888 | NORMAL
285.928 | 0.75 | 288.706 | 0.8 | 2 | 106868.78 | 15636.9285 | 9435.7918 | 2719.558 | NORMAL
285.928 | 0.75 | 288.706 | 1.11 | 1 | 57226.51 | 12776.4068 | 7206.8133 | 2238.16 | NORMAL
285.928 | 0.75 | 288.706 | 1.11 | 1 | 79289.74 | 12972.626 | 7958.6282 | 2002.746 | NORMAL
285.928 | 0.75 | 288.706 | 1.11 | 1 | 101352.97 | 13011.0786 | 8473.1136 | 1877.198 | NORMAL
285.928 | 0.75 | 288.706 | 1.11 | 1 | 106868.78 | 12929.7186 | 8436.1501 | 1856.126 | NORMAL
285.928 | 0.75 | 288.706 | 1.11 | 2 | 57226.51 | 16560.9027 | 7780.0968 | 3351.49 | NORMAL
285.928 | 0.75 | 288.706 | 1.11 | 2 | 79289.74 | 16808.0305 | 9158.7462 | 2983.192 | NORMAL
285.928 | 0.75 | 288.706 | 1.11 | 2 | 101352.97 | 16794.1383 | 10043.9863 | 2796.326 | NORMAL
285.928 | 0.75 | 288.706 | 1.11 | 2 | 106868.78 | 16691.442 | 10416.0941 | 2760.253 | NORMAL
285.928 | 0.75 | 288.706 | 1.42 | 1 | 57226.51 | 13026.6706 | 8164.075 | 2243.8 | NORMAL
285.928 | 0.75 | 288.706 | 1.42 | 1 | 79289.74 | 13305.9789 | 8760.6565 | 2002.25 | NORMAL
285.928 | 0.75 | 288.706 | 1.42 | 1 | 101352.97 | 13405.8324 | 9266.5939 | 1871.577 | NORMAL
285.928 | 0.75 | 288.706 | 1.42 | 1 | 106868.78 | 13332.5322 | 9319.4934 | 1849.452 | NORMAL
285.928 | 0.75 | 288.706 | 1.42 | 2 | 57226.51 | 16948.3587 | 9236.8386 | 3385.07 | NORMAL
285.928 | 0.75 | 288.706 | 1.42 | 2 | 79289.74 | 17336.7233 | 10359.6457 | 3012.5 | NORMAL
285.928 | 0.75 | 288.706 | 1.42 | 2 | 101352.97 | 17420.4865 | 11100.0204 | 2822.72 | NORMAL
285.928 | 0.75 | 288.706 | 1.42 | 2 | 106868.78 | 17323.1536 | 11203.7149 | 2785.212 | NORMAL
285.928 | 0.75 | 291.483 | 0.5 | 1 | 57226.51 | 12591.0903 | 5273.0731 | 2233.933 | NORMAL
285.928 | 0.75 | 291.483 | 0.5 | 1 | 79289.74 | 12422.1278 | 6081.5756 | 2003.354 | NORMAL
285.928 | 0.75 | 291.483 | 0.5 | 1 | 101352.97 | 12186.2544 | 6668.5743 | 1889.179 | NORMAL
285.928 | 0.75 | 291.483 | 0.5 | 1 | 106868.78 | 12060.1114 | 6749.8634 | 1871.7869 | NORMAL
285.928 | 0.75 | 291.483 | 0.5 | 2 | 57226.51 | 15916.6764 | 6461.152 | 3296.52 | NORMAL
285.928 | 0.75 | 291.483 | 0.5 | 2 | 79289.74 | 15516.2661 | 7509.9659 | 2913.295 | NORMAL
285.928 | 0.75 | 291.483 | 0.5 | 2 | 101352.97 | 15122.0985 | 8268.1283 | 2728.688 | NORMAL
285.928 | 0.75 | 291.483 | 0.5 | 2 | 106868.78 | 14970.2814 | 8392.2948 | 2694.4806 | NORMAL
285.928 | 0.75 | 291.483 | 0.8 | 1 | 57226.51 | 13445.6917 | 5691.3596 | 2253.712 | NORMAL
285.928 | 0.75 | 291.483 | 0.8 | 1 | 79289.74 | 13545.6624 | 6806.5599 | 2001.921 | NORMAL
285.928 | 0.75 | 291.483 | 0.8 | 1 | 101352.97 | 13491.442 | 7555.4503 | 1870.324 | NORMAL
285.928 | 0.75 | 291.483 | 0.8 | 1 | 106868.78 | 13386.2251 | 7828.9471 | 1848.495 | NORMAL
285.928 | 0.75 | 291.483 | 0.8 | 2 | 57226.51 | 17234.1149 | 7172.5112 | 3409.312 | NORMAL
285.928 | 0.75 | 291.483 | 0.8 | 2 | 79289.74 | 17327.9601 | 8474.6894 | 3011.867 | NORMAL
285.928 | 0.75 | 291.483 | 0.8 | 2 | 101352.97 | 17163.5405 | 9396.1116 | 2811.761 | NORMAL
285.928 | 0.75 | 291.483 | 0.8 | 2 | 106868.78 | 17019.197 | 9620.7478 | 2773.09 | NORMAL
285.928 | 0.75 | 291.483 | 1.11 | 1 | 57226.51 | 13857.7081 | 7142.0549 | 2264.26 | NORMAL
285.928 | 0.75 | 291.483 | 1.11 | 1 | 79289.74 | 14105.0997 | 8051.4307 | 2002.169 | NORMAL
285.928 | 0.75 | 291.483 | 1.11 | 1 | 101352.97 | 14155.8031 | 8625.1166 | 1861.822 | NORMAL
285.928 | 0.75 | 291.483 | 1.11 | 1 | 106868.78 | 14061.6354 | 8658.5926 | 1837.953 | NORMAL
285.928 | 0.75 | 291.483 | 1.11 | 2 | 57226.51 | 17857.5615 | 7479.3361 | 3466.3 | NORMAL
285.928 | 0.75 | 291.483 | 1.11 | 2 | 79289.74 | 18196.8054 | 9081.2613 | 3060.808 | NORMAL
285.928 | 0.75 | 291.483 | 1.11 | 2 | 101352.97 | 18202.7257 | 10096.342 | 2855.95 | NORMAL
285.928 | 0.75 | 291.483 | 1.11 | 2 | 106868.78 | 18077.374 | 10623.1869 | 2815.719 | NORMAL
285.928 | 0.75 | 291.483 | 1.42 | 1 | 57226.51 | 14111.2837 | 8286.2446 | 2270.81 | NORMAL
285.928 | 0.75 | 291.483 | 1.42 | 1 | 79289.74 | 14450.8499 | 9078.602 | 2002.39 | NORMAL
285.928 | 0.75 | 291.483 | 1.42 | 1 | 101352.97 | 14570.0762 | 9594.3806 | 1856.758 | NORMAL
285.928 | 0.75 | 291.483 | 1.42 | 1 | 106868.78 | 14485.3751 | 9541.9801 | 1831.874 | NORMAL
285.928 | 0.75 | 291.483 | 1.42 | 2 | 57226.51 | 18242.204 | 9105.5596 | 3501.35 | NORMAL
285.928 | 0.75 | 291.483 | 1.42 | 2 | 79289.74 | 18737.6026 | 10409.3378 | 3092.24 | NORMAL
285.928 | 0.75 | 291.483 | 1.42 | 2 | 101352.97 | 18854.7186 | 11208.4326 | 2884.524 | NORMAL
285.928 | 0.75 | 291.483 | 1.42 | 2 | 106868.78 | 18744.0504 | 11457.4695 | 2843.232 | NORMAL
285.928 | 0.75 | 294.26 | 0.5 | 1 | 57226.51 | 13713.5698 | 5267.8073 | 2259.836 | NORMAL
285.928 | 0.75 | 294.26 | 0.5 | 1 | 79289.74 | 13558.646 | 6124.2777 | 2001.539 | NORMAL
285.928 | 0.75 | 294.26 | 0.5 | 1 | 101352.97 | 13296.2485 | 6765.9157 | 1872.917 | NORMAL
285.928 | 0.75 | 294.26 | 0.5 | 1 | 106868.78 | 13156.2427 | 6859.6649 | 1852.3546 | NORMAL
285.928 | 0.75 | 294.26 | 0.5 | 2 | 57226.51 | 17281.653 | 6371.8664 | 3413.479 | NORMAL
285.928 | 0.75 | 294.26 | 0.5 | 2 | 79289.74 | 16951.231 | 7552.4006 | 2990.976 | NORMAL
285.928 | 0.75 | 294.26 | 0.5 | 2 | 101352.97 | 16461.9578 | 8364.1232 | 2782.865 | NORMAL
285.928 | 0.75 | 294.26 | 0.5 | 2 | 106868.78 | 16230.2462 | 8471.6691 | 2742.1013 | NORMAL
285.928 | 0.75 | 294.26 | 0.8 | 1 | 57226.51 | 14570.8089 | 5519.4953 | 2283.204 | NORMAL
285.928 | 0.75 | 294.26 | 0.8 | 1 | 79289.74 | 14724.1794 | 6784.5779 | 2002.579 | NORMAL
285.928 | 0.75 | 294.26 | 0.8 | 1 | 101352.97 | 14673.388 | 7628.6504 | 1855.242 | NORMAL
285.928 | 0.75 | 294.26 | 0.8 | 1 | 106868.78 | 14553.3998 | 7962.4852 | 1830.945 | NORMAL
285.928 | 0.75 | 294.26 | 0.8 | 2 | 57226.51 | 18587.3095 | 7171.5974 | 3531.863 | NORMAL
285.928 | 0.75 | 294.26 | 0.8 | 2 | 79289.74 | 18771.3951 | 8515.1553 | 3093.86 | NORMAL
285.928 | 0.75 | 294.26 | 0.8 | 2 | 101352.97 | 18612.837 | 9507.1394 | 2873.785 | NORMAL
285.928 | 0.75 | 294.26 | 0.8 | 2 | 106868.78 | 18452.3447 | 9736.9886 | 2831.141 | NORMAL
285.928 | 0.75 | 294.26 | 1.11 | 1 | 57226.51 | 14984.8183 | 6947.2315 | 2295.26 | NORMAL
285.928 | 0.75 | 294.26 | 1.11 | 1 | 79289.74 | 15298.095 | 8041.0612 | 2004.529 | NORMAL
285.928 | 0.75 | 294.26 | 1.11 | 1 | 101352.97 | 15367.966 | 8725.3164 | 1847.958 | NORMAL
285.928 | 0.75 | 294.26 | 1.11 | 1 | 106868.78 | 15261.0786 | 8853.089 | 1821.26 | NORMAL
285.928 | 0.75 | 294.26 | 1.11 | 2 | 57226.51 | 19195.252 | 7067.1159 | 3589.16 | NORMAL
285.928 | 0.75 | 294.26 | 1.11 | 2 | 79289.74 | 19651.8757 | 8901.6315 | 3145.694 | NORMAL
285.928 | 0.75 | 294.26 | 1.11 | 2 | 101352.97 | 19690.6506 | 10079.8803 | 2921.824 | NORMAL
285.928 | 0.75 | 294.26 | 1.11 | 2 | 106868.78 | 19550.381 | 10648.1737 | 2877.27 | NORMAL
285.928 | 0.75 | 294.26 | 1.42 | 1 | 57226.51 | 15240.3869 | 8342.3592 | 2302.79 | NORMAL
285.928 | 0.75 | 294.26 | 1.42 | 1 | 79289.74 | 15653.1067 | 9270.709 | 2005.62 | NORMAL
285.928 | 0.75 | 294.26 | 1.42 | 1 | 101352.97 | 15799.9414 | 9777.7147 | 1843.594 | NORMAL
285.928 | 0.75 | 294.26 | 1.42 | 1 | 106868.78 | 15704.0446 | 9684.433 | 1815.587 | NORMAL
285.928 | 0.75 | 294.26 | 1.42 | 2 | 57226.51 | 19572.5381 | 8789.0287 | 3625.29 | NORMAL
285.928 | 0.75 | 294.26 | 1.42 | 2 | 79289.74 | 20196.2192 | 10316.2086 | 3178.97 | NORMAL
285.928 | 0.75 | 294.26 | 1.42 | 2 | 101352.97 | 20359.8183 | 11280.3777 | 2952.631 | NORMAL
285.928 | 0.75 | 294.26 | 1.42 | 2 | 106868.78 | 20237.0457 | 11669.8948 | 2907.011 | NORMAL
285.928 | 0.75 | 297.037 | 0.5 | 1 | 57226.51 | 14900 | 5245.0384 | 2292.132 | NORMAL
285.928 | 0.75 | 297.037 | 0.5 | 1 | 79289.74 | 14778.6049 | 6140.2591 | 2002.128 | NORMAL
285.928 | 0.75 | 297.037 | 0.5 | 1 | 101352.97 | 14495.5451 | 6833.0405 | 1856.891 | NORMAL
285.928 | 0.75 | 297.037 | 0.5 | 1 | 106868.78 | 14335.1993 | 6934.968 | 1834.0424 | NORMAL
285.928 | 0.75 | 297.037 | 0.5 | 2 | 57226.51 | 18712.1336 | 6254.0442 | 3543.725 | NORMAL
285.928 | 0.75 | 297.037 | 0.5 | 2 | 79289.74 | 18439.6835 | 7535.6164 | 3074.677 | NORMAL
285.928 | 0.75 | 297.037 | 0.5 | 2 | 101352.97 | 17931.7995 | 8429.47 | 2844.313 | NORMAL
285.928 | 0.75 | 297.037 | 0.5 | 2 | 106868.78 | 17721.8933 | 8578.6546 | 2801.1989 | NORMAL
285.928 | 0.75 | 297.037 | 0.8 | 1 | 57226.51 | 15750.3517 | 5190.6702 | 2318.507 | NORMAL
285.928 | 0.75 | 297.037 | 0.8 | 1 | 79289.74 | 15972.1864 | 6675.3996 | 2006.326 | NORMAL
285.928 | 0.75 | 297.037 | 0.8 | 1 | 101352.97 | 15936.0786 | 7677.5405 | 1841.787 | NORMAL
285.928 | 0.75 | 297.037 | 0.8 | 1 | 106868.78 | 15799.3552 | 7984.9941 | 1814.44 | NORMAL
285.928 | 0.75 | 297.037 | 0.8 | 2 | 57226.51 | 19989.5076 | 7219.5105 | 3665.715 | NORMAL
285.928 | 0.75 | 297.037 | 0.8 | 2 | 79289.74 | 20294.0211 | 8530.3077 | 3184.345 | NORMAL
285.928 | 0.75 | 297.037 | 0.8 | 2 | 101352.97 | 20156.9168 | 9586.1055 | 2943.079 | NORMAL
285.928 | 0.75 | 297.037 | 0.8 | 2 | 106868.78 | 19978.3118 | 9809.0714 | 2895.757 | NORMAL
285.928 | 0.75 | 297.037 | 1.11 | 1 | 57226.51 | 16160.6096 | 6695.6638 | 2331.75 | NORMAL
285.928 | 0.75 | 297.037 | 1.11 | 1 | 79289.74 | 16557.2685 | 7923.4477 | 2010.281 | NORMAL
285.928 | 0.75 | 297.037 | 1.11 | 1 | 101352.97 | 16654.3963 | 8692.3291 | 1836.143 | NORMAL
285.928 | 0.75 | 297.037 | 1.11 | 1 | 106868.78 | 16535.4045 | 9047.9749 | 1806.048 | NORMAL
285.928 | 0.75 | 297.037 | 1.11 | 2 | 57226.51 | 20573.1536 | 6372.1023 | 3723.58 | NORMAL
285.928 | 0.75 | 297.037 | 1.11 | 2 | 79289.74 | 21179.1911 | 8603.0086 | 3239.048 | NORMAL
285.928 | 0.75 | 297.037 | 1.11 | 2 | 101352.97 | 21263.1888 | 9995.421 | 2994.715 | NORMAL
285.928 | 0.75 | 297.037 | 1.11 | 2 | 106868.78 | 21108.2943 | 10562.8648 | 2945.713 | NORMAL
285.928 | 0.75 | 297.037 | 1.42 | 1 | 57226.51 | 16415.4748 | 8482.1221 | 2340.14 | NORMAL
285.928 | 0.75 | 297.037 | 1.42 | 1 | 79289.74 | 16918.6694 | 9392.7546 | 2012.42 | NORMAL
285.928 | 0.75 | 297.037 | 1.42 | 1 | 101352.97 | 17100.5862 | 10004.1678 | 1832.712 | NORMAL
285.928 | 0.75 | 297.037 | 1.42 | 1 | 106868.78 | 16992.9367 | 9848.9192 | 1801.212 | NORMAL
285.928 | 0.75 | 297.037 | 1.42 | 2 | 57226.51 | 20937.163 | 8437.7604 | 3760.23 | NORMAL
285.928 | 0.75 | 297.037 | 1.42 | 2 | 79289.74 | 21716.9402 | 10106.0867 | 3274.01 | NORMAL
285.928 | 0.75 | 297.037 | 1.42 | 2 | 101352.97 | 21941.9109 | 11143.9455 | 3027.796 | NORMAL
285.928 | 0.75 | 297.037 | 1.42 | 2 | 106868.78 | 21809.6718 | 11887.4488 | 2977.578 | NORMAL
285.928 | 0.75 | 299.814 | 0.5 | 1 | 57226.51 | 16133.8804 | 5228.8293 | 2330.652 | NORMAL
285.928 | 0.75 | 299.814 | 0.5 | 1 | 79289.74 | 16070.8968 | 6138.5844 | 2006.461 | NORMAL
285.928 | 0.75 | 299.814 | 0.5 | 1 | 101352.97 | 15776.905 | 6868.4283 | 1843.319 | NORMAL
285.928 | 0.75 | 299.814 | 0.5 | 1 | 106868.78 | 15595.4865 | 6975.0657 | 1816.952 | NORMAL
285.928 | 0.75 | 299.814 | 0.5 | 2 | 57226.51 | 20184.6131 | 6049.3084 | 3685.121 | NORMAL
285.928 | 0.75 | 299.814 | 0.5 | 2 | 79289.74 | 20010.6096 | 7479.1054 | 3167.118 | NORMAL
285.928 | 0.75 | 299.814 | 0.5 | 2 | 101352.97 | 19484.8476 | 8440.3878 | 2912.511 | NORMAL
285.928 | 0.75 | 299.814 | 0.5 | 2 | 106868.78 | 19249.0621 | 8603.2336 | 2864.4587 | NORMAL
285.928 | 0.75 | 299.814 | 0.8 | 1 | 57226.51 | 16963.7456 | 4865.1683 | 2360.696 | NORMAL
285.928 | 0.75 | 299.814 | 0.8 | 1 | 79289.74 | 17278.7222 | 6537.8711 | 2013.922 | NORMAL
285.928 | 0.75 | 299.814 | 0.8 | 1 | 101352.97 | 17267.9367 | 7722.6875 | 1830.566 | NORMAL
285.928 | 0.75 | 299.814 | 0.8 | 1 | 106868.78 | 17116.1489 | 7989.3219 | 1800 | NORMAL
285.928 | 0.75 | 299.814 | 0.8 | 2 | 57226.51 | 21418.4642 | 7405.9481 | 3809.597 | NORMAL
285.928 | 0.75 | 299.814 | 0.8 | 2 | 79289.74 | 21877.6084 | 8605.6885 | 3283.269 | NORMAL
285.928 | 0.75 | 299.814 | 0.8 | 2 | 101352.97 | 21781.3599 | 9671.7297 | 3019.446 | NORMAL
285.928 | 0.75 | 299.814 | 0.8 | 2 | 106868.78 | 21585.932 | 9828.2259 | 2967.381 | NORMAL
285.928 | 0.75 | 299.814 | 1.11 | 1 | 57226.51 | 17368.7866 | 6220.8741 | 2371.61 | NORMAL
285.928 | 0.75 | 299.814 | 1.11 | 1 | 79289.74 | 17869.109 | 7797.4002 | 2018.218 | NORMAL
285.928 | 0.75 | 299.814 | 1.11 | 1 | 101352.97 | 18003.3998 | 8589.512 | 1827.253 | NORMAL
285.928 | 0.75 | 299.814 | 1.11 | 1 | 106868.78 | 17871.3658 | 9234.8495 | 1793.189 | NORMAL
285.928 | 0.75 | 299.814 | 1.11 | 2 | 57226.51 | 21966.7057 | 5639.4245 | 3872.27 | NORMAL
285.928 | 0.75 | 299.814 | 1.11 | 2 | 79289.74 | 22754.6893 | 8168.0233 | 3342.851 | NORMAL
285.928 | 0.75 | 299.814 | 1.11 | 2 | 101352.97 | 22904.7186 | 9817.535 | 3074.734 | NORMAL
285.928 | 0.75 | 299.814 | 1.11 | 2 | 106868.78 | 22737.6905 | 10422.2979 | 3021.032 | NORMAL
285.928 | 0.75 | 299.814 | 1.42 | 1 | 57226.51 | 17621.9519 | 8918.7518 | 2383.48 | NORMAL
285.928 | 0.75 | 299.814 | 1.42 | 1 | 79289.74 | 18233.8218 | 9451.6109 | 2021.38 | NORMAL
285.928 | 0.75 | 299.814 | 1.42 | 1 | 101352.97 | 18459.5252 | 10239.6832 | 1824.932 | NORMAL
285.928 | 0.75 | 299.814 | 1.42 | 1 | 106868.78 | 18340.973 | 9949.3726 | 1789.373 | NORMAL
285.928 | 0.75 | 299.814 | 1.42 | 2 | 57226.51 | 22314.5369 | 7734.5532 | 3909.08 | NORMAL
285.928 | 0.75 | 299.814 | 1.42 | 2 | 79289.74 | 23282.0633 | 9913.456 | 3375.38 | NORMAL
285.928 | 0.75 | 299.814 | 1.42 | 2 | 101352.97 | 23588.4525 | 10946.7403 | 3110.539 | NORMAL
285.928 | 0.75 | 299.814 | 1.42 | 2 | 106868.78 | 23444.109 | 11970.2104 | 3054.769 | NORMAL
285.928 | 0.75 | 302.591 | 0.5 | 1 | 57226.51 | 17421.1313 | 5159.1287 | 2375.704 | NORMAL
285.928 | 0.75 | 302.591 | 0.5 | 1 | 79289.74 | 17441.1489 | 6117.2039 | 2014.842 | NORMAL
285.928 | 0.75 | 302.591 | 0.5 | 1 | 101352.97 | 17148.4467 | 6875.9269 | 1831.01 | NORMAL
285.928 | 0.75 | 302.591 | 0.5 | 1 | 106868.78 | 16946.0141 | 6986.2654 | 1801.558 | NORMAL
285.928 | 0.75 | 302.591 | 0.5 | 2 | 57226.51 | 21701.4068 | 5787.5482 | 3843.907 | NORMAL
285.928 | 0.75 | 302.591 | 0.5 | 2 | 79289.74 | 21670.3107 | 7380.3444 | 3272.108 | NORMAL
285.928 | 0.75 | 302.591 | 0.5 | 2 | 101352.97 | 21146.6882 | 8409.7841 | 2989.201 | NORMAL
285.928 | 0.75 | 302.591 | 0.5 | 2 | 106868.78 | 20885.9027 | 8585.025 | 2935.75 | NORMAL
285.928 | 0.75 | 302.591 | 0.8 | 1 | 57226.51 | 18222.5088 | 4263.8302 | 2404.316 | NORMAL
285.928 | 0.75 | 302.591 | 0.8 | 1 | 79289.74 | 18651.7292 | 6420.2423 | 2026.062 | NORMAL
285.928 | 0.75 | 302.591 | 0.8 | 1 | 101352.97 | 18677.0809 | 7759.9722 | 1822.192 | NORMAL
285.928 | 0.75 | 302.591 | 0.8 | 1 | 106868.78 | 18507.2685 | 7955.3123 | 1787.967 | NORMAL
285.928 | 0.75 | 302.591 | 0.8 | 2 | 57226.51 | 22872.8898 | 7245.7655 | 3970.195 | NORMAL
285.928 | 0.75 | 302.591 | 0.8 | 2 | 79289.74 | 23527.1102 | 8594.9239 | 3395.166 | NORMAL
285.928 | 0.75 | 302.591 | 0.8 | 2 | 101352.97 | 23491.6178 | 9639.5739 | 3104.413 | NORMAL
285.928 | 0.75 | 302.591 | 0.8 | 2 | 106868.78 | 23281.7409 | 9801.6595 | 3047.014 | NORMAL
285.928 | 0.75 | 302.591 | 1.11 | 1 | 57226.51 | 18619.4607 | 5646.3328 | 2422.18 | NORMAL
285.928 | 0.75 | 302.591 | 1.11 | 1 | 79289.74 | 19240.8558 | 7449.6168 | 2031.7 | NORMAL
285.928 | 0.75 | 302.591 | 1.11 | 1 | 101352.97 | 19417.4678 | 8435.8995 | 1818.565 | NORMAL
285.928 | 0.75 | 302.591 | 1.11 | 1 | 106868.78 | 19273.7397 | 9284.4303 | 1783.549 | NORMAL
285.928 | 0.75 | 302.591 | 1.11 | 2 | 57226.51 | 23392.2626 | 4578.0763 | 4028.81 | NORMAL
285.928 | 0.75 | 302.591 | 1.11 | 2 | 79289.74 | 24388.7456 | 7642.7012 | 3455.531 | NORMAL
285.928 | 0.75 | 302.591 | 1.11 | 2 | 101352.97 | 24622.626 | 9555.1794 | 3163.041 | NORMAL
285.928 | 0.75 | 302.591 | 1.11 | 2 | 106868.78 | 24446.2192 | 10138.2627 | 3104.323 | NORMAL
285.928 | 0.75 | 302.591 | 1.42 | 1 | 57226.51 | 18866.9988 | 8939.467 | 2433.06 | NORMAL
285.928 | 0.75 | 302.591 | 1.42 | 1 | 79289.74 | 19606.3306 | 9729.8376 | 2035.94 | NORMAL
285.928 | 0.75 | 302.591 | 1.42 | 1 | 101352.97 | 19878.6342 | 10296.6555 | 1816.99 | NORMAL
285.928 | 0.75 | 302.591 | 1.42 | 1 | 106868.78 | 19749.1794 | 10007.6004 | 1781.376 | NORMAL
285.928 | 0.75 | 302.591 | 1.42 | 2 | 57226.51 | 23715.4748 | 7067.1166 | 4065.8 | NORMAL
285.928 | 0.75 | 302.591 | 1.42 | 2 | 79289.74 | 24900.5569 | 9418.5111 | 3486.79 | NORMAL
285.928 | 0.75 | 302.591 | 1.42 | 2 | 101352.97 | 25305.2755 | 10703.1446 | 3199.025 | NORMAL
285.928 | 0.75 | 302.591 | 1.42 | 2 | 106868.78 | 25150.8499 | 11808.8019 | 3140.07 | NORMAL
285.928 | 0.75 | 305.368 | 0.5 | 1 | 57226.51 | 18751.5533 | 4968.8429 | 2428.871 | NORMAL
285.928 | 0.75 | 305.368 | 0.5 | 1 | 79289.74 | 18885.3458 | 6028.0513 | 2029.025 | NORMAL
285.928 | 0.75 | 305.368 | 0.5 | 1 | 101352.97 | 18605.9203 | 6866.7009 | 1822.519 | NORMAL
285.928 | 0.75 | 305.368 | 0.5 | 1 | 106868.78 | 18382.4736 | 6970.873 | 1788.909 | NORMAL
285.928 | 0.75 | 305.368 | 0.5 | 2 | 57226.51 | 23250.0586 | 5510.5894 | 4012.713 | NORMAL
285.928 | 0.75 | 305.368 | 0.5 | 2 | 79289.74 | 23408.646 | 7187.7418 | 3387.664 | NORMAL
285.928 | 0.75 | 305.368 | 0.5 | 2 | 101352.97 | 22913.5111 | 8342.6948 | 3075.212 | NORMAL
285.928 | 0.75 | 305.368 | 0.5 | 2 | 106868.78 | 22629.2497 | 8526.4297 | 3015.992 | NORMAL
285.928 | 0.75 | 305.368 | 0.8 | 1 | 57226.51 | 19516.6471 | 3771.5921 | 2460.747 | NORMAL
285.928 | 0.75 | 305.368 | 0.8 | 1 | 79289.74 | 20086.313 | 6271.4089 | 2044.613 | NORMAL
285.928 | 0.75 | 305.368 | 0.8 | 1 | 101352.97 | 20152.4033 | 7809.7415 | 1817.221 | NORMAL
285.928 | 0.75 | 305.368 | 0.8 | 1 | 106868.78 | 19965.211 | 7979.4959 | 1779.78 | NORMAL
285.928 | 0.75 | 305.368 | 0.8 | 2 | 57226.51 | 24349.3259 | 7024.2935 | 4139.854 | NORMAL
285.928 | 0.75 | 305.368 | 0.8 | 2 | 79289.74 | 25235.3458 | 8455.1783 | 3510.311 | NORMAL
285.928 | 0.75 | 305.368 | 0.8 | 2 | 101352.97 | 25280.5686 | 9562.9312 | 3202.082 | NORMAL
285.928 | 0.75 | 305.368 | 0.8 | 2 | 106868.78 | 25059.6424 | 9728.4539 | 3135.612 | NORMAL
285.928 | 0.75 | 305.368 | 1.11 | 1 | 57226.51 | 19901.0551 | 4965.3929 | 2478.1 | NORMAL
285.928 | 0.75 | 305.368 | 1.11 | 1 | 79289.74 | 20666.3247 | 7038.9709 | 2049.919 | NORMAL
285.928 | 0.75 | 305.368 | 1.11 | 1 | 101352.97 | 20882.3564 | 8076.6272 | 1816.437 | NORMAL
285.928 | 0.75 | 305.368 | 1.11 | 1 | 106868.78 | 20719.7831 | 9102.8845 | 1775.683 | NORMAL
285.928 | 0.75 | 305.368 | 1.11 | 2 | 57226.51 | 24833.1477 | 3041.2411 | 4197.59 | NORMAL
285.928 | 0.75 | 305.368 | 1.11 | 2 | 79289.74 | 26071.6002 | 6865.9299 | 3571.011 | NORMAL
285.928 | 0.75 | 305.368 | 1.11 | 2 | 101352.97 | 26406.0082 | 9247.8858 | 3264.933 | NORMAL
285.928 | 0.75 | 305.368 | 1.11 | 2 | 106868.78 | 26222.7433 | 9711.1472 | 3196.441 | NORMAL
285.928 | 0.75 | 305.368 | 1.42 | 1 | 57226.51 | 20143.5522 | 8175.0391 | 2489.12 | NORMAL
285.928 | 0.75 | 305.368 | 1.42 | 1 | 79289.74 | 21029.1911 | 9838.1496 | 2055.25 | NORMAL
285.928 | 0.75 | 305.368 | 1.42 | 1 | 101352.97 | 21346.8933 | 10215.5131 | 1815.024 | NORMAL
285.928 | 0.75 | 305.368 | 1.42 | 1 | 106868.78 | 21190.4455 | 10184.7214 | 1772.234 | NORMAL
285.928 | 0.75 | 305.368 | 1.42 | 2 | 57226.51 | 25135.4924 | 6148.9206 | 4233.86 | NORMAL
285.928 | 0.75 | 305.368 | 1.42 | 2 | 79289.74 | 26567.3505 | 8907.0231 | 3607.74 | NORMAL
285.928 | 0.75 | 305.368 | 1.42 | 2 | 101352.97 | 27082.7667 | 10122.6445 | 3297.028 | NORMAL
285.928 | 0.75 | 305.368 | 1.42 | 2 | 106868.78 | 26923.5639 | 11516.6083 | 3234.082 | NORMAL
285.928 | 0.85 | 288.706 | 0.5 | 1 | 57226.51 | 12062.3681 | 4554.2677 | 2222.535 | NORMAL
285.928 | 0.85 | 288.706 | 0.5 | 1 | 79289.74 | 11837.8957 | 5397.6187 | 2005.589 | NORMAL
285.928 | 0.85 | 288.706 | 0.5 | 1 | 101352.97 | 11512.1923 | 5977.5216 | 1899.342 | NORMAL
285.928 | 0.85 | 288.706 | 0.5 | 1 | 106868.78 | 11420.3693 | 6089.7406 | 1883.7242 | NORMAL
285.928 | 0.85 | 288.706 | 0.5 | 2 | 57226.51 | 15261.7233 | 5750.1595 | 3242.253 | NORMAL
285.928 | 0.85 | 288.706 | 0.5 | 2 | 79289.74 | 14832.1512 | 6847.2626 | 2877.859 | NORMAL
285.928 | 0.85 | 288.706 | 0.5 | 2 | 101352.97 | 14407.0926 | 7619.5223 | 2700.542 | NORMAL
285.928 | 0.85 | 288.706 | 0.5 | 2 | 106868.78 | 14256.3306 | 7752.7779 | 2667.9891 | NORMAL
285.928 | 0.85 | 288.706 | 0.8 | 1 | 57226.51 | 12879.9531 | 5130.5232 | 2240.356 | NORMAL
285.928 | 0.85 | 288.706 | 0.8 | 1 | 79289.74 | 12924.8535 | 6021.3403 | 2002.55 | NORMAL
285.928 | 0.85 | 288.706 | 0.8 | 1 | 101352.97 | 12830.7444 | 6698.6366 | 1879.575 | NORMAL
285.928 | 0.85 | 288.706 | 0.8 | 1 | 106868.78 | 12720.4865 | 6792.3073 | 1859.79 | NORMAL
285.928 | 0.85 | 288.706 | 0.8 | 2 | 57226.51 | 16586.9285 | 6352.2131 | 3353.15 | NORMAL
285.928 | 0.85 | 288.706 | 0.8 | 2 | 79289.74 | 16576.4361 | 7570.707 | 2970.721 | NORMAL
285.928 | 0.85 | 288.706 | 0.8 | 2 | 101352.97 | 16303.2532 | 8437.3085 | 2780.081 | NORMAL
285.928 | 0.85 | 288.706 | 0.8 | 2 | 106868.78 | 16144.0797 | 8571.0695 | 2738.911 | NORMAL
285.928 | 0.85 | 288.706 | 1.11 | 1 | 57226.51 | 13268.0539 | 4981.398 | 2248.92 | NORMAL
285.928 | 0.85 | 288.706 | 1.11 | 1 | 79289.74 | 13451.7878 | 6249.9024 | 2001.981 | NORMAL
285.928 | 0.85 | 288.706 | 1.11 | 1 | 101352.97 | 13459.7304 | 7089.5496 | 1870.903 | NORMAL
285.928 | 0.85 | 288.706 | 1.11 | 1 | 106868.78 | 13361.2837 | 7346.8622 | 1848.975 | NORMAL
285.928 | 0.85 | 288.706 | 1.11 | 2 | 57226.51 | 17198.1243 | 6907.4718 | 3406.26 | NORMAL
285.928 | 0.85 | 288.706 | 1.11 | 2 | 79289.74 | 17433.7925 | 8097.6305 | 3018.063 | NORMAL
285.928 | 0.85 | 288.706 | 1.11 | 2 | 101352.97 | 17370.6917 | 9037.0502 | 2820.552 | NORMAL
285.928 | 0.85 | 288.706 | 1.11 | 2 | 106868.78 | 17241.1489 | 9223.8595 | 2781.926 | NORMAL
285.928 | 0.85 | 288.706 | 1.42 | 1 | 57226.51 | 13507.6202 | 5214.8734 | 2255.35 | NORMAL
285.928 | 0.85 | 288.706 | 1.42 | 1 | 79289.74 | 13778.517 | 6599.4136 | 2001.95 | NORMAL
285.928 | 0.85 | 288.706 | 1.42 | 1 | 101352.97 | 13851.1137 | 7436.7738 | 1865.587 | NORMAL
285.928 | 0.85 | 288.706 | 1.42 | 1 | 106868.78 | 13761.8992 | 7812.4237 | 1842.641 | NORMAL
285.928 | 0.85 | 288.706 | 1.42 | 2 | 57226.51 | 17557.2685 | 6424.6083 | 3437.98 | NORMAL
285.928 | 0.85 | 288.706 | 1.42 | 2 | 79289.74 | 17956.2427 | 8221.2478 | 3047.49 | NORMAL
285.928 | 0.85 | 288.706 | 1.42 | 2 | 101352.97 | 18002.0223 | 9363.2838 | 2847.944 | NORMAL
285.928 | 0.85 | 288.706 | 1.42 | 2 | 106868.78 | 17882.5909 | 9763.1078 | 2807.783 | NORMAL
285.928 | 0.85 | 291.483 | 0.5 | 1 | 57226.51 | 13193.6694 | 4509.8337 | 2247.548 | NORMAL
285.928 | 0.85 | 291.483 | 0.5 | 1 | 79289.74 | 12975.7034 | 5409.6875 | 2002.438 | NORMAL
285.928 | 0.85 | 291.483 | 0.5 | 1 | 101352.97 | 12680.0997 | 6080.2853 | 1881.849 | NORMAL
285.928 | 0.85 | 291.483 | 0.5 | 1 | 106868.78 | 12539.068 | 6191.052 | 1862.9133 | NORMAL
285.928 | 0.85 | 291.483 | 0.5 | 2 | 57226.51 | 16652.4912 | 5657.4674 | 3358.546 | NORMAL
285.928 | 0.85 | 291.483 | 0.5 | 2 | 79289.74 | 16245.4279 | 6851.1193 | 2952.579 | NORMAL
285.928 | 0.85 | 291.483 | 0.5 | 2 | 101352.97 | 15699.3552 | 7658.0513 | 2751.667 | NORMAL
285.928 | 0.85 | 291.483 | 0.5 | 2 | 106868.78 | 15526.9343 | 7818.7896 | 2715.3314 | NORMAL
285.928 | 0.85 | 291.483 | 0.8 | 1 | 57226.51 | 14017.8781 | 5077.7801 | 2268.24 | NORMAL
285.928 | 0.85 | 291.483 | 0.8 | 1 | 79289.74 | 14109.9062 | 6036.5565 | 2001.677 | NORMAL
285.928 | 0.85 | 291.483 | 0.8 | 1 | 101352.97 | 14014.9472 | 6766.4305 | 1863.171 | NORMAL
285.928 | 0.85 | 291.483 | 0.8 | 1 | 106868.78 | 13888.6284 | 6870.5795 | 1840.647 | NORMAL
285.928 | 0.85 | 291.483 | 0.8 | 2 | 57226.51 | 17964.7128 | 6151.6386 | 3475.538 | NORMAL
285.928 | 0.85 | 291.483 | 0.8 | 2 | 79289.74 | 18033.646 | 7543.6905 | 3051.61 | NORMAL
285.928 | 0.85 | 291.483 | 0.8 | 2 | 101352.97 | 17810.0527 | 8513.2943 | 2839.168 | NORMAL
285.928 | 0.85 | 291.483 | 0.8 | 2 | 106868.78 | 17646.6882 | 8671.7767 | 2798.195 | NORMAL
285.928 | 0.85 | 291.483 | 1.11 | 1 | 57226.51 | 14404.5721 | 4818.8623 | 2278.14 | NORMAL
285.928 | 0.85 | 291.483 | 1.11 | 1 | 79289.74 | 14652.6377 | 6264.3543 | 2002.198 | NORMAL
285.928 | 0.85 | 291.483 | 1.11 | 1 | 101352.97 | 14675.9086 | 7166.0407 | 1855.54 | NORMAL
285.928 | 0.85 | 291.483 | 1.11 | 1 | 106868.78 | 14562.6319 | 7458.0626 | 1830.501 | NORMAL
285.928 | 0.85 | 291.483 | 1.11 | 2 | 57226.51 | 18565.8558 | 6800.6544 | 3530.15 | NORMAL
285.928 | 0.85 | 291.483 | 1.11 | 2 | 79289.74 | 18908.7339 | 8137.6005 | 3102.122 | NORMAL
285.928 | 0.85 | 291.483 | 1.11 | 2 | 101352.97 | 18868.5522 | 9138.304 | 2885.128 | NORMAL
285.928 | 0.85 | 291.483 | 1.11 | 2 | 106868.78 | 18721.8347 | 9286.9661 | 2842.328 | NORMAL
285.928 | 0.85 | 291.483 | 1.42 | 1 | 57226.51 | 14644.2849 | 4879.9297 | 2285.39 | NORMAL
285.928 | 0.85 | 291.483 | 1.42 | 1 | 79289.74 | 14986.8699 | 6423.822 | 2003.39 | NORMAL
285.928 | 0.85 | 291.483 | 1.42 | 1 | 101352.97 | 15084.1442 | 7397.5509 | 1850.828 | NORMAL
285.928 | 0.85 | 291.483 | 1.42 | 1 | 106868.78 | 14983.4701 | 7970.7566 | 1824.617 | NORMAL
285.928 | 0.85 | 291.483 | 1.42 | 2 | 57226.51 | 18917.3505 | 6164.4268 | 3563.1 | NORMAL
285.928 | 0.85 | 291.483 | 1.42 | 2 | 79289.74 | 19439.2145 | 8141.4152 | 3133.45 | NORMAL
285.928 | 0.85 | 291.483 | 1.42 | 2 | 101352.97 | 19524.2087 | 9406.4904 | 2914.678 | NORMAL
285.928 | 0.85 | 291.483 | 1.42 | 2 | 106868.78 | 19389.449 | 9766.4073 | 2870.451 | NORMAL
285.928 | 0.85 | 294.26 | 0.5 | 1 | 57226.51 | 14386.8113 | 4417.7294 | 2278.036 | NORMAL
285.928 | 0.85 | 294.26 | 0.5 | 1 | 79289.74 | 14193.4349 | 5389.2472 | 2001.762 | NORMAL
285.928 | 0.85 | 294.26 | 0.5 | 1 | 101352.97 | 13871.2192 | 6114.4334 | 1865.088 | NORMAL
285.928 | 0.85 | 294.26 | 0.5 | 1 | 106868.78 | 13710.0235 | 6237.2381 | 1843.3452 | NORMAL
285.928 | 0.85 | 294.26 | 0.5 | 2 | 57226.51 | 18096.864 | 5527.7052 | 3486.752 | NORMAL
285.928 | 0.85 | 294.26 | 0.5 | 2 | 79289.74 | 17725.5275 | 6796.5522 | 3034.168 | NORMAL
285.928 | 0.85 | 294.26 | 0.5 | 2 | 101352.97 | 17175.7034 | 7712.7496 | 2812.293 | NORMAL
285.928 | 0.85 | 294.26 | 0.5 | 2 | 106868.78 | 16964.4197 | 7875.7997 | 2770.9742 | NORMAL
285.928 | 0.85 | 294.26 | 0.8 | 1 | 57226.51 | 15206.272 | 5053.5612 | 2301.576 | NORMAL
285.928 | 0.85 | 294.26 | 0.8 | 1 | 79289.74 | 15364.3025 | 6016.0309 | 2003.935 | NORMAL
285.928 | 0.85 | 294.26 | 0.8 | 1 | 101352.97 | 15277.9894 | 6798.8428 | 1848.315 | NORMAL
285.928 | 0.85 | 294.26 | 0.8 | 1 | 106868.78 | 15134.9062 | 6907.4047 | 1822.75 | NORMAL
285.928 | 0.85 | 294.26 | 0.8 | 2 | 57226.51 | 19386.313 | 5948.3994 | 3608.777 | NORMAL
285.928 | 0.85 | 294.26 | 0.8 | 2 | 79289.74 | 19566.354 | 7472.6841 | 3140.714 | NORMAL
285.928 | 0.85 | 294.26 | 0.8 | 2 | 101352.97 | 19355.6272 | 8509.5467 | 2906.708 | NORMAL
285.928 | 0.85 | 294.26 | 0.8 | 2 | 106868.78 | 19172.9484 | 8682.0479 | 2861.286 | NORMAL
285.928 | 0.85 | 294.26 | 1.11 | 1 | 57226.51 | 15585.3458 | 4766.5598 | 2312.88 | NORMAL
285.928 | 0.85 | 294.26 | 1.11 | 1 | 79289.74 | 15916.823 | 6249.8679 | 2006.712 | NORMAL
285.928 | 0.85 | 294.26 | 1.11 | 1 | 101352.97 | 15965.6213 | 7247.7056 | 1841.962 | NORMAL
285.928 | 0.85 | 294.26 | 1.11 | 1 | 106868.78 | 15836.313 | 7494.06 | 1813.617 | NORMAL
285.928 | 0.85 | 294.26 | 1.11 | 2 | 57226.51 | 19969.2263 | 6684.1194 | 3664.84 | NORMAL
285.928 | 0.85 | 294.26 | 1.11 | 2 | 79289.74 | 20449.6483 | 8054.2167 | 3194.197 | NORMAL
285.928 | 0.85 | 294.26 | 1.11 | 2 | 101352.97 | 20448.6811 | 9132.5855 | 2956.609 | NORMAL
285.928 | 0.85 | 294.26 | 1.11 | 2 | 106868.78 | 20286.694 | 9294.004 | 2909.2 | NORMAL
285.928 | 0.85 | 294.26 | 1.42 | 1 | 57226.51 | 15823.9742 | 4126.7501 | 2321.13 | NORMAL
285.928 | 0.85 | 294.26 | 1.42 | 1 | 79289.74 | 16255.6858 | 6171.7637 | 2008.22 | NORMAL
285.928 | 0.85 | 294.26 | 1.42 | 1 | 101352.97 | 16386.0199 | 7323.2073 | 1838.151 | NORMAL
285.928 | 0.85 | 294.26 | 1.42 | 1 | 106868.78 | 16273.9742 | 8054.3641 | 1808.416 | NORMAL
285.928 | 0.85 | 294.26 | 1.42 | 2 | 57226.51 | 20309.5838 | 6078.2929 | 3698.14 | NORMAL
285.928 | 0.85 | 294.26 | 1.42 | 2 | 79289.74 | 20982.2098 | 8064.911 | 3227.24 | NORMAL
285.928 | 0.85 | 294.26 | 1.42 | 2 | 101352.97 | 21121.0727 | 9455.2706 | 2988.67 | NORMAL
285.928 | 0.85 | 294.26 | 1.42 | 2 | 106868.78 | 20973.0363 | 9711.5645 | 2939.694 | NORMAL
285.928 | 0.85 | 297.037 | 0.5 | 1 | 57226.51 | 15643.9625 | 4274.525 | 2315.048 | NORMAL
285.928 | 0.85 | 297.037 | 0.5 | 1 | 79289.74 | 15499.0621 | 5342.6507 | 2004.407 | NORMAL
285.928 | 0.85 | 297.037 | 0.5 | 1 | 101352.97 | 15158.9977 | 6116.8829 | 1849.652 | NORMAL
285.928 | 0.85 | 297.037 | 0.5 | 1 | 106868.78 | 14975.9086 | 6249.4017 | 1824.7459 | NORMAL
285.928 | 0.85 | 297.037 | 0.5 | 2 | 57226.51 | 19604.7186 | 5369.5364 | 3628.313 | NORMAL
285.928 | 0.85 | 297.037 | 0.5 | 2 | 79289.74 | 19316.0317 | 6704.4207 | 3125.828 | NORMAL
285.928 | 0.85 | 297.037 | 0.5 | 2 | 101352.97 | 18735.3751 | 7695.2743 | 2879.257 | NORMAL
285.928 | 0.85 | 297.037 | 0.5 | 2 | 106868.78 | 18498.9742 | 7877.2702 | 2833.0976 | NORMAL
285.928 | 0.85 | 297.037 | 0.8 | 1 | 57226.51 | 16450.0293 | 5007.6357 | 2341.173 | NORMAL
285.928 | 0.85 | 297.037 | 0.8 | 1 | 79289.74 | 16694.197 | 5997.3569 | 2009.846 | NORMAL
285.928 | 0.85 | 297.037 | 0.8 | 1 | 101352.97 | 16626.3482 | 6799.9104 | 1835.457 | NORMAL
285.928 | 0.85 | 297.037 | 0.8 | 1 | 106868.78 | 16466.7057 | 6909.8743 | 1806.302 | NORMAL
285.928 | 0.85 | 297.037 | 0.8 | 2 | 57226.51 | 20858.2943 | 5658.1878 | 3747.596 | NORMAL
285.928 | 0.85 | 297.037 | 0.8 | 2 | 79289.74 | 21179.8359 | 7297.3854 | 3239.274 | NORMAL
285.928 | 0.85 | 297.037 | 0.8 | 2 | 101352.97 | 21000.2931 | 8461.3121 | 2982.342 | NORMAL
285.928 | 0.85 | 297.037 | 0.8 | 2 | 106868.78 | 20798.769 | 8644.2388 | 2931.887 | NORMAL
285.928 | 0.85 | 297.037 | 1.11 | 1 | 57226.51 | 16815.7093 | 4707.0197 | 2354.19 | NORMAL
285.928 | 0.85 | 297.037 | 1.11 | 1 | 79289.74 | 17251.0844 | 6263.3685 | 2014.732 | NORMAL
285.928 | 0.85 | 297.037 | 1.11 | 1 | 101352.97 | 17335.0527 | 7306.7941 | 1830.928 | NORMAL
285.928 | 0.85 | 297.037 | 1.11 | 1 | 106868.78 | 17190.9437 | 7525.2497 | 1798.681 | NORMAL
285.928 | 0.85 | 297.037 | 1.11 | 2 | 57226.51 | 21412.5147 | 6587.2818 | 3811.61 | NORMAL
285.928 | 0.85 | 297.037 | 1.11 | 2 | 79289.74 | 22061.6647 | 7976.5934 | 3295.55 | NORMAL
285.928 | 0.85 | 297.037 | 1.11 | 2 | 101352.97 | 22117.3798 | 9078.9632 | 3035.899 | NORMAL
285.928 | 0.85 | 297.037 | 1.11 | 2 | 106868.78 | 21941.5885 | 9250.0691 | 2983.762 | NORMAL
285.928 | 0.85 | 297.037 | 1.42 | 1 | 57226.51 | 17052.286 | 3534.001 | 2363.52 | NORMAL
285.928 | 0.85 | 297.037 | 1.42 | 1 | 79289.74 | 17587.6612 | 5677.7719 | 2017.35 | NORMAL
285.928 | 0.85 | 297.037 | 1.42 | 1 | 101352.97 | 17763.7163 | 7138.9356 | 1828.148 | NORMAL
285.928 | 0.85 | 297.037 | 1.42 | 1 | 106868.78 | 17637.7784 | 7893.4173 | 1794.348 | NORMAL
285.928 | 0.85 | 297.037 | 1.42 | 2 | 57226.51 | 21738.2767 | 5758.013 | 3845.36 | NORMAL
285.928 | 0.85 | 297.037 | 1.42 | 2 | 79289.74 | 22589.7714 | 8022.5992 | 3331.92 | NORMAL
285.928 | 0.85 | 297.037 | 1.42 | 2 | 101352.97 | 22799.0621 | 9470.2288 | 3070.675 | NORMAL
285.928 | 0.85 | 297.037 | 1.42 | 2 | 106868.78 | 22641.5006 | 9631.8528 | 3016.518 | NORMAL
285.928 | 0.85 | 299.814 | 0.5 | 1 | 57226.51 | 16948.4173 | 4056.9596 | 2358.705 | NORMAL
285.928 | 0.85 | 299.814 | 0.5 | 1 | 79289.74 | 16878.9859 | 5269.6532 | 2011.026 | NORMAL
285.928 | 0.85 | 299.814 | 0.5 | 1 | 101352.97 | 16533.7925 | 6084.353 | 1836.281 | NORMAL
285.928 | 0.85 | 299.814 | 0.5 | 1 | 106868.78 | 16329.1032 | 6226.7279 | 1807.874 | NORMAL
285.928 | 0.85 | 299.814 | 0.5 | 2 | 57226.51 | 21151.6706 | 5087.0402 | 3782.18 | NORMAL
285.928 | 0.85 | 299.814 | 0.5 | 2 | 79289.74 | 20989.6249 | 6574.4752 | 3227.378 | NORMAL
285.928 | 0.85 | 299.814 | 0.5 | 2 | 101352.97 | 20401.2603 | 7631.4586 | 2954.433 | NORMAL
285.928 | 0.85 | 299.814 | 0.5 | 2 | 106868.78 | 20137.4853 | 7828.2863 | 2902.764 | NORMAL
285.928 | 0.85 | 299.814 | 0.8 | 1 | 57226.51 | 17729.7186 | 4802.7503 | 2387.17 | NORMAL
285.928 | 0.85 | 299.814 | 0.8 | 1 | 79289.74 | 18084.7011 | 5914.0228 | 2020.275 | NORMAL
285.928 | 0.85 | 299.814 | 0.8 | 1 | 101352.97 | 18046.7761 | 6775.0124 | 1825.396 | NORMAL
285.928 | 0.85 | 299.814 | 0.8 | 1 | 106868.78 | 17870.5158 | 6872.7859 | 1792.405 | NORMAL
285.928 | 0.85 | 299.814 | 0.8 | 2 | 57226.51 | 22348.7104 | 5223.363 | 3909.522 | NORMAL
285.928 | 0.85 | 299.814 | 0.8 | 2 | 79289.74 | 22853.517 | 7082.7163 | 3347.169 | NORMAL
285.928 | 0.85 | 299.814 | 0.8 | 2 | 101352.97 | 22726.8464 | 8369.6157 | 3066.05 | NORMAL
285.928 | 0.85 | 299.814 | 0.8 | 2 | 106868.78 | 22508.9683 | 8557.7522 | 3010.29 | NORMAL
285.928 | 0.85 | 299.814 | 1.11 | 1 | 57226.51 | 18082.5615 | 5078.7044 | 2402.57 | NORMAL
285.928 | 0.85 | 299.814 | 1.11 | 1 | 79289.74 | 18641.6471 | 6229.8148 | 2027.77 | NORMAL
285.928 | 0.85 | 299.814 | 1.11 | 1 | 101352.97 | 18769.49 | 7386.0571 | 1821.503 | NORMAL
285.928 | 0.85 | 299.814 | 1.11 | 1 | 106868.78 | 18611.0785 | 7521.2393 | 1786.397 | NORMAL
285.928 | 0.85 | 299.814 | 1.11 | 2 | 57226.51 | 22879.3083 | 6510.9936 | 3966.77 | NORMAL
285.928 | 0.85 | 299.814 | 1.11 | 2 | 79289.74 | 23723.007 | 7856.9176 | 3405.8 | NORMAL
285.928 | 0.85 | 299.814 | 1.11 | 2 | 101352.97 | 23856.5651 | 9004.5173 | 3123.283 | NORMAL
285.928 | 0.85 | 299.814 | 1.11 | 2 | 106868.78 | 23669.3435 | 9151.2546 | 3065.927 | NORMAL
285.928 | 0.85 | 299.814 | 1.42 | 1 | 57226.51 | 18304.3963 | 2488.0617 | 2413.29 | NORMAL
285.928 | 0.85 | 299.814 | 1.42 | 1 | 79289.74 | 18973.476 | 5266.2211 | 2031.46 | NORMAL
285.928 | 0.85 | 299.814 | 1.42 | 1 | 101352.97 | 19203.4584 | 6994.8405 | 1821.707 | NORMAL
285.928 | 0.85 | 299.814 | 1.42 | 1 | 106868.78 | 19061.1665 | 7563.7187 | 1783.31 | NORMAL
285.928 | 0.85 | 299.814 | 1.42 | 2 | 57226.51 | 23188.4818 | 5373.8147 | 4000 | NORMAL
285.928 | 0.85 | 299.814 | 1.42 | 2 | 79289.74 | 24238.8042 | 7749.2184 | 3444.89 | NORMAL
285.928 | 0.85 | 299.814 | 1.42 | 2 | 101352.97 | 24541.1782 | 9515.621 | 3161.153 | NORMAL
285.928 | 0.85 | 299.814 | 1.42 | 2 | 106868.78 | 24375.4982 | 9465.4204 | 3100.863 | NORMAL
285.928 | 0.85 | 302.591 | 0.5 | 1 | 57226.51 | 18301.612 | 3755.3261 | 2410.093 | NORMAL
285.928 | 0.85 | 302.591 | 0.5 | 1 | 79289.74 | 18339.8593 | 5178.7361 | 2024.283 | NORMAL
285.928 | 0.85 | 302.591 | 0.5 | 1 | 101352.97 | 18002.1395 | 6023.1198 | 1825.661 | NORMAL
285.928 | 0.85 | 302.591 | 0.5 | 1 | 106868.78 | 17775.4396 | 6170.7439 | 1793.318 | NORMAL
285.928 | 0.85 | 302.591 | 0.5 | 2 | 57226.51 | 22732.7667 | 4760.3323 | 3955.632 | NORMAL
285.928 | 0.85 | 302.591 | 0.5 | 2 | 79289.74 | 22752.374 | 6413.6667 | 3340.426 | NORMAL
285.928 | 0.85 | 302.591 | 0.5 | 2 | 101352.97 | 22180.9496 | 7525.486 | 3039.167 | NORMAL
285.928 | 0.85 | 302.591 | 0.5 | 2 | 106868.78 | 21892.9074 | 7738.7487 | 2981.843 | NORMAL
285.928 | 0.85 | 302.591 | 0.8 | 1 | 57226.51 | 19051.6999 | 4592.0884 | 2440.402 | NORMAL
285.928 | 0.85 | 302.591 | 0.8 | 1 | 79289.74 | 19542.3505 | 5688.1333 | 2035.669 | NORMAL
285.928 | 0.85 | 302.591 | 0.8 | 1 | 101352.97 | 19543.6108 | 6701.0351 | 1818.558 | NORMAL
285.928 | 0.85 | 302.591 | 0.8 | 1 | 106868.78 | 19350.2931 | 6818.0564 | 1781.789 | NORMAL
285.928 | 0.85 | 302.591 | 0.8 | 2 | 57226.51 | 23855.5393 | 4811.1136 | 4081.524 | NORMAL
285.928 | 0.85 | 302.591 | 0.8 | 2 | 79289.74 | 24592.0574 | 6755.1923 | 3465.167 | NORMAL
285.928 | 0.85 | 302.591 | 0.8 | 2 | 101352.97 | 24542.7902 | 8236.8549 | 3159.126 | NORMAL
285.928 | 0.85 | 302.591 | 0.8 | 2 | 106868.78 | 24311.6647 | 8436.488 | 3097.722 | NORMAL
285.928 | 0.85 | 302.591 | 1.11 | 1 | 57226.51 | 19384.2028 | 5367.2144 | 2454.81 | NORMAL
285.928 | 0.85 | 302.591 | 1.11 | 1 | 79289.74 | 20092.7902 | 6370.4995 | 2042.336 | NORMAL
285.928 | 0.85 | 302.591 | 1.11 | 1 | 101352.97 | 20269.6366 | 7368.8034 | 1816.602 | NORMAL
285.928 | 0.85 | 302.591 | 1.11 | 1 | 106868.78 | 20095.6624 | 7518.4906 | 1777.775 | NORMAL
285.928 | 0.85 | 302.591 | 1.11 | 2 | 57226.51 | 24351.1723 | 6196.935 | 4139.3 | NORMAL
285.928 | 0.85 | 302.591 | 1.11 | 2 | 79289.74 | 25439.7421 | 7628.819 | 3525.952 | NORMAL
285.928 | 0.85 | 302.591 | 1.11 | 2 | 101352.97 | 25671.5416 | 8901.8124 | 3219.614 | NORMAL
285.928 | 0.85 | 302.591 | 1.11 | 2 | 106868.78 | 25475.9672 | 9013.117 | 3156.991 | NORMAL
285.928 | 0.85 | 302.591 | 1.42 | 1 | 57226.51 | 19594.4021 | 1052.5741 | 2463.92 | NORMAL
285.928 | 0.85 | 302.591 | 1.42 | 1 | 79289.74 | 20417.8195 | 4538.2687 | 2046.85 | NORMAL
285.928 | 0.85 | 302.591 | 1.42 | 1 | 101352.97 | 20702.2567 | 6917.39 | 1815.697 | NORMAL
285.928 | 0.85 | 302.591 | 1.42 | 1 | 106868.78 | 20541.5006 | 7278.9629 | 1775.359 | NORMAL
285.928 | 0.85 | 302.591 | 1.42 | 2 | 57226.51 | 24642.5264 | 5657.2341 | 4171.89 | NORMAL
285.928 | 0.85 | 302.591 | 1.42 | 2 | 79289.74 | 25942.0281 | 7712.5909 | 3561.83 | NORMAL
285.928 | 0.85 | 302.591 | 1.42 | 2 | 101352.97 | 26351.8171 | 9553.008 | 3256.263 | NORMAL
285.928 | 0.85 | 302.591 | 1.42 | 2 | 106868.78 | 26180.041 | 9353.7098 | 3194.17 | NORMAL
285.928 | 0.85 | 305.368 | 0.5 | 1 | 57226.51 | 19700.1465 | 3466.5757 | 2470.02 | NORMAL
285.928 | 0.85 | 305.368 | 0.5 | 1 | 79289.74 | 19873.2415 | 5016.3837 | 2039.309 | NORMAL
285.928 | 0.85 | 305.368 | 0.5 | 1 | 101352.97 | 19558.7925 | 5935.1156 | 1821.075 | NORMAL
285.928 | 0.85 | 305.368 | 0.5 | 1 | 106868.78 | 19307.9133 | 6086.1825 | 1780.933 | NORMAL
285.928 | 0.85 | 305.368 | 0.5 | 2 | 57226.51 | 24341.354 | 4302.6508 | 4138.584 | NORMAL
285.928 | 0.85 | 305.368 | 0.5 | 2 | 79289.74 | 24591.7937 | 6229.5194 | 3464.842 | NORMAL
285.928 | 0.85 | 305.368 | 0.5 | 2 | 101352.97 | 24069.6073 | 7383.7131 | 3134.61 | NORMAL
285.928 | 0.85 | 305.368 | 0.5 | 2 | 106868.78 | 23758.1184 | 7605.0212 | 3069.868 | NORMAL
285.928 | 0.85 | 305.368 | 0.8 | 1 | 57226.51 | 20408.8218 | 4354.2834 | 2501.384 | NORMAL
285.928 | 0.85 | 305.368 | 0.8 | 1 | 79289.74 | 21060.2286 | 5494.3399 | 2056.263 | NORMAL
285.928 | 0.85 | 305.368 | 0.8 | 1 | 101352.97 | 21096.1899 | 6459.358 | 1816.212 | NORMAL
285.928 | 0.85 | 305.368 | 0.8 | 1 | 106868.78 | 20893.8452 | 6743.6557 | 1774.629 | NORMAL
285.928 | 0.85 | 305.368 | 0.8 | 2 | 57226.51 | 25384.0563 | 4344.9635 | 4264.262 | NORMAL
285.928 | 0.85 | 305.368 | 0.8 | 2 | 79289.74 | 26383.8804 | 6275.5115 | 3594.659 | NORMAL
285.928 | 0.85 | 305.368 | 0.8 | 2 | 101352.97 | 26436.5768 | 7909.6387 | 3261.803 | NORMAL
285.928 | 0.85 | 305.368 | 0.8 | 2 | 106868.78 | 26194.4314 | 8284.1985 | 3195.065 | NORMAL
285.928 | 0.85 | 305.368 | 1.11 | 1 | 57226.51 | 20722.714 | 5444.3129 | 2518.31 | NORMAL
285.928 | 0.85 | 305.368 | 1.11 | 1 | 79289.74 | 21599.4138 | 6462.6526 | 2064.887 | NORMAL
285.928 | 0.85 | 305.368 | 1.11 | 1 | 101352.97 | 21819.9883 | 7299.6589 | 1815.259 | NORMAL
285.928 | 0.85 | 305.368 | 1.11 | 1 | 106868.78 | 21620.6624 | 7422.0275 | 1756.397 | NORMAL
285.928 | 0.85 | 305.368 | 1.11 | 2 | 57226.51 | 25844.109 | 5942.9046 | 4322.45 | NORMAL
285.928 | 0.85 | 305.368 | 1.11 | 2 | 79289.74 | 27201.8171 | 7417.6091 | 3656.91 | NORMAL
285.928 | 0.85 | 305.368 | 1.11 | 2 | 101352.97 | 27554.3963 | 8566.2209 | 3324.899 | NORMAL
285.928 | 0.85 | 305.368 | 1.11 | 2 | 106868.78 | 27352.5205 | 8850.4004 | 3257.993 | NORMAL
285.928 | 0.85 | 305.368 | 1.42 | 1 | 57226.51 | 20919.9003 | 4150.4036 | 2528.35 | NORMAL
285.928 | 0.85 | 305.368 | 1.42 | 1 | 79289.74 | 21917.6729 | 3752.2837 | 2070.13 | NORMAL
285.928 | 0.85 | 305.368 | 1.42 | 1 | 101352.97 | 22242.3798 | 6855.3684 | 1768.509 | NORMAL
285.928 | 0.85 | 305.368 | 1.42 | 1 | 106868.78 | 22076.993 | 6890.958 | 1686.668 | NORMAL
285.928 | 0.85 | 305.368 | 1.42 | 2 | 57226.51 | 26116.9695 | 5439.4857 | 4356.99 | NORMAL
285.928 | 0.85 | 305.368 | 1.42 | 2 | 79289.74 | 27685.6389 | 7589.6026 | 3692.91 | NORMAL
285.928 | 0.85 | 305.368 | 1.42 | 2 | 101352.97 | 28224.238 | 9379.1119 | 3362.787 | NORMAL
285.928 | 0.85 | 305.368 | 1.42 | 2 | 106868.78 | 28048.7104 | 9221.4623 | 3297.11 | NORMAL
285.928 | 0.95 | 288.706 | 0.5 | 1 | 57226.51 | 12582.415 | 3869.533 | 2233.587 | NORMAL
285.928 | 0.95 | 288.706 | 0.5 | 1 | 79289.74 | 12310.0235 | 4800.5522 | 2003.897 | NORMAL
285.928 | 0.95 | 288.706 | 0.5 | 1 | 101352.97 | 11991.7644 | 5492.6478 | 1892.502 | NORMAL
285.928 | 0.95 | 288.706 | 0.5 | 1 | 106868.78 | 11864.4783 | 5623.3356 | 1875.1752 | NORMAL
285.928 | 0.95 | 288.706 | 0.5 | 2 | 57226.51 | 15907.6495 | 4958.7802 | 3295.347 | NORMAL
285.928 | 0.95 | 288.706 | 0.5 | 2 | 79289.74 | 15386.5182 | 6177.6255 | 2906.87 | NORMAL
285.928 | 0.95 | 288.706 | 0.5 | 2 | 101352.97 | 14897.8605 | 7080.6402 | 2719.74 | NORMAL
285.928 | 0.95 | 288.706 | 0.5 | 2 | 106868.78 | 14728.8101 | 7254.6459 | 2685.372 | NORMAL
285.928 | 0.95 | 288.706 | 0.8 | 1 | 57226.51 | 13403.2825 | 4004.7534 | 2252.609 | NORMAL
285.928 | 0.95 | 288.706 | 0.8 | 1 | 79289.74 | 13417.4678 | 5064.0073 | 2001.782 | NORMAL
285.928 | 0.95 | 288.706 | 0.8 | 1 | 101352.97 | 13279.66 | 5846.6094 | 1872.987 | NORMAL
285.928 | 0.95 | 288.706 | 0.8 | 1 | 106868.78 | 13154.6014 | 5987.7904 | 1852.189 | NORMAL
285.928 | 0.95 | 288.706 | 0.8 | 2 | 57226.51 | 17224.8242 | 5229.4049 | 3408.225 | NORMAL
285.928 | 0.95 | 288.706 | 0.8 | 2 | 79289.74 | 17183.646 | 6585.7354 | 3004.051 | NORMAL
285.928 | 0.95 | 288.706 | 0.8 | 2 | 101352.97 | 16906.4185 | 7584.8618 | 2801.182 | NORMAL
285.928 | 0.95 | 288.706 | 0.8 | 2 | 106868.78 | 16754.1618 | 7794.4382 | 2762.69 | NORMAL
285.928 | 0.95 | 288.706 | 1.11 | 1 | 57226.51 | 13771.8347 | 4074.0392 | 2261.79 | NORMAL
285.928 | 0.95 | 288.706 | 1.11 | 1 | 79289.74 | 13948.5932 | 5244.5176 | 2001.646 | NORMAL
285.928 | 0.95 | 288.706 | 1.11 | 1 | 101352.97 | 13922.0692 | 6066.834 | 1864.228 | NORMAL
285.928 | 0.95 | 288.706 | 1.11 | 1 | 106868.78 | 13804.3376 | 6205.174 | 1842.05 | NORMAL
285.928 | 0.95 | 288.706 | 1.11 | 2 | 57226.51 | 17831.6237 | 5167.0339 | 3463.05 | NORMAL
285.928 | 0.95 | 288.706 | 1.11 | 2 | 79289.74 | 18050.3224 | 6805.3867 | 3053.215 | NORMAL
285.928 | 0.95 | 288.706 | 1.11 | 2 | 101352.97 | 17940.5041 | 7886.6097 | 2844.977 | NORMAL
285.928 | 0.95 | 288.706 | 1.11 | 2 | 106868.78 | 17792.1747 | 8085.974 | 2804.183 | NORMAL
285.928 | 0.95 | 288.706 | 1.42 | 1 | 57226.51 | 13979.5721 | 4187.6507 | 2267.06 | NORMAL
285.928 | 0.95 | 288.706 | 1.42 | 1 | 79289.74 | 14265.8558 | 5405.1758 | 2002.27 | NORMAL
285.928 | 0.95 | 288.706 | 1.42 | 1 | 101352.97 | 14313.9214 | 6244.6773 | 1860.161 | NORMAL
285.928 | 0.95 | 288.706 | 1.42 | 1 | 106868.78 | 14203.0774 | 6375.5342 | 1836.072 | NORMAL
285.928 | 0.95 | 288.706 | 1.42 | 2 | 57226.51 | 18187.0164 | 5223.2384 | 3494.92 | NORMAL
285.928 | 0.95 | 288.706 | 1.42 | 2 | 79289.74 | 18577.6084 | 6981.8368 | 3083.71 | NORMAL
285.928 | 0.95 | 288.706 | 1.42 | 2 | 101352.97 | 18583.1477 | 8104.2222 | 2872.91 | NORMAL
285.928 | 0.95 | 288.706 | 1.42 | 2 | 106868.78 | 18445.0469 | 8300.8245 | 2830.97 | NORMAL
285.928 | 0.95 | 291.483 | 0.5 | 1 | 57226.51 | 13779.1618 | 3738.6035 | 2262.048 | NORMAL
285.928 | 0.95 | 291.483 | 0.5 | 1 | 79289.74 | 13519.3728 | 4741.7578 | 2001.752 | NORMAL
285.928 | 0.95 | 291.483 | 0.5 | 1 | 101352.97 | 13169.578 | 5502.355 | 1874.603 | NORMAL
285.928 | 0.95 | 291.483 | 0.5 | 1 | 106868.78 | 13012.3974 | 5642.9563 | 1854.6312 | NORMAL
285.928 | 0.95 | 291.483 | 0.5 | 2 | 57226.51 | 17361.9578 | 4777.4031 | 3421.496 | NORMAL
285.928 | 0.95 | 291.483 | 0.5 | 2 | 79289.74 | 16903.8101 | 6120.1766 | 2988.487 | NORMAL
285.928 | 0.95 | 291.483 | 0.5 | 2 | 101352.97 | 16256.4771 | 7051.1007 | 2775.464 | NORMAL
285.928 | 0.95 | 291.483 | 0.5 | 2 | 106868.78 | 16077.0809 | 7251.0368 | 2736.3043 | NORMAL
285.928 | 0.95 | 291.483 | 0.8 | 1 | 57226.51 | 14602.2274 | 3835.3773 | 2283.899 | NORMAL
285.928 | 0.95 | 291.483 | 0.8 | 1 | 79289.74 | 14672.626 | 4993.975 | 2002.191 | NORMAL
285.928 | 0.95 | 291.483 | 0.8 | 1 | 101352.97 | 14535.3751 | 5828.9761 | 1856.674 | NORMAL
285.928 | 0.95 | 291.483 | 0.8 | 1 | 106868.78 | 14392.4091 | 5983.6009 | 1832.936 | NORMAL
285.928 | 0.95 | 291.483 | 0.8 | 2 | 57226.51 | 18666.9988 | 4964.3203 | 3539.129 | NORMAL
285.928 | 0.95 | 291.483 | 0.8 | 2 | 79289.74 | 18721.2192 | 6460.1686 | 3091.23 | NORMAL
285.928 | 0.95 | 291.483 | 0.8 | 2 | 101352.97 | 18447.8312 | 7535.0166 | 2866.791 | NORMAL
285.928 | 0.95 | 291.483 | 0.8 | 2 | 106868.78 | 18264.3611 | 7762.9562 | 2823.448 | NORMAL
285.928 | 0.95 | 291.483 | 1.11 | 1 | 57226.51 | 14967.0868 | 3697.08 | 2294.4 | NORMAL
285.928 | 0.95 | 291.483 | 1.11 | 1 | 79289.74 | 15220.8382 | 5169.7425 | 2003.419 | NORMAL
285.928 | 0.95 | 291.483 | 1.11 | 1 | 101352.97 | 15209.408 | 6039.9449 | 1848.849 | NORMAL
285.928 | 0.95 | 291.483 | 1.11 | 1 | 106868.78 | 15077.2274 | 6189.0963 | 1823.207 | NORMAL
285.928 | 0.95 | 291.483 | 1.11 | 2 | 57226.51 | 19257.034 | 4729.5275 | 3593.19 | NORMAL
285.928 | 0.95 | 291.483 | 1.11 | 2 | 79289.74 | 19602.3447 | 6662.8566 | 3143.649 | NORMAL
285.928 | 0.95 | 291.483 | 1.11 | 2 | 101352.97 | 19522.1278 | 7815.4691 | 2914.567 | NORMAL
285.928 | 0.95 | 291.483 | 1.11 | 2 | 106868.78 | 19356.6823 | 8032.3263 | 2869.158 | NORMAL
285.928 | 0.95 | 291.483 | 1.42 | 1 | 57226.51 | 15172.7433 | 3940.6801 | 2300.36 | NORMAL
285.928 | 0.95 | 291.483 | 1.42 | 1 | 79289.74 | 15542.9074 | 5236.1568 | 2005.3 | NORMAL
285.928 | 0.95 | 291.483 | 1.42 | 1 | 101352.97 | 15618.347 | 6215.368 | 1845.743 | NORMAL
285.928 | 0.95 | 291.483 | 1.42 | 1 | 106868.78 | 15493.8453 | 6354.2893 | 1818.373 | NORMAL
285.928 | 0.95 | 291.483 | 1.42 | 2 | 57226.51 | 19605.51 | 4647.741 | 3628.81 | NORMAL
285.928 | 0.95 | 291.483 | 1.42 | 2 | 79289.74 | 20135.6096 | 6822.0855 | 3175.94 | NORMAL
285.928 | 0.95 | 291.483 | 1.42 | 2 | 101352.97 | 20185.4631 | 8019.523 | 2944.895 | NORMAL
285.928 | 0.95 | 291.483 | 1.42 | 2 | 106868.78 | 20033.4994 | 8231.8651 | 2898.323 | NORMAL
285.928 | 0.95 | 294.26 | 0.5 | 1 | 57226.51 | 15036.694 | 3641.6768 | 2296.453 | NORMAL
285.928 | 0.95 | 294.26 | 0.5 | 1 | 79289.74 | 14813.1008 | 4653.6838 | 2002.468 | NORMAL
285.928 | 0.95 | 294.26 | 0.5 | 1 | 101352.97 | 14438.1594 | 5473.6506 | 1857.895 | NORMAL
285.928 | 0.95 | 294.26 | 0.5 | 1 | 106868.78 | 14258.6753 | 5628.9115 | 1834.9091 | NORMAL
285.928 | 0.95 | 294.26 | 0.5 | 2 | 57226.51 | 18877.6671 | 4551.8775 | 3560.256 | NORMAL
285.928 | 0.95 | 294.26 | 0.5 | 2 | 79289.74 | 18481.3306 | 5972.242 | 3077.256 | NORMAL
285.928 | 0.95 | 294.26 | 0.5 | 2 | 101352.97 | 17862.075 | 7030.4591 | 2841.542 | NORMAL
285.928 | 0.95 | 294.26 | 0.5 | 2 | 106868.78 | 17630.0117 | 7253.3571 | 2797.6 | NORMAL
285.928 | 0.95 | 294.26 | 0.8 | 1 | 57226.51 | 15849.5311 | 3522.0511 | 2321.216 | NORMAL
285.928 | 0.95 | 294.26 | 0.8 | 1 | 79289.74 | 15997.8605 | 4891.5538 | 2006.222 | NORMAL
285.928 | 0.95 | 294.26 | 0.8 | 1 | 101352.97 | 15873.9742 | 5774.3804 | 1842.142 | NORMAL
285.928 | 0.95 | 294.26 | 0.8 | 1 | 106868.78 | 15713.306 | 5940.3053 | 1815.053 | NORMAL
285.928 | 0.95 | 294.26 | 0.8 | 2 | 57226.51 | 20149.6776 | 4670.2318 | 3681.836 | NORMAL
285.928 | 0.95 | 294.26 | 0.8 | 2 | 79289.74 | 20335.4631 | 6291.3652 | 3187.267 | NORMAL
285.928 | 0.95 | 294.26 | 0.8 | 2 | 101352.97 | 20082.5615 | 7430.7084 | 2939.961 | NORMAL
285.928 | 0.95 | 294.26 | 0.8 | 2 | 106868.78 | 19879.9531 | 7681.8723 | 2891.564 | NORMAL
285.928 | 0.95 | 294.26 | 1.11 | 1 | 57226.51 | 16206.3599 | 3375.2013 | 2332.82 | NORMAL
285.928 | 0.95 | 294.26 | 1.11 | 1 | 79289.74 | 16554.7186 | 5031.9061 | 2009.032 | NORMAL
285.928 | 0.95 | 294.26 | 1.11 | 1 | 101352.97 | 16572.7726 | 5974.3354 | 1835.647 | NORMAL
285.928 | 0.95 | 294.26 | 1.11 | 1 | 106868.78 | 16425.9379 | 6131.7205 | 1806.528 | NORMAL
285.928 | 0.95 | 294.26 | 1.11 | 2 | 57226.51 | 20717.6729 | 4234.5266 | 3737.02 | NORMAL
285.928 | 0.95 | 294.26 | 1.11 | 2 | 79289.74 | 21219.578 | 6480.4803 | 3242.768 | NORMAL
285.928 | 0.95 | 294.26 | 1.11 | 2 | 101352.97 | 21188.0129 | 7691.9055 | 2991.578 | NORMAL
285.928 | 0.95 | 294.26 | 1.11 | 2 | 106868.78 | 21007.8839 | 7921.968 | 2941.388 | NORMAL
285.928 | 0.95 | 294.26 | 1.42 | 1 | 57226.51 | 16408.6166 | 3549.8565 | 2339.58 | NORMAL
285.928 | 0.95 | 294.26 | 1.42 | 1 | 79289.74 | 16880.4807 | 5064.6675 | 2012.2 | NORMAL
285.928 | 0.95 | 294.26 | 1.42 | 1 | 101352.97 | 16994.9297 | 6154.2549 | 1833.857 | NORMAL
285.928 | 0.95 | 294.26 | 1.42 | 1 | 106868.78 | 16858.4994 | 6292.6709 | 1801.842 | NORMAL
285.928 | 0.95 | 294.26 | 1.42 | 2 | 57226.51 | 21045.6624 | 4152.4986 | 3769.36 | NORMAL
285.928 | 0.95 | 294.26 | 1.42 | 2 | 79289.74 | 21751.4068 | 6437.9814 | 3276.71 | NORMAL
285.928 | 0.95 | 294.26 | 1.42 | 2 | 101352.97 | 21865.7679 | 7883.5714 | 3024.149 | NORMAL
285.928 | 0.95 | 294.26 | 1.42 | 2 | 106868.78 | 21701.5533 | 8105.617 | 2972.933 | NORMAL
285.928 | 0.95 | 297.037 | 0.5 | 1 | 57226.51 | 16360.9906 | 3457.5354 | 2337.926 | NORMAL
285.928 | 0.95 | 297.037 | 0.5 | 1 | 79289.74 | 16200.3224 | 4518.6749 | 2007.178 | NORMAL
285.928 | 0.95 | 297.037 | 0.5 | 1 | 101352.97 | 15811.6647 | 5406.9094 | 1842.807 | NORMAL
285.928 | 0.95 | 297.037 | 0.5 | 1 | 106868.78 | 15607.4736 | 5579.6874 | 1816.422 | NORMAL
285.928 | 0.95 | 297.037 | 0.5 | 2 | 57226.51 | 20453.8101 | 4264.8035 | 3714.387 | NORMAL
285.928 | 0.95 | 297.037 | 0.5 | 2 | 79289.74 | 20167.3505 | 5762.4977 | 3176.883 | NORMAL
285.928 | 0.95 | 297.037 | 0.5 | 2 | 101352.97 | 19526.6413 | 6928.3452 | 2914.508 | NORMAL
285.928 | 0.95 | 297.037 | 0.5 | 2 | 106868.78 | 19264.3904 | 7179.7227 | 2865.2696 | NORMAL
285.928 | 0.95 | 297.037 | 0.8 | 1 | 57226.51 | 17153.1067 | 3213.3429 | 2365.498 | NORMAL
285.928 | 0.95 | 297.037 | 0.8 | 1 | 79289.74 | 17402.6964 | 4767.1728 | 2014.543 | NORMAL
285.928 | 0.95 | 297.037 | 0.8 | 1 | 101352.97 | 17302.6964 | 5683.8319 | 1830.034 | NORMAL
285.928 | 0.95 | 297.037 | 0.8 | 1 | 106868.78 | 17124.7655 | 5860.2146 | 1799.269 | NORMAL
285.928 | 0.95 | 297.037 | 0.8 | 2 | 57226.51 | 21674.6776 | 4371.4574 | 3839.547 | NORMAL
285.928 | 0.95 | 297.037 | 0.8 | 2 | 79289.74 | 22033.3822 | 6021.5471 | 3293.958 | NORMAL
285.928 | 0.95 | 297.037 | 0.8 | 2 | 101352.97 | 21822.4502 | 7265.6757 | 3021.865 | NORMAL
285.928 | 0.95 | 297.037 | 0.8 | 2 | 106868.78 | 21600.7327 | 7552.329 | 2968.246 | NORMAL
285.928 | 0.95 | 297.037 | 1.11 | 1 | 57226.51 | 17498.5346 | 2955.0475 | 2378.28 | NORMAL
285.928 | 0.95 | 297.037 | 1.11 | 1 | 79289.74 | 17962.6905 | 4879.511 | 2019.073 | NORMAL
285.928 | 0.95 | 297.037 | 1.11 | 1 | 101352.97 | 18019.6366 | 5877.555 | 1825.235 | NORMAL
285.928 | 0.95 | 297.037 | 1.11 | 1 | 106868.78 | 17857.8253 | 6040.1058 | 1792.244 | NORMAL
285.928 | 0.95 | 297.037 | 1.11 | 2 | 57226.51 | 22217.6729 | 3656.1847 | 3893.77 | NORMAL
285.928 | 0.95 | 297.037 | 1.11 | 2 | 79289.74 | 22909.789 | 6208.255 | 3352.158 | NORMAL
285.928 | 0.95 | 297.037 | 1.11 | 2 | 101352.97 | 22946.6882 | 7521.7867 | 3077.49 | NORMAL
285.928 | 0.95 | 297.037 | 1.11 | 2 | 106868.78 | 22753.7222 | 7759.5653 | 3021.987 | NORMAL
285.928 | 0.95 | 297.037 | 1.42 | 1 | 57226.51 | 17694.1676 | 3268.9267 | 2385.66 | NORMAL
285.928 | 0.95 | 297.037 | 1.42 | 1 | 79289.74 | 18289.3611 | 4728.4948 | 2024.1 | NORMAL
285.928 | 0.95 | 297.037 | 1.42 | 1 | 101352.97 | 18451.1137 | 6045.3229 | 1825.235 | NORMAL
285.928 | 0.95 | 297.037 | 1.42 | 1 | 106868.78 | 18301.4654 | 6200.2986 | 1788.464 | NORMAL
285.928 | 0.95 | 297.037 | 1.42 | 2 | 57226.51 | 22529.9238 | 3577.9096 | 3926.53 | NORMAL
285.928 | 0.95 | 297.037 | 1.42 | 2 | 79289.74 | 23434.2907 | 6095.1184 | 3387.51 | NORMAL
285.928 | 0.95 | 297.037 | 1.42 | 2 | 101352.97 | 23631.4478 | 7692.887 | 3112.272 | NORMAL
285.928 | 0.95 | 297.037 | 1.42 | 2 | 106868.78 | 23456.9168 | 7935.7095 | 3055.825 | NORMAL
285.928 | 0.95 | 299.814 | 0.5 | 1 | 57226.51 | 17725.2931 | 3156.3607 | 2387.036 | NORMAL
285.928 | 0.95 | 299.814 | 0.5 | 1 | 79289.74 | 17660.6096 | 4336.2625 | 2016.56 | NORMAL
285.928 | 0.95 | 299.814 | 0.5 | 1 | 101352.97 | 17273.2708 | 5299.4568 | 1830.303 | NORMAL
285.928 | 0.95 | 299.814 | 0.5 | 1 | 106868.78 | 17047.4502 | 5496.0127 | 1800.055 | NORMAL
285.928 | 0.95 | 299.814 | 0.5 | 2 | 57226.51 | 22062.9543 | 4002.8156 | 3879.465 | NORMAL
285.928 | 0.95 | 299.814 | 0.5 | 2 | 79289.74 | 21934.4666 | 5473.79 | 3287.336 | NORMAL
285.928 | 0.95 | 299.814 | 0.5 | 2 | 101352.97 | 21298.2708 | 6756.9403 | 2996.549 | NORMAL
285.928 | 0.95 | 299.814 | 0.5 | 2 | 106868.78 | 21009.6718 | 7059.88 | 2941.272 | NORMAL
285.928 | 0.95 | 299.814 | 0.8 | 1 | 57226.51 | 18487.3095 | 2731.8143 | 2416.745 | NORMAL
285.928 | 0.95 | 299.814 | 0.8 | 1 | 79289.74 | 18866.9695 | 4610.6723 | 2027.831 | NORMAL
285.928 | 0.95 | 299.814 | 0.8 | 1 | 101352.97 | 18803.4291 | 5562.8253 | 1821.222 | NORMAL
285.928 | 0.95 | 299.814 | 0.8 | 1 | 106868.78 | 18608.7632 | 5742.9435 | 1786.319 | NORMAL
285.928 | 0.95 | 299.814 | 0.8 | 2 | 57226.51 | 23218.6108 | 3694.3132 | 4003.767 | NORMAL
285.928 | 0.95 | 299.814 | 0.8 | 2 | 79289.74 | 23787.6612 | 5803.8325 | 3410.855 | NORMAL
285.928 | 0.95 | 299.814 | 0.8 | 2 | 101352.97 | 23644.959 | 7104.5299 | 3113.313 | NORMAL
285.928 | 0.95 | 299.814 | 0.8 | 2 | 106868.78 | 23407.3271 | 7373.7294 | 3053.353 | NORMAL
285.928 | 0.95 | 299.814 | 1.11 | 1 | 57226.51 | 18817.9074 | 2257.9795 | 2429.01 | NORMAL
285.928 | 0.95 | 299.814 | 1.11 | 1 | 79289.74 | 19421.4244 | 4364.4019 | 2034.111 | NORMAL
285.928 | 0.95 | 299.814 | 1.11 | 1 | 101352.97 | 19529.6893 | 5749.5015 | 1818.26 | NORMAL
285.928 | 0.95 | 299.814 | 1.11 | 1 | 106868.78 | 19353.3412 | 5913.7617 | 1781.284 | NORMAL
285.928 | 0.95 | 299.814 | 1.11 | 2 | 57226.51 | 23724.2087 | 2887.7344 | 4059.84 | NORMAL
285.928 | 0.95 | 299.814 | 1.11 | 2 | 79289.74 | 24646.6588 | 5750.0162 | 3469.888 | NORMAL
285.928 | 0.95 | 299.814 | 1.11 | 2 | 101352.97 | 24775.0293 | 7312.0031 | 3171.851 | NORMAL
285.928 | 0.95 | 299.814 | 1.11 | 2 | 106868.78 | 24571.7175 | 7555.41 | 3110.928 | NORMAL
285.928 | 0.95 | 299.814 | 1.42 | 1 | 57226.51 | 19006.8582 | 2466.4249 | 2436.69 | NORMAL
285.928 | 0.95 | 299.814 | 1.42 | 1 | 79289.74 | 19747.5674 | 4341.088 | 2041.77 | NORMAL
285.928 | 0.95 | 299.814 | 1.42 | 1 | 101352.97 | 19963.8335 | 5653.0988 | 1817.044 | NORMAL
285.928 | 0.95 | 299.814 | 1.42 | 1 | 106868.78 | 19800.8793 | 6074.3157 | 1778.735 | NORMAL
285.928 | 0.95 | 299.814 | 1.42 | 2 | 57226.51 | 24018.9332 | 2617.0309 | 4093.5 | NORMAL
285.928 | 0.95 | 299.814 | 1.42 | 2 | 79289.74 | 25156.5944 | 5473.2699 | 3507.5 | NORMAL
285.928 | 0.95 | 299.814 | 1.42 | 2 | 101352.97 | 25458.2943 | 7381.5051 | 3208.716 | NORMAL
285.928 | 0.95 | 299.814 | 1.42 | 2 | 106868.78 | 25277.1395 | 7723.9102 | 3147.087 | NORMAL
285.928 | 0.95 | 302.591 | 0.5 | 1 | 57226.51 | 19140.3282 | 2940.5286 | 2444.313 | NORMAL
285.928 | 0.95 | 302.591 | 0.5 | 1 | 79289.74 | 19202.4912 | 4224.4905 | 2031.879 | NORMAL
285.928 | 0.95 | 302.591 | 0.5 | 1 | 101352.97 | 18831.7116 | 5151.829 | 1821.165 | NORMAL
285.928 | 0.95 | 302.591 | 0.5 | 1 | 106868.78 | 18583.4408 | 5382.4892 | 1786.463 | NORMAL
285.928 | 0.95 | 302.591 | 0.5 | 2 | 57226.51 | 23705.7151 | 3701.3155 | 4061.297 | NORMAL
285.928 | 0.95 | 302.591 | 0.5 | 2 | 79289.74 | 23787.2216 | 5142.6308 | 3410.499 | NORMAL
285.928 | 0.95 | 302.591 | 0.5 | 2 | 101352.97 | 23187.0457 | 6524.1391 | 3089.271 | NORMAL
285.928 | 0.95 | 302.591 | 0.5 | 2 | 106868.78 | 22874.4431 | 6891.2234 | 3027.38 | NORMAL
285.928 | 0.95 | 302.591 | 0.8 | 1 | 57226.51 | 19863.7163 | 2222.4519 | 2476.202 | NORMAL
285.928 | 0.95 | 302.591 | 0.8 | 1 | 79289.74 | 20397.9484 | 4408.2822 | 2046.755 | NORMAL
285.928 | 0.95 | 302.591 | 0.8 | 1 | 101352.97 | 20377.4033 | 5410.8323 | 1816.384 | NORMAL
285.928 | 0.95 | 302.591 | 0.8 | 1 | 106868.78 | 20164.3025 | 5594.4446 | 1777.333 | NORMAL
285.928 | 0.95 | 302.591 | 0.8 | 2 | 57226.51 | 24777.6378 | 3382.767 | 4190.073 | NORMAL
285.928 | 0.95 | 302.591 | 0.8 | 2 | 79289.74 | 25603.517 | 5426.8959 | 3538.803 | NORMAL
285.928 | 0.95 | 302.591 | 0.8 | 2 | 101352.97 | 25555.3927 | 6822.5743 | 3214.325 | NORMAL
285.928 | 0.95 | 302.591 | 0.8 | 2 | 106868.78 | 25306.1841 | 7156.2599 | 3149.017 | NORMAL
285.928 | 0.95 | 302.591 | 1.11 | 1 | 57226.51 | 20171.0434 | 1812.4792 | 2488.88 | NORMAL
285.928 | 0.95 | 302.591 | 1.11 | 1 | 79289.74 | 20945.4572 | 4208.6964 | 2055.139 | NORMAL
285.928 | 0.95 | 302.591 | 1.11 | 1 | 101352.97 | 21096.8054 | 5583.9868 | 1815.144 | NORMAL
285.928 | 0.95 | 302.591 | 1.11 | 1 | 106868.78 | 20900.4689 | 5758.6853 | 1773.963 | NORMAL
285.928 | 0.95 | 302.591 | 1.11 | 2 | 57226.51 | 25246.8933 | 2327.4959 | 4249.8 | NORMAL
285.928 | 0.95 | 302.591 | 1.11 | 2 | 79289.74 | 26435.1993 | 5210.7743 | 3599.989 | NORMAL
285.928 | 0.95 | 302.591 | 1.11 | 2 | 101352.97 | 26678.7515 | 7057.6503 | 3276.916 | NORMAL
285.928 | 0.95 | 302.591 | 1.11 | 2 | 106868.78 | 26467.1747 | 7310.4189 | 3210.703 | NORMAL
285.928 | 0.95 | 302.591 | 1.42 | 1 | 57226.51 | 20358.2943 | 2191.1225 | 2496.56 | NORMAL
285.928 | 0.95 | 302.591 | 1.42 | 1 | 79289.74 | 21266.2661 | 3830.3097 | 2059.82 | NORMAL
285.928 | 0.95 | 302.591 | 1.42 | 1 | 101352.97 | 21532.4736 | 5446.7253 | 1815.338 | NORMAL
285.928 | 0.95 | 302.591 | 1.42 | 1 | 106868.78 | 21354.9531 | 5933.8368 | 1771.652 | NORMAL
285.928 | 0.95 | 302.591 | 1.42 | 2 | 57226.51 | 25529.6893 | 1615.5851 | 4281.77 | NORMAL
285.928 | 0.95 | 302.591 | 1.42 | 2 | 79289.74 | 26927.9015 | 4781.5875 | 3637.19 | NORMAL
285.928 | 0.95 | 302.591 | 1.42 | 2 | 101352.97 | 27354.8066 | 6747.2819 | 3314.397 | NORMAL
285.928 | 0.95 | 302.591 | 1.42 | 2 | 106868.78 | 27167.7902 | 7487.1985 | 3248.165 | NORMAL
285.928 | 0.95 | 305.368 | 0.5 | 1 | 57226.51 | 20594.0211 | 2713.633 | 2510.498 | NORMAL
285.928 | 0.95 | 305.368 | 0.5 | 1 | 79289.74 | 20818.2005 | 3962.0783 | 2052.811 | NORMAL
285.928 | 0.95 | 305.368 | 0.5 | 1 | 101352.97 | 20472.626 | 4972.2686 | 1816.891 | NORMAL
285.928 | 0.95 | 305.368 | 0.5 | 1 | 106868.78 | 20201.524 | 5238.9016 | 1776.572 | NORMAL
285.928 | 0.95 | 305.368 | 0.5 | 2 | 57226.51 | 25355.8617 | 3311.4248 | 4260.66 | NORMAL
285.928 | 0.95 | 305.368 | 0.5 | 2 | 79289.74 | 25714.7421 | 4759.2073 | 3547.05 | NORMAL
285.928 | 0.95 | 305.368 | 0.5 | 2 | 101352.97 | 25185.551 | 6201.9419 | 3194.553 | NORMAL
285.928 | 0.95 | 305.368 | 0.5 | 2 | 106868.78 | 24852.0223 | 6682.1123 | 3124.515 | NORMAL
285.928 | 0.95 | 305.368 | 0.8 | 1 | 57226.51 | 21265.0645 | 1437.0931 | 2540.949 | NORMAL
285.928 | 0.95 | 305.368 | 0.8 | 1 | 79289.74 | 21988.4232 | 4053.9176 | 2073.118 | NORMAL
285.928 | 0.95 | 305.368 | 0.8 | 1 | 101352.97 | 22002.6671 | 5239.9792 | 1804.19 | NORMAL
285.928 | 0.95 | 305.368 | 0.8 | 1 | 106868.78 | 21779.4256 | 5418.8953 | 1733.129 | NORMAL
285.928 | 0.95 | 305.368 | 0.8 | 2 | 57226.51 | 26341.6178 | 2912.5927 | 4385.665 | NORMAL
285.928 | 0.95 | 305.368 | 0.8 | 2 | 79289.74 | 27471.6882 | 5041.9064 | 3679.03 | NORMAL
285.928 | 0.95 | 305.368 | 0.8 | 2 | 101352.97 | 27544.6073 | 6465.766 | 3325.862 | NORMAL
285.928 | 0.95 | 305.368 | 0.8 | 2 | 106868.78 | 27286.4009 | 6905.6423 | 3255.485 | NORMAL
285.928 | 0.95 | 305.368 | 1.11 | 1 | 57226.51 | 21561.5475 | 971.4102 | 2559.18 | NORMAL
285.928 | 0.95 | 305.368 | 1.11 | 1 | 79289.74 | 22518.347 | 3621.1303 | 2083.807 | NORMAL
285.928 | 0.95 | 305.368 | 1.11 | 1 | 101352.97 | 22717.7902 | 5351.4708 | 1692.283 | NORMAL
285.928 | 0.95 | 305.368 | 1.11 | 1 | 106868.78 | 22520.2227 | 5593.7531 | 1616.113 | NORMAL
285.928 | 0.95 | 305.368 | 1.11 | 2 | 57226.51 | 26779.5721 | 1279.8359 | 4441.95 | NORMAL
285.928 | 0.95 | 305.368 | 1.11 | 2 | 79289.74 | 28266.6471 | 4718.3818 | 3741.52 | NORMAL
285.928 | 0.95 | 305.368 | 1.11 | 2 | 101352.97 | 28650.7034 | 6683.0631 | 3390.618 | NORMAL
285.928 | 0.95 | 305.368 | 1.11 | 2 | 106868.78 | 28434.2614 | 7047.1474 | 3320.492 | NORMAL
285.928 | 0.95 | 305.368 | 1.42 | 1 | 57226.51 | 21736.7526 | 1193.6912 | 2568.37 | NORMAL
285.928 | 0.95 | 305.368 | 1.42 | 1 | 79289.74 | 22830.5979 | 3350.2076 | 2089.76 | NORMAL
285.928 | 0.95 | 305.368 | 1.42 | 1 | 101352.97 | 23166.8523 | 4911.697 | 1624.152 | NORMAL
285.928 | 0.95 | 305.368 | 1.42 | 1 | 106868.78 | 22985.1114 | 5789.0761 | 1542.597 | NORMAL
285.928 | 0.95 | 305.368 | 1.42 | 2 | 57226.51 | 27040.0938 | 502.3806 | 4475.56 | NORMAL
285.928 | 0.95 | 305.368 | 1.42 | 2 | 79289.74 | 28738.1301 | 4107.426 | 3780.65 | NORMAL
285.928 | 0.95 | 305.368 | 1.42 | 2 | 101352.97 | 29312.4267 | 6298.4491 | 3430.508 | NORMAL
285.928 | 0.95 | 305.368 | 1.42 | 2 | 106868.78 | 29122.4502 | 6957.9067 | 3361.173 | NORMAL
299.817 | 0.05 | 288.706 | 0.5 | 1 | 57226.51 | 8116.9402 | 8108.6853 | 2941.622 | NORMAL
299.817 | 0.05 | 288.706 | 0.5 | 1 | 79289.74 | 8294.959 | 8283.7276 | 2757.536 | NORMAL
299.817 | 0.05 | 288.706 | 0.5 | 1 | 101352.97 | 8377.5498 | 8373.6794 | 2665.0717 | NORMAL
299.817 | 0.05 | 288.706 | 0.5 | 1 | 106868.78 | 8378.6928 | 8376.3803 | 2651.0753 | NORMAL
299.817 | 0.05 | 288.706 | 0.5 | 2 | 57226.51 | 10046.8347 | 10042.0825 | 3832.08 | NORMAL
299.817 | 0.05 | 288.706 | 0.5 | 2 | 79289.74 | 10277.2274 | 10256.1488 | 3539.573 | NORMAL
299.817 | 0.05 | 288.706 | 0.5 | 2 | 101352.97 | 10391.2954 | 10360.0176 | 3392.0414 | NORMAL
299.817 | 0.05 | 288.706 | 0.5 | 2 | 106868.78 | 10396.3072 | 10394.3734 | 3365.0794 | NORMAL
299.817 | 0.05 | 288.706 | 0.8 | 1 | 57226.51 | 9305.3634 | 9239.3326 | 2985.229 | NORMAL
299.817 | 0.05 | 288.706 | 0.8 | 1 | 79289.74 | 9558.9683 | 9524.5178 | 2766.183 | NORMAL
299.817 | 0.05 | 288.706 | 0.8 | 1 | 101352.97 | 9689.1266 | 9685.1541 | 2653.745 | NORMAL
299.817 | 0.05 | 288.706 | 0.8 | 1 | 106868.78 | 9711.1958 | 9707.2239 | 2634.647 | NORMAL
299.817 | 0.05 | 288.706 | 0.8 | 2 | 57226.51 | 11668.5522 | 11664.5849 | 4005.627 | NORMAL
299.817 | 0.05 | 288.706 | 0.8 | 2 | 79289.74 | 12034.7304 | 12028.1353 | 3655.988 | NORMAL
299.817 | 0.05 | 288.706 | 0.8 | 2 | 101352.97 | 12217.8488 | 12202.2832 | 3475.373 | NORMAL
299.817 | 0.05 | 288.706 | 0.8 | 2 | 106868.78 | 12251.8757 | 12247.9796 | 3443.735 | NORMAL
299.817 | 0.05 | 288.706 | 1.11 | 1 | 57226.51 | 9969.4021 | 9964.3775 | 3010.17 | NORMAL
299.817 | 0.05 | 288.706 | 1.11 | 1 | 79289.74 | 10276.4068 | 10271.3097 | 2773.443 | NORMAL
299.817 | 0.05 | 288.706 | 1.11 | 1 | 101352.97 | 10435.6096 | 10430.4857 | 2650.063 | NORMAL
299.817 | 0.05 | 288.706 | 1.11 | 1 | 106868.78 | 10465.3869 | 10459.5681 | 2627.709 | NORMAL
299.817 | 0.05 | 288.706 | 1.11 | 2 | 57226.51 | 12596.8933 | 12545.6743 | 4107.66 | NORMAL
299.817 | 0.05 | 288.706 | 1.11 | 2 | 79289.74 | 13053.9273 | 13024.3732 | 3724.394 | NORMAL
299.817 | 0.05 | 288.706 | 1.11 | 2 | 101352.97 | 13293.9625 | 13288.4721 | 3526.622 | NORMAL
299.817 | 0.05 | 288.706 | 1.11 | 2 | 106868.78 | 13337.3974 | 13331.9158 | 3491.827 | NORMAL
299.817 | 0.05 | 288.706 | 1.42 | 1 | 57226.51 | 10405.7737 | 10399.9777 | 3027.67 | NORMAL
299.817 | 0.05 | 288.706 | 1.42 | 1 | 79289.74 | 10751.524 | 10743.3851 | 2778.64 | NORMAL
299.817 | 0.05 | 288.706 | 1.42 | 1 | 101352.97 | 10934.4666 | 10928.5073 | 2647.665 | NORMAL
299.817 | 0.05 | 288.706 | 1.42 | 1 | 106868.78 | 10966.8816 | 10960.9046 | 2624.553 | NORMAL
299.817 | 0.05 | 288.706 | 1.42 | 2 | 57226.51 | 13219.1969 | 13174.8994 | 4178.29 | NORMAL
299.817 | 0.05 | 288.706 | 1.42 | 2 | 79289.74 | 13744.9003 | 13738.289 | 3771.51 | NORMAL
299.817 | 0.05 | 288.706 | 1.42 | 2 | 101352.97 | 14024.4724 | 14017.8108 | 3561.918 | NORMAL
299.817 | 0.05 | 288.706 | 1.42 | 2 | 106868.78 | 14075.0586 | 14068.387 | 3525.248 | NORMAL
299.817 | 0.05 | 291.483 | 0.5 | 1 | 57226.51 | 8641.5299 | 8638.393 | 2960.768 | NORMAL
299.817 | 0.05 | 291.483 | 0.5 | 1 | 79289.74 | 8839.3904 | 8809.0536 | 2760.7 | NORMAL
299.817 | 0.05 | 291.483 | 0.5 | 1 | 101352.97 | 8937.7784 | 8926.2755 | 2659.948 | NORMAL
299.817 | 0.05 | 291.483 | 0.5 | 1 | 106868.78 | 8954.6307 | 8951.5682 | 2642.5627 | NORMAL
299.817 | 0.05 | 291.483 | 0.5 | 2 | 57226.51 | 10615.7679 | 10608.3581 | 3892.036 | NORMAL
299.817 | 0.05 | 291.483 | 0.5 | 2 | 79289.74 | 10875.8206 | 10873.1452 | 3579.13 | NORMAL
299.817 | 0.05 | 291.483 | 0.5 | 2 | 101352.97 | 10999.8535 | 10997.2135 | 3420.1604 | NORMAL
299.817 | 0.05 | 291.483 | 0.5 | 2 | 106868.78 | 11003.9273 | 11001.3304 | 3391.5971 | NORMAL
299.817 | 0.05 | 291.483 | 0.8 | 1 | 57226.51 | 9940.9144 | 9922.6033 | 3009.177 | NORMAL
299.817 | 0.05 | 291.483 | 0.8 | 1 | 79289.74 | 10222.7139 | 10217.5515 | 2772.887 | NORMAL
299.817 | 0.05 | 291.483 | 0.8 | 1 | 101352.97 | 10368.5522 | 10363.3783 | 2650.395 | NORMAL
299.817 | 0.05 | 291.483 | 0.8 | 1 | 106868.78 | 10395.8089 | 10390.6318 | 2628.189 | NORMAL
299.817 | 0.05 | 291.483 | 0.8 | 2 | 57226.51 | 12364.9472 | 12344.644 | 4081.954 | NORMAL
299.817 | 0.05 | 291.483 | 0.8 | 2 | 79289.74 | 12766.5006 | 12736.7929 | 3705.033 | NORMAL
299.817 | 0.05 | 291.483 | 0.8 | 2 | 101352.97 | 12977.2861 | 12960.7919 | 3511.5 | NORMAL
299.817 | 0.05 | 291.483 | 0.8 | 2 | 106868.78 | 13015.3576 | 13010.2295 | 3477.512 | NORMAL
299.817 | 0.05 | 291.483 | 1.11 | 1 | 57226.51 | 10667.9074 | 10661.3893 | 3038.11 | NORMAL
299.817 | 0.05 | 291.483 | 1.11 | 1 | 79289.74 | 11010.4631 | 11003.8568 | 2781.715 | NORMAL
299.817 | 0.05 | 291.483 | 1.11 | 1 | 101352.97 | 11191.2075 | 11184.5599 | 2647.148 | NORMAL
299.817 | 0.05 | 291.483 | 1.11 | 1 | 106868.78 | 11224.3552 | 11217.6992 | 2622.872 | NORMAL
299.817 | 0.05 | 291.483 | 1.11 | 2 | 57226.51 | 13368.8453 | 13361.7999 | 4195.16 | NORMAL
299.817 | 0.05 | 291.483 | 1.11 | 2 | 79289.74 | 13877.2274 | 13870.1084 | 3780.613 | NORMAL
299.817 | 0.05 | 291.483 | 1.11 | 2 | 101352.97 | 14147.0106 | 14139.8663 | 3567.919 | NORMAL
299.817 | 0.05 | 291.483 | 1.11 | 2 | 106868.78 | 14195.0176 | 14187.8775 | 3530.718 | NORMAL
299.817 | 0.05 | 291.483 | 1.42 | 1 | 57226.51 | 11144.8124 | 11137.312 | 3058.2 | NORMAL
299.817 | 0.05 | 291.483 | 1.42 | 1 | 79289.74 | 11534.2028 | 11513.6373 | 2788.23 | NORMAL
299.817 | 0.05 | 291.483 | 1.42 | 1 | 101352.97 | 11743.2884 | 11735.5613 | 2644.259 | NORMAL
299.817 | 0.05 | 291.483 | 1.42 | 1 | 106868.78 | 11779.2497 | 11771.499 | 2619.516 | NORMAL
299.817 | 0.05 | 291.483 | 1.42 | 2 | 57226.51 | 14039.0094 | 14030.586 | 4271.8 | NORMAL
299.817 | 0.05 | 291.483 | 1.42 | 2 | 79289.74 | 14627.1981 | 14618.6266 | 3832.87 | NORMAL
299.817 | 0.05 | 291.483 | 1.42 | 2 | 101352.97 | 14943.2298 | 14934.5776 | 3607.036 | NORMAL
299.817 | 0.05 | 291.483 | 1.42 | 2 | 106868.78 | 14999.4431 | 14990.7885 | 3567.48 | NORMAL
299.817 | 0.05 | 294.26 | 0.5 | 1 | 57226.51 | 9184.9648 | 9180.9418 | 2980.454 | NORMAL
299.817 | 0.05 | 294.26 | 0.5 | 1 | 79289.74 | 9398.3001 | 9393.2062 | 2764.72 | NORMAL
299.817 | 0.05 | 294.26 | 0.5 | 1 | 101352.97 | 9506.2427 | 9474.5774 | 2655.065 | NORMAL
299.817 | 0.05 | 294.26 | 0.5 | 1 | 106868.78 | 9524.5311 | 9520.5784 | 2636.4897 | NORMAL
299.817 | 0.05 | 294.26 | 0.5 | 2 | 57226.51 | 11196.4244 | 11187.9151 | 3954.417 | NORMAL
299.817 | 0.05 | 294.26 | 0.5 | 2 | 79289.74 | 11478.3118 | 11474.7995 | 3618.86 | NORMAL
299.817 | 0.05 | 294.26 | 0.5 | 2 | 101352.97 | 11623.2122 | 11619.7485 | 3447.3662 | NORMAL
299.817 | 0.05 | 294.26 | 0.5 | 2 | 106868.78 | 11629.3962 | 11625.9539 | 3418.3525 | NORMAL
299.817 | 0.05 | 294.26 | 0.8 | 1 | 57226.51 | 10588.6284 | 10582.0952 | 3034.807 | NORMAL
299.817 | 0.05 | 294.26 | 0.8 | 1 | 79289.74 | 10901.2309 | 10894.6575 | 2780.363 | NORMAL
299.817 | 0.05 | 294.26 | 0.8 | 1 | 101352.97 | 11065.0352 | 11058.4404 | 2647.109 | NORMAL
299.817 | 0.05 | 294.26 | 0.8 | 1 | 106868.78 | 11094.109 | 11087.508 | 2623.715 | NORMAL
299.817 | 0.05 | 294.26 | 0.8 | 2 | 57226.51 | 13070.4865 | 13063.8206 | 4161.475 | NORMAL
299.817 | 0.05 | 294.26 | 0.8 | 2 | 79289.74 | 13517.2333 | 13510.5693 | 3755.896 | NORMAL
299.817 | 0.05 | 294.26 | 0.8 | 2 | 101352.97 | 13751.2016 | 13744.5598 | 3548.661 | NORMAL
299.817 | 0.05 | 294.26 | 0.8 | 2 | 106868.78 | 13793.5229 | 13786.8882 | 3512.323 | NORMAL
299.817 | 0.05 | 294.26 | 1.11 | 1 | 57226.51 | 11379.1325 | 11370.8826 | 3068.03 | NORMAL
299.817 | 0.05 | 294.26 | 1.11 | 1 | 79289.74 | 11762.3974 | 11754.0108 | 2791.172 | NORMAL
299.817 | 0.05 | 294.26 | 1.11 | 1 | 101352.97 | 11967.8781 | 11959.4288 | 2643.764 | NORMAL
299.817 | 0.05 | 294.26 | 1.11 | 1 | 106868.78 | 12002.4619 | 11994.0002 | 2618.669 | NORMAL
299.817 | 0.05 | 294.26 | 1.11 | 2 | 57226.51 | 14149.9121 | 14140.9552 | 4285.49 | NORMAL
299.817 | 0.05 | 294.26 | 1.11 | 2 | 79289.74 | 14716.5885 | 14707.5378 | 3839.085 | NORMAL
299.817 | 0.05 | 294.26 | 1.11 | 2 | 101352.97 | 15017.7315 | 15008.6458 | 3610.739 | NORMAL
299.817 | 0.05 | 294.26 | 1.11 | 2 | 106868.78 | 15071.4537 | 15062.3656 | 3570.81 | NORMAL
299.817 | 0.05 | 294.26 | 1.42 | 1 | 57226.51 | 11899.0914 | 11889.596 | 3091.04 | NORMAL
299.817 | 0.05 | 294.26 | 1.42 | 1 | 79289.74 | 12335.5803 | 12325.8845 | 2799.17 | NORMAL
299.817 | 0.05 | 294.26 | 1.42 | 1 | 101352.97 | 12571.4537 | 12561.648 | 2643.218 | NORMAL
299.817 | 0.05 | 294.26 | 1.42 | 1 | 106868.78 | 12613.5991 | 12603.7731 | 2615.607 | NORMAL
299.817 | 0.05 | 294.26 | 1.42 | 2 | 57226.51 | 14869.871 | 14839.6257 | 4370.7 | NORMAL
299.817 | 0.05 | 294.26 | 1.42 | 2 | 79289.74 | 15528.6342 | 15517.7797 | 3896.75 | NORMAL
299.817 | 0.05 | 294.26 | 1.42 | 2 | 101352.97 | 15881.3306 | 15870.3725 | 3654.109 | NORMAL
299.817 | 0.05 | 294.26 | 1.42 | 2 | 106868.78 | 15944.4314 | 15933.4616 | 3611.711 | NORMAL
299.817 | 0.05 | 297.037 | 0.5 | 1 | 57226.51 | 9732.3857 | 9727.3054 | 3000.758 | NORMAL
299.817 | 0.05 | 297.037 | 0.5 | 1 | 79289.74 | 9964.5076 | 9959.4656 | 2770.21 | NORMAL
299.817 | 0.05 | 297.037 | 0.5 | 1 | 101352.97 | 10083.3529 | 10078.3314 | 2651.319 | NORMAL
299.817 | 0.05 | 297.037 | 0.5 | 1 | 106868.78 | 10104.9238 | 10099.9016 | 2630.609 | NORMAL
299.817 | 0.05 | 297.037 | 0.5 | 2 | 57226.51 | 11783.4994 | 11770.5493 | 4018.076 | NORMAL
299.817 | 0.05 | 297.037 | 0.5 | 2 | 79289.74 | 12094.1676 | 12060.7998 | 3660.042 | NORMAL
299.817 | 0.05 | 297.037 | 0.5 | 2 | 101352.97 | 12249.7948 | 12245.3482 | 3476.909 | NORMAL
299.817 | 0.05 | 297.037 | 0.5 | 2 | 106868.78 | 12278.5463 | 12274.1629 | 3444.9283 | NORMAL
299.817 | 0.05 | 297.037 | 0.8 | 1 | 57226.51 | 11247.626 | 11239.4603 | 3062.203 | NORMAL
299.817 | 0.05 | 297.037 | 0.8 | 1 | 79289.74 | 11593.1125 | 11584.893 | 2788.99 | NORMAL
299.817 | 0.05 | 297.037 | 0.8 | 1 | 101352.97 | 11776.9343 | 11768.6905 | 2644.126 | NORMAL
299.817 | 0.05 | 297.037 | 0.8 | 1 | 106868.78 | 11807.4443 | 11799.1909 | 2619.89 | NORMAL
299.817 | 0.05 | 297.037 | 0.8 | 2 | 57226.51 | 13787.3681 | 13778.9992 | 4242.728 | NORMAL
299.817 | 0.05 | 297.037 | 0.8 | 2 | 79289.74 | 14279.9238 | 14271.5558 | 3808.593 | NORMAL
299.817 | 0.05 | 297.037 | 0.8 | 2 | 101352.97 | 14539.3904 | 14531.0448 | 3587.148 | NORMAL
299.817 | 0.05 | 297.037 | 0.8 | 2 | 106868.78 | 14585.9906 | 14577.6474 | 3548.524 | NORMAL
299.817 | 0.05 | 297.037 | 1.11 | 1 | 57226.51 | 12103.3705 | 12093.0826 | 3100.08 | NORMAL
299.817 | 0.05 | 297.037 | 1.11 | 1 | 79289.74 | 12529.9238 | 12519.4738 | 2802.094 | NORMAL
299.817 | 0.05 | 297.037 | 1.11 | 1 | 101352.97 | 12759.408 | 12748.8687 | 2643.123 | NORMAL
299.817 | 0.05 | 297.037 | 1.11 | 1 | 106868.78 | 12800.3517 | 12789.7914 | 2615.02 | NORMAL
299.817 | 0.05 | 297.037 | 1.11 | 2 | 57226.51 | 14942.3798 | 14931.2179 | 4379.27 | NORMAL
299.817 | 0.05 | 297.037 | 1.11 | 2 | 79289.74 | 15571.0141 | 15559.7251 | 3899.775 | NORMAL
299.817 | 0.05 | 297.037 | 1.11 | 2 | 101352.97 | 15904.748 | 15893.392 | 3655.317 | NORMAL
299.817 | 0.05 | 297.037 | 1.11 | 2 | 106868.78 | 15964.5369 | 15953.1861 | 3612.655 | NORMAL
299.817 | 0.05 | 297.037 | 1.42 | 1 | 57226.51 | 12666.9695 | 12655.1512 | 3126.3 | NORMAL
299.817 | 0.05 | 297.037 | 1.42 | 1 | 79289.74 | 13155.51 | 13143.4201 | 2811.8 | NORMAL
299.817 | 0.05 | 297.037 | 1.42 | 1 | 101352.97 | 13420.1641 | 13397.0143 | 2643.375 | NORMAL
299.817 | 0.05 | 297.037 | 1.42 | 1 | 106868.78 | 13467.6729 | 13455.4173 | 2613.437 | NORMAL
299.817 | 0.05 | 297.037 | 1.42 | 2 | 57226.51 | 15714.6542 | 15701.4224 | 4471.85 | NORMAL
299.817 | 0.05 | 297.037 | 1.42 | 2 | 79289.74 | 16445.7796 | 16432.2612 | 3963.4 | NORMAL
299.817 | 0.05 | 297.037 | 1.42 | 2 | 101352.97 | 16837.837 | 16824.1984 | 3703.361 | NORMAL
299.817 | 0.05 | 297.037 | 1.42 | 2 | 106868.78 | 16908.2356 | 16894.5569 | 3657.872 | NORMAL
299.817 | 0.05 | 299.814 | 0.5 | 1 | 57226.51 | 10283.4115 | 10277.1386 | 3023.023 | NORMAL
299.817 | 0.05 | 299.814 | 0.5 | 1 | 79289.74 | 10539.9472 | 10533.7076 | 2776.291 | NORMAL
299.817 | 0.05 | 299.814 | 0.5 | 1 | 101352.97 | 10670.6624 | 10664.4414 | 2648.854 | NORMAL
299.817 | 0.05 | 299.814 | 0.5 | 1 | 106868.78 | 10694.9297 | 10688.7159 | 2625.8738 | NORMAL
299.817 | 0.05 | 299.814 | 0.5 | 2 | 57226.51 | 12376.7292 | 12370.974 | 4083.217 | NORMAL
299.817 | 0.05 | 299.814 | 0.5 | 2 | 79289.74 | 12714.1266 | 12687.4269 | 3701.561 | NORMAL
299.817 | 0.05 | 299.814 | 0.5 | 2 | 101352.97 | 12888.8042 | 12883.2491 | 3507.32 | NORMAL
299.817 | 0.05 | 299.814 | 0.5 | 2 | 106868.78 | 12920.7503 | 12915.2719 | 3473.3538 | NORMAL
299.817 | 0.05 | 299.814 | 0.8 | 1 | 57226.51 | 11917.3212 | 11907.2868 | 3091.537 | NORMAL
299.817 | 0.05 | 299.814 | 0.8 | 1 | 79289.74 | 12298.1536 | 12288.0445 | 2798.642 | NORMAL
299.817 | 0.05 | 299.814 | 0.8 | 1 | 101352.97 | 12501.4654 | 12491.3142 | 2643.267 | NORMAL
299.817 | 0.05 | 299.814 | 0.8 | 1 | 106868.78 | 12537.7198 | 12527.5643 | 2615.863 | NORMAL
299.817 | 0.05 | 299.814 | 0.8 | 2 | 57226.51 | 14512.9836 | 14502.6503 | 4327.564 | NORMAL
299.817 | 0.05 | 299.814 | 0.8 | 2 | 79289.74 | 15055.0703 | 15044.7576 | 3863.029 | NORMAL
299.817 | 0.05 | 299.814 | 0.8 | 2 | 101352.97 | 15341.2661 | 15330.9568 | 3626.88 | NORMAL
299.817 | 0.05 | 299.814 | 0.8 | 2 | 106868.78 | 15392.2626 | 15381.9498 | 3585.735 | NORMAL
299.817 | 0.05 | 299.814 | 1.11 | 1 | 57226.51 | 12839.4783 | 12826.8571 | 3134.4 | NORMAL
299.817 | 0.05 | 299.814 | 1.11 | 1 | 79289.74 | 13313.5111 | 13300.6636 | 2814.387 | NORMAL
299.817 | 0.05 | 299.814 | 1.11 | 1 | 101352.97 | 13569.4314 | 13556.4726 | 2643.528 | NORMAL
299.817 | 0.05 | 299.814 | 1.11 | 1 | 106868.78 | 13615.4748 | 13602.4993 | 2613.192 | NORMAL
299.817 | 0.05 | 299.814 | 1.11 | 2 | 57226.51 | 15746.1313 | 15732.4322 | 4475.66 | NORMAL
299.817 | 0.05 | 299.814 | 1.11 | 2 | 79289.74 | 16438.1594 | 16424.3021 | 3962.933 | NORMAL
299.817 | 0.05 | 299.814 | 1.11 | 2 | 101352.97 | 16808.0305 | 16794.0798 | 3701.82 | NORMAL
299.817 | 0.05 | 299.814 | 1.11 | 2 | 106868.78 | 16874.1501 | 16860.1951 | 3656.214 | NORMAL
299.817 | 0.05 | 299.814 | 1.42 | 1 | 57226.51 | 13447.8019 | 13433.3052 | 3164.21 | NORMAL
299.817 | 0.05 | 299.814 | 1.42 | 1 | 79289.74 | 13994.4607 | 13979.6126 | 2825.37 | NORMAL
299.817 | 0.05 | 299.814 | 1.42 | 1 | 101352.97 | 14288.7749 | 14273.7574 | 2644.766 | NORMAL
299.817 | 0.05 | 299.814 | 1.42 | 1 | 106868.78 | 14342.0574 | 14326.9983 | 2612.475 | NORMAL
299.817 | 0.05 | 299.814 | 1.42 | 2 | 57226.51 | 16567.9953 | 16551.7918 | 4577.86 | NORMAL
299.817 | 0.05 | 299.814 | 1.42 | 2 | 79289.74 | 17377.8722 | 17361.3111 | 4033.06 | NORMAL
299.817 | 0.05 | 299.814 | 1.42 | 2 | 101352.97 | 17812.1923 | 17792.5276 | 3754.915 | NORMAL
299.817 | 0.05 | 299.814 | 1.42 | 2 | 106868.78 | 17890.2696 | 17873.5065 | 3706.358 | NORMAL
299.817 | 0.05 | 302.591 | 0.5 | 1 | 57226.51 | 10849.0035 | 10841.3441 | 3045.509 | NORMAL
299.817 | 0.05 | 302.591 | 0.5 | 1 | 79289.74 | 11124.5897 | 11116.9693 | 2783.123 | NORMAL
299.817 | 0.05 | 302.591 | 0.5 | 1 | 101352.97 | 11267.4971 | 11259.914 | 2646.786 | NORMAL
299.817 | 0.05 | 302.591 | 0.5 | 1 | 106868.78 | 11293.7573 | 11286.1792 | 2622.3562 | NORMAL
299.817 | 0.05 | 302.591 | 0.5 | 2 | 57226.51 | 12977.4912 | 12956.6494 | 4150.87 | NORMAL
299.817 | 0.05 | 302.591 | 0.5 | 2 | 79289.74 | 13346.3658 | 13339.4257 | 3744.331 | NORMAL
299.817 | 0.05 | 302.591 | 0.5 | 2 | 101352.97 | 13537.4267 | 13530.5768 | 3538.352 | NORMAL
299.817 | 0.05 | 302.591 | 0.5 | 2 | 106868.78 | 13571.9226 | 13565.0824 | 3502.3719 | NORMAL
299.817 | 0.05 | 302.591 | 0.8 | 1 | 57226.51 | 12596.6295 | 12584.4612 | 3122.708 | NORMAL
299.817 | 0.05 | 302.591 | 0.8 | 1 | 79289.74 | 13015.9437 | 13003.6697 | 2809.579 | NORMAL
299.817 | 0.05 | 302.591 | 0.8 | 1 | 101352.97 | 13240.9437 | 13228.6297 | 2643.201 | NORMAL
299.817 | 0.05 | 302.591 | 0.8 | 1 | 106868.78 | 13281.2134 | 13268.8751 | 2613.821 | NORMAL
299.817 | 0.05 | 302.591 | 0.8 | 2 | 57226.51 | 15247.0106 | 15234.447 | 4415.485 | NORMAL
299.817 | 0.05 | 302.591 | 0.8 | 2 | 79289.74 | 15842.204 | 15829.6411 | 3919.417 | NORMAL
299.817 | 0.05 | 302.591 | 0.8 | 2 | 101352.97 | 16155.5686 | 16143.0157 | 3668.114 | NORMAL
299.817 | 0.05 | 302.591 | 0.8 | 2 | 106868.78 | 16211.5768 | 16199.029 | 3624.401 | NORMAL
299.817 | 0.05 | 302.591 | 1.11 | 1 | 57226.51 | 13586.5475 | 13571.2626 | 3171.07 | NORMAL
299.817 | 0.05 | 302.591 | 1.11 | 1 | 79289.74 | 14113.9508 | 14098.369 | 2827.534 | NORMAL
299.817 | 0.05 | 302.591 | 1.11 | 1 | 101352.97 | 14396.6882 | 14380.967 | 2645.025 | NORMAL
299.817 | 0.05 | 302.591 | 1.11 | 1 | 106868.78 | 14447.7433 | 14431.9952 | 2612.461 | NORMAL
299.817 | 0.05 | 302.591 | 1.11 | 2 | 57226.51 | 16558.0012 | 16541.4266 | 4576.51 | NORMAL
299.817 | 0.05 | 302.591 | 1.11 | 2 | 79289.74 | 17320.2227 | 17303.4221 | 4028.679 | NORMAL
299.817 | 0.05 | 302.591 | 1.11 | 2 | 101352.97 | 17726.6999 | 17709.7886 | 3750.354 | NORMAL
299.817 | 0.05 | 302.591 | 1.11 | 2 | 106868.78 | 17799.6776 | 17782.7501 | 3701.831 | NORMAL
299.817 | 0.05 | 302.591 | 1.42 | 1 | 57226.51 | 14241.354 | 14223.8087 | 3204.82 | NORMAL
299.817 | 0.05 | 302.591 | 1.42 | 1 | 79289.74 | 14849.0621 | 14831.0651 | 2841.46 | NORMAL
299.817 | 0.05 | 302.591 | 1.42 | 1 | 101352.97 | 15177.7843 | 15159.5558 | 2647.603 | NORMAL
299.817 | 0.05 | 302.591 | 1.42 | 1 | 106868.78 | 15237.6026 | 15219.3327 | 2612.867 | NORMAL
299.817 | 0.05 | 302.591 | 1.42 | 2 | 57226.51 | 17431.7995 | 17407.918 | 4688.35 | NORMAL
299.817 | 0.05 | 302.591 | 1.42 | 2 | 79289.74 | 18323.5053 | 18303.4777 | 4105.79 | NORMAL
299.817 | 0.05 | 302.591 | 1.42 | 2 | 101352.97 | 18803.136 | 18782.885 | 3808.96 | NORMAL
299.817 | 0.05 | 302.591 | 1.42 | 2 | 106868.78 | 18889.7128 | 18869.4063 | 3757.363 | NORMAL
299.817 | 0.05 | 305.368 | 0.5 | 1 | 57226.51 | 11418.6108 | 11409.396 | 3069.715 | NORMAL
299.817 | 0.05 | 305.368 | 0.5 | 1 | 79289.74 | 11718.2884 | 11709.1247 | 2790.624 | NORMAL
299.817 | 0.05 | 305.368 | 0.5 | 1 | 101352.97 | 11875.9086 | 11866.776 | 2643.929 | NORMAL
299.817 | 0.05 | 305.368 | 0.5 | 1 | 106868.78 | 11902.5791 | 11893.4499 | 2619.2947 | NORMAL
299.817 | 0.05 | 305.368 | 0.5 | 2 | 57226.51 | 13586.5475 | 13577.9472 | 4219.652 | NORMAL
299.817 | 0.05 | 305.368 | 0.5 | 2 | 79289.74 | 13987.0457 | 13978.6255 | 3788.275 | NORMAL
299.817 | 0.05 | 305.368 | 0.5 | 2 | 101352.97 | 14194.4314 | 14186.1135 | 3570.278 | NORMAL
299.817 | 0.05 | 305.368 | 0.5 | 2 | 106868.78 | 14231.3013 | 14223.0044 | 3532.3826 | NORMAL
299.817 | 0.05 | 305.368 | 0.8 | 1 | 57226.51 | 13284.6717 | 13269.0357 | 3155.886 | NORMAL
299.817 | 0.05 | 305.368 | 0.8 | 1 | 79289.74 | 13747.5088 | 13732.799 | 2821.065 | NORMAL
299.817 | 0.05 | 305.368 | 0.8 | 1 | 101352.97 | 13994.1383 | 13979.3605 | 2644.135 | NORMAL
299.817 | 0.05 | 305.368 | 0.8 | 1 | 106868.78 | 14038.6577 | 14023.8609 | 2612.692 | NORMAL
299.817 | 0.05 | 305.368 | 0.8 | 2 | 57226.51 | 15990.211 | 15975.1482 | 4505.664 | NORMAL
299.817 | 0.05 | 305.368 | 0.8 | 2 | 79289.74 | 16639.83 | 16624.7543 | 3977.773 | NORMAL
299.817 | 0.05 | 305.368 | 0.8 | 2 | 101352.97 | 16981.9461 | 16966.8661 | 3710.908 | NORMAL
299.817 | 0.05 | 305.368 | 0.8 | 2 | 106868.78 | 17043.2005 | 17028.1343 | 3664.481 | NORMAL
299.817 | 0.05 | 305.368 | 1.11 | 1 | 57226.51 | 14344.8124 | 14326.5084 | 3210.22 | NORMAL
299.817 | 0.05 | 305.368 | 1.11 | 1 | 79289.74 | 14927.9894 | 14909.3444 | 2843.015 | NORMAL
299.817 | 0.05 | 305.368 | 1.11 | 1 | 101352.97 | 15240.7093 | 15221.8717 | 2647.87 | NORMAL
299.817 | 0.05 | 305.368 | 1.11 | 1 | 106868.78 | 15297.6846 | 15278.8226 | 2612.947 | NORMAL
299.817 | 0.05 | 305.368 | 1.11 | 2 | 57226.51 | 17378.0188 | 17354.1587 | 4681.42 | NORMAL
299.817 | 0.05 | 305.368 | 1.11 | 2 | 79289.74 | 18213.3939 | 18193.2863 | 4097.216 | NORMAL
299.817 | 0.05 | 305.368 | 1.11 | 2 | 101352.97 | 18659.4666 | 18639.2024 | 3801.013 | NORMAL
299.817 | 0.05 | 305.368 | 1.11 | 2 | 106868.78 | 18739.5369 | 18719.2608 | 3749.611 | NORMAL
299.817 | 0.05 | 305.368 | 1.42 | 1 | 57226.51 | 15046.0141 | 15025.0249 | 3248.28 | NORMAL
299.817 | 0.05 | 305.368 | 1.42 | 1 | 79289.74 | 15720.6331 | 15670.6572 | 2859.52 | NORMAL
299.817 | 0.05 | 305.368 | 1.42 | 1 | 101352.97 | 16085.9027 | 16057.4628 | 2651.863 | NORMAL
299.817 | 0.05 | 305.368 | 1.42 | 1 | 106868.78 | 16152.5791 | 16130.6762 | 2614.642 | NORMAL
299.817 | 0.05 | 305.368 | 1.42 | 2 | 57226.51 | 18302.2274 | 18234.436 | 4803.25 | NORMAL
299.817 | 0.05 | 305.368 | 1.42 | 2 | 79289.74 | 19281.9754 | 19258.0272 | 4181.87 | NORMAL
299.817 | 0.05 | 305.368 | 1.42 | 2 | 101352.97 | 19810.4338 | 19786.2056 | 3865.643 | NORMAL
299.817 | 0.05 | 305.368 | 1.42 | 2 | 106868.78 | 19905.51 | 19881.2252 | 3810.86 | NORMAL
299.817 | 0.15 | 288.706 | 0.5 | 1 | 57226.51 | 8122.8898 | 8111.1035 | 2941.754 | NORMAL
299.817 | 0.15 | 288.706 | 0.5 | 1 | 79289.74 | 8297.4795 | 8295.123 | 2757.558 | NORMAL
299.817 | 0.15 | 288.706 | 0.5 | 1 | 101352.97 | 8384.408 | 8382.0687 | 2665.0081 | NORMAL
299.817 | 0.15 | 288.706 | 0.5 | 1 | 106868.78 | 8397.6553 | 8395.3292 | 2650.7206 | NORMAL
299.817 | 0.15 | 288.706 | 0.5 | 2 | 57226.51 | 10057.7374 | 10055.7057 | 3832.661 | NORMAL
299.817 | 0.15 | 288.706 | 0.5 | 2 | 79289.74 | 10288.2474 | 10258.7818 | 3540.301 | NORMAL
299.817 | 0.15 | 288.706 | 0.5 | 2 | 101352.97 | 10402.1102 | 10400.165 | 3392.5651 | NORMAL
299.817 | 0.15 | 288.706 | 0.5 | 2 | 106868.78 | 10403.898 | 10401.9837 | 3365.4094 | NORMAL
299.817 | 0.15 | 288.706 | 0.8 | 1 | 57226.51 | 9311.3716 | 9307.4329 | 2985.446 | NORMAL
299.817 | 0.15 | 288.706 | 0.8 | 1 | 79289.74 | 9564.7714 | 9560.8116 | 2766.233 | NORMAL
299.817 | 0.15 | 288.706 | 0.8 | 1 | 101352.97 | 9693.8453 | 9689.8708 | 2653.71 | NORMAL
299.817 | 0.15 | 288.706 | 0.8 | 1 | 106868.78 | 9715.8558 | 9711.882 | 2634.476 | NORMAL
299.817 | 0.15 | 288.706 | 0.8 | 2 | 57226.51 | 11680.6858 | 11676.7144 | 4006.895 | NORMAL
299.817 | 0.15 | 288.706 | 0.8 | 2 | 79289.74 | 12037.2509 | 12033.2906 | 3656.161 | NORMAL
299.817 | 0.15 | 288.706 | 0.8 | 2 | 101352.97 | 12224.5897 | 12220.6411 | 3475.687 | NORMAL
299.817 | 0.15 | 288.706 | 0.8 | 2 | 106868.78 | 12258.2356 | 12254.2885 | 3444.005 | NORMAL
299.817 | 0.15 | 288.706 | 1.11 | 1 | 57226.51 | 9975.6741 | 9970.6563 | 3010.41 | NORMAL
299.817 | 0.15 | 288.706 | 1.11 | 1 | 79289.74 | 10281.3013 | 10276.2121 | 2773.493 | NORMAL
299.817 | 0.15 | 288.706 | 1.11 | 1 | 101352.97 | 10439.6249 | 10434.499 | 2650.03 | NORMAL
299.817 | 0.15 | 288.706 | 1.11 | 1 | 106868.78 | 10469.3728 | 10464.2428 | 2627.569 | NORMAL
299.817 | 0.15 | 288.706 | 1.11 | 2 | 57226.51 | 12609.2614 | 12603.8394 | 4109.05 | NORMAL
299.817 | 0.15 | 288.706 | 1.11 | 2 | 79289.74 | 13060.9906 | 13055.5181 | 3724.89 | NORMAL
299.817 | 0.15 | 288.706 | 1.11 | 2 | 101352.97 | 13299.9121 | 13294.4325 | 3526.912 | NORMAL
299.817 | 0.15 | 288.706 | 1.11 | 2 | 106868.78 | 13342.9367 | 13337.4528 | 3492.068 | NORMAL
299.817 | 0.15 | 288.706 | 1.42 | 1 | 57226.51 | 10411.1372 | 10389.5965 | 3027.89 | NORMAL
299.817 | 0.15 | 288.706 | 1.42 | 1 | 79289.74 | 10755.7737 | 10749.8688 | 2778.69 | NORMAL
299.817 | 0.15 | 288.706 | 1.42 | 1 | 101352.97 | 10937.9543 | 10931.9931 | 2647.659 | NORMAL
299.817 | 0.15 | 288.706 | 1.42 | 1 | 106868.78 | 10969.9297 | 10963.962 | 2624.654 | NORMAL
299.817 | 0.15 | 288.706 | 1.42 | 2 | 57226.51 | 13226.9343 | 13211.0488 | 4179.16 | NORMAL
299.817 | 0.15 | 288.706 | 1.42 | 2 | 79289.74 | 13751.1137 | 13737.2939 | 3771.95 | NORMAL
299.817 | 0.15 | 288.706 | 1.42 | 2 | 101352.97 | 14029.9238 | 14023.2596 | 3562.174 | NORMAL
299.817 | 0.15 | 288.706 | 1.42 | 2 | 106868.78 | 14079.9531 | 14073.2792 | 3525.473 | NORMAL
299.817 | 0.15 | 291.483 | 0.5 | 1 | 57226.51 | 8658.0012 | 8654.8756 | 2960.781 | NORMAL
299.817 | 0.15 | 291.483 | 0.5 | 1 | 79289.74 | 8849.6776 | 8846.5625 | 2760.623 | NORMAL
299.817 | 0.15 | 291.483 | 0.5 | 1 | 101352.97 | 8945.1348 | 8942.0309 | 2659.909 | NORMAL
299.817 | 0.15 | 291.483 | 0.5 | 1 | 106868.78 | 8961.3423 | 8958.2417 | 2642.6384 | NORMAL
299.817 | 0.15 | 291.483 | 0.5 | 2 | 57226.51 | 10633.8511 | 10631.0969 | 3893.985 | NORMAL
299.817 | 0.15 | 291.483 | 0.5 | 2 | 79289.74 | 10884.8183 | 10871.6694 | 3579.726 | NORMAL
299.817 | 0.15 | 291.483 | 0.5 | 2 | 101352.97 | 11010.0821 | 10999.4793 | 3420.5653 | NORMAL
299.817 | 0.15 | 291.483 | 0.5 | 2 | 106868.78 | 11026.612 | 11024.0097 | 3392.4391 | NORMAL
299.817 | 0.15 | 291.483 | 0.8 | 1 | 57226.51 | 9950.6741 | 9941.002 | 3009.572 | NORMAL
299.817 | 0.15 | 291.483 | 0.8 | 1 | 79289.74 | 10230.4807 | 10225.3245 | 2772.973 | NORMAL
299.817 | 0.15 | 291.483 | 0.8 | 1 | 101352.97 | 10374.8535 | 10369.6764 | 2650.37 | NORMAL
299.817 | 0.15 | 291.483 | 0.8 | 1 | 106868.78 | 10401.7878 | 10396.6181 | 2628.149 | NORMAL
299.817 | 0.15 | 291.483 | 0.8 | 2 | 57226.51 | 12378.3998 | 12373.1761 | 4083.447 | NORMAL
299.817 | 0.15 | 291.483 | 0.8 | 2 | 79289.74 | 12777.1395 | 12771.9392 | 3705.748 | NORMAL
299.817 | 0.15 | 291.483 | 0.8 | 2 | 101352.97 | 12986.0786 | 12980.8971 | 3511.909 | NORMAL
299.817 | 0.15 | 291.483 | 0.8 | 2 | 106868.78 | 13023.5932 | 13018.4098 | 3477.872 | NORMAL
299.817 | 0.15 | 291.483 | 1.11 | 1 | 57226.51 | 10676.1137 | 10669.612 | 3038.45 | NORMAL
299.817 | 0.15 | 291.483 | 1.11 | 1 | 79289.74 | 11016.9109 | 11010.3228 | 2781.795 | NORMAL
299.817 | 0.15 | 291.483 | 1.11 | 1 | 101352.97 | 11196.483 | 11189.6867 | 2647.132 | NORMAL
299.817 | 0.15 | 291.483 | 1.11 | 1 | 106868.78 | 11229.3083 | 11222.6606 | 2622.846 | NORMAL
299.817 | 0.15 | 291.483 | 1.11 | 2 | 57226.51 | 13380.3341 | 13373.2827 | 4196.46 | NORMAL
299.817 | 0.15 | 291.483 | 1.11 | 2 | 79289.74 | 13886.4302 | 13879.3204 | 3781.25 | NORMAL
299.817 | 0.15 | 291.483 | 1.11 | 2 | 101352.97 | 14154.6307 | 14147.4968 | 3568.285 | NORMAL
299.817 | 0.15 | 291.483 | 1.11 | 2 | 106868.78 | 14202.1688 | 14195.0251 | 3531.035 | NORMAL
299.817 | 0.15 | 291.483 | 1.42 | 1 | 57226.51 | 11151.8757 | 11144.3817 | 3058.5 | NORMAL
299.817 | 0.15 | 291.483 | 1.42 | 1 | 79289.74 | 11539.8007 | 11532.1614 | 2788.3 | NORMAL
299.817 | 0.15 | 291.483 | 1.42 | 1 | 101352.97 | 11748.007 | 11740.2886 | 2644.204 | NORMAL
299.817 | 0.15 | 291.483 | 1.42 | 1 | 106868.78 | 11783.5873 | 11775.8573 | 2619.5 | NORMAL
299.817 | 0.15 | 291.483 | 1.42 | 2 | 57226.51 | 14049.0035 | 14040.5882 | 4272.96 | NORMAL
299.817 | 0.15 | 291.483 | 1.42 | 2 | 79289.74 | 14636.0492 | 14627.4872 | 3833.44 | NORMAL
299.817 | 0.15 | 291.483 | 1.42 | 2 | 101352.97 | 14949.9707 | 14941.3446 | 3607.374 | NORMAL
299.817 | 0.15 | 291.483 | 1.42 | 2 | 106868.78 | 15005.7151 | 14997.0718 | 3567.788 | NORMAL
299.817 | 0.15 | 294.26 | 0.5 | 1 | 57226.51 | 9198.7397 | 9194.7015 | 2981.042 | NORMAL
299.817 | 0.15 | 294.26 | 0.5 | 1 | 79289.74 | 9409.8769 | 9405.8683 | 2764.816 | NORMAL
299.817 | 0.15 | 294.26 | 0.5 | 1 | 101352.97 | 9515.8558 | 9511.8687 | 2654.904 | NORMAL
299.817 | 0.15 | 294.26 | 0.5 | 1 | 106868.78 | 9533.4408 | 9529.4558 | 2636.4067 | NORMAL
299.817 | 0.15 | 294.26 | 0.5 | 2 | 57226.51 | 11215.4748 | 11207.9492 | 3956.427 | NORMAL
299.817 | 0.15 | 294.26 | 0.5 | 2 | 79289.74 | 11491.1489 | 11474.2569 | 3619.863 | NORMAL
299.817 | 0.15 | 294.26 | 0.5 | 2 | 101352.97 | 11634.7304 | 11631.2516 | 3447.888 | NORMAL
299.817 | 0.15 | 294.26 | 0.5 | 2 | 106868.78 | 11658.0891 | 11654.65 | 3419.5263 | NORMAL
299.817 | 0.15 | 294.26 | 0.8 | 1 | 57226.51 | 10601.3775 | 10594.8576 | 3035.318 | NORMAL
299.817 | 0.15 | 294.26 | 0.8 | 1 | 79289.74 | 10910.9906 | 10904.4113 | 2780.487 | NORMAL
299.817 | 0.15 | 294.26 | 0.8 | 1 | 101352.97 | 11073.095 | 11066.4954 | 2647.057 | NORMAL
299.817 | 0.15 | 294.26 | 0.8 | 1 | 106868.78 | 11101.5827 | 11094.9883 | 2623.722 | NORMAL
299.817 | 0.15 | 294.26 | 0.8 | 2 | 57226.51 | 13087.2216 | 13080.5471 | 4163.377 | NORMAL
299.817 | 0.15 | 294.26 | 0.8 | 2 | 79289.74 | 13530.6565 | 13523.9994 | 3756.835 | NORMAL
299.817 | 0.15 | 294.26 | 0.8 | 2 | 101352.97 | 13762.4267 | 13755.7795 | 3549.202 | NORMAL
299.817 | 0.15 | 294.26 | 0.8 | 2 | 106868.78 | 13804.1325 | 13797.4927 | 3512.796 | NORMAL
299.817 | 0.15 | 294.26 | 1.11 | 1 | 57226.51 | 11389.8007 | 11367.5792 | 3068.49 | NORMAL
299.817 | 0.15 | 294.26 | 1.11 | 1 | 79289.74 | 11770.7503 | 11762.3813 | 2791.287 | NORMAL
299.817 | 0.15 | 294.26 | 1.11 | 1 | 101352.97 | 11974.7655 | 11964.9223 | 2643.75 | NORMAL
299.817 | 0.15 | 294.26 | 1.11 | 1 | 106868.78 | 12008.9977 | 12000.5553 | 2618.614 | NORMAL
299.817 | 0.15 | 294.26 | 1.11 | 2 | 57226.51 | 14164.5956 | 14155.6577 | 4287.18 | NORMAL
299.817 | 0.15 | 294.26 | 1.11 | 2 | 79289.74 | 14727.9601 | 14718.9172 | 3839.918 | NORMAL
299.817 | 0.15 | 294.26 | 1.11 | 2 | 101352.97 | 15027.5205 | 15018.4439 | 3611.228 | NORMAL
299.817 | 0.15 | 294.26 | 1.11 | 2 | 106868.78 | 15080.6272 | 15071.5336 | 3571.26 | NORMAL
299.817 | 0.15 | 294.26 | 1.42 | 1 | 57226.51 | 11908.2356 | 11898.7686 | 3091.45 | NORMAL
299.817 | 0.15 | 294.26 | 1.42 | 1 | 79289.74 | 12342.8781 | 12333.1889 | 2799.27 | NORMAL
299.817 | 0.15 | 294.26 | 1.42 | 1 | 101352.97 | 12577.5498 | 12567.7519 | 2643.225 | NORMAL
299.817 | 0.15 | 294.26 | 1.42 | 1 | 106868.78 | 12619.2556 | 12609.4504 | 2615.584 | NORMAL
299.817 | 0.15 | 294.26 | 1.42 | 2 | 57226.51 | 14882.2978 | 14871.6569 | 4372.21 | NORMAL
299.817 | 0.15 | 294.26 | 1.42 | 2 | 79289.74 | 15539.0387 | 15528.1924 | 3897.5 | NORMAL
299.817 | 0.15 | 294.26 | 1.42 | 2 | 101352.97 | 15890.0352 | 15879.0869 | 3654.562 | NORMAL
299.817 | 0.15 | 294.26 | 1.42 | 2 | 106868.78 | 15952.6377 | 15941.6783 | 3612.102 | NORMAL
299.817 | 0.15 | 297.037 | 0.5 | 1 | 57226.51 | 9749.1208 | 9744.0415 | 3001.949 | NORMAL
299.817 | 0.15 | 297.037 | 0.5 | 1 | 79289.74 | 9979.6014 | 9974.5517 | 2770.367 | NORMAL
299.817 | 0.15 | 297.037 | 0.5 | 1 | 101352.97 | 10095.5744 | 10090.5469 | 2651.237 | NORMAL
299.817 | 0.15 | 297.037 | 0.5 | 1 | 106868.78 | 10116.3247 | 10111.2969 | 2630.5452 | NORMAL
299.817 | 0.15 | 297.037 | 0.5 | 2 | 57226.51 | 11807.796 | 11803.1792 | 4020.738 | NORMAL
299.817 | 0.15 | 297.037 | 0.5 | 2 | 79289.74 | 12110.3165 | 12105.7994 | 3661.105 | NORMAL
299.817 | 0.15 | 297.037 | 0.5 | 2 | 101352.97 | 12261.9871 | 12257.536 | 3477.417 | NORMAL
299.817 | 0.15 | 297.037 | 0.5 | 2 | 106868.78 | 12293.1418 | 12288.704 | 3446.0132 | NORMAL
299.817 | 0.15 | 297.037 | 0.8 | 1 | 57226.51 | 11263.9801 | 11255.8362 | 3062.894 | NORMAL
299.817 | 0.15 | 297.037 | 0.8 | 1 | 79289.74 | 11605.8617 | 11597.6447 | 2789.162 | NORMAL
299.817 | 0.15 | 297.037 | 0.8 | 1 | 101352.97 | 11787.2802 | 11779.0409 | 2644.107 | NORMAL
299.817 | 0.15 | 297.037 | 0.8 | 1 | 106868.78 | 11817.2919 | 11809.0434 | 2619.807 | NORMAL
299.817 | 0.15 | 297.037 | 0.8 | 2 | 57226.51 | 13809.2614 | 13800.8792 | 4245.242 | NORMAL
299.817 | 0.15 | 297.037 | 0.8 | 2 | 79289.74 | 14297.3329 | 14288.969 | 3809.803 | NORMAL
299.817 | 0.15 | 297.037 | 0.8 | 2 | 101352.97 | 14553.7222 | 14545.3683 | 3587.842 | NORMAL
299.817 | 0.15 | 297.037 | 0.8 | 2 | 106868.78 | 14600.2345 | 14591.8831 | 3549.04 | NORMAL
299.817 | 0.15 | 297.037 | 1.11 | 1 | 57226.51 | 12116.7057 | 12106.4308 | 3100.69 | NORMAL
299.817 | 0.15 | 297.037 | 1.11 | 1 | 79289.74 | 12540.7679 | 12530.3214 | 2802.26 | NORMAL
299.817 | 0.15 | 297.037 | 1.11 | 1 | 101352.97 | 12768.347 | 12757.8259 | 2643.123 | NORMAL
299.817 | 0.15 | 297.037 | 1.11 | 1 | 106868.78 | 12808.7632 | 12798.2088 | 2614.993 | NORMAL
299.817 | 0.15 | 297.037 | 1.11 | 2 | 57226.51 | 14960.9906 | 14949.8447 | 4381.47 | NORMAL
299.817 | 0.15 | 297.037 | 1.11 | 2 | 79289.74 | 15586.1079 | 15574.8235 | 3900.88 | NORMAL
299.817 | 0.15 | 297.037 | 1.11 | 2 | 101352.97 | 15917.2919 | 15905.9588 | 3655.962 | NORMAL
299.817 | 0.15 | 297.037 | 1.11 | 2 | 106868.78 | 15976.4068 | 15965.0636 | 3613.213 | NORMAL
299.817 | 0.15 | 297.037 | 1.42 | 1 | 57226.51 | 12679.1032 | 12667.3243 | 3126.86 | NORMAL
299.817 | 0.15 | 297.037 | 1.42 | 1 | 79289.74 | 13164.9765 | 13152.9043 | 2811.96 | NORMAL
299.817 | 0.15 | 297.037 | 1.42 | 1 | 101352.97 | 13428.0188 | 13415.7993 | 2643.391 | NORMAL
299.817 | 0.15 | 297.037 | 1.42 | 1 | 106868.78 | 13474.9414 | 13460.0246 | 2613.43 | NORMAL
299.817 | 0.15 | 297.037 | 1.42 | 2 | 57226.51 | 15730.9496 | 15717.7356 | 4473.82 | NORMAL
299.817 | 0.15 | 297.037 | 1.42 | 2 | 79289.74 | 16459.0856 | 16433.1296 | 3964.39 | NORMAL
299.817 | 0.15 | 297.037 | 1.42 | 2 | 101352.97 | 16850.5862 | 16836.954 | 3703.943 | NORMAL
299.817 | 0.15 | 297.037 | 1.42 | 2 | 106868.78 | 16918.7866 | 16905.1332 | 3658.421 | NORMAL
299.817 | 0.15 | 299.814 | 0.5 | 1 | 57226.51 | 10308.2943 | 10302.0062 | 3024.043 | NORMAL
299.817 | 0.15 | 299.814 | 0.5 | 1 | 79289.74 | 10559.1149 | 10552.8639 | 2776.503 | NORMAL
299.817 | 0.15 | 299.814 | 0.5 | 1 | 101352.97 | 10686.1665 | 10679.9471 | 2648.759 | NORMAL
299.817 | 0.15 | 299.814 | 0.5 | 1 | 106868.78 | 10709.3787 | 10703.1565 | 2625.7946 | NORMAL
299.817 | 0.15 | 299.814 | 0.5 | 2 | 57226.51 | 12408.7632 | 12402.9807 | 4086.778 | NORMAL
299.817 | 0.15 | 299.814 | 0.5 | 2 | 79289.74 | 12656.3013 | 12650.6692 | 3699.619 | NORMAL
299.817 | 0.15 | 299.814 | 0.5 | 2 | 101352.97 | 12847.5674 | 12842.0301 | 3505.326 | NORMAL
299.817 | 0.15 | 299.814 | 0.5 | 2 | 106868.78 | 12876.4654 | 12870.9543 | 3471.4263 | NORMAL
299.817 | 0.15 | 299.814 | 0.8 | 1 | 57226.51 | 11938.0129 | 11927.9969 | 3092.418 | NORMAL
299.817 | 0.15 | 299.814 | 0.8 | 1 | 79289.74 | 12314.449 | 12304.3388 | 2798.88 | NORMAL
299.817 | 0.15 | 299.814 | 0.8 | 1 | 101352.97 | 12514.7714 | 12504.6219 | 2643.248 | NORMAL
299.817 | 0.15 | 299.814 | 0.8 | 1 | 106868.78 | 12550.2638 | 12540.1106 | 2615.82 | NORMAL
299.817 | 0.15 | 299.814 | 0.8 | 2 | 57226.51 | 14540.5041 | 14530.1804 | 4330.782 | NORMAL
299.817 | 0.15 | 299.814 | 0.8 | 2 | 79289.74 | 15077.0809 | 15066.7531 | 3864.566 | NORMAL
299.817 | 0.15 | 299.814 | 0.8 | 2 | 101352.97 | 15359.3787 | 15349.0725 | 3627.796 | NORMAL
299.817 | 0.15 | 299.814 | 0.8 | 2 | 106868.78 | 15409.3201 | 15399.0112 | 3586.536 | NORMAL
299.817 | 0.15 | 299.814 | 1.11 | 1 | 57226.51 | 12856.9168 | 12844.3298 | 3135.23 | NORMAL
299.817 | 0.15 | 299.814 | 1.11 | 1 | 79289.74 | 13327.4326 | 13314.6116 | 2814.616 | NORMAL
299.817 | 0.15 | 299.814 | 1.11 | 1 | 101352.97 | 13580.891 | 13567.9484 | 2643.549 | NORMAL
299.817 | 0.15 | 299.814 | 1.11 | 1 | 106868.78 | 13626.2603 | 13613.3017 | 2613.164 | NORMAL
299.817 | 0.15 | 299.814 | 1.11 | 2 | 57226.51 | 15769.6659 | 15755.9936 | 4478.51 | NORMAL
299.817 | 0.15 | 299.814 | 1.11 | 2 | 79289.74 | 16458.265 | 16444.4235 | 3964.344 | NORMAL
299.817 | 0.15 | 299.814 | 1.11 | 2 | 101352.97 | 16823.9742 | 16810.044 | 3702.657 | NORMAL
299.817 | 0.15 | 299.814 | 1.11 | 2 | 106868.78 | 16889.1852 | 16875.2348 | 3656.952 | NORMAL
299.817 | 0.15 | 299.814 | 1.42 | 1 | 57226.51 | 13462.925 | 13448.4927 | 3164.96 | NORMAL
299.817 | 0.15 | 299.814 | 1.42 | 1 | 79289.74 | 14006.5944 | 13991.7894 | 2825.59 | NORMAL
299.817 | 0.15 | 299.814 | 1.42 | 1 | 101352.97 | 14298.8863 | 14283.8867 | 2644.804 | NORMAL
299.817 | 0.15 | 299.814 | 1.42 | 1 | 106868.78 | 14351.612 | 14336.5858 | 2612.469 | NORMAL
299.817 | 0.15 | 299.814 | 1.42 | 2 | 57226.51 | 16589.3025 | 16565.8286 | 4580.44 | NORMAL
299.817 | 0.15 | 299.814 | 1.42 | 2 | 79289.74 | 17394.7831 | 17378.2581 | 4034.35 | NORMAL
299.817 | 0.15 | 299.814 | 1.42 | 2 | 101352.97 | 17826.4068 | 17809.7035 | 3755.68 | NORMAL
299.817 | 0.15 | 299.814 | 1.42 | 2 | 106868.78 | 17903.6635 | 17886.9057 | 3707.04 | NORMAL
299.817 | 0.15 | 302.591 | 0.5 | 1 | 57226.51 | 10880.7444 | 10873.0735 | 3046.79 | NORMAL
299.817 | 0.15 | 302.591 | 0.5 | 1 | 79289.74 | 11148.857 | 11141.2312 | 2783.42 | NORMAL
299.817 | 0.15 | 302.591 | 0.5 | 1 | 101352.97 | 11287.1923 | 11279.596 | 2646.638 | NORMAL
299.817 | 0.15 | 302.591 | 0.5 | 1 | 106868.78 | 11312.1336 | 11304.5432 | 2622.2422 | NORMAL
299.817 | 0.15 | 302.591 | 0.5 | 2 | 57226.51 | 13018.5522 | 13011.431 | 4155.153 | NORMAL
299.817 | 0.15 | 302.591 | 0.5 | 2 | 79289.74 | 13271.0141 | 13264.1795 | 3738.319 | NORMAL
299.817 | 0.15 | 302.591 | 0.5 | 2 | 101352.97 | 13501.5533 | 13494.7351 | 3536.331 | NORMAL
299.817 | 0.15 | 302.591 | 0.5 | 2 | 106868.78 | 13515.3283 | 13508.5571 | 3499.8067 | NORMAL
299.817 | 0.15 | 302.591 | 0.8 | 1 | 57226.51 | 12622.8605 | 12607.5111 | 3123.918 | NORMAL
299.817 | 0.15 | 302.591 | 0.8 | 1 | 79289.74 | 13036.6354 | 13024.3679 | 2809.923 | NORMAL
299.817 | 0.15 | 302.591 | 0.8 | 1 | 101352.97 | 13257.8253 | 13245.5088 | 2643.207 | NORMAL
299.817 | 0.15 | 302.591 | 0.8 | 1 | 106868.78 | 13297.1278 | 13284.8013 | 2613.785 | NORMAL
299.817 | 0.15 | 302.591 | 0.8 | 2 | 57226.51 | 15281.0668 | 15268.5058 | 4419.589 | NORMAL
299.817 | 0.15 | 302.591 | 0.8 | 2 | 79289.74 | 15869.8417 | 15857.2887 | 3921.432 | NORMAL
299.817 | 0.15 | 302.591 | 0.8 | 2 | 101352.97 | 16178.3998 | 16165.8453 | 3669.297 | NORMAL
299.817 | 0.15 | 302.591 | 0.8 | 2 | 106868.78 | 16233.177 | 16220.6288 | 3625.422 | NORMAL
299.817 | 0.15 | 302.591 | 1.11 | 1 | 57226.51 | 13608.6753 | 13584.5471 | 3172.17 | NORMAL
299.817 | 0.15 | 302.591 | 1.11 | 1 | 79289.74 | 14131.6237 | 14116.0789 | 2827.871 | NORMAL
299.817 | 0.15 | 302.591 | 1.11 | 1 | 101352.97 | 14411.2251 | 14395.5313 | 2645.065 | NORMAL
299.817 | 0.15 | 302.591 | 1.11 | 1 | 106868.78 | 14461.5475 | 14445.8278 | 2612.459 | NORMAL
299.817 | 0.15 | 302.591 | 1.11 | 2 | 57226.51 | 16587.4267 | 16570.8891 | 4580.22 | NORMAL
299.817 | 0.15 | 302.591 | 1.11 | 2 | 79289.74 | 17344.2849 | 17327.4956 | 4030.514 | NORMAL
299.817 | 0.15 | 302.591 | 1.11 | 2 | 101352.97 | 17746.8054 | 17729.9104 | 3751.442 | NORMAL
299.817 | 0.15 | 302.591 | 1.11 | 2 | 106868.78 | 17818.6108 | 17801.7009 | 3702.776 | NORMAL
299.817 | 0.15 | 302.591 | 1.42 | 1 | 57226.51 | 14260.551 | 14243.0818 | 3205.82 | NORMAL
299.817 | 0.15 | 302.591 | 1.42 | 1 | 79289.74 | 14864.5662 | 14846.6247 | 2841.76 | NORMAL
299.817 | 0.15 | 302.591 | 1.42 | 1 | 101352.97 | 15190.7093 | 15172.526 | 2647.655 | NORMAL
299.817 | 0.15 | 302.591 | 1.42 | 1 | 106868.78 | 15249.7655 | 15231.5268 | 2612.875 | NORMAL
299.817 | 0.15 | 302.591 | 1.42 | 2 | 57226.51 | 17457.3271 | 17437.8098 | 4691.72 | NORMAL
299.817 | 0.15 | 302.591 | 1.42 | 2 | 79289.74 | 18345.1348 | 18325.1386 | 4107.48 | NORMAL
299.817 | 0.15 | 302.591 | 1.42 | 2 | 101352.97 | 18820.9555 | 18800.7229 | 3809.98 | NORMAL
299.817 | 0.15 | 302.591 | 1.42 | 2 | 106868.78 | 18906.7409 | 18886.4729 | 3758.24 | NORMAL
299.817 | 0.15 | 305.368 | 0.5 | 1 | 57226.51 | 11458.265 | 11449.0296 | 3071.344 | NORMAL
299.817 | 0.15 | 305.368 | 0.5 | 1 | 79289.74 | 11748.6225 | 11739.4468 | 2791.034 | NORMAL
299.817 | 0.15 | 305.368 | 0.5 | 1 | 101352.97 | 11900.5276 | 11891.3879 | 2643.884 | NORMAL
299.817 | 0.15 | 305.368 | 0.5 | 1 | 106868.78 | 11925.762 | 11916.6269 | 2619.1451 | NORMAL
299.817 | 0.15 | 305.368 | 0.5 | 2 | 57226.51 | 13475.2931 | 13466.9114 | 4206.871 | NORMAL
299.817 | 0.15 | 305.368 | 0.5 | 2 | 79289.74 | 13949.8242 | 13941.4124 | 3785.433 | NORMAL
299.817 | 0.15 | 305.368 | 0.5 | 2 | 101352.97 | 14180.5393 | 14172.2011 | 3569.726 | NORMAL
299.817 | 0.15 | 305.368 | 0.5 | 2 | 106868.78 | 14178.136 | 14169.9127 | 3530.1852 | NORMAL
299.817 | 0.15 | 305.368 | 0.8 | 1 | 57226.51 | 13318.1125 | 13303.5692 | 3157.512 | NORMAL
299.817 | 0.15 | 305.368 | 0.8 | 1 | 79289.74 | 13773.857 | 13759.1603 | 2821.523 | NORMAL
299.817 | 0.15 | 305.368 | 0.8 | 1 | 101352.97 | 14015.592 | 14000.8196 | 2644.177 | NORMAL
299.817 | 0.15 | 305.368 | 0.8 | 1 | 106868.78 | 14058.9683 | 14044.1924 | 2612.667 | NORMAL
299.817 | 0.15 | 305.368 | 0.8 | 2 | 57226.51 | 16033.0012 | 16017.9462 | 4510.924 | NORMAL
299.817 | 0.15 | 305.368 | 0.8 | 2 | 79289.74 | 16674.2966 | 16659.223 | 3980.349 | NORMAL
299.817 | 0.15 | 305.368 | 0.8 | 2 | 101352.97 | 17010.5217 | 16995.4504 | 3712.436 | NORMAL
299.817 | 0.15 | 305.368 | 0.8 | 2 | 106868.78 | 17070.1348 | 17055.0619 | 3665.804 | NORMAL
299.817 | 0.15 | 305.368 | 1.11 | 1 | 57226.51 | 14372.3329 | 14354.1088 | 3211.66 | NORMAL
299.817 | 0.15 | 305.368 | 1.11 | 1 | 79289.74 | 14950.3517 | 14931.7385 | 2843.487 | NORMAL
299.817 | 0.15 | 305.368 | 1.11 | 1 | 101352.97 | 15259.3201 | 15240.5206 | 2647.95 | NORMAL
299.817 | 0.15 | 305.368 | 1.11 | 1 | 106868.78 | 15315.211 | 15296.3733 | 2612.969 | NORMAL
299.817 | 0.15 | 305.368 | 1.11 | 2 | 57226.51 | 17414.7128 | 17391.0114 | 4686.12 | NORMAL
299.817 | 0.15 | 305.368 | 1.11 | 2 | 79289.74 | 18243.4349 | 18223.3489 | 4099.569 | NORMAL
299.817 | 0.15 | 305.368 | 1.11 | 2 | 101352.97 | 18684.7011 | 18664.4655 | 3802.423 | NORMAL
299.817 | 0.15 | 305.368 | 1.11 | 2 | 106868.78 | 18763.3353 | 18743.0709 | 3750.852 | NORMAL
299.817 | 0.15 | 305.368 | 1.42 | 1 | 57226.51 | 15070.0762 | 15049.2041 | 3249.61 | NORMAL
299.817 | 0.15 | 305.368 | 1.42 | 1 | 79289.74 | 15740.2696 | 15718.7842 | 2859.97 | NORMAL
299.817 | 0.15 | 305.368 | 1.42 | 1 | 101352.97 | 16102.3154 | 16080.5289 | 2651.963 | NORMAL
299.817 | 0.15 | 305.368 | 1.42 | 1 | 106868.78 | 16167.9074 | 16146.0484 | 2614.676 | NORMAL
299.817 | 0.15 | 305.368 | 1.42 | 2 | 57226.51 | 18334.0563 | 18280.1541 | 4807.56 | NORMAL
299.817 | 0.15 | 305.368 | 1.42 | 2 | 79289.74 | 19308.5873 | 19284.7026 | 4184.01 | NORMAL
299.817 | 0.15 | 305.368 | 1.42 | 2 | 101352.97 | 19832.9133 | 19808.7171 | 3866.964 | NORMAL
299.817 | 0.15 | 305.368 | 1.42 | 2 | 106868.78 | 19926.7878 | 19902.5369 | 3812.005 | NORMAL
299.817 | 0.25 | 288.706 | 0.5 | 1 | 57226.51 | 8133.5873 | 8131.2042 | 2942.139 | NORMAL
299.817 | 0.25 | 288.706 | 0.5 | 1 | 79289.74 | 8304.6307 | 8302.2722 | 2757.511 | NORMAL
299.817 | 0.25 | 288.706 | 0.5 | 1 | 101352.97 | 8390.0645 | 8387.7153 | 2664.961 | NORMAL
299.817 | 0.25 | 288.706 | 0.5 | 1 | 106868.78 | 8403.0481 | 8400.7036 | 2650.6484 | NORMAL
299.817 | 0.25 | 288.706 | 0.5 | 2 | 57226.51 | 10285.7855 | 9759.3487 | 3858.669 | NORMAL
299.817 | 0.25 | 288.706 | 0.5 | 2 | 79289.74 | 10530.3341 | 9959.7901 | 3552.454 | NORMAL
299.817 | 0.25 | 288.706 | 0.5 | 2 | 101352.97 | 10622.8605 | 10093.4915 | 3402.5949 | NORMAL
299.817 | 0.25 | 288.706 | 0.5 | 2 | 106868.78 | 10610.2872 | 10211.2661 | 3374.0806 | NORMAL
299.817 | 0.25 | 288.706 | 0.8 | 1 | 57226.51 | 9319.0211 | 9315.0792 | 2985.648 | NORMAL
299.817 | 0.25 | 288.706 | 0.8 | 1 | 79289.74 | 9570.6038 | 9566.6415 | 2766.297 | NORMAL
299.817 | 0.25 | 288.706 | 0.8 | 1 | 101352.97 | 9698.5639 | 9694.5972 | 2653.684 | NORMAL
299.817 | 0.25 | 288.706 | 0.8 | 1 | 106868.78 | 9720.34 | 9716.3644 | 2634.453 | NORMAL
299.817 | 0.25 | 288.706 | 0.8 | 2 | 57226.51 | 11691.2075 | 11687.2208 | 4007.998 | NORMAL
299.817 | 0.25 | 288.706 | 0.8 | 2 | 79289.74 | 12045.4865 | 12041.5235 | 3656.712 | NORMAL
299.817 | 0.25 | 288.706 | 0.8 | 2 | 101352.97 | 12231.3013 | 12227.3506 | 3476.013 | NORMAL
299.817 | 0.25 | 288.706 | 0.8 | 2 | 106868.78 | 12264.6835 | 12260.7342 | 3444.283 | NORMAL
299.817 | 0.25 | 288.706 | 1.11 | 1 | 57226.51 | 9981.9754 | 9976.9644 | 3010.65 | NORMAL
299.817 | 0.25 | 288.706 | 1.11 | 1 | 79289.74 | 10286.1958 | 10281.1041 | 2773.547 | NORMAL
299.817 | 0.25 | 288.706 | 1.11 | 1 | 101352.97 | 10443.6108 | 10438.4934 | 2650.014 | NORMAL
299.817 | 0.25 | 288.706 | 1.11 | 1 | 106868.78 | 10473.1829 | 10468.0615 | 2627.541 | NORMAL
299.817 | 0.25 | 288.706 | 1.11 | 2 | 57226.51 | 12618.1712 | 12612.7453 | 4110.03 | NORMAL
299.817 | 0.25 | 288.706 | 1.11 | 2 | 79289.74 | 13068.0832 | 13062.6208 | 3725.378 | NORMAL
299.817 | 0.25 | 288.706 | 1.11 | 2 | 101352.97 | 13305.7737 | 13300.2918 | 3527.169 | NORMAL
299.817 | 0.25 | 288.706 | 1.11 | 2 | 106868.78 | 13348.5639 | 13343.0776 | 3492.317 | NORMAL
299.817 | 0.25 | 288.706 | 1.42 | 1 | 57226.51 | 10416.5299 | 10410.7383 | 3028.1 | NORMAL
299.817 | 0.25 | 288.706 | 1.42 | 1 | 79289.74 | 10760.0235 | 10754.1269 | 2778.74 | NORMAL
299.817 | 0.25 | 288.706 | 1.42 | 1 | 101352.97 | 10941.5006 | 10935.5484 | 2647.598 | NORMAL
299.817 | 0.25 | 288.706 | 1.42 | 1 | 106868.78 | 10973.2708 | 10962.8462 | 2624.642 | NORMAL
299.817 | 0.25 | 288.706 | 1.42 | 2 | 57226.51 | 13234.6424 | 13211.5215 | 4180.04 | NORMAL
299.817 | 0.25 | 288.706 | 1.42 | 2 | 79289.74 | 13757.3564 | 13748.5792 | 3772.37 | NORMAL
299.817 | 0.25 | 288.706 | 1.42 | 2 | 101352.97 | 14035.5217 | 14028.8548 | 3562.425 | NORMAL
299.817 | 0.25 | 288.706 | 1.42 | 2 | 106868.78 | 14084.9062 | 14078.244 | 3525.703 | NORMAL
299.817 | 0.25 | 291.483 | 0.5 | 1 | 57226.51 | 8670.1641 | 8667.0169 | 2961.034 | NORMAL
299.817 | 0.25 | 291.483 | 0.5 | 1 | 79289.74 | 8810.0821 | 8806.9633 | 2760.473 | NORMAL
299.817 | 0.25 | 291.483 | 0.5 | 1 | 101352.97 | 8910.0528 | 8906.9877 | 2660.145 | NORMAL
299.817 | 0.25 | 291.483 | 0.5 | 1 | 106868.78 | 8968.2298 | 8965.1357 | 2642.4811 | NORMAL
299.817 | 0.25 | 291.483 | 0.5 | 2 | 57226.51 | 10958.7632 | 10244.482 | 3927.686 | NORMAL
299.817 | 0.25 | 291.483 | 0.5 | 2 | 79289.74 | 11220.0469 | 10468.0569 | 3601.768 | NORMAL
299.817 | 0.25 | 291.483 | 0.5 | 2 | 101352.97 | 11326.1137 | 10637.3501 | 3433.791 | NORMAL
299.817 | 0.25 | 291.483 | 0.5 | 2 | 106868.78 | 11305.5686 | 10763.4779 | 3404.1776 | NORMAL
299.817 | 0.25 | 291.483 | 0.8 | 1 | 57226.51 | 9960.551 | 9955.4213 | 3009.899 | NORMAL
299.817 | 0.25 | 291.483 | 0.8 | 1 | 79289.74 | 10238.0715 | 10232.9115 | 2773.054 | NORMAL
299.817 | 0.25 | 291.483 | 0.8 | 1 | 101352.97 | 10381.1254 | 10375.9556 | 2650.293 | NORMAL
299.817 | 0.25 | 291.483 | 0.8 | 1 | 106868.78 | 10407.6788 | 10402.5062 | 2628.108 | NORMAL
299.817 | 0.25 | 291.483 | 0.8 | 2 | 57226.51 | 12391.9402 | 12386.7232 | 4084.94 | NORMAL
299.817 | 0.25 | 291.483 | 0.8 | 2 | 79289.74 | 12787.7784 | 12782.5738 | 3706.474 | NORMAL
299.817 | 0.25 | 291.483 | 0.8 | 2 | 101352.97 | 12912.3974 | 12907.2454 | 3509.702 | NORMAL
299.817 | 0.25 | 291.483 | 0.8 | 2 | 106868.78 | 13030.9496 | 13025.7633 | 3478.547 | NORMAL
299.817 | 0.25 | 291.483 | 1.11 | 1 | 57226.51 | 10684.3201 | 10677.8347 | 3038.79 | NORMAL
299.817 | 0.25 | 291.483 | 1.11 | 1 | 79289.74 | 11023.3587 | 11013.1952 | 2781.865 | NORMAL
299.817 | 0.25 | 291.483 | 1.11 | 1 | 101352.97 | 11201.7292 | 11195.0866 | 2647.121 | NORMAL
299.817 | 0.25 | 291.483 | 1.11 | 1 | 106868.78 | 11234.4373 | 11227.7865 | 2622.776 | NORMAL
299.817 | 0.25 | 291.483 | 1.11 | 2 | 57226.51 | 13391.823 | 13384.7789 | 4197.76 | NORMAL
299.817 | 0.25 | 291.483 | 1.11 | 2 | 79289.74 | 13895.6038 | 13888.5031 | 3781.885 | NORMAL
299.817 | 0.25 | 291.483 | 1.11 | 2 | 101352.97 | 14162.2216 | 14155.0838 | 3568.656 | NORMAL
299.817 | 0.25 | 291.483 | 1.11 | 2 | 106868.78 | 14209.4373 | 14202.3041 | 3531.368 | NORMAL
299.817 | 0.25 | 291.483 | 1.42 | 1 | 57226.51 | 11158.9977 | 11151.5323 | 3058.79 | NORMAL
299.817 | 0.25 | 291.483 | 1.42 | 1 | 79289.74 | 11545.4279 | 11537.7964 | 2788.37 | NORMAL
299.817 | 0.25 | 291.483 | 1.42 | 1 | 101352.97 | 11753.0188 | 11745.3088 | 2644.161 | NORMAL
299.817 | 0.25 | 291.483 | 1.42 | 1 | 106868.78 | 11786.8406 | 11772.4253 | 2619.985 | NORMAL
299.817 | 0.25 | 291.483 | 1.42 | 2 | 57226.51 | 14059.027 | 14050.6197 | 4274.1 | NORMAL
299.817 | 0.25 | 291.483 | 1.42 | 2 | 79289.74 | 14644.109 | 14628.4691 | 3834.02 | NORMAL
299.817 | 0.25 | 291.483 | 1.42 | 2 | 101352.97 | 14956.7116 | 14948.0816 | 3607.714 | NORMAL
299.817 | 0.25 | 291.483 | 1.42 | 2 | 106868.78 | 15012.1923 | 15003.5452 | 3568.088 | NORMAL
299.817 | 0.25 | 294.26 | 0.5 | 1 | 57226.51 | 9121.7175 | 9117.8134 | 2977.623 | NORMAL
299.817 | 0.25 | 294.26 | 0.5 | 1 | 79289.74 | 9356.9168 | 9352.9681 | 2764.265 | NORMAL
299.817 | 0.25 | 294.26 | 0.5 | 1 | 101352.97 | 9487.3681 | 9483.4119 | 2655.284 | NORMAL
299.817 | 0.25 | 294.26 | 0.5 | 1 | 106868.78 | 9500.2345 | 9496.2824 | 2636.8744 | NORMAL
299.817 | 0.25 | 294.26 | 0.5 | 2 | 57226.51 | 11644.3728 | 10702.7972 | 4003.287 | NORMAL
299.817 | 0.25 | 294.26 | 0.5 | 2 | 79289.74 | 11942.4091 | 10971.1211 | 3649.302 | NORMAL
299.817 | 0.25 | 294.26 | 0.5 | 2 | 101352.97 | 12054.3669 | 11165.4659 | 3467.944 | NORMAL
299.817 | 0.25 | 294.26 | 0.5 | 2 | 106868.78 | 12031.1254 | 11234.5927 | 3434.5092 | NORMAL
299.817 | 0.25 | 294.26 | 0.8 | 1 | 57226.51 | 10614.0387 | 10606.4497 | 3035.833 | NORMAL
299.817 | 0.25 | 294.26 | 0.8 | 1 | 79289.74 | 10920.8675 | 10914.3041 | 2780.602 | NORMAL
299.817 | 0.25 | 294.26 | 0.8 | 1 | 101352.97 | 11081.1547 | 11074.5615 | 2647.031 | NORMAL
299.817 | 0.25 | 294.26 | 0.8 | 1 | 106868.78 | 11109.4373 | 11102.8383 | 2623.586 | NORMAL
299.817 | 0.25 | 294.26 | 0.8 | 2 | 57226.51 | 13104.5428 | 13097.8595 | 4165.283 | NORMAL
299.817 | 0.25 | 294.26 | 0.8 | 2 | 79289.74 | 13424.9414 | 13418.4706 | 3750.194 | NORMAL
299.817 | 0.25 | 294.26 | 0.8 | 2 | 101352.97 | 13651.1723 | 13644.729 | 3543.869 | NORMAL
299.817 | 0.25 | 294.26 | 0.8 | 2 | 106868.78 | 13718.6987 | 13712.2235 | 3509.327 | NORMAL
299.817 | 0.25 | 294.26 | 1.11 | 1 | 57226.51 | 11400.4982 | 11392.2671 | 3068.93 | NORMAL
299.817 | 0.25 | 294.26 | 1.11 | 1 | 79289.74 | 11779.1618 | 11770.7986 | 2791.398 | NORMAL
299.817 | 0.25 | 294.26 | 1.11 | 1 | 101352.97 | 11981.5358 | 11973.1007 | 2643.74 | NORMAL
299.817 | 0.25 | 294.26 | 1.11 | 1 | 106868.78 | 12015.8851 | 12005.5995 | 2618.583 | NORMAL
299.817 | 0.25 | 294.26 | 1.11 | 2 | 57226.51 | 14179.3083 | 14170.3754 | 4288.88 | NORMAL
299.817 | 0.25 | 294.26 | 1.11 | 2 | 79289.74 | 14739.8007 | 14730.7652 | 3840.756 | NORMAL
299.817 | 0.25 | 294.26 | 1.11 | 2 | 101352.97 | 15037.3388 | 15028.2563 | 3611.712 | NORMAL
299.817 | 0.25 | 294.26 | 1.11 | 2 | 106868.78 | 15089.7128 | 15080.6288 | 3571.742 | NORMAL
299.817 | 0.25 | 294.26 | 1.42 | 1 | 57226.51 | 11917.4091 | 11903.6803 | 3091.82 | NORMAL
299.817 | 0.25 | 294.26 | 1.42 | 1 | 79289.74 | 12350.1758 | 12339.8141 | 2799.38 | NORMAL
299.817 | 0.25 | 294.26 | 1.42 | 1 | 101352.97 | 12583.2063 | 12573.4166 | 2643.213 | NORMAL
299.817 | 0.25 | 294.26 | 1.42 | 1 | 106868.78 | 12625.0293 | 12615.2323 | 2615.572 | NORMAL
299.817 | 0.25 | 294.26 | 1.42 | 2 | 57226.51 | 14895.1055 | 14884.4853 | 4373.71 | NORMAL
299.817 | 0.25 | 294.26 | 1.42 | 2 | 79289.74 | 15549.4724 | 15538.65 | 3898.26 | NORMAL
299.817 | 0.25 | 294.26 | 1.42 | 2 | 101352.97 | 15898.7397 | 15887.8014 | 3655.004 | NORMAL
299.817 | 0.25 | 294.26 | 1.42 | 2 | 106868.78 | 15960.9613 | 15950.0121 | 3612.494 | NORMAL
299.817 | 0.25 | 297.037 | 0.5 | 1 | 57226.51 | 9689.0973 | 9684.088 | 2999.214 | NORMAL
299.817 | 0.25 | 297.037 | 0.5 | 1 | 79289.74 | 9977.755 | 9972.7062 | 2770.237 | NORMAL
299.817 | 0.25 | 297.037 | 0.5 | 1 | 101352.97 | 10122.1571 | 10101.2548 | 2651.133 | NORMAL
299.817 | 0.25 | 297.037 | 0.5 | 1 | 106868.78 | 10091.2075 | 10086.2325 | 2630.6954 | NORMAL
299.817 | 0.25 | 297.037 | 0.5 | 2 | 57226.51 | 12365.973 | 11151.6468 | 4082.123 | NORMAL
299.817 | 0.25 | 297.037 | 0.5 | 2 | 79289.74 | 12694.2556 | 11434.4142 | 3700.434 | NORMAL
299.817 | 0.25 | 297.037 | 0.5 | 2 | 101352.97 | 12817.7608 | 11680.4025 | 3504.124 | NORMAL
299.817 | 0.25 | 297.037 | 0.5 | 2 | 106868.78 | 12789.1266 | 11772.0202 | 3467.7927 | NORMAL
299.817 | 0.25 | 297.037 | 0.8 | 1 | 57226.51 | 11280.0703 | 11271.9261 | 3063.71 | NORMAL
299.817 | 0.25 | 297.037 | 0.8 | 1 | 79289.74 | 11618.5815 | 11610.3671 | 2789.333 | NORMAL
299.817 | 0.25 | 297.037 | 0.8 | 1 | 101352.97 | 11797.7139 | 11789.4791 | 2644.083 | NORMAL
299.817 | 0.25 | 297.037 | 0.8 | 1 | 106868.78 | 11827.2567 | 11819.0131 | 2619.759 | NORMAL
299.817 | 0.25 | 297.037 | 0.8 | 2 | 57226.51 | 13574.8242 | 13566.8829 | 4219.188 | NORMAL
299.817 | 0.25 | 297.037 | 0.8 | 2 | 79289.74 | 14184.2907 | 14176.1915 | 3800.043 | NORMAL
299.817 | 0.25 | 297.037 | 0.8 | 2 | 101352.97 | 14516.1196 | 14507.9034 | 3585.826 | NORMAL
299.817 | 0.25 | 297.037 | 0.8 | 2 | 106868.78 | 14497.7139 | 14489.5807 | 3544.553 | NORMAL
299.817 | 0.25 | 297.037 | 1.11 | 1 | 57226.51 | 12130.51 | 12120.2597 | 3101.29 | NORMAL
299.817 | 0.25 | 297.037 | 1.11 | 1 | 79289.74 | 12551.905 | 12541.487 | 2802.414 | NORMAL
299.817 | 0.25 | 297.037 | 1.11 | 1 | 101352.97 | 12777.2861 | 12766.7703 | 2643.115 | NORMAL
299.817 | 0.25 | 297.037 | 1.11 | 1 | 106868.78 | 12817.3505 | 12806.8147 | 2614.967 | NORMAL
299.817 | 0.25 | 297.037 | 1.11 | 2 | 57226.51 | 14979.8652 | 14968.7351 | 4383.67 | NORMAL
299.817 | 0.25 | 297.037 | 1.11 | 2 | 79289.74 | 15601.2016 | 15589.9376 | 3901.973 | NORMAL
299.817 | 0.25 | 297.037 | 1.11 | 2 | 101352.97 | 15929.8652 | 15918.5231 | 3656.609 | NORMAL
299.817 | 0.25 | 297.037 | 1.11 | 2 | 106868.78 | 15988.4232 | 15977.0714 | 3613.801 | NORMAL
299.817 | 0.25 | 297.037 | 1.42 | 1 | 57226.51 | 12690.9144 | 12666.7002 | 3127.41 | NORMAL
299.817 | 0.25 | 297.037 | 1.42 | 1 | 79289.74 | 13174.4138 | 13162.3724 | 2812.11 | NORMAL
299.817 | 0.25 | 297.037 | 1.42 | 1 | 101352.97 | 13435.8441 | 13423.6443 | 2643.393 | NORMAL
299.817 | 0.25 | 297.037 | 1.42 | 1 | 106868.78 | 13482.2685 | 13470.04 | 2613.411 | NORMAL
299.817 | 0.25 | 297.037 | 1.42 | 2 | 57226.51 | 15747.245 | 15734.0646 | 4475.78 | NORMAL
299.817 | 0.25 | 297.037 | 1.42 | 2 | 79289.74 | 16472.3916 | 16458.9171 | 3965.39 | NORMAL
299.817 | 0.25 | 297.037 | 1.42 | 2 | 101352.97 | 16860.3165 | 16846.6934 | 3704.54 | NORMAL
299.817 | 0.25 | 297.037 | 1.42 | 2 | 106868.78 | 16929.5135 | 16915.8683 | 3658.946 | NORMAL
299.817 | 0.25 | 299.814 | 0.5 | 1 | 57226.51 | 10328.0481 | 10321.7583 | 3024.231 | NORMAL
299.817 | 0.25 | 299.814 | 0.5 | 1 | 79289.74 | 10646.6588 | 10444.6598 | 2777.492 | NORMAL
299.817 | 0.25 | 299.814 | 0.5 | 1 | 101352.97 | 10799.7362 | 10538.307 | 2648.249 | NORMAL
299.817 | 0.25 | 299.814 | 0.5 | 1 | 106868.78 | 10770.9848 | 10613.793 | 2626.015 | NORMAL
299.817 | 0.25 | 299.814 | 0.5 | 2 | 57226.51 | 13143.5522 | 11613.9844 | 4168.966 | NORMAL
299.817 | 0.25 | 299.814 | 0.5 | 2 | 79289.74 | 13480.8324 | 12069.2005 | 3753.878 | NORMAL
299.817 | 0.25 | 299.814 | 0.5 | 2 | 101352.97 | 13613.3353 | 12273.6742 | 3542.141 | NORMAL
299.817 | 0.25 | 299.814 | 0.5 | 2 | 106868.78 | 13578.5756 | 12333.0808 | 3502.8711 | NORMAL
299.817 | 0.25 | 299.814 | 0.8 | 1 | 57226.51 | 11958.558 | 11948.5487 | 3093.453 | NORMAL
299.817 | 0.25 | 299.814 | 0.8 | 1 | 79289.74 | 12330.9789 | 12320.8798 | 2799.123 | NORMAL
299.817 | 0.25 | 299.814 | 0.8 | 1 | 101352.97 | 12528.1067 | 12517.9714 | 2643.243 | NORMAL
299.817 | 0.25 | 299.814 | 0.8 | 1 | 106868.78 | 12563.0422 | 12552.9038 | 2615.771 | NORMAL
299.817 | 0.25 | 299.814 | 0.8 | 2 | 57226.51 | 14336.8992 | 14327.1071 | 4306.868 | NORMAL
299.817 | 0.25 | 299.814 | 0.8 | 2 | 79289.74 | 15047.7139 | 15037.5417 | 3860.508 | NORMAL
299.817 | 0.25 | 299.814 | 0.8 | 2 | 101352.97 | 15405.3634 | 15395.0726 | 3629.956 | NORMAL
299.817 | 0.25 | 299.814 | 0.8 | 2 | 106868.78 | 15395.8968 | 15385.7048 | 3585.831 | NORMAL
299.817 | 0.25 | 299.814 | 1.11 | 1 | 57226.51 | 12874.4431 | 12861.8906 | 3136.06 | NORMAL
299.817 | 0.25 | 299.814 | 1.11 | 1 | 79289.74 | 13341.354 | 13328.5463 | 2814.854 | NORMAL
299.817 | 0.25 | 299.814 | 1.11 | 1 | 101352.97 | 13592.3798 | 13579.4671 | 2643.557 | NORMAL
299.817 | 0.25 | 299.814 | 1.11 | 1 | 106868.78 | 13637.2509 | 13624.3091 | 2613.144 | NORMAL
299.817 | 0.25 | 299.814 | 1.11 | 2 | 57226.51 | 15793.2591 | 15779.6137 | 4481.35 | NORMAL
299.817 | 0.25 | 299.814 | 1.11 | 2 | 79289.74 | 16477.374 | 16463.533 | 3965.763 | NORMAL
299.817 | 0.25 | 299.814 | 1.11 | 2 | 101352.97 | 16839.9179 | 16825.9913 | 3703.492 | NORMAL
299.817 | 0.25 | 299.814 | 1.11 | 2 | 106868.78 | 16904.5135 | 16890.5673 | 3657.698 | NORMAL
299.817 | 0.25 | 299.814 | 1.42 | 1 | 57226.51 | 13478.0481 | 13448.2751 | 3165.72 | NORMAL
299.817 | 0.25 | 299.814 | 1.42 | 1 | 79289.74 | 14018.7573 | 14003.9816 | 2825.81 | NORMAL
299.817 | 0.25 | 299.814 | 1.42 | 1 | 101352.97 | 14309.027 | 14284.0577 | 2644.831 | NORMAL
299.817 | 0.25 | 299.814 | 1.42 | 1 | 106868.78 | 14361.313 | 14346.3054 | 2612.475 | NORMAL
299.817 | 0.25 | 299.814 | 1.42 | 2 | 57226.51 | 16609.789 | 16593.6775 | 4583.05 | NORMAL
299.817 | 0.25 | 299.814 | 1.42 | 2 | 79289.74 | 17411.694 | 17395.1877 | 4035.64 | NORMAL
299.817 | 0.25 | 299.814 | 1.42 | 2 | 101352.97 | 17840.6213 | 17823.9225 | 3756.464 | NORMAL
299.817 | 0.25 | 299.814 | 1.42 | 2 | 106868.78 | 17917.3505 | 17900.6336 | 3707.722 | NORMAL
299.817 | 0.25 | 302.591 | 0.5 | 1 | 57226.51 | 11008.3529 | 10749.1722 | 3052.178 | NORMAL
299.817 | 0.25 | 302.591 | 0.5 | 1 | 79289.74 | 11362.6612 | 10895.4058 | 2785.944 | NORMAL
299.817 | 0.25 | 302.591 | 0.5 | 1 | 101352.97 | 11520.4572 | 11011.7945 | 2646.031 | NORMAL
299.817 | 0.25 | 302.591 | 0.5 | 1 | 106868.78 | 11482.5029 | 11094.4747 | 2621.1863 | NORMAL
299.817 | 0.25 | 302.591 | 0.5 | 2 | 57226.51 | 13991.6764 | 11980.9746 | 4265.358 | NORMAL
299.817 | 0.25 | 302.591 | 0.5 | 2 | 79289.74 | 14366.8816 | 12343.9241 | 3814.927 | NORMAL
299.817 | 0.25 | 302.591 | 0.5 | 2 | 101352.97 | 14493.4056 | 12647.8878 | 3585.191 | NORMAL
299.817 | 0.25 | 302.591 | 0.5 | 2 | 106868.78 | 14412.7491 | 12781.2403 | 3540.8008 | NORMAL
299.817 | 0.25 | 302.591 | 0.8 | 1 | 57226.51 | 12648.7984 | 12636.6682 | 3125.259 | NORMAL
299.817 | 0.25 | 302.591 | 0.8 | 1 | 79289.74 | 13058.2063 | 13045.9577 | 2809.575 | NORMAL
299.817 | 0.25 | 302.591 | 0.8 | 1 | 101352.97 | 13274.7948 | 13262.4891 | 2643.254 | NORMAL
299.817 | 0.25 | 302.591 | 0.8 | 1 | 106868.78 | 13313.3646 | 13301.0497 | 2613.751 | NORMAL
299.817 | 0.25 | 302.591 | 0.8 | 2 | 57226.51 | 15168.8746 | 15156.7546 | 4405.887 | NORMAL
299.817 | 0.25 | 302.591 | 0.8 | 2 | 79289.74 | 15952.5791 | 15915.2661 | 3925.279 | NORMAL
299.817 | 0.25 | 302.591 | 0.8 | 2 | 101352.97 | 16330.7444 | 16095.3857 | 3677.746 | NORMAL
299.817 | 0.25 | 302.591 | 0.8 | 2 | 106868.78 | 16326.5533 | 16268.0553 | 3629.846 | NORMAL
299.817 | 0.25 | 302.591 | 1.11 | 1 | 57226.51 | 13630.9203 | 13594.4303 | 3173.33 | NORMAL
299.817 | 0.25 | 302.591 | 1.11 | 1 | 79289.74 | 14149.3259 | 14133.8183 | 2828.205 | NORMAL
299.817 | 0.25 | 302.591 | 1.11 | 1 | 101352.97 | 14426.2016 | 14410.5348 | 2645.108 | NORMAL
299.817 | 0.25 | 302.591 | 1.11 | 1 | 106868.78 | 14475.9379 | 14460.246 | 2612.45 | NORMAL
299.817 | 0.25 | 302.591 | 1.11 | 2 | 57226.51 | 16616.823 | 16600.3225 | 4584 | NORMAL
299.817 | 0.25 | 302.591 | 1.11 | 2 | 79289.74 | 17368.3763 | 17351.6158 | 4032.367 | NORMAL
299.817 | 0.25 | 302.591 | 1.11 | 2 | 101352.97 | 17767.1454 | 17750.2666 | 3752.542 | NORMAL
299.817 | 0.25 | 302.591 | 1.11 | 2 | 106868.78 | 17837.9543 | 17821.0617 | 3703.755 | NORMAL
299.817 | 0.25 | 302.591 | 1.42 | 1 | 57226.51 | 14279.4842 | 14256.6941 | 3206.85 | NORMAL
299.817 | 0.25 | 302.591 | 1.42 | 1 | 79289.74 | 14880.0703 | 14862.1696 | 2842.08 | NORMAL
299.817 | 0.25 | 302.591 | 1.42 | 1 | 101352.97 | 15203.6635 | 15185.5104 | 2647.716 | NORMAL
299.817 | 0.25 | 302.591 | 1.42 | 1 | 106868.78 | 15262.1923 | 15233.5451 | 2612.887 | NORMAL
299.817 | 0.25 | 302.591 | 1.42 | 2 | 57226.51 | 17482.7374 | 17449.5901 | 4695.09 | NORMAL
299.817 | 0.25 | 302.591 | 1.42 | 2 | 79289.74 | 18366.3247 | 18346.3789 | 4109.13 | NORMAL
299.817 | 0.25 | 302.591 | 1.42 | 2 | 101352.97 | 18839.068 | 18818.8537 | 3810.989 | NORMAL
299.817 | 0.25 | 302.591 | 1.42 | 2 | 106868.78 | 18924.0621 | 18903.8134 | 3759.141 | NORMAL
299.817 | 0.25 | 305.368 | 0.5 | 1 | 57226.51 | 11734.2614 | 11187.3275 | 3082.909 | NORMAL
299.817 | 0.25 | 305.368 | 0.5 | 1 | 79289.74 | 12105.2169 | 11317.1673 | 2795.882 | NORMAL
299.817 | 0.25 | 305.368 | 0.5 | 1 | 101352.97 | 12277.3154 | 11476.4661 | 2643.818 | NORMAL
299.817 | 0.25 | 305.368 | 0.5 | 1 | 106868.78 | 12229.5135 | 11568.655 | 2617.1089 | NORMAL
299.817 | 0.25 | 305.368 | 0.5 | 2 | 57226.51 | 14847.6846 | 12362.5831 | 4367.388 | NORMAL
299.817 | 0.25 | 305.368 | 0.5 | 2 | 79289.74 | 15275.3224 | 12768.5503 | 3878.926 | NORMAL
299.817 | 0.25 | 305.368 | 0.5 | 2 | 101352.97 | 15405.2462 | 13118.3836 | 3630.372 | NORMAL
299.817 | 0.25 | 305.368 | 0.5 | 2 | 106868.78 | 15348.7104 | 13244.9241 | 3583.7141 | NORMAL
299.817 | 0.25 | 305.368 | 0.8 | 1 | 57226.51 | 13350.4982 | 13335.9862 | 3159.277 | NORMAL
299.817 | 0.25 | 305.368 | 0.8 | 1 | 79289.74 | 13799.7948 | 13785.1119 | 2821.991 | NORMAL
299.817 | 0.25 | 305.368 | 0.8 | 1 | 101352.97 | 14037.0164 | 14022.2635 | 2644.225 | NORMAL
299.817 | 0.25 | 305.368 | 0.8 | 1 | 106868.78 | 14079.4549 | 14064.6855 | 2612.641 | NORMAL
299.817 | 0.25 | 305.368 | 0.8 | 2 | 57226.51 | 16040.0352 | 16025.2302 | 4510.602 | NORMAL
299.817 | 0.25 | 305.368 | 0.8 | 2 | 79289.74 | 16894.4021 | 16560.2646 | 3994.304 | NORMAL
299.817 | 0.25 | 305.368 | 0.8 | 2 | 101352.97 | 17307.6202 | 16756.009 | 3728.374 | NORMAL
299.817 | 0.25 | 305.368 | 0.8 | 2 | 106868.78 | 17297.1864 | 16947.3335 | 3676.901 | NORMAL
299.817 | 0.25 | 305.368 | 1.11 | 1 | 57226.51 | 14400.4103 | 14382.2514 | 3213.15 | NORMAL
299.817 | 0.25 | 305.368 | 1.11 | 1 | 79289.74 | 14972.8605 | 14954.3091 | 2843.917 | NORMAL
299.817 | 0.25 | 305.368 | 1.11 | 1 | 101352.97 | 15277.9601 | 15259.1835 | 2648.036 | NORMAL
299.817 | 0.25 | 305.368 | 1.11 | 1 | 106868.78 | 15333.0891 | 15314.2907 | 2612.99 | NORMAL
299.817 | 0.25 | 305.368 | 1.11 | 2 | 57226.51 | 17450.9086 | 17431.2065 | 4690.89 | NORMAL
299.817 | 0.25 | 305.368 | 1.11 | 2 | 79289.74 | 18273.5932 | 18253.5471 | 4101.932 | NORMAL
299.817 | 0.25 | 305.368 | 1.11 | 2 | 101352.97 | 18328.9859 | 18309.8688 | 3783.439 | NORMAL
299.817 | 0.25 | 305.368 | 1.11 | 2 | 106868.78 | 18526.8171 | 18507.3269 | 3738.765 | NORMAL
299.817 | 0.25 | 305.368 | 1.42 | 1 | 57226.51 | 15094.871 | 15074.0854 | 3250.91 | NORMAL
299.817 | 0.25 | 305.368 | 1.42 | 1 | 79289.74 | 15759.4959 | 15735.9985 | 2860.41 | NORMAL
299.817 | 0.25 | 305.368 | 1.42 | 1 | 101352.97 | 16118.8159 | 16097.0717 | 2652.073 | NORMAL
299.817 | 0.25 | 305.368 | 1.42 | 1 | 106868.78 | 16183.9683 | 16162.1685 | 2614.715 | NORMAL
299.817 | 0.25 | 305.368 | 1.42 | 2 | 57226.51 | 18365.973 | 18342.7952 | 4811.82 | NORMAL
299.817 | 0.25 | 305.368 | 1.42 | 2 | 79289.74 | 19335.3165 | 19311.4954 | 4186.18 | NORMAL
299.817 | 0.25 | 305.368 | 1.42 | 2 | 101352.97 | 19855.422 | 19831.2778 | 3868.274 | NORMAL
299.817 | 0.25 | 305.368 | 1.42 | 2 | 106868.78 | 19948.476 | 19924.2785 | 3813.174 | NORMAL
299.817 | 0.35 | 288.706 | 0.5 | 1 | 57226.51 | 8370.5158 | 7795.4949 | 2950.375 | NORMAL
299.817 | 0.35 | 288.706 | 0.5 | 1 | 79289.74 | 8548.476 | 7939.3201 | 2759.29 | NORMAL
299.817 | 0.35 | 288.706 | 0.5 | 1 | 101352.97 | 8621.0727 | 8058.4529 | 2662.04 | NORMAL
299.817 | 0.35 | 288.706 | 0.5 | 1 | 106868.78 | 8595.5744 | 8116.1305 | 2647.096 | NORMAL
299.817 | 0.35 | 288.706 | 0.5 | 2 | 57226.51 | 10892.4971 | 9028.0501 | 3920.796 | NORMAL
299.817 | 0.35 | 288.706 | 0.5 | 2 | 79289.74 | 11043.0832 | 9342.5036 | 3590.557 | NORMAL
299.817 | 0.35 | 288.706 | 0.5 | 2 | 101352.97 | 11072.4502 | 9613.057 | 3422.8903 | NORMAL
299.817 | 0.35 | 288.706 | 0.5 | 2 | 106868.78 | 11036.1665 | 9727.9945 | 3392.9188 | NORMAL
299.817 | 0.35 | 288.706 | 0.8 | 1 | 57226.51 | 9326.6706 | 9322.7347 | 2985.877 | NORMAL
299.817 | 0.35 | 288.706 | 0.8 | 1 | 79289.74 | 9576.4068 | 9572.4422 | 2766.347 | NORMAL
299.817 | 0.35 | 288.706 | 0.8 | 1 | 101352.97 | 9703.1946 | 9699.226 | 2653.705 | NORMAL
299.817 | 0.35 | 288.706 | 0.8 | 1 | 106868.78 | 9724.9121 | 9720.9443 | 2634.349 | NORMAL
299.817 | 0.35 | 288.706 | 0.8 | 2 | 57226.51 | 11901.6706 | 11430.1621 | 4031.53 | NORMAL
299.817 | 0.35 | 288.706 | 0.8 | 2 | 79289.74 | 12318.5815 | 11681.1565 | 3674.688 | NORMAL
299.817 | 0.35 | 288.706 | 0.8 | 2 | 101352.97 | 12511.7526 | 11889.6308 | 3489.627 | NORMAL
299.817 | 0.35 | 288.706 | 0.8 | 2 | 106868.78 | 12497.3623 | 11997.0554 | 3454.924 | NORMAL
299.817 | 0.35 | 288.706 | 1.11 | 1 | 57226.51 | 9988.0715 | 9983.0575 | 3011 | NORMAL
299.817 | 0.35 | 288.706 | 1.11 | 1 | 79289.74 | 10291.1489 | 10286.0651 | 2773.602 | NORMAL
299.817 | 0.35 | 288.706 | 1.11 | 1 | 101352.97 | 10447.626 | 10442.5067 | 2650.005 | NORMAL
299.817 | 0.35 | 288.706 | 1.11 | 1 | 106868.78 | 10477.0516 | 10471.9283 | 2627.536 | NORMAL
299.817 | 0.35 | 288.706 | 1.11 | 2 | 57226.51 | 12433.7046 | 12428.6316 | 4088.65 | NORMAL
299.817 | 0.35 | 288.706 | 1.11 | 2 | 79289.74 | 12992.1161 | 12986.8413 | 3719.392 | NORMAL
299.817 | 0.35 | 288.706 | 1.11 | 2 | 101352.97 | 13286.0786 | 13280.7375 | 3526.476 | NORMAL
299.817 | 0.35 | 288.706 | 1.11 | 2 | 106868.78 | 13290.6506 | 13285.361 | 3490.01 | NORMAL
299.817 | 0.35 | 288.706 | 1.42 | 1 | 57226.51 | 10422.0106 | 10401.4792 | 3028.24 | NORMAL
299.817 | 0.35 | 288.706 | 1.42 | 1 | 79289.74 | 10764.2732 | 10758.3851 | 2778.79 | NORMAL
299.817 | 0.35 | 288.706 | 1.42 | 1 | 101352.97 | 10944.9883 | 10939.0451 | 2647.591 | NORMAL
299.817 | 0.35 | 288.706 | 1.42 | 1 | 106868.78 | 10976.8171 | 10970.8567 | 2624.493 | NORMAL
299.817 | 0.35 | 288.706 | 1.42 | 2 | 57226.51 | 13242.3798 | 13235.8778 | 4180.89 | NORMAL
299.817 | 0.35 | 288.706 | 1.42 | 2 | 79289.74 | 13763.5698 | 13756.9632 | 3772.81 | NORMAL
299.817 | 0.35 | 288.706 | 1.42 | 2 | 101352.97 | 14040.7386 | 14034.0833 | 3562.681 | NORMAL
299.817 | 0.35 | 288.706 | 1.42 | 2 | 106868.78 | 14090.1231 | 14083.4585 | 3525.929 | NORMAL
299.817 | 0.35 | 291.483 | 0.5 | 1 | 57226.51 | 8999.4724 | 8220.0371 | 2973.139 | NORMAL
299.817 | 0.35 | 291.483 | 0.5 | 1 | 79289.74 | 9201.2896 | 8349.3146 | 2762.762 | NORMAL
299.817 | 0.35 | 291.483 | 0.5 | 1 | 101352.97 | 9271.2485 | 8481.811 | 2656.952 | NORMAL
299.817 | 0.35 | 291.483 | 0.5 | 1 | 106868.78 | 9243.2591 | 8560.8847 | 2638.8119 | NORMAL
299.817 | 0.35 | 291.483 | 0.5 | 2 | 57226.51 | 11653.6635 | 9422.1734 | 4002.803 | NORMAL
299.817 | 0.35 | 291.483 | 0.5 | 2 | 79289.74 | 11825.5862 | 9802.2757 | 3642.426 | NORMAL
299.817 | 0.35 | 291.483 | 0.5 | 2 | 101352.97 | 11855.8324 | 10095.4072 | 3458.526 | NORMAL
299.817 | 0.35 | 291.483 | 0.5 | 2 | 106868.78 | 11814.5369 | 10189.8609 | 3425.7224 | NORMAL
299.817 | 0.35 | 291.483 | 0.8 | 1 | 57226.51 | 9963.4232 | 9958.312 | 3010.231 | NORMAL
299.817 | 0.35 | 291.483 | 0.8 | 1 | 79289.74 | 10134.4666 | 10129.4602 | 2771.281 | NORMAL
299.817 | 0.35 | 291.483 | 0.8 | 1 | 101352.97 | 10304.3669 | 10299.3075 | 2650.111 | NORMAL
299.817 | 0.35 | 291.483 | 0.8 | 1 | 106868.78 | 10342.4384 | 10337.3707 | 2628.647 | NORMAL
299.817 | 0.35 | 291.483 | 0.8 | 2 | 57226.51 | 12680.8324 | 12131.2578 | 4117.393 | NORMAL
299.817 | 0.35 | 291.483 | 0.8 | 2 | 79289.74 | 13152.0809 | 12454.4551 | 3730.708 | NORMAL
299.817 | 0.35 | 291.483 | 0.8 | 2 | 101352.97 | 13368.4056 | 12691.3494 | 3530.48 | NORMAL
299.817 | 0.35 | 291.483 | 0.8 | 2 | 106868.78 | 13350 | 12785.5753 | 3492.654 | NORMAL
299.817 | 0.35 | 291.483 | 1.11 | 1 | 57226.51 | 10692.4678 | 10685.9881 | 3039.22 | NORMAL
299.817 | 0.35 | 291.483 | 1.11 | 1 | 79289.74 | 11029.8945 | 11023.3096 | 2781.954 | NORMAL
299.817 | 0.35 | 291.483 | 1.11 | 1 | 101352.97 | 11207.0047 | 11199.0589 | 2647.095 | NORMAL
299.817 | 0.35 | 291.483 | 1.11 | 1 | 106868.78 | 11239.4783 | 11232.8358 | 2622.753 | NORMAL
299.817 | 0.35 | 291.483 | 1.11 | 2 | 57226.51 | 13282.0633 | 13275.3293 | 4185.15 | NORMAL
299.817 | 0.35 | 291.483 | 1.11 | 2 | 79289.74 | 13856.5358 | 13849.5798 | 3778.994 | NORMAL
299.817 | 0.35 | 291.483 | 1.11 | 2 | 101352.97 | 14165.2696 | 14158.2153 | 3568.807 | NORMAL
299.817 | 0.35 | 291.483 | 1.11 | 2 | 106868.78 | 14170.4572 | 14163.457 | 3529.362 | NORMAL
299.817 | 0.35 | 291.483 | 1.42 | 1 | 57226.51 | 11166.0903 | 11138.0522 | 3059.08 | NORMAL
299.817 | 0.35 | 291.483 | 1.42 | 1 | 79289.74 | 11550.9965 | 11543.3728 | 2788.44 | NORMAL
299.817 | 0.35 | 291.483 | 1.42 | 1 | 101352.97 | 11757.6202 | 11749.9189 | 2644.151 | NORMAL
299.817 | 0.35 | 291.483 | 1.42 | 1 | 106868.78 | 11791.2368 | 11783.5253 | 2619.967 | NORMAL
299.817 | 0.35 | 291.483 | 1.42 | 2 | 57226.51 | 14068.9918 | 14060.6067 | 4275.25 | NORMAL
299.817 | 0.35 | 291.483 | 1.42 | 2 | 79289.74 | 14652.2274 | 14643.6852 | 3834.59 | NORMAL
299.817 | 0.35 | 291.483 | 1.42 | 2 | 101352.97 | 14835.6096 | 14827.0346 | 3605.098 | NORMAL
299.817 | 0.35 | 291.483 | 1.42 | 2 | 106868.78 | 15018.6401 | 15010.0044 | 3568.359 | NORMAL
299.817 | 0.35 | 294.26 | 0.5 | 1 | 57226.51 | 9710.932 | 8547.339 | 2999.8 | NORMAL
299.817 | 0.35 | 294.26 | 0.5 | 1 | 79289.74 | 9917.8488 | 8832.1518 | 2769.94 | NORMAL
299.817 | 0.35 | 294.26 | 0.5 | 1 | 101352.97 | 9945.1348 | 8992.8981 | 2651.997 | NORMAL
299.817 | 0.35 | 294.26 | 0.5 | 1 | 106868.78 | 9906.0668 | 8939.5517 | 2632.5535 | NORMAL
299.817 | 0.35 | 294.26 | 0.5 | 2 | 57226.51 | 12439.6249 | 9756.1241 | 4090.536 | NORMAL
299.817 | 0.35 | 294.26 | 0.5 | 2 | 79289.74 | 12647.8898 | 10201.5603 | 3697.579 | NORMAL
299.817 | 0.35 | 294.26 | 0.5 | 2 | 101352.97 | 12679.7773 | 10568.2139 | 3497.465 | NORMAL
299.817 | 0.35 | 294.26 | 0.5 | 2 | 106868.78 | 12630.5979 | 10628.3955 | 3460.7838 | NORMAL
299.817 | 0.35 | 294.26 | 0.8 | 1 | 57226.51 | 10459.8476 | 10453.6449 | 3029.605 | NORMAL
299.817 | 0.35 | 294.26 | 0.8 | 1 | 79289.74 | 10840.2696 | 10833.8305 | 2779.939 | NORMAL
299.817 | 0.35 | 294.26 | 0.8 | 1 | 101352.97 | 11059.2614 | 11052.7475 | 2647.156 | NORMAL
299.817 | 0.35 | 294.26 | 0.8 | 1 | 106868.78 | 11033.5873 | 11027.1327 | 2624.061 | NORMAL
299.817 | 0.35 | 294.26 | 0.8 | 2 | 57226.51 | 13558.9097 | 12518.521 | 4218.067 | NORMAL
299.817 | 0.35 | 294.26 | 0.8 | 2 | 79289.74 | 14086.2251 | 12819.31 | 3794.845 | NORMAL
299.817 | 0.35 | 294.26 | 0.8 | 2 | 101352.97 | 14252.1395 | 13121.6171 | 3573.162 | NORMAL
299.817 | 0.35 | 294.26 | 0.8 | 2 | 106868.78 | 14224.1794 | 13277.7309 | 3531.836 | NORMAL
299.817 | 0.35 | 294.26 | 1.11 | 1 | 57226.51 | 11410.8441 | 11396.706 | 3069.52 | NORMAL
299.817 | 0.35 | 294.26 | 1.11 | 1 | 79289.74 | 11787.544 | 11779.1984 | 2791.513 | NORMAL
299.817 | 0.35 | 294.26 | 1.11 | 1 | 101352.97 | 11988.3646 | 11979.9368 | 2643.733 | NORMAL
299.817 | 0.35 | 294.26 | 1.11 | 1 | 106868.78 | 12022.5088 | 12014.081 | 2618.547 | NORMAL
299.817 | 0.35 | 294.26 | 1.11 | 2 | 57226.51 | 14134.9062 | 14126.2415 | 4283.34 | NORMAL
299.817 | 0.35 | 294.26 | 1.11 | 2 | 79289.74 | 14829.8945 | 14820.8779 | 3847.389 | NORMAL
299.817 | 0.35 | 294.26 | 1.11 | 2 | 101352.97 | 15189.5076 | 15053.5008 | 3619.427 | NORMAL
299.817 | 0.35 | 294.26 | 1.11 | 2 | 106868.78 | 15182.5322 | 15173.4531 | 3575.918 | NORMAL
299.817 | 0.35 | 294.26 | 1.42 | 1 | 57226.51 | 11926.4068 | 11894.3009 | 3092.28 | NORMAL
299.817 | 0.35 | 294.26 | 1.42 | 1 | 79289.74 | 12357.4443 | 12347.7931 | 2799.49 | NORMAL
299.817 | 0.35 | 294.26 | 1.42 | 1 | 101352.97 | 12589.2439 | 12579.4746 | 2643.211 | NORMAL
299.817 | 0.35 | 294.26 | 1.42 | 1 | 106868.78 | 12630.7444 | 12616.8506 | 2615.551 | NORMAL
299.817 | 0.35 | 294.26 | 1.42 | 2 | 57226.51 | 14467.5557 | 14457.6454 | 4331.46 | NORMAL
299.817 | 0.35 | 294.26 | 1.42 | 2 | 79289.74 | 15329.66 | 15319.3892 | 3880.34 | NORMAL
299.817 | 0.35 | 294.26 | 1.42 | 2 | 101352.97 | 15768.4056 | 15757.8723 | 3648.299 | NORMAL
299.817 | 0.35 | 294.26 | 1.42 | 2 | 106868.78 | 15770.3107 | 15759.8392 | 3603.598 | NORMAL
299.817 | 0.35 | 297.037 | 0.5 | 1 | 57226.51 | 10444.7245 | 8875.6762 | 3028.835 | NORMAL
299.817 | 0.35 | 297.037 | 0.5 | 1 | 79289.74 | 10665.4455 | 9132.1597 | 2777.826 | NORMAL
299.817 | 0.35 | 297.037 | 0.5 | 1 | 101352.97 | 10726.7878 | 9321.3748 | 2648.621 | NORMAL
299.817 | 0.35 | 297.037 | 0.5 | 1 | 106868.78 | 10678.517 | 9426.5783 | 2626.7943 | NORMAL
299.817 | 0.35 | 297.037 | 0.5 | 2 | 57226.51 | 13338.1008 | 10098.9697 | 4191.36 | NORMAL
299.817 | 0.35 | 297.037 | 0.5 | 2 | 79289.74 | 13520.1641 | 10575.9321 | 3755.382 | NORMAL
299.817 | 0.35 | 297.037 | 0.5 | 2 | 101352.97 | 13545.4279 | 10964.8884 | 3539.236 | NORMAL
299.817 | 0.35 | 297.037 | 0.5 | 2 | 106868.78 | 13491.5006 | 11001.6981 | 3498.9625 | NORMAL
299.817 | 0.35 | 297.037 | 0.8 | 1 | 57226.51 | 11204.8359 | 11196.9477 | 3060.194 | NORMAL
299.817 | 0.35 | 297.037 | 0.8 | 1 | 79289.74 | 11641.735 | 11633.5509 | 2788.542 | NORMAL
299.817 | 0.35 | 297.037 | 0.8 | 1 | 101352.97 | 11860.8148 | 11766.8059 | 2643.891 | NORMAL
299.817 | 0.35 | 297.037 | 0.8 | 1 | 106868.78 | 11827.6084 | 11819.4119 | 2619.178 | NORMAL
299.817 | 0.35 | 297.037 | 0.8 | 2 | 57226.51 | 14453.6928 | 13003.1636 | 4320.867 | NORMAL
299.817 | 0.35 | 297.037 | 0.8 | 2 | 79289.74 | 15035.9906 | 13347.6594 | 3861.175 | NORMAL
299.817 | 0.35 | 297.037 | 0.8 | 2 | 101352.97 | 15284.3787 | 13670.9291 | 3624.304 | NORMAL
299.817 | 0.35 | 297.037 | 0.8 | 2 | 106868.78 | 15249.8535 | 13829.5431 | 3579.061 | NORMAL
299.817 | 0.35 | 297.037 | 1.11 | 1 | 57226.51 | 12143.728 | 12133.5151 | 3102.1 | NORMAL
299.817 | 0.35 | 297.037 | 1.11 | 1 | 79289.74 | 12562.6026 | 12545.4169 | 2802.584 | NORMAL
299.817 | 0.35 | 297.037 | 1.11 | 1 | 101352.97 | 12786.2251 | 12772.7484 | 2643.118 | NORMAL
299.817 | 0.35 | 297.037 | 1.11 | 1 | 106868.78 | 12825.9379 | 12815.4078 | 2614.944 | NORMAL
299.817 | 0.35 | 297.037 | 1.11 | 2 | 57226.51 | 15038.0129 | 15027.0351 | 4388.46 | NORMAL
299.817 | 0.35 | 297.037 | 1.11 | 2 | 79289.74 | 15812.6612 | 15525.0763 | 3916.619 | NORMAL
299.817 | 0.35 | 297.037 | 1.11 | 2 | 101352.97 | 16202.6084 | 15759.7425 | 3670.622 | NORMAL
299.817 | 0.35 | 297.037 | 1.11 | 2 | 106868.78 | 16190.1231 | 15974.6488 | 3623.378 | NORMAL
299.817 | 0.35 | 297.037 | 1.42 | 1 | 57226.51 | 12702.5205 | 12678.373 | 3128.04 | NORMAL
299.817 | 0.35 | 297.037 | 1.42 | 1 | 79289.74 | 13183.4994 | 13150.8966 | 2812.25 | NORMAL
299.817 | 0.35 | 297.037 | 1.42 | 1 | 101352.97 | 13443.6987 | 13431.5322 | 2643.41 | NORMAL
299.817 | 0.35 | 297.037 | 1.42 | 1 | 106868.78 | 13490.211 | 13478.0024 | 2613.399 | NORMAL
299.817 | 0.35 | 297.037 | 1.42 | 2 | 57226.51 | 15398.0657 | 15385.8858 | 4434 | NORMAL
299.817 | 0.35 | 297.037 | 1.42 | 2 | 79289.74 | 16312.4854 | 16299.5659 | 3953.55 | NORMAL
299.817 | 0.35 | 297.037 | 1.42 | 2 | 101352.97 | 16799.1207 | 16785.8662 | 3701.313 | NORMAL
299.817 | 0.35 | 297.037 | 1.42 | 2 | 106868.78 | 16802.7843 | 16789.6109 | 3652.721 | NORMAL
299.817 | 0.35 | 299.814 | 0.5 | 1 | 57226.51 | 11209.8183 | 9222.8332 | 3060.631 | NORMAL
299.817 | 0.35 | 299.814 | 0.5 | 1 | 79289.74 | 11448.388 | 9495.751 | 2787.572 | NORMAL
299.817 | 0.35 | 299.814 | 0.5 | 1 | 101352.97 | 11515.4162 | 9720.1052 | 2645.4 | NORMAL
299.817 | 0.35 | 299.814 | 0.5 | 1 | 106868.78 | 11458.0012 | 9833.0274 | 2621.3107 | NORMAL
299.817 | 0.35 | 299.814 | 0.5 | 2 | 57226.51 | 14256.0082 | 10381.1681 | 4295.906 | NORMAL
299.817 | 0.35 | 299.814 | 0.5 | 2 | 79289.74 | 14502.4619 | 10938.8734 | 3824.105 | NORMAL
299.817 | 0.35 | 299.814 | 0.5 | 2 | 101352.97 | 14512.8371 | 11350.5479 | 3586.134 | NORMAL
299.817 | 0.35 | 299.814 | 0.5 | 2 | 106868.78 | 14397.0985 | 11313.3264 | 3540.1517 | NORMAL
299.817 | 0.35 | 299.814 | 0.8 | 1 | 57226.51 | 11976.2603 | 11966.3918 | 3094.15 | NORMAL
299.817 | 0.35 | 299.814 | 0.8 | 1 | 79289.74 | 12460.3165 | 12233.9749 | 2799.995 | NORMAL
299.817 | 0.35 | 299.814 | 0.8 | 1 | 101352.97 | 12695.3693 | 12344.5074 | 2643.088 | NORMAL
299.817 | 0.35 | 299.814 | 0.8 | 1 | 106868.78 | 12657.5322 | 12487.1239 | 2615.457 | NORMAL
299.817 | 0.35 | 299.814 | 0.8 | 2 | 57226.51 | 15384.789 | 13480.906 | 4430.171 | NORMAL
299.817 | 0.35 | 299.814 | 0.8 | 2 | 79289.74 | 16025.2931 | 13869.779 | 3932.815 | NORMAL
299.817 | 0.35 | 299.814 | 0.8 | 2 | 101352.97 | 16307.034 | 14232.6488 | 3676.124 | NORMAL
299.817 | 0.35 | 299.814 | 0.8 | 2 | 106868.78 | 16264.5956 | 14406.3818 | 3626.977 | NORMAL
299.817 | 0.35 | 299.814 | 1.11 | 1 | 57226.51 | 12891.5299 | 12879.0122 | 3137.01 | NORMAL
299.817 | 0.35 | 299.814 | 1.11 | 1 | 79289.74 | 13356.3599 | 13342.7364 | 2814.184 | NORMAL
299.817 | 0.35 | 299.814 | 1.11 | 1 | 101352.97 | 13359.1735 | 13346.7228 | 2643.771 | NORMAL
299.817 | 0.35 | 299.814 | 1.11 | 1 | 106868.78 | 13648.1243 | 13635.1995 | 2613.243 | NORMAL
299.817 | 0.35 | 299.814 | 1.11 | 2 | 57226.51 | 15947.3329 | 15924.2412 | 4501.28 | NORMAL
299.817 | 0.35 | 299.814 | 1.11 | 2 | 79289.74 | 16812.7784 | 16181.3409 | 3991.527 | NORMAL
299.817 | 0.35 | 299.814 | 1.11 | 2 | 101352.97 | 17252.6378 | 16492.6591 | 3725.201 | NORMAL
299.817 | 0.35 | 299.814 | 1.11 | 2 | 106868.78 | 17238.0422 | 16683.8391 | 3674.042 | NORMAL
299.817 | 0.35 | 299.814 | 1.42 | 1 | 57226.51 | 13492.7022 | 13478.3595 | 3166.56 | NORMAL
299.817 | 0.35 | 299.814 | 1.42 | 1 | 79289.74 | 14030.9203 | 14002.1709 | 2825.85 | NORMAL
299.817 | 0.35 | 299.814 | 1.42 | 1 | 101352.97 | 14319.1676 | 14304.2184 | 2644.866 | NORMAL
299.817 | 0.35 | 299.814 | 1.42 | 1 | 106868.78 | 14371.0141 | 14356.0395 | 2612.473 | NORMAL
299.817 | 0.35 | 299.814 | 1.42 | 2 | 57226.51 | 16319.959 | 16304.8957 | 4547.02 | NORMAL
299.817 | 0.35 | 299.814 | 1.42 | 2 | 79289.74 | 17323.1243 | 17307.1177 | 4029.61 | NORMAL
299.817 | 0.35 | 299.814 | 1.42 | 2 | 101352.97 | 17867.3505 | 17850.9126 | 3757.899 | NORMAL
299.817 | 0.35 | 299.814 | 1.42 | 2 | 106868.78 | 17869.0504 | 17852.7538 | 3705.381 | NORMAL
299.817 | 0.35 | 302.591 | 0.5 | 1 | 57226.51 | 12011.313 | 9535.361 | 3095.93 | NORMAL
299.817 | 0.35 | 302.591 | 0.5 | 1 | 79289.74 | 12280.5393 | 9839.4751 | 2798.751 | NORMAL
299.817 | 0.35 | 302.591 | 0.5 | 1 | 101352.97 | 12348.3001 | 10091.6853 | 2643.8 | NORMAL
299.817 | 0.35 | 302.591 | 0.5 | 1 | 106868.78 | 12282.3564 | 10196.1613 | 2616.88 | NORMAL
299.817 | 0.35 | 302.591 | 0.5 | 2 | 57226.51 | 15207.2978 | 10611.5307 | 4410.689 | NORMAL
299.817 | 0.35 | 302.591 | 0.5 | 2 | 79289.74 | 15512.8957 | 11244.2742 | 3894.639 | NORMAL
299.817 | 0.35 | 302.591 | 0.5 | 2 | 101352.97 | 15514.6835 | 11682.2153 | 3636.043 | NORMAL
299.817 | 0.35 | 302.591 | 0.5 | 2 | 106868.78 | 15432.5322 | 11686.0536 | 3587.6467 | NORMAL
299.817 | 0.35 | 302.591 | 0.8 | 1 | 57226.51 | 12774.7069 | 12663.6947 | 3131.972 | NORMAL
299.817 | 0.35 | 302.591 | 0.8 | 1 | 79289.74 | 13316.9402 | 12758.5742 | 2813.418 | NORMAL
299.817 | 0.35 | 302.591 | 0.8 | 1 | 101352.97 | 13579.9824 | 12914.862 | 2643.934 | NORMAL
299.817 | 0.35 | 302.591 | 0.8 | 1 | 106868.78 | 13536.313 | 13060.1461 | 2613.525 | NORMAL
299.817 | 0.35 | 302.591 | 0.8 | 2 | 57226.51 | 16329.5428 | 13936.4973 | 4548.92 | NORMAL
299.817 | 0.35 | 302.591 | 0.8 | 2 | 79289.74 | 17065.4455 | 14391.1366 | 4009.615 | NORMAL
299.817 | 0.35 | 302.591 | 0.8 | 2 | 101352.97 | 17380.129 | 14774.726 | 3732.171 | NORMAL
299.817 | 0.35 | 302.591 | 0.8 | 2 | 106868.78 | 17329.9531 | 14967.7592 | 3678.633 | NORMAL
299.817 | 0.35 | 302.591 | 1.11 | 1 | 57226.51 | 13653.0188 | 13622.9685 | 3174.53 | NORMAL
299.817 | 0.35 | 302.591 | 1.11 | 1 | 79289.74 | 13843.2298 | 13828.5975 | 2823.76 | NORMAL
299.817 | 0.35 | 302.591 | 1.11 | 1 | 101352.97 | 14217.8488 | 14202.8347 | 2644.919 | NORMAL
299.817 | 0.35 | 302.591 | 1.11 | 1 | 106868.78 | 14195.252 | 14180.3612 | 2612.611 | NORMAL
299.817 | 0.35 | 302.591 | 1.11 | 2 | 57226.51 | 16895.8382 | 16581.7615 | 4620.58 | NORMAL
299.817 | 0.35 | 302.591 | 1.11 | 2 | 79289.74 | 17864.8593 | 16808.4209 | 4068.564 | NORMAL
299.817 | 0.35 | 302.591 | 1.11 | 2 | 101352.97 | 18347.5674 | 17150.829 | 3783.929 | NORMAL
299.817 | 0.35 | 302.591 | 1.11 | 2 | 106868.78 | 18330.3927 | 17408.4106 | 3728.721 | NORMAL
299.817 | 0.35 | 302.591 | 1.42 | 1 | 57226.51 | 14298.0657 | 14280.7364 | 3207.98 | NORMAL
299.817 | 0.35 | 302.591 | 1.42 | 1 | 79289.74 | 14895.6331 | 14877.7881 | 2842.4 | NORMAL
299.817 | 0.35 | 302.591 | 1.42 | 1 | 101352.97 | 15216.6178 | 15198.51 | 2647.777 | NORMAL
299.817 | 0.35 | 302.591 | 1.42 | 1 | 106868.78 | 15274.619 | 15256.3658 | 2612.905 | NORMAL
299.817 | 0.35 | 302.591 | 1.42 | 2 | 57226.51 | 17260.1407 | 17241.7414 | 4667.98 | NORMAL
299.817 | 0.35 | 302.591 | 1.42 | 2 | 79289.74 | 18376.5827 | 18356.9565 | 4110.83 | NORMAL
299.817 | 0.35 | 302.591 | 1.42 | 2 | 101352.97 | 18977.6084 | 18957.4732 | 3818.788 | NORMAL
299.817 | 0.35 | 302.591 | 1.42 | 2 | 106868.78 | 18971.8347 | 18951.8574 | 3761.709 | NORMAL
299.817 | 0.35 | 305.368 | 0.5 | 1 | 57226.51 | 12859.4959 | 9861.1115 | 3134.48 | NORMAL
299.817 | 0.35 | 305.368 | 0.5 | 1 | 79289.74 | 13155.3634 | 10176.5287 | 2812.086 | NORMAL
299.817 | 0.35 | 305.368 | 0.5 | 1 | 101352.97 | 13235.6096 | 10472.054 | 2643.704 | NORMAL
299.817 | 0.35 | 305.368 | 0.5 | 1 | 106868.78 | 13152.7843 | 10513.1389 | 2614.112 | NORMAL
299.817 | 0.35 | 305.368 | 0.5 | 2 | 57226.51 | 16212.3974 | 10827.3199 | 4532.649 | NORMAL
299.817 | 0.35 | 305.368 | 0.5 | 2 | 79289.74 | 16574.9707 | 11505.1181 | 3971.95 | NORMAL
299.817 | 0.35 | 305.368 | 0.5 | 2 | 101352.97 | 16580.9496 | 11998.1575 | 3690.421 | NORMAL
299.817 | 0.35 | 305.368 | 0.5 | 2 | 106868.78 | 16487.4267 | 11997.3893 | 3637.6021 | NORMAL
299.817 | 0.35 | 305.368 | 0.8 | 1 | 57226.51 | 13595.0469 | 13111.3895 | 3172.488 | NORMAL
299.817 | 0.35 | 305.368 | 0.8 | 1 | 79289.74 | 14214.5662 | 13265.0616 | 2829.139 | NORMAL
299.817 | 0.35 | 305.368 | 0.8 | 1 | 101352.97 | 14494.0797 | 13453.0569 | 2645.423 | NORMAL
299.817 | 0.35 | 305.368 | 0.8 | 1 | 106868.78 | 14451.2896 | 13634.8062 | 2612.73 | NORMAL
299.817 | 0.35 | 305.368 | 0.8 | 2 | 57226.51 | 17322.4209 | 14393.4247 | 4673.906 | NORMAL
299.817 | 0.35 | 305.368 | 0.8 | 2 | 79289.74 | 18148.095 | 14851.8565 | 4092.332 | NORMAL
299.817 | 0.35 | 305.368 | 0.8 | 2 | 101352.97 | 18497.3622 | 15302.5163 | 3792.4 | NORMAL
299.817 | 0.35 | 305.368 | 0.8 | 2 | 106868.78 | 18446.102 | 15514.7581 | 3734.742 | NORMAL
299.817 | 0.35 | 305.368 | 1.11 | 1 | 57226.51 | 14005.6858 | 13988.977 | 3192.16 | NORMAL
299.817 | 0.35 | 305.368 | 1.11 | 1 | 79289.74 | 14753.8101 | 14736.0465 | 2840.713 | NORMAL
299.817 | 0.35 | 305.368 | 1.11 | 1 | 101352.97 | 15155.7737 | 15137.5413 | 2647.696 | NORMAL
299.817 | 0.35 | 305.368 | 1.11 | 1 | 106868.78 | 15122.3623 | 15104.3213 | 2612.624 | NORMAL
299.817 | 0.35 | 305.368 | 1.11 | 2 | 57226.51 | 17879.1618 | 17199.5212 | 4746.75 | NORMAL
299.817 | 0.35 | 305.368 | 1.11 | 2 | 79289.74 | 18959.6718 | 17408.7516 | 4153.341 | NORMAL
299.817 | 0.35 | 305.368 | 1.11 | 2 | 101352.97 | 19492.3798 | 17794.1452 | 3847.544 | NORMAL
299.817 | 0.35 | 305.368 | 1.11 | 2 | 106868.78 | 19460.0821 | 18059.7929 | 3787.213 | NORMAL
299.817 | 0.35 | 305.368 | 1.42 | 1 | 57226.51 | 15117.8781 | 15097.2119 | 3252.39 | NORMAL
299.817 | 0.35 | 305.368 | 1.42 | 1 | 79289.74 | 15779.2497 | 15757.9162 | 2860.87 | NORMAL
299.817 | 0.35 | 305.368 | 1.42 | 1 | 101352.97 | 16135.3165 | 16113.6307 | 2652.181 | NORMAL
299.817 | 0.35 | 305.368 | 1.42 | 1 | 106868.78 | 16199.7655 | 16178.0092 | 2614.759 | NORMAL
299.817 | 0.35 | 305.368 | 1.42 | 2 | 57226.51 | 18230.7151 | 18208.5466 | 4795.89 | NORMAL
299.817 | 0.35 | 305.368 | 1.42 | 2 | 79289.74 | 19475.9379 | 19452.2162 | 4197.53 | NORMAL
299.817 | 0.35 | 305.368 | 1.42 | 2 | 101352.97 | 20129.1325 | 19891.8905 | 3884.197 | NORMAL
299.817 | 0.35 | 305.368 | 1.42 | 2 | 106868.78 | 20121.7468 | 20097.5403 | 3822.464 | NORMAL
299.817 | 0.45 | 288.706 | 0.5 | 1 | 57226.51 | 8852.7257 | 7049.7442 | 2966.954 | NORMAL
299.817 | 0.45 | 288.706 | 0.5 | 1 | 79289.74 | 8971.8347 | 7355.2357 | 2761.165 | NORMAL
299.817 | 0.45 | 288.706 | 0.5 | 1 | 101352.97 | 8986.2251 | 7606.3453 | 2659.402 | NORMAL
299.817 | 0.45 | 288.706 | 0.5 | 1 | 106868.78 | 8946.3072 | 7648.189 | 2642.5694 | NORMAL
299.817 | 0.45 | 288.706 | 0.5 | 2 | 57226.51 | 11482.034 | 8303.0721 | 3984.847 | NORMAL
299.817 | 0.45 | 288.706 | 0.5 | 2 | 79289.74 | 11561.694 | 8809.0859 | 3624.665 | NORMAL
299.817 | 0.45 | 288.706 | 0.5 | 2 | 101352.97 | 11521.4537 | 9138.2871 | 3443.5342 | NORMAL
299.817 | 0.45 | 288.706 | 0.5 | 2 | 106868.78 | 11469.6952 | 9180.0917 | 3411.5647 | NORMAL
299.817 | 0.45 | 288.706 | 0.8 | 1 | 57226.51 | 9548.6518 | 9001.495 | 2993.764 | NORMAL
299.817 | 0.45 | 288.706 | 0.8 | 1 | 79289.74 | 9807.1219 | 9165.4125 | 2768.612 | NORMAL
299.817 | 0.45 | 288.706 | 0.8 | 1 | 101352.97 | 9905.7444 | 9351.7855 | 2652.372 | NORMAL
299.817 | 0.45 | 288.706 | 0.8 | 1 | 106868.78 | 9880.891 | 9525.7915 | 2632.764 | NORMAL
299.817 | 0.45 | 288.706 | 0.8 | 2 | 57226.51 | 12480.041 | 10620.2404 | 4094.495 | NORMAL
299.817 | 0.45 | 288.706 | 0.8 | 2 | 79289.74 | 12841.9988 | 10905.2841 | 3710.33 | NORMAL
299.817 | 0.45 | 288.706 | 0.8 | 2 | 101352.97 | 12983.4701 | 11158.0981 | 3511.975 | NORMAL
299.817 | 0.45 | 288.706 | 0.8 | 2 | 106868.78 | 12949.2673 | 11283.2016 | 3474.915 | NORMAL
299.817 | 0.45 | 288.706 | 1.11 | 1 | 57226.51 | 9904.3376 | 9899.5241 | 3006.73 | NORMAL
299.817 | 0.45 | 288.706 | 1.11 | 1 | 79289.74 | 10271.4537 | 10266.4618 | 2773.343 | NORMAL
299.817 | 0.45 | 288.706 | 1.11 | 1 | 101352.97 | 10463.218 | 10458.1434 | 2649.957 | NORMAL
299.817 | 0.45 | 288.706 | 1.11 | 1 | 106868.78 | 10441.0023 | 10435.9907 | 2627.841 | NORMAL
299.817 | 0.45 | 288.706 | 1.11 | 2 | 57226.51 | 12964.7714 | 12115.6567 | 4148.77 | NORMAL
299.817 | 0.45 | 288.706 | 1.11 | 2 | 79289.74 | 13506.7409 | 12419.1376 | 3754.997 | NORMAL
299.817 | 0.45 | 288.706 | 1.11 | 2 | 101352.97 | 13753.4584 | 12719.102 | 3548.639 | NORMAL
299.817 | 0.45 | 288.706 | 1.11 | 2 | 106868.78 | 13733.3236 | 12916.0947 | 3509.797 | NORMAL
299.817 | 0.45 | 288.706 | 1.42 | 1 | 57226.51 | 10426.9343 | 10421.1683 | 3028.72 | NORMAL
299.817 | 0.45 | 288.706 | 1.42 | 1 | 79289.74 | 10768.4935 | 10762.6032 | 2778.83 | NORMAL
299.817 | 0.45 | 288.706 | 1.42 | 1 | 101352.97 | 10921.4244 | 10915.4831 | 2647.636 | NORMAL
299.817 | 0.45 | 288.706 | 1.42 | 1 | 106868.78 | 10980.1583 | 10969.7271 | 2624.475 | NORMAL
299.817 | 0.45 | 288.706 | 1.42 | 2 | 57226.51 | 13371.6002 | 13365.1016 | 4196.6 | NORMAL
299.817 | 0.45 | 288.706 | 1.42 | 2 | 79289.74 | 13987.3974 | 13634.0478 | 3788.09 | NORMAL
299.817 | 0.45 | 288.706 | 1.42 | 2 | 101352.97 | 14244.959 | 13926.7266 | 3572.763 | NORMAL
299.817 | 0.45 | 288.706 | 1.42 | 2 | 106868.78 | 14228.6928 | 14122.3191 | 3532.202 | NORMAL
299.817 | 0.45 | 291.483 | 0.5 | 1 | 57226.51 | 9606.7116 | 7379.53 | 2995.133 | NORMAL
299.817 | 0.45 | 291.483 | 0.5 | 1 | 79289.74 | 9674.4431 | 7680.3082 | 2767.297 | NORMAL
299.817 | 0.45 | 291.483 | 0.5 | 1 | 101352.97 | 9703.6635 | 7944.2729 | 2653.609 | NORMAL
299.817 | 0.45 | 291.483 | 0.5 | 1 | 106868.78 | 9655.7737 | 7934.8252 | 2635.1113 | NORMAL
299.817 | 0.45 | 291.483 | 0.5 | 2 | 57226.51 | 12323.5346 | 8498.7531 | 4077.996 | NORMAL
299.817 | 0.45 | 291.483 | 0.5 | 2 | 79289.74 | 12433.2943 | 9139.926 | 3682.815 | NORMAL
299.817 | 0.45 | 291.483 | 0.5 | 2 | 101352.97 | 12384.408 | 9523.2877 | 3484.171 | NORMAL
299.817 | 0.45 | 291.483 | 0.5 | 2 | 106868.78 | 12325.4689 | 9548.9968 | 3447.3823 | NORMAL
299.817 | 0.45 | 291.483 | 0.8 | 1 | 57226.51 | 10310.6975 | 9442.6708 | 3022.819 | NORMAL
299.817 | 0.45 | 291.483 | 0.8 | 1 | 79289.74 | 10612.8077 | 9622.8238 | 2777.218 | NORMAL
299.817 | 0.45 | 291.483 | 0.8 | 1 | 101352.97 | 10750.2052 | 9810.8737 | 2648.526 | NORMAL
299.817 | 0.45 | 291.483 | 0.8 | 1 | 106868.78 | 10711.8992 | 9955.7141 | 2626.493 | NORMAL
299.817 | 0.45 | 291.483 | 0.8 | 2 | 57226.51 | 13411.694 | 10794.8177 | 4199.695 | NORMAL
299.817 | 0.45 | 291.483 | 0.8 | 2 | 79289.74 | 13745.3107 | 11338.7817 | 3770.704 | NORMAL
299.817 | 0.45 | 291.483 | 0.8 | 2 | 101352.97 | 13923.8863 | 11787.0292 | 3557.158 | NORMAL
299.817 | 0.45 | 291.483 | 0.8 | 2 | 106868.78 | 13881.7116 | 11916.9636 | 3516.513 | NORMAL
299.817 | 0.45 | 291.483 | 1.11 | 1 | 57226.51 | 10673.7104 | 10667.3809 | 3038.03 | NORMAL
299.817 | 0.45 | 291.483 | 1.11 | 1 | 79289.74 | 11080.0117 | 11073.4302 | 2782.567 | NORMAL
299.817 | 0.45 | 291.483 | 1.11 | 1 | 101352.97 | 11292.0574 | 11218.1735 | 2646.692 | NORMAL
299.817 | 0.45 | 291.483 | 1.11 | 1 | 106868.78 | 11264.7714 | 11258.1815 | 2622.549 | NORMAL
299.817 | 0.45 | 291.483 | 1.11 | 2 | 57226.51 | 13949.7655 | 12539.6116 | 4262.57 | NORMAL
299.817 | 0.45 | 291.483 | 1.11 | 2 | 79289.74 | 14533.1184 | 12943.5876 | 3825.924 | NORMAL
299.817 | 0.45 | 291.483 | 1.11 | 2 | 101352.97 | 14796.8933 | 13268.9217 | 3600.066 | NORMAL
299.817 | 0.45 | 291.483 | 1.11 | 2 | 106868.78 | 14771.4537 | 13485.7907 | 3556.945 | NORMAL
299.817 | 0.45 | 291.483 | 1.42 | 1 | 57226.51 | 10909.4373 | 10902.5316 | 3047.33 | NORMAL
299.817 | 0.45 | 291.483 | 1.42 | 1 | 79289.74 | 11382.1512 | 11374.8894 | 2785.41 | NORMAL
299.817 | 0.45 | 291.483 | 1.42 | 1 | 101352.97 | 11640.7093 | 11633.2592 | 2645.308 | NORMAL
299.817 | 0.45 | 291.483 | 1.42 | 1 | 106868.78 | 11662.1043 | 11654.6173 | 2620.122 | NORMAL
299.817 | 0.45 | 291.483 | 1.42 | 2 | 57226.51 | 14300.5862 | 14087.4931 | 4301.39 | NORMAL
299.817 | 0.45 | 291.483 | 1.42 | 2 | 79289.74 | 14992.1161 | 14276.0176 | 3858.42 | NORMAL
299.817 | 0.45 | 291.483 | 1.42 | 2 | 101352.97 | 15341.4713 | 14589.5244 | 3626.951 | NORMAL
299.817 | 0.45 | 291.483 | 1.42 | 2 | 106868.78 | 15326.612 | 14816.2511 | 3582.648 | NORMAL
299.817 | 0.45 | 294.26 | 0.5 | 1 | 57226.51 | 10381.0082 | 7644.4083 | 3026.382 | NORMAL
299.817 | 0.45 | 294.26 | 0.5 | 1 | 79289.74 | 10513.5405 | 8005.672 | 2776.081 | NORMAL
299.817 | 0.45 | 294.26 | 0.5 | 1 | 101352.97 | 10508.1184 | 8292.1664 | 2649.637 | NORMAL
299.817 | 0.45 | 294.26 | 0.5 | 1 | 106868.78 | 10447.2743 | 8295.9089 | 2627.7429 | NORMAL
299.817 | 0.45 | 294.26 | 0.5 | 2 | 57226.51 | 13276.524 | 8725.9025 | 4184.129 | NORMAL
299.817 | 0.45 | 294.26 | 0.5 | 2 | 79289.74 | 13352.6964 | 9339.2364 | 3744.724 | NORMAL
299.817 | 0.45 | 294.26 | 0.5 | 2 | 101352.97 | 13298.6225 | 9821.5381 | 3527.606 | NORMAL
299.817 | 0.45 | 294.26 | 0.5 | 2 | 106868.78 | 13229.7186 | 9881.171 | 3487.3364 | NORMAL
299.817 | 0.45 | 294.26 | 0.8 | 1 | 57226.51 | 11100.8792 | 9852.541 | 3056.117 | NORMAL
299.817 | 0.45 | 294.26 | 0.8 | 1 | 79289.74 | 11448.7104 | 10065.8665 | 2787.001 | NORMAL
299.817 | 0.45 | 294.26 | 0.8 | 1 | 101352.97 | 11595.252 | 10287.3076 | 2645.167 | NORMAL
299.817 | 0.45 | 294.26 | 0.8 | 1 | 106868.78 | 11549.0035 | 10446.8128 | 2620.757 | NORMAL
299.817 | 0.45 | 294.26 | 0.8 | 2 | 57226.51 | 14366.4713 | 11210.1863 | 4309.536 | NORMAL
299.817 | 0.45 | 294.26 | 0.8 | 2 | 79289.74 | 14821.5416 | 11713.5236 | 3846.644 | NORMAL
299.817 | 0.45 | 294.26 | 0.8 | 2 | 101352.97 | 14984.9648 | 12175.3589 | 3609.405 | NORMAL
299.817 | 0.45 | 294.26 | 0.8 | 2 | 106868.78 | 14928.8687 | 12364.313 | 3564.288 | NORMAL
299.817 | 0.45 | 294.26 | 1.11 | 1 | 57226.51 | 11474.8828 | 11466.7241 | 3071.41 | NORMAL
299.817 | 0.45 | 294.26 | 1.11 | 1 | 79289.74 | 11929.8652 | 11669.5197 | 2793.362 | NORMAL
299.817 | 0.45 | 294.26 | 1.11 | 1 | 101352.97 | 12162.2216 | 11808.605 | 2643.888 | NORMAL
299.817 | 0.45 | 294.26 | 1.11 | 1 | 106868.78 | 12127.8722 | 12013.8945 | 2618.147 | NORMAL
299.817 | 0.45 | 294.26 | 1.11 | 2 | 57226.51 | 14903.136 | 13110.706 | 4374.24 | NORMAL
299.817 | 0.45 | 294.26 | 1.11 | 2 | 79289.74 | 15565.6799 | 13469.8701 | 3899.099 | NORMAL
299.817 | 0.45 | 294.26 | 1.11 | 2 | 101352.97 | 15864.1559 | 13856.9753 | 3653.503 | NORMAL
299.817 | 0.45 | 294.26 | 1.11 | 2 | 106868.78 | 15828.2532 | 14095.2811 | 3606.217 | NORMAL
299.817 | 0.45 | 294.26 | 1.42 | 1 | 57226.51 | 11711.4595 | 11702.6291 | 3081.81 | NORMAL
299.817 | 0.45 | 294.26 | 1.42 | 1 | 79289.74 | 12220.9261 | 12211.6016 | 2797.96 | NORMAL
299.817 | 0.45 | 294.26 | 1.42 | 1 | 101352.97 | 12522.8898 | 12513.3474 | 2643.271 | NORMAL
299.817 | 0.45 | 294.26 | 1.42 | 1 | 106868.78 | 12503.3998 | 12493.9597 | 2616.044 | NORMAL
299.817 | 0.45 | 294.26 | 1.42 | 2 | 57226.51 | 15247.8312 | 14669.6944 | 4415.64 | NORMAL
299.817 | 0.45 | 294.26 | 1.42 | 2 | 79289.74 | 16036.0492 | 14953.4395 | 3933.31 | NORMAL
299.817 | 0.45 | 294.26 | 1.42 | 2 | 101352.97 | 16426.1723 | 15255.0848 | 3682.142 | NORMAL
299.817 | 0.45 | 294.26 | 1.42 | 2 | 106868.78 | 16407.8546 | 15544.1288 | 3633.729 | NORMAL
299.817 | 0.45 | 297.037 | 0.5 | 1 | 57226.51 | 11209.2614 | 7855.5849 | 3060.275 | NORMAL
299.817 | 0.45 | 297.037 | 0.5 | 1 | 79289.74 | 11356.3013 | 8304.8404 | 2786.061 | NORMAL
299.817 | 0.45 | 297.037 | 0.5 | 1 | 101352.97 | 11344.959 | 8607.0346 | 2646.071 | NORMAL
299.817 | 0.45 | 297.037 | 0.5 | 1 | 106868.78 | 11274.1501 | 8587.7456 | 2622.434 | NORMAL
299.817 | 0.45 | 297.037 | 0.5 | 2 | 57226.51 | 14259.6717 | 8834.9219 | 4297.109 | NORMAL
299.817 | 0.45 | 297.037 | 0.5 | 2 | 79289.74 | 14392.2626 | 9591.6371 | 3816.999 | NORMAL
299.817 | 0.45 | 297.037 | 0.5 | 2 | 101352.97 | 14261.9578 | 10088.7806 | 3575.089 | NORMAL
299.817 | 0.45 | 297.037 | 0.5 | 2 | 106868.78 | 14182.796 | 10167.1501 | 3529.9799 | NORMAL
299.817 | 0.45 | 297.037 | 0.8 | 1 | 57226.51 | 11939.1559 | 10264.7012 | 3092.002 | NORMAL
299.817 | 0.45 | 297.037 | 0.8 | 1 | 79289.74 | 12325.8499 | 10469.429 | 2798.894 | NORMAL
299.817 | 0.45 | 297.037 | 0.8 | 1 | 101352.97 | 12485.9613 | 10750.4002 | 2643.506 | NORMAL
299.817 | 0.45 | 297.037 | 0.8 | 1 | 106868.78 | 12432.3857 | 10931.0135 | 2616.31 | NORMAL
299.817 | 0.45 | 297.037 | 0.8 | 2 | 57226.51 | 15357.0926 | 11589.1224 | 4427.421 | NORMAL
299.817 | 0.45 | 297.037 | 0.8 | 2 | 79289.74 | 15886.694 | 12111.3006 | 3922.793 | NORMAL
299.817 | 0.45 | 297.037 | 0.8 | 2 | 101352.97 | 16072.8312 | 12615.6295 | 3664.146 | NORMAL
299.817 | 0.45 | 297.037 | 0.8 | 2 | 106868.78 | 16009.3201 | 12849.5285 | 3614.798 | NORMAL
299.817 | 0.45 | 297.037 | 1.11 | 1 | 57226.51 | 12299.8242 | 12127.0239 | 3109.92 | NORMAL
299.817 | 0.45 | 297.037 | 1.11 | 1 | 79289.74 | 12818.6987 | 12239.05 | 2806.436 | NORMAL
299.817 | 0.45 | 297.037 | 1.11 | 1 | 101352.97 | 13078.7222 | 12403.7685 | 2643.549 | NORMAL
299.817 | 0.45 | 297.037 | 1.11 | 1 | 106868.78 | 13035.17 | 12625.1617 | 2614.434 | NORMAL
299.817 | 0.45 | 297.037 | 1.11 | 2 | 57226.51 | 15900.5862 | 13634.2756 | 4493.42 | NORMAL
299.817 | 0.45 | 297.037 | 1.11 | 2 | 79289.74 | 16647.0399 | 14011.1642 | 3977.917 | NORMAL
299.817 | 0.45 | 297.037 | 1.11 | 2 | 101352.97 | 16982.9719 | 14424.7759 | 3711.251 | NORMAL
299.817 | 0.45 | 297.037 | 1.11 | 2 | 106868.78 | 16940.68 | 14693.2955 | 3659.531 | NORMAL
299.817 | 0.45 | 297.037 | 1.42 | 1 | 57226.51 | 12539.0387 | 12527.8915 | 3120.23 | NORMAL
299.817 | 0.45 | 297.037 | 1.42 | 1 | 79289.74 | 13141.735 | 13129.9863 | 2810.51 | NORMAL
299.817 | 0.45 | 297.037 | 1.42 | 1 | 101352.97 | 13453.3998 | 13441.359 | 2643.479 | NORMAL
299.817 | 0.45 | 297.037 | 1.42 | 1 | 106868.78 | 13423.9742 | 13412.0671 | 2613.477 | NORMAL
299.817 | 0.45 | 297.037 | 1.42 | 2 | 57226.51 | 16244.2556 | 15314.4019 | 4535.99 | NORMAL
299.817 | 0.45 | 297.037 | 1.42 | 2 | 79289.74 | 17124.8242 | 15567.2871 | 4013.76 | NORMAL
299.817 | 0.45 | 297.037 | 1.42 | 2 | 101352.97 | 17564.9473 | 15947.1453 | 3741.654 | NORMAL
299.817 | 0.45 | 297.037 | 1.42 | 2 | 106868.78 | 17539.3611 | 16218.6297 | 3688.892 | NORMAL
299.817 | 0.45 | 299.814 | 0.5 | 1 | 57226.51 | 12063.7163 | 8026.6057 | 3098.215 | NORMAL
299.817 | 0.45 | 299.814 | 0.5 | 1 | 79289.74 | 12245.3693 | 8524.6383 | 2797.914 | NORMAL
299.817 | 0.45 | 299.814 | 0.5 | 1 | 101352.97 | 12231.9168 | 8876.5919 | 2643.826 | NORMAL
299.817 | 0.45 | 299.814 | 0.5 | 1 | 106868.78 | 12149.2966 | 8850.9934 | 2617.5349 | NORMAL
299.817 | 0.45 | 299.814 | 0.5 | 2 | 57226.51 | 15285.2286 | 8909.0872 | 4419.233 | NORMAL
299.817 | 0.45 | 299.814 | 0.5 | 2 | 79289.74 | 15473.388 | 9767.9166 | 3892.89 | NORMAL
299.817 | 0.45 | 299.814 | 0.5 | 2 | 101352.97 | 15384.9648 | 10344.3734 | 3629.609 | NORMAL
299.817 | 0.45 | 299.814 | 0.5 | 2 | 106868.78 | 15283.265 | 10456.7793 | 3580.7317 | NORMAL
299.817 | 0.45 | 299.814 | 0.8 | 1 | 57226.51 | 12802.2567 | 10702.3666 | 3131.985 | NORMAL
299.817 | 0.45 | 299.814 | 0.8 | 1 | 79289.74 | 13241.823 | 10900.8276 | 2813.309 | NORMAL
299.817 | 0.45 | 299.814 | 0.8 | 1 | 101352.97 | 13419.8124 | 11191.5063 | 2643.513 | NORMAL
299.817 | 0.45 | 299.814 | 0.8 | 1 | 106868.78 | 13357.9719 | 11385.9345 | 2613.616 | NORMAL
299.817 | 0.45 | 299.814 | 0.8 | 2 | 57226.51 | 16375.5862 | 11948.0043 | 4553.589 | NORMAL
299.817 | 0.45 | 299.814 | 0.8 | 2 | 79289.74 | 16996.483 | 12524.0455 | 4004.468 | NORMAL
299.817 | 0.45 | 299.814 | 0.8 | 2 | 101352.97 | 17213.5697 | 13055.8385 | 3723.386 | NORMAL
299.817 | 0.45 | 299.814 | 0.8 | 2 | 106868.78 | 17140.7679 | 13291.02 | 3669.321 | NORMAL
299.817 | 0.45 | 299.814 | 1.11 | 1 | 57226.51 | 13162.1923 | 12687.7216 | 3150.03 | NORMAL
299.817 | 0.45 | 299.814 | 1.11 | 1 | 79289.74 | 13744.7538 | 12762.9798 | 2821.712 | NORMAL
299.817 | 0.45 | 299.814 | 1.11 | 1 | 101352.97 | 14034.3787 | 12981.4073 | 2644.721 | NORMAL
299.817 | 0.45 | 299.814 | 1.11 | 1 | 106868.78 | 13981.2134 | 13225.5288 | 2612.638 | NORMAL
299.817 | 0.45 | 299.814 | 1.11 | 2 | 57226.51 | 16909.2028 | 14116.6311 | 4621.25 | NORMAL
299.817 | 0.45 | 299.814 | 1.11 | 2 | 79289.74 | 17767.8781 | 14546.8461 | 4062.475 | NORMAL
299.817 | 0.45 | 299.814 | 1.11 | 2 | 101352.97 | 18149.0328 | 14993.2064 | 3773.518 | NORMAL
299.817 | 0.45 | 299.814 | 1.11 | 2 | 106868.78 | 18100.8206 | 15255.4802 | 3717.101 | NORMAL
299.817 | 0.45 | 299.814 | 1.42 | 1 | 57226.51 | 13400.9379 | 13387.1483 | 3161.99 | NORMAL
299.817 | 0.45 | 299.814 | 1.42 | 1 | 79289.74 | 14068.0539 | 14053.4372 | 2826.42 | NORMAL
299.817 | 0.45 | 299.814 | 1.42 | 1 | 101352.97 | 14420.3693 | 14405.4009 | 2645.221 | NORMAL
299.817 | 0.45 | 299.814 | 1.42 | 1 | 106868.78 | 14384.2028 | 14369.4015 | 2612.286 | NORMAL
299.817 | 0.45 | 299.814 | 1.42 | 2 | 57226.51 | 17244.578 | 15962.5298 | 4664.96 | NORMAL
299.817 | 0.45 | 299.814 | 1.42 | 2 | 79289.74 | 18248.6518 | 16196.3172 | 4099.85 | NORMAL
299.817 | 0.45 | 299.814 | 1.42 | 2 | 101352.97 | 18744.2263 | 16626.0162 | 3805.7 | NORMAL
299.817 | 0.45 | 299.814 | 1.42 | 2 | 106868.78 | 18714.9179 | 16928.1486 | 3748.48 | NORMAL
299.817 | 0.45 | 302.591 | 0.5 | 1 | 57226.51 | 12967.3798 | 8217.2341 | 3140.187 | NORMAL
299.817 | 0.45 | 302.591 | 0.5 | 1 | 79289.74 | 13184.7597 | 8735.3252 | 2812.285 | NORMAL
299.817 | 0.45 | 302.591 | 0.5 | 1 | 101352.97 | 13177.7843 | 9126.6962 | 2643.56 | NORMAL
299.817 | 0.45 | 302.591 | 0.5 | 1 | 106868.78 | 13079.279 | 9093.3818 | 2614.319 | NORMAL
299.817 | 0.45 | 302.591 | 0.5 | 2 | 57226.51 | 16357.5029 | 8945.1823 | 4550.45 | NORMAL
299.817 | 0.45 | 302.591 | 0.5 | 2 | 79289.74 | 16609.789 | 9882.1434 | 3976.05 | NORMAL
299.817 | 0.45 | 302.591 | 0.5 | 2 | 101352.97 | 16525.6155 | 10547.1601 | 3687.554 | NORMAL
299.817 | 0.45 | 302.591 | 0.5 | 2 | 106868.78 | 16409.4666 | 10708.4897 | 3633.8982 | NORMAL
299.817 | 0.45 | 302.591 | 0.8 | 1 | 57226.51 | 13699.4724 | 11122.2181 | 3176.123 | NORMAL
299.817 | 0.45 | 302.591 | 0.8 | 1 | 79289.74 | 14196.1899 | 11323.4631 | 2830.045 | NORMAL
299.817 | 0.45 | 302.591 | 0.8 | 1 | 101352.97 | 14402.8722 | 11628.2597 | 2645.126 | NORMAL
299.817 | 0.45 | 302.591 | 0.8 | 1 | 106868.78 | 14333.0305 | 11836.6609 | 2612.322 | NORMAL
299.817 | 0.45 | 302.591 | 0.8 | 2 | 57226.51 | 17429.9824 | 12263.0733 | 4687.962 | NORMAL
299.817 | 0.45 | 302.591 | 0.8 | 2 | 79289.74 | 18156.5944 | 12923.7549 | 4092.985 | NORMAL
299.817 | 0.45 | 302.591 | 0.8 | 2 | 101352.97 | 18408.5873 | 13474.7914 | 3787.526 | NORMAL
299.817 | 0.45 | 302.591 | 0.8 | 2 | 106868.78 | 18331.9754 | 13650.0439 | 3728.889 | NORMAL
299.817 | 0.45 | 302.591 | 1.11 | 1 | 57226.51 | 14054.0152 | 13317.2476 | 3195.14 | NORMAL
299.817 | 0.45 | 302.591 | 1.11 | 1 | 79289.74 | 14714.5076 | 13322.2062 | 2839.655 | NORMAL
299.817 | 0.45 | 302.591 | 1.11 | 1 | 101352.97 | 15038.5991 | 13545.2211 | 2647.748 | NORMAL
299.817 | 0.45 | 302.591 | 1.11 | 1 | 106868.78 | 14982.8253 | 13811.4381 | 2612.861 | NORMAL
299.817 | 0.45 | 302.591 | 1.11 | 2 | 57226.51 | 17955.129 | 14582.7966 | 4756.63 | NORMAL
299.817 | 0.45 | 302.591 | 1.11 | 2 | 79289.74 | 18924.3845 | 15032.1874 | 4153.146 | NORMAL
299.817 | 0.45 | 302.591 | 1.11 | 2 | 101352.97 | 19367.9074 | 15542.7457 | 3841.09 | NORMAL
299.817 | 0.45 | 302.591 | 1.11 | 2 | 106868.78 | 19314.3904 | 15845.9122 | 3779.756 | NORMAL
299.817 | 0.45 | 302.591 | 1.42 | 1 | 57226.51 | 14300.9086 | 14284.0192 | 3207.3 | NORMAL
299.817 | 0.45 | 302.591 | 1.42 | 1 | 79289.74 | 15038.3646 | 14931.6674 | 2845 | NORMAL
299.817 | 0.45 | 302.591 | 1.42 | 1 | 101352.97 | 15440.2403 | 15154.5187 | 2648.96 | NORMAL
299.817 | 0.45 | 302.591 | 1.42 | 1 | 106868.78 | 15398.095 | 15379.9252 | 2613.382 | NORMAL
299.817 | 0.45 | 302.591 | 1.42 | 2 | 57226.51 | 18278.7222 | 16488.3579 | 4801.25 | NORMAL
299.817 | 0.45 | 302.591 | 1.42 | 2 | 79289.74 | 19412.8077 | 16827.08 | 4192.41 | NORMAL
299.817 | 0.45 | 302.591 | 1.42 | 2 | 101352.97 | 19972.3622 | 17262.9116 | 3875.099 | NORMAL
299.817 | 0.45 | 302.591 | 1.42 | 2 | 106868.78 | 19939.9179 | 17603.8967 | 3813 | NORMAL
299.817 | 0.45 | 305.368 | 0.5 | 1 | 57226.51 | 13896.7761 | 8465.2628 | 3186.918 | NORMAL
299.817 | 0.45 | 305.368 | 0.5 | 1 | 79289.74 | 14174.5311 | 8969.2038 | 2829.425 | NORMAL
299.817 | 0.45 | 305.368 | 0.5 | 1 | 101352.97 | 14176.6413 | 9376.8417 | 2644.977 | NORMAL
299.817 | 0.45 | 305.368 | 0.5 | 1 | 106868.78 | 14066.1196 | 9317.5101 | 2612.556 | NORMAL
299.817 | 0.45 | 305.368 | 0.5 | 2 | 57226.51 | 17455.422 | 8894.323 | 4693.06 | NORMAL
299.817 | 0.45 | 305.368 | 0.5 | 2 | 79289.74 | 17812.7198 | 9957.3638 | 4066.737 | NORMAL
299.817 | 0.45 | 305.368 | 0.5 | 2 | 101352.97 | 17737.163 | 10698.5246 | 3751.202 | NORMAL
299.817 | 0.45 | 305.368 | 0.5 | 2 | 106868.78 | 17607.0633 | 10941.082 | 3692.352 | NORMAL
299.817 | 0.45 | 305.368 | 0.8 | 1 | 57226.51 | 14627.9308 | 11482.5307 | 3224.67 | NORMAL
299.817 | 0.45 | 305.368 | 0.8 | 1 | 79289.74 | 15199.6776 | 11718.693 | 2849.624 | NORMAL
299.817 | 0.45 | 305.368 | 0.8 | 1 | 101352.97 | 15444.959 | 12074.7608 | 2649.264 | NORMAL
299.817 | 0.45 | 305.368 | 0.8 | 1 | 106868.78 | 15365.5041 | 12288.1931 | 2613.313 | NORMAL
299.817 | 0.45 | 305.368 | 0.8 | 2 | 57226.51 | 18513.0422 | 12657.9224 | 4831.492 | NORMAL
299.817 | 0.45 | 305.368 | 0.8 | 2 | 79289.74 | 19362.8664 | 13248.4991 | 4188.476 | NORMAL
299.817 | 0.45 | 305.368 | 0.8 | 2 | 101352.97 | 19665.0059 | 13879.5021 | 3857.709 | NORMAL
299.817 | 0.45 | 305.368 | 0.8 | 2 | 106868.78 | 19582.0926 | 13953.8859 | 3793.907 | NORMAL
299.817 | 0.45 | 305.368 | 1.11 | 1 | 57226.51 | 14977.9308 | 13770.6347 | 3244.49 | NORMAL
299.817 | 0.45 | 305.368 | 1.11 | 1 | 79289.74 | 15723.007 | 13830.4759 | 2860.741 | NORMAL
299.817 | 0.45 | 305.368 | 1.11 | 1 | 101352.97 | 16080.3634 | 14089.4215 | 2651.958 | NORMAL
299.817 | 0.45 | 305.368 | 1.11 | 1 | 106868.78 | 16026.6999 | 14366.0613 | 2614.687 | NORMAL
299.817 | 0.45 | 305.368 | 1.11 | 2 | 57226.51 | 19019.6073 | 15035.437 | 4901.19 | NORMAL
299.817 | 0.45 | 305.368 | 1.11 | 2 | 79289.74 | 20128.0481 | 15449.4644 | 4250.813 | NORMAL
299.817 | 0.45 | 305.368 | 1.11 | 2 | 101352.97 | 20638.1008 | 16103.9101 | 3914.49 | NORMAL
299.817 | 0.45 | 305.368 | 1.11 | 2 | 106868.78 | 20579.4549 | 16434.2793 | 3847.744 | NORMAL
299.817 | 0.45 | 305.368 | 1.42 | 1 | 57226.51 | 15222.1278 | 15201.7758 | 3257.3 | NORMAL
299.817 | 0.45 | 305.368 | 1.42 | 1 | 79289.74 | 16044.5487 | 15615.5495 | 2867.81 | NORMAL
299.817 | 0.45 | 305.368 | 1.42 | 1 | 101352.97 | 16496.8054 | 15795.6582 | 2654.582 | NORMAL
299.817 | 0.45 | 305.368 | 1.42 | 1 | 106868.78 | 16451.9343 | 16126.219 | 2616.039 | NORMAL
299.817 | 0.45 | 305.368 | 1.42 | 2 | 57226.51 | 19343.347 | 17074.0629 | 4945.82 | NORMAL
299.817 | 0.45 | 305.368 | 1.42 | 2 | 79289.74 | 20614.5369 | 17367.6031 | 4291.62 | NORMAL
299.817 | 0.45 | 305.368 | 1.42 | 2 | 101352.97 | 21247.8605 | 17901.1312 | 3950.134 | NORMAL
299.817 | 0.45 | 305.368 | 1.42 | 2 | 106868.78 | 21213.3939 | 18261.635 | 3882.776 | NORMAL
299.817 | 0.55 | 288.706 | 0.5 | 1 | 57226.51 | 9308.0012 | 6285.9724 | 2984.514 | NORMAL
299.817 | 0.55 | 288.706 | 0.5 | 1 | 79289.74 | 9388.1301 | 6738.5933 | 2764.821 | NORMAL
299.817 | 0.55 | 288.706 | 0.5 | 1 | 101352.97 | 9353.5756 | 7058.4888 | 2656.081 | NORMAL
299.817 | 0.55 | 288.706 | 0.5 | 1 | 106868.78 | 9300.0586 | 7081.0274 | 2638.1069 | NORMAL
299.817 | 0.55 | 288.706 | 0.5 | 2 | 57226.51 | 12049.7655 | 7312.8461 | 4049.368 | NORMAL
299.817 | 0.55 | 288.706 | 0.5 | 2 | 79289.74 | 12076.6413 | 8101.1438 | 3658.997 | NORMAL
299.817 | 0.55 | 288.706 | 0.5 | 2 | 101352.97 | 11973.5932 | 8568.1117 | 3464.408 | NORMAL
299.817 | 0.55 | 288.706 | 0.5 | 2 | 106868.78 | 11903.3998 | 8653.0098 | 3428.9536 | NORMAL
299.817 | 0.55 | 288.706 | 0.8 | 1 | 57226.51 | 10038.7456 | 8032.6027 | 3012.011 | NORMAL
299.817 | 0.55 | 288.706 | 0.8 | 1 | 79289.74 | 10264.0387 | 8320.6045 | 2773.509 | NORMAL
299.817 | 0.55 | 288.706 | 0.8 | 1 | 101352.97 | 10341.2661 | 8583.1268 | 2650.582 | NORMAL
299.817 | 0.55 | 288.706 | 0.8 | 1 | 106868.78 | 10300.3224 | 8741.4716 | 2628.927 | NORMAL
299.817 | 0.55 | 288.706 | 0.8 | 2 | 57226.51 | 13034.8769 | 9406.4755 | 4157.382 | NORMAL
299.817 | 0.55 | 288.706 | 0.8 | 2 | 79289.74 | 13369.3142 | 9982.8669 | 3745.41 | NORMAL
299.817 | 0.55 | 288.706 | 0.8 | 2 | 101352.97 | 13457.3857 | 10455.2044 | 3534.71 | NORMAL
299.817 | 0.55 | 288.706 | 0.8 | 2 | 106868.78 | 13405.4807 | 10448.4193 | 3495.216 | NORMAL
299.817 | 0.55 | 288.706 | 1.11 | 1 | 57226.51 | 10378.9273 | 9303.8469 | 3025.62 | NORMAL
299.817 | 0.55 | 288.706 | 1.11 | 1 | 79289.74 | 10706.8582 | 9464.4879 | 2777.883 | NORMAL
299.817 | 0.55 | 288.706 | 1.11 | 1 | 101352.97 | 10854.279 | 9705.6684 | 2648.018 | NORMAL
299.817 | 0.55 | 288.706 | 1.11 | 1 | 106868.78 | 10816.4127 | 9882.0477 | 2625.024 | NORMAL
299.817 | 0.55 | 288.706 | 1.11 | 2 | 57226.51 | 13620.4279 | 10824.2494 | 4225.36 | NORMAL
299.817 | 0.55 | 288.706 | 1.11 | 2 | 79289.74 | 14100.5862 | 11280.8497 | 3795.893 | NORMAL
299.817 | 0.55 | 288.706 | 1.11 | 2 | 101352.97 | 14213.4232 | 11769.4393 | 3571.728 | NORMAL
299.817 | 0.55 | 288.706 | 1.11 | 2 | 106868.78 | 14179.5428 | 11998.7858 | 3529.925 | NORMAL
299.817 | 0.55 | 288.706 | 1.42 | 1 | 57226.51 | 10595.1055 | 10382.3664 | 3034.51 | NORMAL
299.817 | 0.55 | 288.706 | 1.42 | 1 | 79289.74 | 10984.8183 | 10496.7848 | 2781.26 | NORMAL
299.817 | 0.55 | 288.706 | 1.42 | 1 | 101352.97 | 11177.3154 | 10638.4682 | 2647.24 | NORMAL
299.817 | 0.55 | 288.706 | 1.42 | 1 | 106868.78 | 11146.7175 | 10884.2234 | 2623.288 | NORMAL
299.817 | 0.55 | 288.706 | 1.42 | 2 | 57226.51 | 13947.1864 | 11967.4251 | 4262.3 | NORMAL
299.817 | 0.55 | 288.706 | 1.42 | 2 | 79289.74 | 14529.6307 | 12362.885 | 3825.85 | NORMAL
299.817 | 0.55 | 288.706 | 1.42 | 2 | 101352.97 | 14795.6331 | 12776.4582 | 3599.651 | NORMAL
299.817 | 0.55 | 288.706 | 1.42 | 2 | 106868.78 | 14767.4091 | 13020.4394 | 3556.81 | NORMAL
299.817 | 0.55 | 291.483 | 0.5 | 1 | 57226.51 | 10171.0141 | 6488.6188 | 3017.794 | NORMAL
299.817 | 0.55 | 291.483 | 0.5 | 1 | 79289.74 | 10227.4326 | 6997.006 | 2773.163 | NORMAL
299.817 | 0.55 | 291.483 | 0.5 | 1 | 101352.97 | 10177.1395 | 7337.2698 | 2651.326 | NORMAL
299.817 | 0.55 | 291.483 | 0.5 | 1 | 106868.78 | 10092.966 | 7336.9908 | 2630.7415 | NORMAL
299.817 | 0.55 | 291.483 | 0.5 | 2 | 57226.51 | 12960.9027 | 7320.0457 | 4148.844 | NORMAL
299.817 | 0.55 | 291.483 | 0.5 | 2 | 79289.74 | 13030.3927 | 8257.4771 | 3723.078 | NORMAL
299.817 | 0.55 | 291.483 | 0.5 | 2 | 101352.97 | 12918.1418 | 8832.3015 | 3509.131 | NORMAL
299.817 | 0.55 | 291.483 | 0.5 | 2 | 106868.78 | 12836.0199 | 8956.7051 | 3469.9175 | NORMAL
299.817 | 0.55 | 291.483 | 0.8 | 1 | 57226.51 | 10872.3916 | 8362.1738 | 3045.685 | NORMAL
299.817 | 0.55 | 291.483 | 0.8 | 1 | 79289.74 | 11127.374 | 8685.2047 | 2783.276 | NORMAL
299.817 | 0.55 | 291.483 | 0.8 | 1 | 101352.97 | 11214.3318 | 8988.2981 | 2648.108 | NORMAL
299.817 | 0.55 | 291.483 | 0.8 | 1 | 106868.78 | 11159.9355 | 9165.8559 | 2623.217 | NORMAL
299.817 | 0.55 | 291.483 | 0.8 | 2 | 57226.51 | 14095.0469 | 9681.6481 | 4278.335 | NORMAL
299.817 | 0.55 | 291.483 | 0.8 | 2 | 79289.74 | 14453.4877 | 10355.577 | 3820.41 | NORMAL
299.817 | 0.55 | 291.483 | 0.8 | 2 | 101352.97 | 14542.585 | 10848.623 | 3587.33 | NORMAL
299.817 | 0.55 | 291.483 | 0.8 | 2 | 106868.78 | 14434.9355 | 10843.2782 | 3541.94 | NORMAL
299.817 | 0.55 | 291.483 | 1.11 | 1 | 57226.51 | 11217.8781 | 9805.7828 | 3060.32 | NORMAL
299.817 | 0.55 | 291.483 | 1.11 | 1 | 79289.74 | 11589.449 | 9958.2225 | 2788.725 | NORMAL
299.817 | 0.55 | 291.483 | 1.11 | 1 | 101352.97 | 11756.7702 | 10193.0963 | 2644.52 | NORMAL
299.817 | 0.55 | 291.483 | 1.11 | 1 | 106868.78 | 11709.9941 | 10422.4803 | 2619.839 | NORMAL
299.817 | 0.55 | 291.483 | 1.11 | 2 | 57226.51 | 14618.9332 | 11169.1573 | 4339.91 | NORMAL
299.817 | 0.55 | 291.483 | 1.11 | 2 | 79289.74 | 15167.8488 | 11744.4653 | 3870.789 | NORMAL
299.817 | 0.55 | 291.483 | 1.11 | 2 | 101352.97 | 15384.2028 | 12240.6563 | 3629.021 | NORMAL
299.817 | 0.55 | 291.483 | 1.11 | 2 | 106868.78 | 15333.7339 | 12466.295 | 3583.021 | NORMAL
299.817 | 0.55 | 291.483 | 1.42 | 1 | 57226.51 | 11435.6975 | 10908.9922 | 3069.91 | NORMAL
299.817 | 0.55 | 291.483 | 1.42 | 1 | 79289.74 | 11877.6377 | 10978.9638 | 2792.62 | NORMAL
299.817 | 0.55 | 291.483 | 1.42 | 1 | 101352.97 | 12097.8019 | 11200.2539 | 2643.985 | NORMAL
299.817 | 0.55 | 291.483 | 1.42 | 1 | 106868.78 | 12058.9683 | 11464.3044 | 2618.877 | NORMAL
299.817 | 0.55 | 291.483 | 1.42 | 2 | 57226.51 | 14949.9707 | 12505.6206 | 4378.17 | NORMAL
299.817 | 0.55 | 291.483 | 1.42 | 2 | 79289.74 | 15616.8523 | 12877.469 | 3902.95 | NORMAL
299.817 | 0.55 | 291.483 | 1.42 | 2 | 101352.97 | 15922.9484 | 13334.9916 | 3656.134 | NORMAL
299.817 | 0.55 | 291.483 | 1.42 | 2 | 106868.78 | 15884.3201 | 13625.0773 | 3608.854 | NORMAL
299.817 | 0.55 | 294.26 | 0.5 | 1 | 57226.51 | 11027.755 | 6594.818 | 3052.781 | NORMAL
299.817 | 0.55 | 294.26 | 0.5 | 1 | 79289.74 | 11101.3775 | 7170.4796 | 2782.965 | NORMAL
299.817 | 0.55 | 294.26 | 0.5 | 1 | 101352.97 | 11037.5146 | 7572.0662 | 2647.574 | NORMAL
299.817 | 0.55 | 294.26 | 0.5 | 1 | 106868.78 | 10953.9273 | 7588.837 | 2624.6211 | NORMAL
299.817 | 0.55 | 294.26 | 0.5 | 2 | 57226.51 | 14054.9824 | 7427.5803 | 4273.687 | NORMAL
299.817 | 0.55 | 294.26 | 0.5 | 2 | 79289.74 | 14107.5616 | 8404.2412 | 3796.906 | NORMAL
299.817 | 0.55 | 294.26 | 0.5 | 2 | 101352.97 | 13925.5862 | 9015.4106 | 3557.628 | NORMAL
299.817 | 0.55 | 294.26 | 0.5 | 2 | 106868.78 | 13827.6671 | 9185.9128 | 3514.1838 | NORMAL
299.817 | 0.55 | 294.26 | 0.8 | 1 | 57226.51 | 11740.3869 | 8685.0099 | 3083.074 | NORMAL
299.817 | 0.55 | 294.26 | 0.8 | 1 | 79289.74 | 12036.6647 | 9038.9454 | 2795.036 | NORMAL
299.817 | 0.55 | 294.26 | 0.8 | 1 | 101352.97 | 12138.687 | 9375.4727 | 2643.875 | NORMAL
299.817 | 0.55 | 294.26 | 0.8 | 1 | 106868.78 | 12075.4982 | 9571.1727 | 2618.581 | NORMAL
299.817 | 0.55 | 294.26 | 0.8 | 2 | 57226.51 | 15127.1395 | 9870.8367 | 4400.64 | NORMAL
299.817 | 0.55 | 294.26 | 0.8 | 2 | 79289.74 | 15558.7339 | 10621.123 | 3898.935 | NORMAL
299.817 | 0.55 | 294.26 | 0.8 | 2 | 101352.97 | 15661.5182 | 11172.2536 | 3643.039 | NORMAL
299.817 | 0.55 | 294.26 | 0.8 | 2 | 106868.78 | 15583.9683 | 11178.2402 | 3594.754 | NORMAL
299.817 | 0.55 | 294.26 | 1.11 | 1 | 57226.51 | 12084.3201 | 10152.0856 | 3099.06 | NORMAL
299.817 | 0.55 | 294.26 | 1.11 | 1 | 79289.74 | 12508.5287 | 10411.9742 | 2801.741 | NORMAL
299.817 | 0.55 | 294.26 | 1.11 | 1 | 101352.97 | 12702.8429 | 10713.8445 | 2643.557 | NORMAL
299.817 | 0.55 | 294.26 | 1.11 | 1 | 106868.78 | 12650.0879 | 10936.4438 | 2615.691 | NORMAL
299.817 | 0.55 | 294.26 | 1.11 | 2 | 57226.51 | 15649.8535 | 11530.1391 | 4463.98 | NORMAL
299.817 | 0.55 | 294.26 | 1.11 | 2 | 79289.74 | 16291.5299 | 12153.074 | 3951.922 | NORMAL
299.817 | 0.55 | 294.26 | 1.11 | 2 | 101352.97 | 16542.4091 | 12738.7303 | 3688.065 | NORMAL
299.817 | 0.55 | 294.26 | 1.11 | 2 | 106868.78 | 16483.8804 | 12984.8471 | 3637.42 | NORMAL
299.817 | 0.55 | 294.26 | 1.42 | 1 | 57226.51 | 12310.2286 | 11443.2808 | 3108.83 | NORMAL
299.817 | 0.55 | 294.26 | 1.42 | 1 | 79289.74 | 12810.6389 | 11545.6524 | 2806.26 | NORMAL
299.817 | 0.55 | 294.26 | 1.42 | 1 | 101352.97 | 13058.7339 | 11763.3205 | 2643.549 | NORMAL
299.817 | 0.55 | 294.26 | 1.42 | 1 | 106868.78 | 13014.9179 | 12028.0618 | 2614.694 | NORMAL
299.817 | 0.55 | 294.26 | 1.42 | 2 | 57226.51 | 15976.1137 | 12897.6125 | 4504 | NORMAL
299.817 | 0.55 | 294.26 | 1.42 | 2 | 79289.74 | 16749.1207 | 13404.5391 | 3985.73 | NORMAL
299.817 | 0.55 | 294.26 | 1.42 | 2 | 101352.97 | 17099.0914 | 13906.4175 | 3717.028 | NORMAL
299.817 | 0.55 | 294.26 | 1.42 | 2 | 106868.78 | 17055.0703 | 14231.3306 | 3665.094 | NORMAL
299.817 | 0.55 | 297.037 | 0.5 | 1 | 57226.51 | 11931.7409 | 6635.444 | 3091.9 | NORMAL
299.817 | 0.55 | 297.037 | 0.5 | 1 | 79289.74 | 12031.1547 | 7298.8805 | 2795.101 | NORMAL
299.817 | 0.55 | 297.037 | 0.5 | 1 | 101352.97 | 11962.3095 | 7761.4215 | 2644.178 | NORMAL
299.817 | 0.55 | 297.037 | 0.5 | 1 | 106868.78 | 11863.1301 | 7815.8809 | 2620.4638 | NORMAL
299.817 | 0.55 | 297.037 | 0.5 | 2 | 57226.51 | 15134.9062 | 7374.6647 | 4400.788 | NORMAL
299.817 | 0.55 | 297.037 | 0.5 | 2 | 79289.74 | 15227.755 | 8477.1541 | 3875.825 | NORMAL
299.817 | 0.55 | 297.037 | 0.5 | 2 | 101352.97 | 15070.9848 | 9220.0517 | 3613.901 | NORMAL
299.817 | 0.55 | 297.037 | 0.5 | 2 | 106868.78 | 14951.5533 | 9416.2192 | 3565.4084 | NORMAL
299.817 | 0.55 | 297.037 | 0.8 | 1 | 57226.51 | 12641.735 | 8974.1654 | 3124.946 | NORMAL
299.817 | 0.55 | 297.037 | 0.8 | 1 | 79289.74 | 13000.3517 | 9355.5601 | 2809.428 | NORMAL
299.817 | 0.55 | 297.037 | 0.8 | 1 | 101352.97 | 13113.8042 | 9763.4371 | 2643.396 | NORMAL
299.817 | 0.55 | 297.037 | 0.8 | 1 | 106868.78 | 13039.0094 | 9873.0727 | 2614.45 | NORMAL
299.817 | 0.55 | 297.037 | 0.8 | 2 | 57226.51 | 16200.7913 | 9979.2338 | 4532.43 | NORMAL
299.817 | 0.55 | 297.037 | 0.8 | 2 | 79289.74 | 16723.9742 | 10855.5317 | 3984.379 | NORMAL
299.817 | 0.55 | 297.037 | 0.8 | 2 | 101352.97 | 16852.7257 | 11459.4659 | 3704.487 | NORMAL
299.817 | 0.55 | 297.037 | 0.8 | 2 | 106868.78 | 16764.8593 | 11448.3201 | 3650.989 | NORMAL
299.817 | 0.55 | 297.037 | 1.11 | 1 | 57226.51 | 12997.5088 | 10539.5629 | 3141.37 | NORMAL
299.817 | 0.55 | 297.037 | 1.11 | 1 | 79289.74 | 13479.3083 | 10788.9597 | 2817.075 | NORMAL
299.817 | 0.55 | 297.037 | 1.11 | 1 | 101352.97 | 13701.0551 | 11168.4014 | 2644.202 | NORMAL
299.817 | 0.55 | 297.037 | 1.11 | 1 | 106868.78 | 13640.2989 | 11441.21 | 2613.473 | NORMAL
299.817 | 0.55 | 297.037 | 1.11 | 2 | 57226.51 | 16716.9988 | 11967.9335 | 4597.37 | NORMAL
299.817 | 0.55 | 297.037 | 1.11 | 2 | 79289.74 | 17468.0832 | 12543.4463 | 4039.782 | NORMAL
299.817 | 0.55 | 297.037 | 1.11 | 2 | 101352.97 | 17761.5182 | 13148.8697 | 3752.272 | NORMAL
299.817 | 0.55 | 297.037 | 1.11 | 2 | 106868.78 | 17695.6331 | 13491.5046 | 3696.729 | NORMAL
299.817 | 0.55 | 297.037 | 1.42 | 1 | 57226.51 | 13211.782 | 12001.0939 | 3152.44 | NORMAL
299.817 | 0.55 | 297.037 | 1.42 | 1 | 79289.74 | 13789.1559 | 12058.1894 | 2822.52 | NORMAL
299.817 | 0.55 | 297.037 | 1.42 | 1 | 101352.97 | 14069.8417 | 12347.0037 | 2644.794 | NORMAL
299.817 | 0.55 | 297.037 | 1.42 | 1 | 106868.78 | 14019.3142 | 12615.2939 | 2613.082 | NORMAL
299.817 | 0.55 | 297.037 | 1.42 | 2 | 57226.51 | 17038.3939 | 13357.9475 | 4638.32 | NORMAL
299.817 | 0.55 | 297.037 | 1.42 | 2 | 79289.74 | 17930.129 | 13880.43 | 4075.24 | NORMAL
299.817 | 0.55 | 297.037 | 1.42 | 2 | 101352.97 | 18333.2356 | 14462.6129 | 3783.159 | NORMAL
299.817 | 0.55 | 297.037 | 1.42 | 2 | 106868.78 | 18283.4701 | 14798.7504 | 3726.281 | NORMAL
299.817 | 0.55 | 299.814 | 0.5 | 1 | 57226.51 | 12870.1348 | 6612.8683 | 3135.559 | NORMAL
299.817 | 0.55 | 299.814 | 0.5 | 1 | 79289.74 | 13012.925 | 7395.7658 | 2809.69 | NORMAL
299.817 | 0.55 | 299.814 | 0.5 | 1 | 101352.97 | 12941.9988 | 7908.519 | 2643.634 | NORMAL
299.817 | 0.55 | 299.814 | 0.5 | 1 | 106868.78 | 12832.6202 | 8022.043 | 2614.9721 | NORMAL
299.817 | 0.55 | 299.814 | 0.5 | 2 | 57226.51 | 16254.4842 | 7252.377 | 4537.89 | NORMAL
299.817 | 0.55 | 299.814 | 0.5 | 2 | 79289.74 | 16417.7022 | 8539.241 | 3961.818 | NORMAL
299.817 | 0.55 | 299.814 | 0.5 | 2 | 101352.97 | 16258.6166 | 9379.8886 | 3673.801 | NORMAL
299.817 | 0.55 | 299.814 | 0.5 | 2 | 106868.78 | 16124.6483 | 9595.8266 | 3620.3575 | NORMAL
299.817 | 0.55 | 299.814 | 0.8 | 1 | 57226.51 | 13578.2825 | 9338.3552 | 3170.666 | NORMAL
299.817 | 0.55 | 299.814 | 0.8 | 1 | 79289.74 | 14003.1067 | 9663.712 | 2826.473 | NORMAL
299.817 | 0.55 | 299.814 | 0.8 | 1 | 101352.97 | 14138.5698 | 10110.8447 | 2644.623 | NORMAL
299.817 | 0.55 | 299.814 | 0.8 | 1 | 106868.78 | 14054.8066 | 10122.9182 | 2612.632 | NORMAL
299.817 | 0.55 | 299.814 | 0.8 | 2 | 57226.51 | 17301.4068 | 10160.3723 | 4672.907 | NORMAL
299.817 | 0.55 | 299.814 | 0.8 | 2 | 79289.74 | 17938.1301 | 11065.0818 | 4076.34 | NORMAL
299.817 | 0.55 | 299.814 | 0.8 | 2 | 101352.97 | 18103.8687 | 11738.9286 | 3771.156 | NORMAL
299.817 | 0.55 | 299.814 | 0.8 | 2 | 106868.78 | 18005.422 | 11680.6574 | 3712.295 | NORMAL
299.817 | 0.55 | 299.814 | 1.11 | 1 | 57226.51 | 13927.6084 | 11009.1338 | 3188.35 | NORMAL
299.817 | 0.55 | 299.814 | 1.11 | 1 | 79289.74 | 14489.83 | 11183.7145 | 2835.122 | NORMAL
299.817 | 0.55 | 299.814 | 1.11 | 1 | 101352.97 | 14745.8968 | 11594.1678 | 2646.749 | NORMAL
299.817 | 0.55 | 299.814 | 1.11 | 1 | 106868.78 | 14672.4502 | 11914.1763 | 2612.396 | NORMAL
299.817 | 0.55 | 299.814 | 1.11 | 2 | 57226.51 | 17806.3013 | 12349.4534 | 4738.92 | NORMAL
299.817 | 0.55 | 299.814 | 1.11 | 2 | 79289.74 | 18686.2544 | 12905.3439 | 4134.222 | NORMAL
299.817 | 0.55 | 299.814 | 1.11 | 2 | 101352.97 | 19032.8546 | 13565.3245 | 3822.326 | NORMAL
299.817 | 0.55 | 299.814 | 1.11 | 2 | 106868.78 | 18960.4924 | 13919.7886 | 3761.119 | NORMAL
299.817 | 0.55 | 299.814 | 1.42 | 1 | 57226.51 | 14154.1325 | 12546.8741 | 3199.6 | NORMAL
299.817 | 0.55 | 299.814 | 1.42 | 1 | 79289.74 | 14806.5358 | 12586.5919 | 2841.62 | NORMAL
299.817 | 0.55 | 299.814 | 1.42 | 1 | 101352.97 | 15125.4689 | 12928.6004 | 2648.036 | NORMAL
299.817 | 0.55 | 299.814 | 1.42 | 1 | 106868.78 | 15062.7784 | 13185.3387 | 2612.611 | NORMAL
299.817 | 0.55 | 299.814 | 1.42 | 2 | 57226.51 | 18121.8054 | 13886.8844 | 4780.43 | NORMAL
299.817 | 0.55 | 299.814 | 1.42 | 2 | 79289.74 | 19148.2415 | 14340.4053 | 4171.11 | NORMAL
299.817 | 0.55 | 299.814 | 1.42 | 2 | 101352.97 | 19614.8593 | 14998.9533 | 3854.671 | NORMAL
299.817 | 0.55 | 299.814 | 1.42 | 2 | 106868.78 | 19559.6424 | 15344.0505 | 3792.562 | NORMAL
299.817 | 0.55 | 302.591 | 0.5 | 1 | 57226.51 | 13856.0961 | 6540.3822 | 3183.918 | NORMAL
299.817 | 0.55 | 302.591 | 0.5 | 1 | 79289.74 | 14050.4103 | 7422.5227 | 2827.427 | NORMAL
299.817 | 0.55 | 302.591 | 0.5 | 1 | 101352.97 | 13986.4302 | 8018.6163 | 2644.719 | NORMAL
299.817 | 0.55 | 302.591 | 0.5 | 1 | 106868.78 | 13861.6354 | 8215.1537 | 2612.824 | NORMAL
299.817 | 0.55 | 302.591 | 0.5 | 2 | 57226.51 | 17415.3576 | 7114.0342 | 4685.903 | NORMAL
299.817 | 0.55 | 302.591 | 0.5 | 2 | 79289.74 | 17676.6706 | 8557.0464 | 4056.186 | NORMAL
299.817 | 0.55 | 302.591 | 0.5 | 2 | 101352.97 | 17527.3154 | 9500.4534 | 3739.969 | NORMAL
299.817 | 0.55 | 302.591 | 0.5 | 2 | 106868.78 | 17374.9707 | 9734.032 | 3680.7157 | NORMAL
299.817 | 0.55 | 302.591 | 0.8 | 1 | 57226.51 | 14551.1137 | 9556.2257 | 3221.198 | NORMAL
299.817 | 0.55 | 302.591 | 0.8 | 1 | 79289.74 | 15056.7409 | 9981.3243 | 2846.674 | NORMAL
299.817 | 0.55 | 302.591 | 0.8 | 1 | 101352.97 | 15219.49 | 10436.7653 | 2647.774 | NORMAL
299.817 | 0.55 | 302.591 | 0.8 | 1 | 106868.78 | 15127.0809 | 10363.6841 | 2612.604 | NORMAL
299.817 | 0.55 | 302.591 | 0.8 | 2 | 57226.51 | 18440.8265 | 10473.4121 | 4822.036 | NORMAL
299.817 | 0.55 | 302.591 | 0.8 | 2 | 79289.74 | 19200.8206 | 11300.0286 | 4175.25 | NORMAL
299.817 | 0.55 | 302.591 | 0.8 | 2 | 101352.97 | 19419.6073 | 11914.4145 | 3844.172 | NORMAL
299.817 | 0.55 | 302.591 | 0.8 | 2 | 106868.78 | 19313.5991 | 11917.6881 | 3779.601 | NORMAL
299.817 | 0.55 | 302.591 | 1.11 | 1 | 57226.51 | 14903.2532 | 11464.5213 | 3239.67 | NORMAL
299.817 | 0.55 | 302.591 | 1.11 | 1 | 79289.74 | 15545.5158 | 11600.8256 | 2856.477 | NORMAL
299.817 | 0.55 | 302.591 | 1.11 | 1 | 101352.97 | 15838.0422 | 12022.6262 | 2650.735 | NORMAL
299.817 | 0.55 | 302.591 | 1.11 | 1 | 106868.78 | 15762.1336 | 12354.4392 | 2613.533 | NORMAL
299.817 | 0.55 | 302.591 | 1.11 | 2 | 57226.51 | 18922.5967 | 12640.6163 | 4889.46 | NORMAL
299.817 | 0.55 | 302.591 | 1.11 | 2 | 79289.74 | 19950.4103 | 13327.313 | 4236.298 | NORMAL
299.817 | 0.55 | 302.591 | 1.11 | 2 | 101352.97 | 20363.0129 | 13998.1867 | 3898.396 | NORMAL
299.817 | 0.55 | 302.591 | 1.11 | 2 | 106868.78 | 20284.9355 | 14308.1416 | 3831.454 | NORMAL
299.817 | 0.55 | 302.591 | 1.42 | 1 | 57226.51 | 15120.3107 | 12955.1427 | 3251.75 | NORMAL
299.817 | 0.55 | 302.591 | 1.42 | 1 | 79289.74 | 15859.3787 | 13006.5936 | 2863.38 | NORMAL
299.817 | 0.55 | 302.591 | 1.42 | 1 | 101352.97 | 16232.2685 | 13440.4644 | 2653.679 | NORMAL
299.817 | 0.55 | 302.591 | 1.42 | 1 | 106868.78 | 16162.3388 | 13741.8023 | 2614.425 | NORMAL
299.817 | 0.55 | 302.591 | 1.42 | 2 | 57226.51 | 19228.5463 | 14352.7638 | 4931.47 | NORMAL
299.817 | 0.55 | 302.591 | 1.42 | 2 | 79289.74 | 20408.7046 | 14747.0646 | 4274.39 | NORMAL
299.817 | 0.55 | 302.591 | 1.42 | 2 | 101352.97 | 20950.9672 | 15461.0386 | 3932.384 | NORMAL
299.817 | 0.55 | 302.591 | 1.42 | 2 | 106868.78 | 20893.3177 | 15847.9367 | 3864.698 | NORMAL
299.817 | 0.55 | 305.368 | 0.5 | 1 | 57226.51 | 14873.5346 | 6392.8683 | 3238.081 | NORMAL
299.817 | 0.55 | 305.368 | 0.5 | 1 | 79289.74 | 15142.9367 | 7398.4906 | 2848.619 | NORMAL
299.817 | 0.55 | 305.368 | 0.5 | 1 | 101352.97 | 15093.4349 | 8074.4141 | 2647.949 | NORMAL
299.817 | 0.55 | 305.368 | 0.5 | 1 | 106868.78 | 14955.9203 | 8367.5233 | 2612.462 | NORMAL
299.817 | 0.55 | 305.368 | 0.5 | 2 | 57226.51 | 18599.619 | 6896.0133 | 4845.22 | NORMAL
299.817 | 0.55 | 305.368 | 0.5 | 2 | 79289.74 | 18999.5604 | 8550.8281 | 4159.381 | NORMAL
299.817 | 0.55 | 305.368 | 0.5 | 2 | 101352.97 | 18873.8863 | 9578.3274 | 3813.255 | NORMAL
299.817 | 0.55 | 305.368 | 0.5 | 2 | 106868.78 | 18705.891 | 9840.0095 | 3747.596 | NORMAL
299.817 | 0.55 | 305.368 | 0.8 | 1 | 57226.51 | 15554.3962 | 9711.4962 | 3276.861 | NORMAL
299.817 | 0.55 | 305.368 | 0.8 | 1 | 79289.74 | 16156.6237 | 10315.3095 | 2870.73 | NORMAL
299.817 | 0.55 | 305.368 | 0.8 | 1 | 101352.97 | 16357.7667 | 10721.0439 | 2653.427 | NORMAL
299.817 | 0.55 | 305.368 | 0.8 | 1 | 106868.78 | 16255.8031 | 10563.2159 | 2614.639 | NORMAL
299.817 | 0.55 | 305.368 | 0.8 | 2 | 57226.51 | 19596.0434 | 10478.6511 | 4981.149 | NORMAL
299.817 | 0.55 | 305.368 | 0.8 | 2 | 79289.74 | 20512.6612 | 11337.1427 | 4282.757 | NORMAL
299.817 | 0.55 | 305.368 | 0.8 | 2 | 101352.97 | 20797.9484 | 12012.3959 | 3924.024 | NORMAL
299.817 | 0.55 | 305.368 | 0.8 | 2 | 106868.78 | 20683.9097 | 12157.7746 | 3853.417 | NORMAL
299.817 | 0.55 | 305.368 | 1.11 | 1 | 57226.51 | 15891.9109 | 11880.3476 | 3296.39 | NORMAL
299.817 | 0.55 | 305.368 | 1.11 | 1 | 79289.74 | 16645.3986 | 12056.978 | 2881.456 | NORMAL
299.817 | 0.55 | 305.368 | 1.11 | 1 | 101352.97 | 16987.925 | 12477.1043 | 2657.754 | NORMAL
299.817 | 0.55 | 305.368 | 1.11 | 1 | 106868.78 | 16904.1032 | 12766.7394 | 2616.95 | NORMAL
299.817 | 0.55 | 305.368 | 1.11 | 2 | 57226.51 | 20059.3787 | 13047.3019 | 5048.93 | NORMAL
299.817 | 0.55 | 305.368 | 1.11 | 2 | 79289.74 | 21255.3048 | 13631.5158 | 4346.137 | NORMAL
299.817 | 0.55 | 305.368 | 1.11 | 2 | 101352.97 | 21747.6846 | 14431.4373 | 3981.27 | NORMAL
299.817 | 0.55 | 305.368 | 1.11 | 2 | 106868.78 | 21666.6764 | 14544.4716 | 3908.325 | NORMAL
299.817 | 0.55 | 305.368 | 1.42 | 1 | 57226.51 | 16111.4595 | 13463.2351 | 3309.03 | NORMAL
299.817 | 0.55 | 305.368 | 1.42 | 1 | 79289.74 | 16960.9613 | 13391.527 | 2889.25 | NORMAL
299.817 | 0.55 | 305.368 | 1.42 | 1 | 101352.97 | 17389.7714 | 13893.3492 | 2662.032 | NORMAL
299.817 | 0.55 | 305.368 | 1.42 | 1 | 106868.78 | 17312.7198 | 14256.7824 | 2618.751 | NORMAL
299.817 | 0.55 | 305.368 | 1.42 | 2 | 57226.51 | 20355.3048 | 14823.4454 | 5091.09 | NORMAL
299.817 | 0.55 | 305.368 | 1.42 | 2 | 79289.74 | 21706.272 | 15261.5062 | 4385.33 | NORMAL
299.817 | 0.55 | 305.368 | 1.42 | 2 | 101352.97 | 22337.8077 | 15959.1797 | 4016.689 | NORMAL
299.817 | 0.55 | 305.368 | 1.42 | 2 | 106868.78 | 22278.2825 | 16349.2295 | 3943.086 | NORMAL
299.817 | 0.65 | 288.706 | 0.5 | 1 | 57226.51 | 9843.9039 | 5401.2122 | 3004.888 | NORMAL
299.817 | 0.65 | 288.706 | 0.5 | 1 | 79289.74 | 9825.2931 | 6057.47 | 2769.307 | NORMAL
299.817 | 0.65 | 288.706 | 0.5 | 1 | 101352.97 | 9721.3365 | 6451.3025 | 2653.435 | NORMAL
299.817 | 0.65 | 288.706 | 0.5 | 1 | 106868.78 | 9650.5276 | 6545.2773 | 2635.0391 | NORMAL
299.817 | 0.65 | 288.706 | 0.5 | 2 | 57226.51 | 12610.932 | 6553.1321 | 4110.967 | NORMAL
299.817 | 0.65 | 288.706 | 0.5 | 2 | 79289.74 | 12590.0938 | 7478.8808 | 3693.606 | NORMAL
299.817 | 0.65 | 288.706 | 0.5 | 2 | 101352.97 | 12427.5205 | 8040.2329 | 3486.1 | NORMAL
299.817 | 0.65 | 288.706 | 0.5 | 2 | 106868.78 | 12339.3904 | 8142.8994 | 3448.0873 | NORMAL
299.817 | 0.65 | 288.706 | 0.8 | 1 | 57226.51 | 10516.735 | 7003.8721 | 3031.494 | NORMAL
299.817 | 0.65 | 288.706 | 0.8 | 1 | 79289.74 | 10703.7515 | 7509.4095 | 2778.259 | NORMAL
299.817 | 0.65 | 288.706 | 0.8 | 1 | 101352.97 | 10740.4455 | 7863.0157 | 2648.454 | NORMAL
299.817 | 0.65 | 288.706 | 0.8 | 1 | 106868.78 | 10680.0997 | 7851.9238 | 2625.95 | NORMAL
299.817 | 0.65 | 288.706 | 0.8 | 2 | 57226.51 | 13678.4584 | 7983.2271 | 4234.382 | NORMAL
299.817 | 0.65 | 288.706 | 0.8 | 2 | 79289.74 | 13920.34 | 8907.9596 | 3786.319 | NORMAL
299.817 | 0.65 | 288.706 | 0.8 | 2 | 101352.97 | 13931.8582 | 9431.4221 | 3557.846 | NORMAL
299.817 | 0.65 | 288.706 | 0.8 | 2 | 106868.78 | 13861.1372 | 9596.8831 | 3515.667 | NORMAL
299.817 | 0.65 | 288.706 | 1.11 | 1 | 57226.51 | 10845.9848 | 8140.9745 | 3045.13 | NORMAL
299.817 | 0.65 | 288.706 | 1.11 | 1 | 79289.74 | 11140.1231 | 8490.4225 | 2783.179 | NORMAL
299.817 | 0.65 | 288.706 | 1.11 | 1 | 101352.97 | 11251.143 | 8828.0744 | 2646.67 | NORMAL
299.817 | 0.65 | 288.706 | 1.11 | 1 | 106868.78 | 11196.8054 | 9036.0011 | 2622.983 | NORMAL
299.817 | 0.65 | 288.706 | 1.11 | 2 | 57226.51 | 14188.4232 | 9555.3497 | 4291.86 | NORMAL
299.817 | 0.65 | 288.706 | 1.11 | 2 | 79289.74 | 14638.0129 | 10233.2152 | 3833.543 | NORMAL
299.817 | 0.65 | 288.706 | 1.11 | 2 | 101352.97 | 14781.7116 | 10843.2132 | 3599.084 | NORMAL
299.817 | 0.65 | 288.706 | 1.11 | 2 | 106868.78 | 14727.9601 | 10859.3374 | 3555.036 | NORMAL
299.817 | 0.65 | 288.706 | 1.42 | 1 | 57226.51 | 11049.8535 | 8974.7131 | 3053.93 | NORMAL
299.817 | 0.65 | 288.706 | 1.42 | 1 | 79289.74 | 11411.694 | 9246.462 | 2786.59 | NORMAL
299.817 | 0.65 | 288.706 | 1.42 | 1 | 101352.97 | 11573.2708 | 9557.832 | 2645.437 | NORMAL
299.817 | 0.65 | 288.706 | 1.42 | 1 | 106868.78 | 11525 | 9834.6628 | 2620.936 | NORMAL
299.817 | 0.65 | 288.706 | 1.42 | 2 | 57226.51 | 14504.4256 | 10514.2291 | 4327.52 | NORMAL
299.817 | 0.65 | 288.706 | 1.42 | 2 | 79289.74 | 15067.9367 | 11183.2267 | 3863.93 | NORMAL
299.817 | 0.65 | 288.706 | 1.42 | 2 | 101352.97 | 15298.1243 | 11711.2343 | 3624.746 | NORMAL
299.817 | 0.65 | 288.706 | 1.42 | 2 | 106868.78 | 15247.8898 | 11974.4576 | 3579.052 | NORMAL
299.817 | 0.65 | 291.483 | 0.5 | 1 | 57226.51 | 10725.2638 | 5407.4313 | 3039.628 | NORMAL
299.817 | 0.65 | 291.483 | 0.5 | 1 | 79289.74 | 10729.8652 | 6150.9918 | 2778.545 | NORMAL
299.817 | 0.65 | 291.483 | 0.5 | 1 | 101352.97 | 10622.8019 | 6649.1198 | 2648.809 | NORMAL
299.817 | 0.65 | 291.483 | 0.5 | 1 | 106868.78 | 10533.8218 | 6759.9432 | 2627.8478 | NORMAL
299.817 | 0.65 | 291.483 | 0.5 | 2 | 57226.51 | 13698.3587 | 6605.8965 | 4234.817 | NORMAL
299.817 | 0.65 | 291.483 | 0.5 | 2 | 79289.74 | 13622.626 | 7548.7603 | 3763.645 | NORMAL
299.817 | 0.65 | 291.483 | 0.5 | 2 | 101352.97 | 13453.4291 | 8228.467 | 3534.922 | NORMAL
299.817 | 0.65 | 291.483 | 0.5 | 2 | 106868.78 | 13351.3775 | 8344.1837 | 3492.8817 | NORMAL
299.817 | 0.65 | 291.483 | 0.8 | 1 | 57226.51 | 11409.2028 | 7104.9898 | 3069.26 | NORMAL
299.817 | 0.65 | 291.483 | 0.8 | 1 | 79289.74 | 11635.8734 | 7730.0016 | 2789.618 | NORMAL
299.817 | 0.65 | 291.483 | 0.8 | 1 | 101352.97 | 11684.1149 | 8124.3507 | 2644.682 | NORMAL
299.817 | 0.65 | 291.483 | 0.8 | 1 | 106868.78 | 11609.2028 | 8095.8401 | 2620.397 | NORMAL
299.817 | 0.65 | 291.483 | 0.8 | 2 | 57226.51 | 14752.6377 | 7985.7946 | 4355.158 | NORMAL
299.817 | 0.65 | 291.483 | 0.8 | 2 | 79289.74 | 15083.1477 | 8982.7385 | 3865.226 | NORMAL
299.817 | 0.65 | 291.483 | 0.8 | 2 | 101352.97 | 15117.6436 | 9689.6688 | 3616.189 | NORMAL
299.817 | 0.65 | 291.483 | 0.8 | 2 | 106868.78 | 15030.51 | 9868.2663 | 3569.032 | NORMAL
299.817 | 0.65 | 291.483 | 1.11 | 1 | 57226.51 | 11744.49 | 8443.2078 | 3083.69 | NORMAL
299.817 | 0.65 | 291.483 | 1.11 | 1 | 79289.74 | 12088.8628 | 8801.2241 | 2795.609 | NORMAL
299.817 | 0.65 | 291.483 | 1.11 | 1 | 101352.97 | 12219.4607 | 9241.6026 | 2643.858 | NORMAL
299.817 | 0.65 | 291.483 | 1.11 | 1 | 106868.78 | 12157.415 | 9479.5985 | 2617.733 | NORMAL
299.817 | 0.65 | 291.483 | 1.11 | 2 | 57226.51 | 15257.8546 | 9732.4514 | 4416.43 | NORMAL
299.817 | 0.65 | 291.483 | 1.11 | 2 | 79289.74 | 15792.5557 | 10539.2568 | 3915.79 | NORMAL
299.817 | 0.65 | 291.483 | 1.11 | 2 | 101352.97 | 15968.8159 | 11165.0288 | 3658.629 | NORMAL
299.817 | 0.65 | 291.483 | 1.11 | 2 | 106868.78 | 15896.8347 | 11146.8923 | 3609.434 | NORMAL
299.817 | 0.65 | 291.483 | 1.42 | 1 | 57226.51 | 11951.0551 | 9485.0266 | 3093.08 | NORMAL
299.817 | 0.65 | 291.483 | 1.42 | 1 | 79289.74 | 12369.6366 | 9692.4514 | 2799.64 | NORMAL
299.817 | 0.65 | 291.483 | 1.42 | 1 | 101352.97 | 12556.653 | 10028.5467 | 2643.167 | NORMAL
299.817 | 0.65 | 291.483 | 1.42 | 1 | 106868.78 | 12502.1981 | 10304.9493 | 2615.993 | NORMAL
299.817 | 0.65 | 291.483 | 1.42 | 2 | 57226.51 | 15571.3951 | 10865.3302 | 4454.1 | NORMAL
299.817 | 0.65 | 291.483 | 1.42 | 2 | 79289.74 | 16233.1477 | 11510.9737 | 3947.82 | NORMAL
299.817 | 0.65 | 291.483 | 1.42 | 2 | 101352.97 | 16503.517 | 12203.4596 | 3686.084 | NORMAL
299.817 | 0.65 | 291.483 | 1.42 | 2 | 106868.78 | 16445.5744 | 12490.8414 | 3635.514 | NORMAL
299.817 | 0.65 | 294.26 | 0.5 | 1 | 57226.51 | 11647.5674 | 5378.008 | 3079.062 | NORMAL
299.817 | 0.65 | 294.26 | 0.5 | 1 | 79289.74 | 11678.9566 | 6235.9789 | 2790.246 | NORMAL
299.817 | 0.65 | 294.26 | 0.5 | 1 | 101352.97 | 11563.1301 | 6800.1496 | 2644.984 | NORMAL
299.817 | 0.65 | 294.26 | 0.5 | 1 | 106868.78 | 11461.5768 | 6939.6982 | 2621.2726 | NORMAL
299.817 | 0.65 | 294.26 | 0.5 | 2 | 57226.51 | 14808.5287 | 6645.0459 | 4362.915 | NORMAL
299.817 | 0.65 | 294.26 | 0.5 | 2 | 79289.74 | 14818.7866 | 7677.2132 | 3846.761 | NORMAL
299.817 | 0.65 | 294.26 | 0.5 | 2 | 101352.97 | 14606.9168 | 8395.7344 | 3590.915 | NORMAL
299.817 | 0.65 | 294.26 | 0.5 | 2 | 106868.78 | 14447.6846 | 8499.255 | 3542.6947 | NORMAL
299.817 | 0.65 | 294.26 | 0.8 | 1 | 57226.51 | 12344.7831 | 7316.3826 | 3110.659 | NORMAL
299.817 | 0.65 | 294.26 | 0.8 | 1 | 79289.74 | 12617.2333 | 7891.8649 | 2803.393 | NORMAL
299.817 | 0.65 | 294.26 | 0.8 | 1 | 101352.97 | 12678.2825 | 8361.3147 | 2643.618 | NORMAL
299.817 | 0.65 | 294.26 | 0.8 | 1 | 106868.78 | 12594.7538 | 8316.2782 | 2615.738 | NORMAL
299.817 | 0.65 | 294.26 | 0.8 | 2 | 57226.51 | 15857.6495 | 7884.5819 | 4488.546 | NORMAL
299.817 | 0.65 | 294.26 | 0.8 | 2 | 79289.74 | 16277.2861 | 9029.6128 | 3951.167 | NORMAL
299.817 | 0.65 | 294.26 | 0.8 | 2 | 101352.97 | 16332.5029 | 9809.1216 | 3677.553 | NORMAL
299.817 | 0.65 | 294.26 | 0.8 | 2 | 106868.78 | 16234.5838 | 10097.4403 | 3625.555 | NORMAL
299.817 | 0.65 | 294.26 | 1.11 | 1 | 57226.51 | 12677.1102 | 8794.5677 | 3126.53 | NORMAL
299.817 | 0.65 | 294.26 | 1.11 | 1 | 79289.74 | 13083.646 | 9106.3746 | 2810.666 | NORMAL
299.817 | 0.65 | 294.26 | 1.11 | 1 | 101352.97 | 13237.3095 | 9562.0102 | 2643.667 | NORMAL
299.817 | 0.65 | 294.26 | 1.11 | 1 | 106868.78 | 13167.1454 | 9833.1847 | 2614.187 | NORMAL
299.817 | 0.65 | 294.26 | 1.11 | 2 | 57226.51 | 16360.7268 | 9841.877 | 4550.25 | NORMAL
299.817 | 0.65 | 294.26 | 1.11 | 2 | 79289.74 | 17000.0879 | 10776.6107 | 4004.554 | NORMAL
299.817 | 0.65 | 294.26 | 1.11 | 2 | 101352.97 | 17214.8886 | 11427.5013 | 3723.245 | NORMAL
299.817 | 0.65 | 294.26 | 1.11 | 2 | 106868.78 | 17134.5545 | 11400.4244 | 3668.816 | NORMAL
299.817 | 0.65 | 294.26 | 1.42 | 1 | 57226.51 | 12881.4478 | 9801.3262 | 3137.97 | NORMAL
299.817 | 0.65 | 294.26 | 1.42 | 1 | 79289.74 | 13371.6002 | 10081.8389 | 2815.38 | NORMAL
299.817 | 0.65 | 294.26 | 1.42 | 1 | 101352.97 | 13588.3939 | 10518.3137 | 2643.571 | NORMAL
299.817 | 0.65 | 294.26 | 1.42 | 1 | 106868.78 | 13526.4068 | 10802.1344 | 2613.415 | NORMAL
299.817 | 0.65 | 294.26 | 1.42 | 2 | 57226.51 | 16667.1161 | 11263.3037 | 4590.3 | NORMAL
299.817 | 0.65 | 294.26 | 1.42 | 2 | 79289.74 | 17445.7503 | 11869.8094 | 4038.26 | NORMAL
299.817 | 0.65 | 294.26 | 1.42 | 2 | 101352.97 | 17766.735 | 12599.671 | 3752.528 | NORMAL
299.817 | 0.65 | 294.26 | 1.42 | 2 | 106868.78 | 17701.524 | 12937.6545 | 3696.793 | NORMAL
299.817 | 0.65 | 297.037 | 0.5 | 1 | 57226.51 | 12622.2157 | 5330.7277 | 3123.508 | NORMAL
299.817 | 0.65 | 297.037 | 0.5 | 1 | 79289.74 | 12690.2696 | 6277.3434 | 2804.718 | NORMAL
299.817 | 0.65 | 297.037 | 0.5 | 1 | 101352.97 | 12568.8159 | 6925.0405 | 2643.62 | NORMAL
299.817 | 0.65 | 297.037 | 0.5 | 1 | 106868.78 | 12454.3962 | 7093.3516 | 2616.247 | NORMAL
299.817 | 0.65 | 297.037 | 0.5 | 2 | 57226.51 | 15973.5932 | 6689.2776 | 4503.26 | NORMAL
299.817 | 0.65 | 297.037 | 0.5 | 2 | 79289.74 | 16049.8828 | 7748.2575 | 3934.869 | NORMAL
299.817 | 0.65 | 297.037 | 0.5 | 2 | 101352.97 | 15822.8312 | 8527.1927 | 3651.652 | NORMAL
299.817 | 0.65 | 297.037 | 0.5 | 2 | 106868.78 | 15678.2532 | 8647.1054 | 3599.2929 | NORMAL
299.817 | 0.65 | 297.037 | 0.8 | 1 | 57226.51 | 13318.4642 | 7487.5873 | 3156.986 | NORMAL
299.817 | 0.65 | 297.037 | 0.8 | 1 | 79289.74 | 13652.755 | 8095.9745 | 2820.05 | NORMAL
299.817 | 0.65 | 297.037 | 0.8 | 1 | 101352.97 | 13733.6753 | 8599.3133 | 2644.302 | NORMAL
299.817 | 0.65 | 297.037 | 0.8 | 1 | 106868.78 | 13639.9765 | 8510.1178 | 2613.41 | NORMAL
299.817 | 0.65 | 297.037 | 0.8 | 2 | 57226.51 | 17000.7913 | 7662.5797 | 4632.58 | NORMAL
299.817 | 0.65 | 297.037 | 0.8 | 2 | 79289.74 | 17533.4701 | 9000.9997 | 4044.903 | NORMAL
299.817 | 0.65 | 297.037 | 0.8 | 2 | 101352.97 | 17622.3329 | 9866.6209 | 3745.136 | NORMAL
299.817 | 0.65 | 297.037 | 0.8 | 2 | 106868.78 | 17511.1079 | 10300.8216 | 3687.356 | NORMAL
299.817 | 0.65 | 297.037 | 1.11 | 1 | 57226.51 | 13648.007 | 9174.941 | 3174.04 | NORMAL
299.817 | 0.65 | 297.037 | 1.11 | 1 | 79289.74 | 14129.0739 | 9480.9477 | 2828.735 | NORMAL
299.817 | 0.65 | 297.037 | 1.11 | 1 | 101352.97 | 14313.306 | 9913.2526 | 2645.434 | NORMAL
299.817 | 0.65 | 297.037 | 1.11 | 1 | 106868.78 | 14234.2321 | 10110.7174 | 2612.739 | NORMAL
299.817 | 0.65 | 297.037 | 1.11 | 2 | 57226.51 | 17496.1606 | 9942.5082 | 4694.62 | NORMAL
299.817 | 0.65 | 297.037 | 1.11 | 2 | 79289.74 | 18261.5475 | 10943.5428 | 4101.007 | NORMAL
299.817 | 0.65 | 297.037 | 1.11 | 2 | 101352.97 | 18528.5463 | 11682.3967 | 3793.912 | NORMAL
299.817 | 0.65 | 297.037 | 1.11 | 2 | 106868.78 | 18439.6835 | 11600.3496 | 3733.827 | NORMAL
299.817 | 0.65 | 297.037 | 1.42 | 1 | 57226.51 | 13851.4654 | 10103.4667 | 3185.97 | NORMAL
299.817 | 0.65 | 297.037 | 1.42 | 1 | 79289.74 | 14422.5381 | 10386.1601 | 2834.17 | NORMAL
299.817 | 0.65 | 297.037 | 1.42 | 1 | 101352.97 | 14675.8499 | 10907.3412 | 2645.939 | NORMAL
299.817 | 0.65 | 297.037 | 1.42 | 1 | 106868.78 | 14605.9789 | 11300.8065 | 2612.59 | NORMAL
299.817 | 0.65 | 297.037 | 1.42 | 2 | 57226.51 | 17794.2849 | 11709.4224 | 4736.4 | NORMAL
299.817 | 0.65 | 297.037 | 1.42 | 2 | 79289.74 | 18709.6424 | 12258.9132 | 4136.22 | NORMAL
299.817 | 0.65 | 297.037 | 1.42 | 2 | 101352.97 | 19092.2626 | 12974.7389 | 3825.134 | NORMAL
299.817 | 0.65 | 297.037 | 1.42 | 2 | 106868.78 | 19020.4865 | 13264.3357 | 3763.781 | NORMAL
299.817 | 0.65 | 299.814 | 0.5 | 1 | 57226.51 | 13626.8757 | 5241.1962 | 3172.562 | NORMAL
299.817 | 0.65 | 299.814 | 0.5 | 1 | 79289.74 | 13754.8066 | 6295.6712 | 2822.164 | NORMAL
299.817 | 0.65 | 299.814 | 0.5 | 1 | 101352.97 | 13637.4854 | 7033.8058 | 2643.993 | NORMAL
299.817 | 0.65 | 299.814 | 0.5 | 1 | 106868.78 | 13508.0305 | 7214.6661 | 2613.518 | NORMAL
299.817 | 0.65 | 299.814 | 0.5 | 2 | 57226.51 | 17173.3587 | 6737.5036 | 4655.113 | NORMAL
299.817 | 0.65 | 299.814 | 0.5 | 2 | 79289.74 | 17346.7468 | 7813.4605 | 4031.057 | NORMAL
299.817 | 0.65 | 299.814 | 0.5 | 2 | 101352.97 | 17122.5088 | 8619.0771 | 3718.654 | NORMAL
299.817 | 0.65 | 299.814 | 0.5 | 2 | 106868.78 | 16959.5545 | 8737.783 | 3660.5642 | NORMAL
299.817 | 0.65 | 299.814 | 0.8 | 1 | 57226.51 | 14310.2579 | 7479.6427 | 3208.557 | NORMAL
299.817 | 0.65 | 299.814 | 0.8 | 1 | 79289.74 | 14733.8511 | 8212.9138 | 2839.853 | NORMAL
299.817 | 0.65 | 299.814 | 0.8 | 1 | 101352.97 | 14844.109 | 8726.5993 | 2647.222 | NORMAL
299.817 | 0.65 | 299.814 | 0.8 | 1 | 106868.78 | 14740.1524 | 8698.5619 | 2612.903 | NORMAL
299.817 | 0.65 | 299.814 | 0.8 | 2 | 57226.51 | 18168.2005 | 7403.6144 | 4785.621 | NORMAL
299.817 | 0.65 | 299.814 | 0.8 | 2 | 79289.74 | 18836.8992 | 8880.7691 | 4146.464 | NORMAL
299.817 | 0.65 | 299.814 | 0.8 | 2 | 101352.97 | 18975.5275 | 9866.2496 | 3819.012 | NORMAL
299.817 | 0.65 | 299.814 | 0.8 | 2 | 106868.78 | 18853.8394 | 10343.4802 | 3755.312 | NORMAL
299.817 | 0.65 | 299.814 | 1.11 | 1 | 57226.51 | 14646.6002 | 9442.9708 | 3226.2 | NORMAL
299.817 | 0.65 | 299.814 | 1.11 | 1 | 79289.74 | 15217.204 | 9772.8536 | 2850.179 | NORMAL
299.817 | 0.65 | 299.814 | 1.11 | 1 | 101352.97 | 15439.6542 | 10304.4098 | 2649.428 | NORMAL
299.817 | 0.65 | 299.814 | 1.11 | 1 | 106868.78 | 15352.3447 | 10299.1972 | 2613.303 | NORMAL
299.817 | 0.65 | 299.814 | 1.11 | 2 | 57226.51 | 18643.4642 | 10111.3574 | 4850.14 | NORMAL
299.817 | 0.65 | 299.814 | 1.11 | 2 | 79289.74 | 19563.9801 | 11129.7331 | 4204.76 | NORMAL
299.817 | 0.65 | 299.814 | 1.11 | 2 | 101352.97 | 19897.245 | 11923.245 | 3870.816 | NORMAL
299.817 | 0.65 | 299.814 | 1.11 | 2 | 106868.78 | 19801.2016 | 11758.6268 | 3804.653 | NORMAL
299.817 | 0.65 | 299.814 | 1.42 | 1 | 57226.51 | 14848.2415 | 10608.2222 | 3238.6 | NORMAL
299.817 | 0.65 | 299.814 | 1.42 | 1 | 79289.74 | 15513.7163 | 10801.456 | 2856.35 | NORMAL
299.817 | 0.65 | 299.814 | 1.42 | 1 | 101352.97 | 15811.8699 | 11276.8991 | 2650.766 | NORMAL
299.817 | 0.65 | 299.814 | 1.42 | 1 | 106868.78 | 15735.17 | 11683.285 | 2613.913 | NORMAL
299.817 | 0.65 | 299.814 | 1.42 | 2 | 57226.51 | 18936.9578 | 11926.6854 | 4890.56 | NORMAL
299.817 | 0.65 | 299.814 | 1.42 | 2 | 79289.74 | 20009.3494 | 12621.9776 | 4241.29 | NORMAL
299.817 | 0.65 | 299.814 | 1.42 | 2 | 101352.97 | 20468.347 | 13357.0087 | 3903.829 | NORMAL
299.817 | 0.65 | 299.814 | 1.42 | 2 | 106868.78 | 20391.6471 | 13479.1846 | 3836.453 | NORMAL
299.817 | 0.65 | 302.591 | 0.5 | 1 | 57226.51 | 14673.1536 | 5090.3811 | 3227.327 | NORMAL
299.817 | 0.65 | 302.591 | 0.5 | 1 | 79289.74 | 14879.1325 | 6307.175 | 2843.227 | NORMAL
299.817 | 0.65 | 302.591 | 0.5 | 1 | 101352.97 | 14775.0879 | 7107.4526 | 2646.564 | NORMAL
299.817 | 0.65 | 302.591 | 0.5 | 1 | 106868.78 | 14633.0891 | 7313.2521 | 2612.7 | NORMAL
299.817 | 0.65 | 302.591 | 0.5 | 2 | 57226.51 | 18410.4338 | 6646.4796 | 4818.662 | NORMAL
299.817 | 0.65 | 302.591 | 0.5 | 2 | 79289.74 | 18713.3353 | 7792.8878 | 4136.731 | NORMAL
299.817 | 0.65 | 302.591 | 0.5 | 2 | 101352.97 | 18508.3236 | 8663.2465 | 3793.296 | NORMAL
299.817 | 0.65 | 302.591 | 0.5 | 2 | 106868.78 | 18329.2497 | 8792.3028 | 3728.617 | NORMAL
299.817 | 0.65 | 302.591 | 0.8 | 1 | 57226.51 | 15344.49 | 7374.8228 | 3265.043 | NORMAL
299.817 | 0.65 | 302.591 | 0.8 | 1 | 79289.74 | 15865.592 | 8206.3664 | 2863.459 | NORMAL
299.817 | 0.65 | 302.591 | 0.8 | 1 | 101352.97 | 16011.1665 | 8767.1704 | 2651.667 | NORMAL
299.817 | 0.65 | 302.591 | 0.8 | 1 | 106868.78 | 15902.4912 | 8890.7648 | 2614.679 | NORMAL
299.817 | 0.65 | 302.591 | 0.8 | 2 | 57226.51 | 19360.7268 | 6984.1305 | 4948.573 | NORMAL
299.817 | 0.65 | 302.591 | 0.8 | 2 | 79289.74 | 20192.6143 | 8646.7399 | 4256.534 | NORMAL
299.817 | 0.65 | 302.591 | 0.8 | 2 | 101352.97 | 20398.1243 | 9761.1756 | 3900.181 | NORMAL
299.817 | 0.65 | 302.591 | 0.8 | 2 | 106868.78 | 20267.8195 | 10306.6726 | 3830.121 | NORMAL
299.817 | 0.65 | 302.591 | 1.11 | 1 | 57226.51 | 15675.8206 | 9624.1858 | 3284.72 | NORMAL
299.817 | 0.65 | 302.591 | 1.11 | 1 | 79289.74 | 16353.4584 | 9992.9933 | 2875.593 | NORMAL
299.817 | 0.65 | 302.591 | 1.11 | 1 | 101352.97 | 16624.0328 | 10642.6393 | 2656.172 | NORMAL
299.817 | 0.65 | 302.591 | 1.11 | 1 | 106868.78 | 16529.8945 | 10428.9253 | 2616.457 | NORMAL
299.817 | 0.65 | 302.591 | 1.11 | 2 | 57226.51 | 19818.2298 | 10472.2103 | 5013.05 | NORMAL
299.817 | 0.65 | 302.591 | 1.11 | 2 | 79289.74 | 20910.3165 | 11354.8664 | 4316.822 | NORMAL
299.817 | 0.65 | 302.591 | 1.11 | 2 | 101352.97 | 21325.9379 | 11971.6564 | 3954.71 | NORMAL
299.817 | 0.65 | 302.591 | 1.11 | 2 | 106868.78 | 21225.6741 | 11934.114 | 3881.927 | NORMAL
299.817 | 0.65 | 302.591 | 1.42 | 1 | 57226.51 | 15877.374 | 11051.3668 | 3295.38 | NORMAL
299.817 | 0.65 | 302.591 | 1.42 | 1 | 79289.74 | 16650.9379 | 11228.46 | 2882.5 | NORMAL
299.817 | 0.65 | 302.591 | 1.42 | 1 | 101352.97 | 17003.2825 | 11723.5083 | 2658.292 | NORMAL
299.817 | 0.65 | 302.591 | 1.42 | 1 | 106868.78 | 16921.2485 | 12061.5167 | 2617.765 | NORMAL
299.817 | 0.65 | 302.591 | 1.42 | 2 | 57226.51 | 20101.2896 | 12367.2581 | 5053.84 | NORMAL
299.817 | 0.65 | 302.591 | 1.42 | 2 | 79289.74 | 21349.9707 | 12810.2173 | 4354.53 | NORMAL
299.817 | 0.65 | 302.591 | 1.42 | 2 | 101352.97 | 21899.7362 | 13799.3085 | 3989.519 | NORMAL
299.817 | 0.65 | 302.591 | 1.42 | 2 | 106868.78 | 21821.6882 | 13604.9061 | 3915.528 | NORMAL
299.817 | 0.65 | 305.368 | 0.5 | 1 | 57226.51 | 15755.1876 | 4998.9792 | 3288.033 | NORMAL
299.817 | 0.65 | 305.368 | 0.5 | 1 | 79289.74 | 16059.8183 | 6324.0674 | 2868.527 | NORMAL
299.817 | 0.65 | 305.368 | 0.5 | 1 | 101352.97 | 15980.8617 | 7179.9295 | 2651.151 | NORMAL
299.817 | 0.65 | 305.368 | 0.5 | 1 | 106868.78 | 15825.9965 | 7382.3368 | 2614.176 | NORMAL
299.817 | 0.65 | 305.368 | 0.5 | 2 | 57226.51 | 19676.4361 | 6557.5659 | 4993.249 | NORMAL
299.817 | 0.65 | 305.368 | 0.5 | 2 | 79289.74 | 20143.1125 | 7752.3186 | 4252.401 | NORMAL
299.817 | 0.65 | 305.368 | 0.5 | 2 | 101352.97 | 19978.4877 | 8671.6026 | 3875.972 | NORMAL
299.817 | 0.65 | 305.368 | 0.5 | 2 | 106868.78 | 19783.558 | 8809.4206 | 3804.465 | NORMAL
299.817 | 0.65 | 305.368 | 0.8 | 1 | 57226.51 | 16408.558 | 7173.559 | 3327.184 | NORMAL
299.817 | 0.65 | 305.368 | 0.8 | 1 | 79289.74 | 17043.7573 | 8109.147 | 2891.288 | NORMAL
299.817 | 0.65 | 305.368 | 0.8 | 1 | 101352.97 | 17241.6764 | 8705.3397 | 2659.725 | NORMAL
299.817 | 0.65 | 305.368 | 0.8 | 1 | 106868.78 | 17126.2603 | 9110.7594 | 2619.378 | NORMAL
299.817 | 0.65 | 305.368 | 0.8 | 2 | 57226.51 | 20572.9777 | 6351.4543 | 5121.044 | NORMAL
299.817 | 0.65 | 305.368 | 0.8 | 2 | 79289.74 | 21595.1055 | 8350.0715 | 4375.719 | NORMAL
299.817 | 0.65 | 305.368 | 0.8 | 2 | 101352.97 | 21889.1852 | 9540.5108 | 3989.45 | NORMAL
299.817 | 0.65 | 305.368 | 0.8 | 2 | 106868.78 | 21750.0293 | 10170.7052 | 3912.315 | NORMAL
299.817 | 0.65 | 305.368 | 1.11 | 1 | 57226.51 | 16730.5686 | 9355.3491 | 3346.71 | NORMAL
299.817 | 0.65 | 305.368 | 1.11 | 1 | 79289.74 | 17533.5873 | 10342.1164 | 2905.28 | NORMAL
299.817 | 0.65 | 305.368 | 1.11 | 1 | 101352.97 | 17864.9473 | 10883.0222 | 2665.71 | NORMAL
299.817 | 0.65 | 305.368 | 1.11 | 1 | 106868.78 | 17764.4197 | 10586.2263 | 2622.406 | NORMAL
299.817 | 0.65 | 305.368 | 1.11 | 2 | 57226.51 | 21007.6495 | 10444.9403 | 5184.87 | NORMAL
299.817 | 0.65 | 305.368 | 1.11 | 2 | 79289.74 | 22295.1348 | 11371.6335 | 4437.506 | NORMAL
299.817 | 0.65 | 305.368 | 1.11 | 2 | 101352.97 | 22807.034 | 11925.3875 | 4044.1 | NORMAL
299.817 | 0.65 | 305.368 | 1.11 | 2 | 106868.78 | 22708.5287 | 12159.2363 | 3966.369 | NORMAL
299.817 | 0.65 | 305.368 | 1.42 | 1 | 57226.51 | 16930.51 | 11300.6752 | 3359.12 | NORMAL
299.817 | 0.65 | 305.368 | 1.42 | 1 | 79289.74 | 17830.6565 | 11471.0854 | 2913.02 | NORMAL
299.817 | 0.65 | 305.368 | 1.42 | 1 | 101352.97 | 18248.769 | 12162.4396 | 2669.084 | NORMAL
299.817 | 0.65 | 305.368 | 1.42 | 1 | 106868.78 | 18162.5147 | 12584.8246 | 2624.495 | NORMAL
299.817 | 0.65 | 305.368 | 1.42 | 2 | 57226.51 | 21281.3306 | 12250.6192 | 5225.6 | NORMAL
299.817 | 0.65 | 305.368 | 1.42 | 2 | 79289.74 | 22725.4982 | 13224.4219 | 4476.2 | NORMAL
299.817 | 0.65 | 305.368 | 1.42 | 2 | 101352.97 | 23381.7409 | 14051.0234 | 4082.675 | NORMAL
299.817 | 0.65 | 305.368 | 1.42 | 2 | 106868.78 | 23303.8687 | 13758.441 | 4001.423 | NORMAL
299.817 | 0.75 | 288.706 | 0.5 | 1 | 57226.51 | 10312.9836 | 4752.9035 | 3023.466 | NORMAL
299.817 | 0.75 | 288.706 | 0.5 | 1 | 79289.74 | 10266.8523 | 5465.0352 | 2773.652 | NORMAL
299.817 | 0.75 | 288.706 | 0.5 | 1 | 101352.97 | 10132.4736 | 5964.5718 | 2651.57 | NORMAL
299.817 | 0.75 | 288.706 | 0.5 | 1 | 106868.78 | 10000.2931 | 6012.1962 | 2631.4704 | NORMAL
299.817 | 0.75 | 288.706 | 0.5 | 2 | 57226.51 | 13228.5463 | 5916.7451 | 4179.177 | NORMAL
299.817 | 0.75 | 288.706 | 0.5 | 2 | 79289.74 | 13100.3517 | 6865.0821 | 3728.325 | NORMAL
299.817 | 0.75 | 288.706 | 0.5 | 2 | 101352.97 | 12883.4994 | 7530.3539 | 3507.629 | NORMAL
299.817 | 0.75 | 288.706 | 0.5 | 2 | 106868.78 | 12777.0809 | 7635.5835 | 3467.4467 | NORMAL
299.817 | 0.75 | 288.706 | 0.8 | 1 | 57226.51 | 10975.8792 | 5495.4142 | 3050.524 | NORMAL
299.817 | 0.75 | 288.706 | 0.8 | 1 | 79289.74 | 11136.8992 | 6324.7675 | 2783.376 | NORMAL
299.817 | 0.75 | 288.706 | 0.8 | 1 | 101352.97 | 11137.3388 | 6867.7063 | 2647.023 | NORMAL
299.817 | 0.75 | 288.706 | 0.8 | 1 | 106868.78 | 11059.5838 | 6995.2642 | 2623.834 | NORMAL
299.817 | 0.75 | 288.706 | 0.8 | 2 | 57226.51 | 14248.0363 | 6426.1494 | 4297.892 | NORMAL
299.817 | 0.75 | 288.706 | 0.8 | 2 | 79289.74 | 14493.0539 | 7691.4492 | 3824.129 | NORMAL
299.817 | 0.75 | 288.706 | 0.8 | 2 | 101352.97 | 14469.0211 | 8522.1811 | 3584.317 | NORMAL
299.817 | 0.75 | 288.706 | 0.8 | 2 | 106868.78 | 14313.4818 | 8715.0211 | 3536.888 | NORMAL
299.817 | 0.75 | 288.706 | 1.11 | 1 | 57226.51 | 11293.4935 | 6701.4687 | 3064.11 | NORMAL
299.817 | 0.75 | 288.706 | 1.11 | 1 | 79289.74 | 11567.1747 | 7375.6586 | 2787.916 | NORMAL
299.817 | 0.75 | 288.706 | 1.11 | 1 | 101352.97 | 11648.5639 | 7815.138 | 2644.271 | NORMAL
299.817 | 0.75 | 288.706 | 1.11 | 1 | 106868.78 | 11579.3962 | 7784.1797 | 2620.561 | NORMAL
299.817 | 0.75 | 288.706 | 1.11 | 2 | 57226.51 | 14740.5041 | 7430.7176 | 4354.77 | NORMAL
299.817 | 0.75 | 288.706 | 1.11 | 2 | 79289.74 | 15179.0739 | 8619.9987 | 3870.756 | NORMAL
299.817 | 0.75 | 288.706 | 1.11 | 2 | 101352.97 | 15288.5991 | 9393.1165 | 3624.655 | NORMAL
299.817 | 0.75 | 288.706 | 1.11 | 2 | 106868.78 | 15210.1993 | 9638.3687 | 3577.34 | NORMAL
299.817 | 0.75 | 288.706 | 1.42 | 1 | 57226.51 | 11488.4818 | 7744.8222 | 3072.61 | NORMAL
299.817 | 0.75 | 288.706 | 1.42 | 1 | 79289.74 | 11831.7702 | 8108.8446 | 2791.36 | NORMAL
299.817 | 0.75 | 288.706 | 1.42 | 1 | 101352.97 | 11965.3576 | 8520.8303 | 2643.649 | NORMAL
299.817 | 0.75 | 288.706 | 1.42 | 1 | 106868.78 | 11903.2825 | 8695.5383 | 2619.105 | NORMAL
299.817 | 0.75 | 288.706 | 1.42 | 2 | 57226.51 | 15042.0574 | 8791.2402 | 4389.97 | NORMAL
299.817 | 0.75 | 288.706 | 1.42 | 2 | 79289.74 | 15601.8464 | 9745.3969 | 3900.79 | NORMAL
299.817 | 0.75 | 288.706 | 1.42 | 2 | 101352.97 | 15800.3517 | 10440.4616 | 3650.369 | NORMAL
299.817 | 0.75 | 288.706 | 1.42 | 2 | 106868.78 | 15733.8511 | 10386.8592 | 3601.87 | NORMAL
299.817 | 0.75 | 291.483 | 0.5 | 1 | 57226.51 | 11255.4807 | 4815.6011 | 3061.671 | NORMAL
299.817 | 0.75 | 291.483 | 0.5 | 1 | 79289.74 | 11226.0258 | 5557.2083 | 2784.575 | NORMAL
299.817 | 0.75 | 291.483 | 0.5 | 1 | 101352.97 | 11073.9742 | 6101.6048 | 2646.762 | NORMAL
299.817 | 0.75 | 291.483 | 0.5 | 1 | 106868.78 | 10967.4384 | 6170.8402 | 2624.4497 | NORMAL
299.817 | 0.75 | 291.483 | 0.5 | 2 | 57226.51 | 14357.9132 | 5893.5501 | 4311.172 | NORMAL
299.817 | 0.75 | 291.483 | 0.5 | 2 | 79289.74 | 14282.5616 | 6923.1146 | 3809.364 | NORMAL
299.817 | 0.75 | 291.483 | 0.5 | 2 | 101352.97 | 13985.551 | 7631.104 | 3560.649 | NORMAL
299.817 | 0.75 | 291.483 | 0.5 | 2 | 106868.78 | 13862.6319 | 7749.6271 | 3515.8642 | NORMAL
299.817 | 0.75 | 291.483 | 0.8 | 1 | 57226.51 | 11925.8792 | 5373.2168 | 3091.384 | NORMAL
299.817 | 0.75 | 291.483 | 0.8 | 1 | 79289.74 | 12132.1219 | 6331.0872 | 2796.42 | NORMAL
299.817 | 0.75 | 291.483 | 0.8 | 1 | 101352.97 | 12143.728 | 6949.9891 | 2643.51 | NORMAL
299.817 | 0.75 | 291.483 | 0.8 | 1 | 106868.78 | 12053.517 | 7181.9435 | 2618.596 | NORMAL
299.817 | 0.75 | 291.483 | 0.8 | 2 | 57226.51 | 15379.279 | 6346.7362 | 4430.474 | NORMAL
299.817 | 0.75 | 291.483 | 0.8 | 2 | 79289.74 | 15708.2356 | 7728.6718 | 3910.351 | NORMAL
299.817 | 0.75 | 291.483 | 0.8 | 2 | 101352.97 | 15703.2825 | 8652.5558 | 3645.657 | NORMAL
299.817 | 0.75 | 291.483 | 0.8 | 2 | 106868.78 | 15595.6624 | 8907.9148 | 3595.433 | NORMAL
299.817 | 0.75 | 291.483 | 1.11 | 1 | 57226.51 | 12244.2263 | 6922.5672 | 3106.74 | NORMAL
299.817 | 0.75 | 291.483 | 1.11 | 1 | 79289.74 | 12576.993 | 7517.0926 | 2802.026 | NORMAL
299.817 | 0.75 | 291.483 | 1.11 | 1 | 101352.97 | 12677.755 | 8047.1289 | 2643.132 | NORMAL
299.817 | 0.75 | 291.483 | 1.11 | 1 | 106868.78 | 12600.9672 | 7980.2051 | 2615.654 | NORMAL
299.817 | 0.75 | 291.483 | 1.11 | 2 | 57226.51 | 15866.1489 | 7275.7716 | 4489.65 | NORMAL
299.817 | 0.75 | 291.483 | 1.11 | 2 | 79289.74 | 16408.1477 | 8574.5206 | 3959.302 | NORMAL
299.817 | 0.75 | 291.483 | 1.11 | 2 | 101352.97 | 16552.1102 | 9451.5032 | 3688.942 | NORMAL
299.817 | 0.75 | 291.483 | 1.11 | 2 | 106868.78 | 16463.3353 | 9847.4288 | 3636.53 | NORMAL
299.817 | 0.75 | 291.483 | 1.42 | 1 | 57226.51 | 12441.4127 | 7971.9845 | 3115.49 | NORMAL
299.817 | 0.75 | 291.483 | 1.42 | 1 | 79289.74 | 12849.7069 | 8363.2189 | 2806.11 | NORMAL
299.817 | 0.75 | 291.483 | 1.42 | 1 | 101352.97 | 13009.5545 | 8914.8493 | 2643.045 | NORMAL
299.817 | 0.75 | 291.483 | 1.42 | 1 | 106868.78 | 12941.5299 | 8894.3511 | 2614.675 | NORMAL
299.817 | 0.75 | 291.483 | 1.42 | 2 | 57226.51 | 16164.0094 | 8967.8247 | 4526.68 | NORMAL
299.817 | 0.75 | 291.483 | 1.42 | 2 | 79289.74 | 16839.2438 | 9944.4828 | 3990.93 | NORMAL
299.817 | 0.75 | 291.483 | 1.42 | 2 | 101352.97 | 17082.796 | 10625.5162 | 3716.634 | NORMAL
299.817 | 0.75 | 291.483 | 1.42 | 2 | 106868.78 | 17008.7339 | 10608.2453 | 3662.936 | NORMAL
299.817 | 0.75 | 294.26 | 0.5 | 1 | 57226.51 | 12240.0938 | 4843.3684 | 3105.449 | NORMAL
299.817 | 0.75 | 294.26 | 0.5 | 1 | 79289.74 | 12247.6553 | 5614.3497 | 2798.145 | NORMAL
299.817 | 0.75 | 294.26 | 0.5 | 1 | 101352.97 | 12086.313 | 6197.4987 | 2644.037 | NORMAL
299.817 | 0.75 | 294.26 | 0.5 | 1 | 106868.78 | 11965.3576 | 6275.1959 | 2618.6246 | NORMAL
299.817 | 0.75 | 294.26 | 0.5 | 2 | 57226.51 | 15546.0141 | 5842.1144 | 4450.932 | NORMAL
299.817 | 0.75 | 294.26 | 0.5 | 2 | 79289.74 | 15525.7327 | 6934.5996 | 3897.156 | NORMAL
299.817 | 0.75 | 294.26 | 0.5 | 2 | 101352.97 | 15243.2591 | 7730.2987 | 3622.564 | NORMAL
299.817 | 0.75 | 294.26 | 0.5 | 2 | 106868.78 | 15094.4021 | 7858.8401 | 3572.0992 | NORMAL
299.817 | 0.75 | 294.26 | 0.8 | 1 | 57226.51 | 12910.7855 | 5189.1933 | 3137.243 | NORMAL
299.817 | 0.75 | 294.26 | 0.8 | 1 | 79289.74 | 13179.1618 | 6281.1226 | 2812.303 | NORMAL
299.817 | 0.75 | 294.26 | 0.8 | 1 | 101352.97 | 13206.9754 | 6998.9706 | 2643.261 | NORMAL
299.817 | 0.75 | 294.26 | 0.8 | 1 | 106868.78 | 13107.6495 | 7347.0079 | 2614.297 | NORMAL
299.817 | 0.75 | 294.26 | 0.8 | 2 | 57226.51 | 16546.0434 | 6214.4953 | 4574.444 | NORMAL
299.817 | 0.75 | 294.26 | 0.8 | 2 | 79289.74 | 16987.075 | 7728.5925 | 4004.192 | NORMAL
299.817 | 0.75 | 294.26 | 0.8 | 2 | 101352.97 | 17007.7081 | 8735.499 | 3712.684 | NORMAL
299.817 | 0.75 | 294.26 | 0.8 | 2 | 106868.78 | 16886.6061 | 9019.6767 | 3657.009 | NORMAL
299.817 | 0.75 | 294.26 | 1.11 | 1 | 57226.51 | 13229.3962 | 6962.5916 | 3153.52 | NORMAL
299.817 | 0.75 | 294.26 | 1.11 | 1 | 79289.74 | 13633.558 | 7730.5819 | 2819.876 | NORMAL
299.817 | 0.75 | 294.26 | 1.11 | 1 | 101352.97 | 13763.1301 | 8234.7423 | 2643.841 | NORMAL
299.817 | 0.75 | 294.26 | 1.11 | 1 | 106868.78 | 13677.1688 | 8126.9737 | 2613.125 | NORMAL
299.817 | 0.75 | 294.26 | 1.11 | 2 | 57226.51 | 17020.252 | 6929.4212 | 4635.39 | NORMAL
299.817 | 0.75 | 294.26 | 1.11 | 2 | 79289.74 | 17690.3869 | 8465.1509 | 4055.217 | NORMAL
299.817 | 0.75 | 294.26 | 1.11 | 2 | 101352.97 | 17882.1512 | 9442.2587 | 3759.243 | NORMAL
299.817 | 0.75 | 294.26 | 1.11 | 2 | 106868.78 | 17785.0235 | 10029.0281 | 3701.199 | NORMAL
299.817 | 0.75 | 294.26 | 1.42 | 1 | 57226.51 | 13426.8171 | 8066.3618 | 3163.01 | NORMAL
299.817 | 0.75 | 294.26 | 1.42 | 1 | 79289.74 | 13914.3025 | 8591.4417 | 2823.87 | NORMAL
299.817 | 0.75 | 294.26 | 1.42 | 1 | 101352.97 | 14107.6495 | 9190.7809 | 2644.38 | NORMAL
299.817 | 0.75 | 294.26 | 1.42 | 1 | 106868.78 | 14030.8324 | 9107.4834 | 2612.523 | NORMAL
299.817 | 0.75 | 294.26 | 1.42 | 2 | 57226.51 | 17311.1079 | 8904.0376 | 4673.07 | NORMAL
299.817 | 0.75 | 294.26 | 1.42 | 2 | 79289.74 | 18123.3001 | 9978.3809 | 4088.26 | NORMAL
299.817 | 0.75 | 294.26 | 1.42 | 2 | 101352.97 | 18425.9379 | 10719.0498 | 3788.709 | NORMAL
299.817 | 0.75 | 294.26 | 1.42 | 2 | 106868.78 | 18345.1641 | 10785.2321 | 3729.484 | NORMAL
299.817 | 0.75 | 297.037 | 0.5 | 1 | 57226.51 | 13275.1465 | 4805.8022 | 3154.449 | NORMAL
299.817 | 0.75 | 297.037 | 0.5 | 1 | 79289.74 | 13335.4044 | 5631.5413 | 2814.907 | NORMAL
299.817 | 0.75 | 297.037 | 0.5 | 1 | 101352.97 | 13172.8898 | 6263.0109 | 2643.505 | NORMAL
299.817 | 0.75 | 297.037 | 0.5 | 1 | 106868.78 | 13037.4854 | 6349.4118 | 2614.4515 | NORMAL
299.817 | 0.75 | 297.037 | 0.5 | 2 | 57226.51 | 16786.8699 | 5741.4452 | 4602.641 | NORMAL
299.817 | 0.75 | 297.037 | 0.5 | 2 | 79289.74 | 16851.5827 | 6915.2829 | 3994.031 | NORMAL
299.817 | 0.75 | 297.037 | 0.5 | 2 | 101352.97 | 16563.0715 | 7773.9439 | 3689.571 | NORMAL
299.817 | 0.75 | 297.037 | 0.5 | 2 | 106868.78 | 16394.4021 | 7915.2009 | 3633.2659 | NORMAL
299.817 | 0.75 | 297.037 | 0.8 | 1 | 57226.51 | 13936.2251 | 4794.591 | 3188.48 | NORMAL
299.817 | 0.75 | 297.037 | 0.8 | 1 | 79289.74 | 14284.408 | 6130.6822 | 2831.488 | NORMAL
299.817 | 0.75 | 297.037 | 0.8 | 1 | 101352.97 | 14336.3716 | 6987.8773 | 2645.367 | NORMAL
299.817 | 0.75 | 297.037 | 0.8 | 1 | 106868.78 | 14226.7292 | 7408.8253 | 2612.668 | NORMAL
299.817 | 0.75 | 297.037 | 0.8 | 2 | 57226.51 | 17751.0551 | 6093.0319 | 4729.9 | NORMAL
299.817 | 0.75 | 297.037 | 0.8 | 2 | 79289.74 | 18329.5135 | 7711.3546 | 4106.982 | NORMAL
299.817 | 0.75 | 297.037 | 0.8 | 2 | 101352.97 | 18392.6436 | 8780.9056 | 3786.874 | NORMAL
299.817 | 0.75 | 297.037 | 0.8 | 2 | 106868.78 | 18258.9683 | 9086.1374 | 3725.094 | NORMAL
299.817 | 0.75 | 297.037 | 1.11 | 1 | 57226.51 | 14251.2309 | 6842.415 | 3205.46 | NORMAL
299.817 | 0.75 | 297.037 | 1.11 | 1 | 79289.74 | 14744.7538 | 7731.2937 | 2840.395 | NORMAL
299.817 | 0.75 | 297.037 | 1.11 | 1 | 101352.97 | 14910.6682 | 8266.2806 | 2646.718 | NORMAL
299.817 | 0.75 | 297.037 | 1.11 | 1 | 106868.78 | 14816.5299 | 8297.0789 | 2612.576 | NORMAL
299.817 | 0.75 | 297.037 | 1.11 | 2 | 57226.51 | 18205.7444 | 6404.7263 | 4790.47 | NORMAL
299.817 | 0.75 | 297.037 | 1.11 | 2 | 79289.74 | 19028.4877 | 8208.2426 | 4159.313 | NORMAL
299.817 | 0.75 | 297.037 | 1.11 | 2 | 101352.97 | 19284.6131 | 9330.9758 | 3836.484 | NORMAL
299.817 | 0.75 | 297.037 | 1.11 | 2 | 106868.78 | 19177.9601 | 10015.4595 | 3772.467 | NORMAL
299.817 | 0.75 | 297.037 | 1.42 | 1 | 57226.51 | 14446.5123 | 7947.402 | 3215.83 | NORMAL
299.817 | 0.75 | 297.037 | 1.42 | 1 | 79289.74 | 15029.8652 | 8955.455 | 2845.07 | NORMAL
299.817 | 0.75 | 297.037 | 1.42 | 1 | 101352.97 | 15265.7093 | 9425.919 | 2648.05 | NORMAL
299.817 | 0.75 | 297.037 | 1.42 | 1 | 106868.78 | 15181.5065 | 9282.6714 | 2612.47 | NORMAL
299.817 | 0.75 | 297.037 | 1.42 | 2 | 57226.51 | 18486.6647 | 8667.14 | 4829.17 | NORMAL
299.817 | 0.75 | 297.037 | 1.42 | 2 | 79289.74 | 19458.7925 | 9940.4269 | 4193.56 | NORMAL
299.817 | 0.75 | 297.037 | 1.42 | 2 | 101352.97 | 19834.6718 | 10664.9047 | 3867.641 | NORMAL
299.817 | 0.75 | 297.037 | 1.42 | 2 | 106868.78 | 19749.0621 | 10981.3672 | 3802.628 | NORMAL
299.817 | 0.75 | 299.814 | 0.5 | 1 | 57226.51 | 14346.9226 | 4779.2325 | 3208.279 | NORMAL
299.817 | 0.75 | 299.814 | 0.5 | 1 | 79289.74 | 14480.2169 | 5620.6265 | 2835.139 | NORMAL
299.817 | 0.75 | 299.814 | 0.5 | 1 | 101352.97 | 14327.1981 | 6293.8092 | 2645.134 | NORMAL
299.817 | 0.75 | 299.814 | 0.5 | 1 | 106868.78 | 14176.0844 | 6388.098 | 2612.706 | NORMAL
299.817 | 0.75 | 299.814 | 0.5 | 2 | 57226.51 | 18052.0516 | 5612.3467 | 4769.932 | NORMAL
299.817 | 0.75 | 299.814 | 0.5 | 2 | 79289.74 | 18243.2005 | 6864.2231 | 4100.098 | NORMAL
299.817 | 0.75 | 299.814 | 0.5 | 2 | 101352.97 | 17966.7937 | 7775.7049 | 3763.702 | NORMAL
299.817 | 0.75 | 299.814 | 0.5 | 2 | 106868.78 | 17779.9531 | 7928.5256 | 3700.9937 | NORMAL
299.817 | 0.75 | 299.814 | 0.8 | 1 | 57226.51 | 14988.8042 | 4372.0693 | 3244.749 | NORMAL
299.817 | 0.75 | 299.814 | 0.8 | 1 | 79289.74 | 15434.7304 | 5940.9821 | 2854.366 | NORMAL
299.817 | 0.75 | 299.814 | 0.8 | 1 | 101352.97 | 15523.6225 | 6932.9895 | 2649.575 | NORMAL
299.817 | 0.75 | 299.814 | 0.8 | 1 | 106868.78 | 15403.9566 | 7362.9988 | 2613.219 | NORMAL
299.817 | 0.75 | 299.814 | 0.8 | 2 | 57226.51 | 18976.2603 | 6027.2018 | 4894.816 | NORMAL
299.817 | 0.75 | 299.814 | 0.8 | 2 | 79289.74 | 19720.252 | 7672.2429 | 4218.164 | NORMAL
299.817 | 0.75 | 299.814 | 0.8 | 2 | 101352.97 | 19843.8159 | 8834.8637 | 3868.134 | NORMAL
299.817 | 0.75 | 299.814 | 0.8 | 2 | 106868.78 | 19701.0551 | 9118.3772 | 3800.05 | NORMAL
299.817 | 0.75 | 299.814 | 1.11 | 1 | 57226.51 | 15298.9742 | 6478.0293 | 3262.47 | NORMAL
299.817 | 0.75 | 299.814 | 1.11 | 1 | 79289.74 | 15898.1243 | 7677.4109 | 2864.775 | NORMAL
299.817 | 0.75 | 299.814 | 1.11 | 1 | 101352.97 | 16111.8406 | 8274.9124 | 2652.26 | NORMAL
299.817 | 0.75 | 299.814 | 1.11 | 1 | 106868.78 | 16010.1993 | 8458.2843 | 2614.404 | NORMAL
299.817 | 0.75 | 299.814 | 1.11 | 2 | 57226.51 | 19406.4771 | 5904.6341 | 4954.7 | NORMAL
299.817 | 0.75 | 299.814 | 1.11 | 2 | 79289.74 | 20406.3013 | 7867.7719 | 4271.297 | NORMAL
299.817 | 0.75 | 299.814 | 1.11 | 2 | 101352.97 | 20745.1348 | 9098.4427 | 3920.706 | NORMAL
299.817 | 0.75 | 299.814 | 1.11 | 2 | 106868.78 | 20630.422 | 9873.328 | 3850.169 | NORMAL
299.817 | 0.75 | 299.814 | 1.42 | 1 | 57226.51 | 15491.5592 | 8059.6541 | 3273.11 | NORMAL
299.817 | 0.75 | 299.814 | 1.42 | 1 | 79289.74 | 16185.8148 | 9064.9789 | 2869.89 | NORMAL
299.817 | 0.75 | 299.814 | 1.42 | 1 | 101352.97 | 16474.8828 | 9461.5087 | 2654.406 | NORMAL
299.817 | 0.75 | 299.814 | 1.42 | 1 | 106868.78 | 16384.408 | 9327.3649 | 2614.579 | NORMAL
299.817 | 0.75 | 299.814 | 1.42 | 2 | 57226.51 | 19679.6893 | 8210.4451 | 4992.64 | NORMAL
299.817 | 0.75 | 299.814 | 1.42 | 2 | 79289.74 | 20830.2462 | 9810.6085 | 4306.5 | NORMAL
299.817 | 0.75 | 299.814 | 1.42 | 2 | 101352.97 | 21294.4607 | 10603.7897 | 3953.32 | NORMAL
299.817 | 0.75 | 299.814 | 1.42 | 2 | 106868.78 | 21206.0668 | 11140.9465 | 3882.039 | NORMAL
299.817 | 0.75 | 302.591 | 0.5 | 1 | 57226.51 | 15452.8136 | 4769.5727 | 3269.576 | NORMAL
299.817 | 0.75 | 302.591 | 0.5 | 1 | 79289.74 | 15687.8371 | 5607.8997 | 2859.773 | NORMAL
299.817 | 0.75 | 302.591 | 0.5 | 1 | 101352.97 | 15557.0926 | 6305.243 | 2649.345 | NORMAL
299.817 | 0.75 | 302.591 | 0.5 | 1 | 106868.78 | 15391.442 | 6396.2061 | 2613.144 | NORMAL
299.817 | 0.75 | 302.591 | 0.5 | 2 | 57226.51 | 19353.7808 | 5391.5375 | 4947.485 | NORMAL
299.817 | 0.75 | 302.591 | 0.5 | 2 | 79289.74 | 19705.6858 | 6761.8681 | 4216.889 | NORMAL
299.817 | 0.75 | 302.591 | 0.5 | 2 | 101352.97 | 19463.1008 | 7743.239 | 3846.442 | NORMAL
299.817 | 0.75 | 302.591 | 0.5 | 2 | 106868.78 | 19259.1149 | 7904.9615 | 3776.746 | NORMAL
299.817 | 0.75 | 302.591 | 0.8 | 1 | 57226.51 | 16068.5815 | 3698.2965 | 3306.892 | NORMAL
299.817 | 0.75 | 302.591 | 0.8 | 1 | 79289.74 | 16639.9765 | 5675.9459 | 2880.805 | NORMAL
299.817 | 0.75 | 302.591 | 0.8 | 1 | 101352.97 | 16776.4654 | 6834.4971 | 2656.755 | NORMAL
299.817 | 0.75 | 302.591 | 0.8 | 1 | 106868.78 | 16648.0657 | 7213.3738 | 2616.408 | NORMAL
299.817 | 0.75 | 302.591 | 0.8 | 2 | 57226.51 | 20226.6706 | 5833.5741 | 5070.344 | NORMAL
299.817 | 0.75 | 302.591 | 0.8 | 2 | 79289.74 | 21162.9543 | 7657.0955 | 4339.126 | NORMAL
299.817 | 0.75 | 302.591 | 0.8 | 2 | 101352.97 | 21368.2884 | 8885.4685 | 3957.693 | NORMAL
299.817 | 0.75 | 302.591 | 0.8 | 2 | 106868.78 | 21217.3798 | 9116.1958 | 3882.695 | NORMAL
299.817 | 0.75 | 302.591 | 1.11 | 1 | 57226.51 | 16375.4982 | 6273.6335 | 3325.01 | NORMAL
299.817 | 0.75 | 302.591 | 1.11 | 1 | 79289.74 | 17101.5827 | 7484.2169 | 2891.963 | NORMAL
299.817 | 0.75 | 302.591 | 1.11 | 1 | 101352.97 | 17372.9484 | 8097.1143 | 2660.938 | NORMAL
299.817 | 0.75 | 302.591 | 1.11 | 1 | 106868.78 | 17265.4162 | 8642.1868 | 2619.107 | NORMAL
299.817 | 0.75 | 302.591 | 1.11 | 2 | 57226.51 | 20626.6413 | 4926.4257 | 5127.68 | NORMAL
299.817 | 0.75 | 302.591 | 1.11 | 2 | 79289.74 | 21825.9965 | 7459.3835 | 4396.074 | NORMAL
299.817 | 0.75 | 302.591 | 1.11 | 2 | 101352.97 | 22270.9555 | 8792.3282 | 4013.199 | NORMAL
299.817 | 0.75 | 302.591 | 1.11 | 2 | 106868.78 | 22151.5827 | 9621.9165 | 3935.74 | NORMAL
299.817 | 0.75 | 302.591 | 1.42 | 1 | 57226.51 | 16564.0387 | 7805.3726 | 3335.97 | NORMAL
299.817 | 0.75 | 302.591 | 1.42 | 1 | 79289.74 | 17387.163 | 9220.569 | 2899.16 | NORMAL
299.817 | 0.75 | 302.591 | 1.42 | 1 | 101352.97 | 17741.4127 | 9658.2654 | 2663.974 | NORMAL
299.817 | 0.75 | 302.591 | 1.42 | 1 | 106868.78 | 17646.3072 | 9367.0304 | 2619.624 | NORMAL
299.817 | 0.75 | 302.591 | 1.42 | 2 | 57226.51 | 20887.1336 | 7960.2955 | 5165.82 | NORMAL
299.817 | 0.75 | 302.591 | 1.42 | 2 | 79289.74 | 22239.2732 | 9493.79 | 4428.11 | NORMAL
299.817 | 0.75 | 302.591 | 1.42 | 2 | 101352.97 | 22811.6354 | 10356.7106 | 4047.081 | NORMAL
299.817 | 0.75 | 302.591 | 1.42 | 2 | 106868.78 | 22722.8019 | 11331.1569 | 3968.982 | NORMAL
299.817 | 0.75 | 305.368 | 0.5 | 1 | 57226.51 | 16590.7679 | 4757.4691 | 3337.515 | NORMAL
299.817 | 0.75 | 305.368 | 0.5 | 1 | 79289.74 | 16953.3998 | 5584.4668 | 2889.233 | NORMAL
299.817 | 0.75 | 305.368 | 0.5 | 1 | 101352.97 | 16862.0164 | 6294.4221 | 2656.996 | NORMAL
299.817 | 0.75 | 305.368 | 0.5 | 1 | 106868.78 | 16680.9203 | 6382.2535 | 2616.53 | NORMAL
299.817 | 0.75 | 305.368 | 0.5 | 2 | 57226.51 | 20678.9859 | 5148.9848 | 5136.228 | NORMAL
299.817 | 0.75 | 305.368 | 0.5 | 2 | 79289.74 | 21229.1325 | 6589.6713 | 4344.544 | NORMAL
299.817 | 0.75 | 305.368 | 0.5 | 2 | 101352.97 | 21046.102 | 7680.6697 | 3938.402 | NORMAL
299.817 | 0.75 | 305.368 | 0.5 | 2 | 106868.78 | 20827.9895 | 7847.6532 | 3861.081 | NORMAL
299.817 | 0.75 | 305.368 | 0.8 | 1 | 57226.51 | 17178.4291 | 2938.5593 | 3375.582 | NORMAL
299.817 | 0.75 | 305.368 | 0.8 | 1 | 79289.74 | 17887.456 | 5235.4258 | 2914.25 | NORMAL
299.817 | 0.75 | 305.368 | 0.8 | 1 | 101352.97 | 18091.2368 | 6700.8494 | 2667.519 | NORMAL
299.817 | 0.75 | 305.368 | 0.8 | 1 | 106868.78 | 17953.4291 | 7051.1195 | 2621.456 | NORMAL
299.817 | 0.75 | 305.368 | 0.8 | 2 | 57226.51 | 21493.2884 | 5706.9624 | 5254.564 | NORMAL
299.817 | 0.75 | 305.368 | 0.8 | 2 | 79289.74 | 22650.4982 | 7638.6087 | 4470.182 | NORMAL
299.817 | 0.75 | 305.368 | 0.8 | 2 | 101352.97 | 22957.9426 | 8917.6684 | 4057.26 | NORMAL
299.817 | 0.75 | 305.368 | 0.8 | 2 | 106868.78 | 22803.7808 | 9092.5059 | 3973.763 | NORMAL
299.817 | 0.75 | 305.368 | 1.11 | 1 | 57226.51 | 17472.4795 | 5721.7129 | 3394.01 | NORMAL
299.817 | 0.75 | 305.368 | 1.11 | 1 | 79289.74 | 18346.2192 | 7321.1872 | 2925.372 | NORMAL
299.817 | 0.75 | 305.368 | 1.11 | 1 | 101352.97 | 18690.5041 | 7879.0381 | 2673.864 | NORMAL
299.817 | 0.75 | 305.368 | 1.11 | 1 | 106868.78 | 18579.8359 | 8842.274 | 2627.016 | NORMAL
299.817 | 0.75 | 305.368 | 1.11 | 2 | 57226.51 | 21861.8699 | 4082.7698 | 5309.75 | NORMAL
299.817 | 0.75 | 305.368 | 1.11 | 2 | 79289.74 | 23286.7233 | 6713.4925 | 4527.577 | NORMAL
299.817 | 0.75 | 305.368 | 1.11 | 2 | 101352.97 | 23853.0188 | 8323.4393 | 4114.203 | NORMAL
299.817 | 0.75 | 305.368 | 1.11 | 2 | 106868.78 | 23733.9977 | 9293.4265 | 4029.579 | NORMAL
299.817 | 0.75 | 305.368 | 1.42 | 1 | 57226.51 | 17660.6975 | 8185.3448 | 3406.04 | NORMAL
299.817 | 0.75 | 305.368 | 1.42 | 1 | 79289.74 | 18630.3341 | 9054.3983 | 2933.3 | NORMAL
299.817 | 0.75 | 305.368 | 1.42 | 1 | 101352.97 | 19060.1114 | 9843.9567 | 2677.695 | NORMAL
299.817 | 0.75 | 305.368 | 1.42 | 1 | 106868.78 | 18964.3025 | 9437.0352 | 2627.375 | NORMAL
299.817 | 0.75 | 305.368 | 1.42 | 2 | 57226.51 | 22110.6975 | 7145.094 | 5346.61 | NORMAL
299.817 | 0.75 | 305.368 | 1.42 | 2 | 79289.74 | 23672.6846 | 9293.4699 | 4562.88 | NORMAL
299.817 | 0.75 | 305.368 | 1.42 | 2 | 101352.97 | 24383.7925 | 9962.5593 | 4149.376 | NORMAL
299.817 | 0.75 | 305.368 | 1.42 | 2 | 106868.78 | 24294.0504 | 11278.7558 | 4063.898 | NORMAL
299.817 | 0.85 | 288.706 | 0.5 | 1 | 57226.51 | 10780.5686 | 4104.3349 | 3042.152 | NORMAL
299.817 | 0.85 | 288.706 | 0.5 | 1 | 79289.74 | 10697.8312 | 4879.4199 | 2778.509 | NORMAL
299.817 | 0.85 | 288.706 | 0.5 | 1 | 101352.97 | 10514.3318 | 5443.2906 | 2649.319 | NORMAL
299.817 | 0.85 | 288.706 | 0.5 | 1 | 106868.78 | 10406.7995 | 5529.8403 | 2628.0557 | NORMAL
299.817 | 0.85 | 288.706 | 0.5 | 2 | 57226.51 | 13799.619 | 5189.2363 | 4244.261 | NORMAL
299.817 | 0.85 | 288.706 | 0.5 | 2 | 79289.74 | 13600.8792 | 6233.7998 | 3762.489 | NORMAL
299.817 | 0.85 | 288.706 | 0.5 | 2 | 101352.97 | 13334.4959 | 6992.3296 | 3529.235 | NORMAL
299.817 | 0.85 | 288.706 | 0.5 | 2 | 106868.78 | 13211.6061 | 7123.447 | 3486.7629 | NORMAL
299.817 | 0.85 | 288.706 | 0.8 | 1 | 57226.51 | 11414.068 | 4576.7787 | 3068.997 | NORMAL
299.817 | 0.85 | 288.706 | 0.8 | 1 | 79289.74 | 11563.4818 | 5420.6712 | 2788.954 | NORMAL
299.817 | 0.85 | 288.706 | 0.8 | 1 | 101352.97 | 11537.1043 | 6064.202 | 2645.196 | NORMAL
299.817 | 0.85 | 288.706 | 0.8 | 1 | 106868.78 | 11443.2591 | 6160.1467 | 2621.363 | NORMAL
299.817 | 0.85 | 288.706 | 0.8 | 2 | 57226.51 | 14814.5369 | 5757.9364 | 4361.838 | NORMAL
299.817 | 0.85 | 288.706 | 0.8 | 2 | 79289.74 | 15041.9988 | 6905.8719 | 3863.051 | NORMAL
299.817 | 0.85 | 288.706 | 0.8 | 2 | 101352.97 | 14976.143 | 7758.8102 | 3609.359 | NORMAL
299.817 | 0.85 | 288.706 | 0.8 | 2 | 106868.78 | 14863.7749 | 7892.2929 | 3561.466 | NORMAL
299.817 | 0.85 | 288.706 | 1.11 | 1 | 57226.51 | 11713.1594 | 4389.4479 | 3082.53 | NORMAL
299.817 | 0.85 | 288.706 | 1.11 | 1 | 79289.74 | 11981.8875 | 5623.2316 | 2794.243 | NORMAL
299.817 | 0.85 | 288.706 | 1.11 | 1 | 101352.97 | 12041.2075 | 6375.1571 | 2644.085 | NORMAL
299.817 | 0.85 | 288.706 | 1.11 | 1 | 106868.78 | 11959.5252 | 6684.4537 | 2618.676 | NORMAL
299.817 | 0.85 | 288.706 | 1.11 | 2 | 57226.51 | 15273.5346 | 5968.2558 | 4416 | NORMAL
299.817 | 0.85 | 288.706 | 1.11 | 2 | 79289.74 | 15720.8382 | 7311.3374 | 3911.787 | NORMAL
299.817 | 0.85 | 288.706 | 1.11 | 2 | 101352.97 | 15801.993 | 8247.866 | 3650.621 | NORMAL
299.817 | 0.85 | 288.706 | 1.11 | 2 | 106868.78 | 15705.0703 | 8468.488 | 3600.655 | NORMAL
299.817 | 0.85 | 288.706 | 1.42 | 1 | 57226.51 | 11893.4642 | 5152.8553 | 3090.6 | NORMAL
299.817 | 0.85 | 288.706 | 1.42 | 1 | 79289.74 | 12237.7198 | 6209.3701 | 2797.11 | NORMAL
299.817 | 0.85 | 288.706 | 1.42 | 1 | 101352.97 | 12351.5827 | 6869.6538 | 2643.711 | NORMAL
299.817 | 0.85 | 288.706 | 1.42 | 1 | 106868.78 | 12280.3634 | 7101.6973 | 2616.928 | NORMAL
299.817 | 0.85 | 288.706 | 1.42 | 2 | 57226.51 | 15548.5639 | 5499.7136 | 4449.38 | NORMAL
299.817 | 0.85 | 288.706 | 1.42 | 2 | 79289.74 | 16128.2532 | 7353.3706 | 3940.6 | NORMAL
299.817 | 0.85 | 288.706 | 1.42 | 2 | 101352.97 | 16310.3458 | 8520.3616 | 3676.635 | NORMAL
299.817 | 0.85 | 288.706 | 1.42 | 2 | 106868.78 | 16223.4173 | 8990.8719 | 3625.291 | NORMAL
299.817 | 0.85 | 291.483 | 0.5 | 1 | 57226.51 | 11779.9824 | 4071.7627 | 3084.928 | NORMAL
299.817 | 0.85 | 291.483 | 0.5 | 1 | 79289.74 | 11723.2415 | 4892.859 | 2791.115 | NORMAL
299.817 | 0.85 | 291.483 | 0.5 | 1 | 101352.97 | 11525.2052 | 5510.604 | 2645.259 | NORMAL
299.817 | 0.85 | 291.483 | 0.5 | 1 | 106868.78 | 11402.8722 | 5608.3545 | 2621.5639 | NORMAL
299.817 | 0.85 | 291.483 | 0.5 | 2 | 57226.51 | 14999.7948 | 5095.1753 | 4385.639 | NORMAL
299.817 | 0.85 | 291.483 | 0.5 | 2 | 79289.74 | 14888.6284 | 6236.4444 | 3852.006 | NORMAL
299.817 | 0.85 | 291.483 | 0.5 | 2 | 101352.97 | 14569.0504 | 7055.5871 | 3589.189 | NORMAL
299.817 | 0.85 | 291.483 | 0.5 | 2 | 106868.78 | 14366.5592 | 7170.0767 | 3539.667 | NORMAL
299.817 | 0.85 | 291.483 | 0.8 | 1 | 57226.51 | 12409.1735 | 4599.274 | 3113.522 | NORMAL
299.817 | 0.85 | 291.483 | 0.8 | 1 | 79289.74 | 12619.4314 | 5479.0669 | 2803.701 | NORMAL
299.817 | 0.85 | 291.483 | 0.8 | 1 | 101352.97 | 12605.1583 | 6155.6282 | 2643.671 | NORMAL
299.817 | 0.85 | 291.483 | 0.8 | 1 | 106868.78 | 12499.0621 | 6240.3443 | 2616.147 | NORMAL
299.817 | 0.85 | 291.483 | 0.8 | 2 | 57226.51 | 16006.7995 | 5681.2774 | 4506.2 | NORMAL
299.817 | 0.85 | 291.483 | 0.8 | 2 | 79289.74 | 16332.9426 | 6874.2252 | 3956.146 | NORMAL
299.817 | 0.85 | 291.483 | 0.8 | 2 | 101352.97 | 16285.7561 | 7796.8058 | 3675.436 | NORMAL
299.817 | 0.85 | 291.483 | 0.8 | 2 | 106868.78 | 16159.6424 | 7943.5146 | 3622.152 | NORMAL
299.817 | 0.85 | 291.483 | 1.11 | 1 | 57226.51 | 12707.5616 | 4124.8364 | 3128.01 | NORMAL
299.817 | 0.85 | 291.483 | 1.11 | 1 | 79289.74 | 13047.245 | 5506.6811 | 2810.137 | NORMAL
299.817 | 0.85 | 291.483 | 1.11 | 1 | 101352.97 | 13130.2169 | 6400.4293 | 2643.564 | NORMAL
299.817 | 0.85 | 291.483 | 1.11 | 1 | 106868.78 | 13040.3283 | 6811.8763 | 2614.513 | NORMAL
299.817 | 0.85 | 291.483 | 1.11 | 2 | 57226.51 | 16454.2204 | 5957.086 | 4561.34 | NORMAL
299.817 | 0.85 | 291.483 | 1.11 | 2 | 79289.74 | 17023.095 | 7329.3616 | 4007.559 | NORMAL
299.817 | 0.85 | 291.483 | 1.11 | 2 | 101352.97 | 17144.3142 | 8326.0505 | 3720.108 | NORMAL
299.817 | 0.85 | 291.483 | 1.11 | 2 | 106868.78 | 17036.1079 | 8529.5022 | 3664.415 | NORMAL
299.817 | 0.85 | 291.483 | 1.42 | 1 | 57226.51 | 12888.7456 | 4898.1744 | 3136.76 | NORMAL
299.817 | 0.85 | 291.483 | 1.42 | 1 | 79289.74 | 13307.6495 | 6146.6835 | 2814.39 | NORMAL
299.817 | 0.85 | 291.483 | 1.42 | 1 | 101352.97 | 13453.6635 | 6843.8517 | 2643.774 | NORMAL
299.817 | 0.85 | 291.483 | 1.42 | 1 | 106868.78 | 13374.4431 | 7253.4554 | 2613.709 | NORMAL
299.817 | 0.85 | 291.483 | 1.42 | 2 | 57226.51 | 16717.6143 | 5091.433 | 4594.96 | NORMAL
299.817 | 0.85 | 291.483 | 1.42 | 2 | 79289.74 | 17434.8183 | 7183.302 | 4037.99 | NORMAL
299.817 | 0.85 | 291.483 | 1.42 | 2 | 101352.97 | 17670.1641 | 8533.3994 | 3748.275 | NORMAL
299.817 | 0.85 | 291.483 | 1.42 | 2 | 106868.78 | 17573.8863 | 8958.1831 | 3690.947 | NORMAL
299.817 | 0.85 | 294.26 | 0.5 | 1 | 57226.51 | 12824.0914 | 4001.5654 | 3133.048 | NORMAL
299.817 | 0.85 | 294.26 | 0.5 | 1 | 79289.74 | 12814.068 | 4876.3936 | 2806.692 | NORMAL
299.817 | 0.85 | 294.26 | 0.5 | 1 | 101352.97 | 12607.796 | 5543.1436 | 2643.659 | NORMAL
299.817 | 0.85 | 294.26 | 0.5 | 1 | 106868.78 | 12470.3107 | 5651.6446 | 2616.2526 | NORMAL
299.817 | 0.85 | 294.26 | 0.5 | 2 | 57226.51 | 16252.8136 | 4976.6928 | 4537.822 | NORMAL
299.817 | 0.85 | 294.26 | 0.5 | 2 | 79289.74 | 16215.592 | 6177.7514 | 3947.416 | NORMAL
299.817 | 0.85 | 294.26 | 0.5 | 2 | 101352.97 | 15876.3482 | 7065.2607 | 3654.506 | NORMAL
299.817 | 0.85 | 294.26 | 0.5 | 2 | 106868.78 | 15706.3306 | 7223.844 | 3600.6992 | NORMAL
299.817 | 0.85 | 294.26 | 0.8 | 1 | 57226.51 | 13440.8265 | 4616.44 | 3163.254 | NORMAL
299.817 | 0.85 | 294.26 | 0.8 | 1 | 79289.74 | 13730.6858 | 5482.9375 | 2821.799 | NORMAL
299.817 | 0.85 | 294.26 | 0.8 | 1 | 101352.97 | 13738.1301 | 6187.173 | 2644.12 | NORMAL
299.817 | 0.85 | 294.26 | 0.8 | 1 | 106868.78 | 13618.8159 | 6281.7333 | 2613.259 | NORMAL
299.817 | 0.85 | 294.26 | 0.8 | 2 | 57226.51 | 17232.2978 | 5480.1636 | 4661.418 | NORMAL
299.817 | 0.85 | 294.26 | 0.8 | 2 | 79289.74 | 17687.0457 | 6816.499 | 4057.706 | NORMAL
299.817 | 0.85 | 294.26 | 0.8 | 2 | 101352.97 | 17673.8277 | 7787.7777 | 3748.162 | NORMAL
299.817 | 0.85 | 294.26 | 0.8 | 2 | 106868.78 | 17534.8183 | 7946.0257 | 3688.849 | NORMAL
299.817 | 0.85 | 294.26 | 1.11 | 1 | 57226.51 | 13735.2872 | 3785.6237 | 3178.53 | NORMAL
299.817 | 0.85 | 294.26 | 1.11 | 1 | 79289.74 | 14162.0457 | 5387.6529 | 2829.317 | NORMAL
299.817 | 0.85 | 294.26 | 1.11 | 1 | 101352.97 | 14279.1618 | 6401.3625 | 2645.23 | NORMAL
299.817 | 0.85 | 294.26 | 1.11 | 1 | 106868.78 | 14179.8652 | 6793.6868 | 2612.658 | NORMAL
299.817 | 0.85 | 294.26 | 1.11 | 2 | 57226.51 | 17662.925 | 6180.7873 | 4716.84 | NORMAL
299.817 | 0.85 | 294.26 | 1.11 | 2 | 79289.74 | 18378.9859 | 7387.9848 | 4111.545 | NORMAL
299.817 | 0.85 | 294.26 | 1.11 | 2 | 101352.97 | 18556.6823 | 8395.7297 | 3796.234 | NORMAL
299.817 | 0.85 | 294.26 | 1.11 | 2 | 106868.78 | 18438.4525 | 8542.8116 | 3734.481 | NORMAL
299.817 | 0.85 | 294.26 | 1.42 | 1 | 57226.51 | 13915.3576 | 4170.6414 | 3187.86 | NORMAL
299.817 | 0.85 | 294.26 | 1.42 | 1 | 79289.74 | 14426.4947 | 5885.678 | 2834.22 | NORMAL
299.817 | 0.85 | 294.26 | 1.42 | 1 | 101352.97 | 14613.0422 | 6765.8385 | 2646.085 | NORMAL
299.817 | 0.85 | 294.26 | 1.42 | 1 | 106868.78 | 14526.5533 | 7370.7877 | 2612.512 | NORMAL
299.817 | 0.85 | 294.26 | 1.42 | 2 | 57226.51 | 17913.9508 | 4661.21 | 4750.27 | NORMAL
299.817 | 0.85 | 294.26 | 1.42 | 2 | 79289.74 | 18791.0317 | 6972.8445 | 4143.27 | NORMAL
299.817 | 0.85 | 294.26 | 1.42 | 2 | 101352.97 | 19093.6987 | 8496.4095 | 3826.271 | NORMAL
299.817 | 0.85 | 294.26 | 1.42 | 2 | 106868.78 | 18989.9473 | 8858.1457 | 3762.957 | NORMAL
299.817 | 0.85 | 297.037 | 0.5 | 1 | 57226.51 | 13917.5264 | 3810.7161 | 3186.586 | NORMAL
299.817 | 0.85 | 297.037 | 0.5 | 1 | 79289.74 | 13974.2087 | 4836.4457 | 2826.076 | NORMAL
299.817 | 0.85 | 297.037 | 0.5 | 1 | 101352.97 | 13771.3072 | 5545.3611 | 2644.169 | NORMAL
299.817 | 0.85 | 297.037 | 0.5 | 1 | 106868.78 | 13616.7937 | 5662.7207 | 2613.274 | NORMAL
299.817 | 0.85 | 297.037 | 0.5 | 2 | 57226.51 | 17552.3447 | 4753.4909 | 4704.35 | NORMAL
299.817 | 0.85 | 297.037 | 0.5 | 2 | 79289.74 | 17627.8429 | 6086.0304 | 4052.963 | NORMAL
299.817 | 0.85 | 297.037 | 0.5 | 2 | 101352.97 | 17290.1231 | 7038.2212 | 3727.727 | NORMAL
299.817 | 0.85 | 297.037 | 0.5 | 2 | 106868.78 | 17100 | 7211.3778 | 3667.5202 | NORMAL
299.817 | 0.85 | 297.037 | 0.8 | 1 | 57226.51 | 14513.0715 | 4534.0287 | 3218.669 | NORMAL
299.817 | 0.85 | 297.037 | 0.8 | 1 | 79289.74 | 14902.7257 | 5449.5244 | 2843.673 | NORMAL
299.817 | 0.85 | 297.037 | 0.8 | 1 | 101352.97 | 14942.3212 | 6186.375 | 2647.078 | NORMAL
299.817 | 0.85 | 297.037 | 0.8 | 1 | 106868.78 | 14811.5182 | 6287.9486 | 2612.572 | NORMAL
299.817 | 0.85 | 297.037 | 0.8 | 2 | 57226.51 | 18493.7573 | 5275.8991 | 4828.434 | NORMAL
299.817 | 0.85 | 297.037 | 0.8 | 2 | 79289.74 | 19106.1548 | 6699.9935 | 4168.823 | NORMAL
299.817 | 0.85 | 297.037 | 0.8 | 2 | 101352.97 | 19146.4537 | 7742.6727 | 3828.821 | NORMAL
299.817 | 0.85 | 297.037 | 0.8 | 2 | 106868.78 | 18995.2227 | 7905.8117 | 3763.066 | NORMAL
299.817 | 0.85 | 297.037 | 1.11 | 1 | 57226.51 | 14797.4209 | 3263.4084 | 3234.56 | NORMAL
299.817 | 0.85 | 297.037 | 1.11 | 1 | 79289.74 | 15330.2755 | 5136.2402 | 2852.39 | NORMAL
299.817 | 0.85 | 297.037 | 1.11 | 1 | 101352.97 | 15495.6331 | 6408.0641 | 2649.524 | NORMAL
299.817 | 0.85 | 297.037 | 1.11 | 1 | 106868.78 | 15386.0492 | 6690.9312 | 2613.128 | NORMAL
299.817 | 0.85 | 297.037 | 1.11 | 2 | 57226.51 | 18903.0481 | 6064.3058 | 4882.89 | NORMAL
299.817 | 0.85 | 297.037 | 1.11 | 2 | 79289.74 | 19791.9695 | 7313.964 | 4224.723 | NORMAL
299.817 | 0.85 | 297.037 | 1.11 | 2 | 101352.97 | 20044.6659 | 8346.1378 | 3879.997 | NORMAL
299.817 | 0.85 | 297.037 | 1.11 | 2 | 106868.78 | 19918.6987 | 8509.9055 | 3811.921 | NORMAL
299.817 | 0.85 | 297.037 | 1.42 | 1 | 57226.51 | 14975.4982 | 3807.0113 | 3244.41 | NORMAL
299.817 | 0.85 | 297.037 | 1.42 | 1 | 79289.74 | 15596.102 | 5562.3498 | 2858.01 | NORMAL
299.817 | 0.85 | 297.037 | 1.42 | 1 | 101352.97 | 15834.9355 | 6438.0731 | 2651.113 | NORMAL
299.817 | 0.85 | 297.037 | 1.42 | 1 | 106868.78 | 15741.5885 | 7468.0142 | 2613.735 | NORMAL
299.817 | 0.85 | 297.037 | 1.42 | 2 | 57226.51 | 19139.4197 | 3889.1684 | 4915.88 | NORMAL
299.817 | 0.85 | 297.037 | 1.42 | 2 | 79289.74 | 20197.1864 | 6680.8253 | 4257.57 | NORMAL
299.817 | 0.85 | 297.037 | 1.42 | 2 | 101352.97 | 20586.4303 | 8418.4295 | 3911.929 | NORMAL
299.817 | 0.85 | 297.037 | 1.42 | 2 | 106868.78 | 20478.0188 | 8663.8197 | 3842.192 | NORMAL
299.817 | 0.85 | 299.814 | 0.5 | 1 | 57226.51 | 15042.1747 | 3666.1691 | 3246.939 | NORMAL
299.817 | 0.85 | 299.814 | 0.5 | 1 | 79289.74 | 15192.8488 | 4773.9121 | 2849.544 | NORMAL
299.817 | 0.85 | 299.814 | 0.5 | 1 | 101352.97 | 15006.4478 | 5515.7099 | 2647.325 | NORMAL
299.817 | 0.85 | 299.814 | 0.5 | 1 | 106868.78 | 14835.7855 | 5640.1354 | 2612.593 | NORMAL
299.817 | 0.85 | 299.814 | 0.5 | 2 | 57226.51 | 18883.8218 | 4360.5388 | 4879.408 | NORMAL
299.817 | 0.85 | 299.814 | 0.5 | 2 | 79289.74 | 19105.7151 | 5959.6266 | 4168.566 | NORMAL
299.817 | 0.85 | 299.814 | 0.5 | 2 | 101352.97 | 18792.3212 | 6968.2303 | 3809.089 | NORMAL
299.817 | 0.85 | 299.814 | 0.5 | 2 | 106868.78 | 18583.8218 | 7155.9422 | 3741.878 | NORMAL
299.817 | 0.85 | 299.814 | 0.8 | 1 | 57226.51 | 15611.1958 | 4486.6889 | 3279.973 | NORMAL
299.817 | 0.85 | 299.814 | 0.8 | 1 | 79289.74 | 16122.7139 | 5391.5323 | 2869.921 | NORMAL
299.817 | 0.85 | 299.814 | 0.8 | 1 | 101352.97 | 16208.1477 | 6164.9797 | 2653.062 | NORMAL
299.817 | 0.85 | 299.814 | 0.8 | 1 | 106868.78 | 16066.6764 | 6255.8818 | 2614.475 | NORMAL
299.817 | 0.85 | 299.814 | 0.8 | 2 | 57226.51 | 19770.1934 | 4945.6127 | 5005.864 | NORMAL
299.817 | 0.85 | 299.814 | 0.8 | 2 | 79289.74 | 20571.9812 | 6450.3241 | 4289.077 | NORMAL
299.817 | 0.85 | 299.814 | 0.8 | 2 | 101352.97 | 20686.8992 | 7660.4415 | 3917.397 | NORMAL
299.817 | 0.85 | 299.814 | 0.8 | 2 | 106868.78 | 20526.9637 | 7826.5412 | 3844.689 | NORMAL
299.817 | 0.85 | 299.814 | 1.11 | 1 | 57226.51 | 15884.2614 | 3986.489 | 3298.57 | NORMAL
299.817 | 0.85 | 299.814 | 1.11 | 1 | 79289.74 | 16543.0246 | 4891.1934 | 2879.844 | NORMAL
299.817 | 0.85 | 299.814 | 1.11 | 1 | 101352.97 | 16770.34 | 6407.0748 | 2656.605 | NORMAL
299.817 | 0.85 | 299.814 | 1.11 | 1 | 106868.78 | 16649.2966 | 6514.0206 | 2616.312 | NORMAL
299.817 | 0.85 | 299.814 | 1.11 | 2 | 57226.51 | 20155.4513 | 5952.5498 | 5058.33 | NORMAL
299.817 | 0.85 | 299.814 | 1.11 | 2 | 79289.74 | 21244.4607 | 7187.7234 | 4346.907 | NORMAL
299.817 | 0.85 | 299.814 | 1.11 | 2 | 101352.97 | 21590.1524 | 8260.0685 | 3971.553 | NORMAL
299.817 | 0.85 | 299.814 | 1.11 | 2 | 106868.78 | 21460.4631 | 8430.9575 | 3896.568 | NORMAL
299.817 | 0.85 | 299.814 | 1.42 | 1 | 57226.51 | 16056.9754 | 2811.5603 | 3306.27 | NORMAL
299.817 | 0.85 | 299.814 | 1.42 | 1 | 79289.74 | 16805.7151 | 5275.7677 | 2886.08 | NORMAL
299.817 | 0.85 | 299.814 | 1.42 | 1 | 101352.97 | 17109.8476 | 6202.9186 | 2659.049 | NORMAL
299.817 | 0.85 | 299.814 | 1.42 | 1 | 106868.78 | 17011.2544 | 7296.3822 | 2617.845 | NORMAL
299.817 | 0.85 | 299.814 | 1.42 | 2 | 57226.51 | 20378.0188 | 3292.4561 | 5090.73 | NORMAL
299.817 | 0.85 | 299.814 | 1.42 | 2 | 79289.74 | 21638.7456 | 6189.0707 | 4380.4 | NORMAL
299.817 | 0.85 | 299.814 | 1.42 | 2 | 101352.97 | 22131.5065 | 8333.1983 | 4005.299 | NORMAL
299.817 | 0.85 | 299.814 | 1.42 | 2 | 106868.78 | 22021.1899 | 8370.981 | 3928.631 | NORMAL
299.817 | 0.85 | 302.591 | 0.5 | 1 | 57226.51 | 16203.2825 | 3380.9769 | 3313.587 | NORMAL
299.817 | 0.85 | 302.591 | 0.5 | 1 | 79289.74 | 16475.0879 | 4678.2495 | 2877.959 | NORMAL
299.817 | 0.85 | 302.591 | 0.5 | 1 | 101352.97 | 16321.6882 | 5461.4817 | 2653.725 | NORMAL
299.817 | 0.85 | 302.591 | 0.5 | 1 | 106868.78 | 16136.2544 | 5591.0992 | 2614.665 | NORMAL
299.817 | 0.85 | 302.591 | 0.5 | 2 | 57226.51 | 20233.5287 | 4182.0681 | 5072.688 | NORMAL
299.817 | 0.85 | 302.591 | 0.5 | 2 | 79289.74 | 20653.5463 | 5809.7806 | 4295.685 | NORMAL
299.817 | 0.85 | 302.591 | 0.5 | 2 | 101352.97 | 20390.3576 | 6863.5371 | 3900.009 | NORMAL
299.817 | 0.85 | 302.591 | 0.5 | 2 | 106868.78 | 20164.6542 | 7061.0771 | 3825.217 | NORMAL
299.817 | 0.85 | 302.591 | 0.8 | 1 | 57226.51 | 16741.9988 | 4440.5138 | 3348.748 | NORMAL
299.817 | 0.85 | 302.591 | 0.8 | 1 | 79289.74 | 17395.7503 | 5376.9916 | 2901.132 | NORMAL
299.817 | 0.85 | 302.591 | 0.8 | 1 | 101352.97 | 17542.9953 | 6124.2246 | 2662.5 | NORMAL
299.817 | 0.85 | 302.591 | 0.8 | 1 | 106868.78 | 17392.0867 | 6194.4874 | 2619.594 | NORMAL
299.817 | 0.85 | 302.591 | 0.8 | 2 | 57226.51 | 21067.5264 | 4702.0612 | 5191.358 | NORMAL
299.817 | 0.85 | 302.591 | 0.8 | 2 | 79289.74 | 22088.687 | 6201.2222 | 4419.81 | NORMAL
299.817 | 0.85 | 302.591 | 0.8 | 2 | 101352.97 | 22301.8464 | 7506.0432 | 4015.171 | NORMAL
299.817 | 0.85 | 302.591 | 0.8 | 2 | 106868.78 | 22135.551 | 7713.2213 | 3934.997 | NORMAL
299.817 | 0.85 | 302.591 | 1.11 | 1 | 57226.51 | 16994.7245 | 2490.254 | 3363.81 | NORMAL
299.817 | 0.85 | 302.591 | 1.11 | 1 | 79289.74 | 17805.6565 | 4710.3084 | 2912.163 | NORMAL
299.817 | 0.85 | 302.591 | 1.11 | 1 | 101352.97 | 18108.7339 | 6444.6811 | 2667.663 | NORMAL
299.817 | 0.85 | 302.591 | 1.11 | 1 | 106868.78 | 17978.4291 | 6338.4929 | 2622.778 | NORMAL
299.817 | 0.85 | 302.591 | 1.11 | 2 | 57226.51 | 21426.5827 | 5769.0217 | 5243.64 | NORMAL
299.817 | 0.85 | 302.591 | 1.11 | 2 | 79289.74 | 22736.3423 | 7093.9662 | 4478.633 | NORMAL
299.817 | 0.85 | 302.591 | 1.11 | 2 | 101352.97 | 23200.381 | 8163.4717 | 4072.684 | NORMAL
299.817 | 0.85 | 302.591 | 1.11 | 2 | 106868.78 | 23068.7573 | 8301.6614 | 3989.805 | NORMAL
299.817 | 0.85 | 302.591 | 1.42 | 1 | 57226.51 | 17161.7526 | 1563.5712 | 3373.96 | NORMAL
299.817 | 0.85 | 302.591 | 1.42 | 1 | 79289.74 | 18059.8769 | 4405.9598 | 2919.02 | NORMAL
299.817 | 0.85 | 302.591 | 1.42 | 1 | 101352.97 | 18445.0469 | 5724.033 | 2670.956 | NORMAL
299.817 | 0.85 | 302.591 | 1.42 | 1 | 106868.78 | 18341.6471 | 7023.7687 | 2625.125 | NORMAL
299.817 | 0.85 | 302.591 | 1.42 | 2 | 57226.51 | 21635.3751 | 2632.9602 | 5274.92 | NORMAL
299.817 | 0.85 | 302.591 | 1.42 | 2 | 79289.74 | 23118.7573 | 5917.5465 | 4513.52 | NORMAL
299.817 | 0.85 | 302.591 | 1.42 | 2 | 101352.97 | 23736.2544 | 8256.4662 | 4107.373 | NORMAL
299.817 | 0.85 | 302.591 | 1.42 | 2 | 106868.78 | 23626.6999 | 7992.5818 | 4023.452 | NORMAL
299.817 | 0.85 | 305.368 | 0.5 | 1 | 57226.51 | 17396.9226 | 3111.2656 | 3387.295 | NORMAL
299.817 | 0.85 | 305.368 | 0.5 | 1 | 79289.74 | 17815.5627 | 4519.5054 | 2912.015 | NORMAL
299.817 | 0.85 | 305.368 | 0.5 | 1 | 101352.97 | 17714.1852 | 5385.4135 | 2663.971 | NORMAL
299.817 | 0.85 | 305.368 | 0.5 | 1 | 106868.78 | 17515.8558 | 5518.5806 | 2620.24 | NORMAL
299.817 | 0.85 | 305.368 | 0.5 | 2 | 57226.51 | 21610.6096 | 3693.3396 | 5273.444 | NORMAL
299.817 | 0.85 | 305.368 | 0.5 | 2 | 79289.74 | 22260.7562 | 5643.5914 | 4433.118 | NORMAL
299.817 | 0.85 | 305.368 | 0.5 | 2 | 101352.97 | 22077.8429 | 6725.3746 | 4001.267 | NORMAL
299.817 | 0.85 | 305.368 | 0.5 | 2 | 106868.78 | 21839.7128 | 6931.8593 | 3918.101 | NORMAL
299.817 | 0.85 | 305.368 | 0.8 | 1 | 57226.51 | 17895.6037 | 4351.6919 | 3424.063 | NORMAL
299.817 | 0.85 | 305.368 | 0.8 | 1 | 79289.74 | 18716.735 | 5305.5955 | 2938.012 | NORMAL
299.817 | 0.85 | 305.368 | 0.8 | 1 | 101352.97 | 18942.7608 | 6062.498 | 2676.267 | NORMAL
299.817 | 0.85 | 305.368 | 0.8 | 1 | 106868.78 | 18785.932 | 6115.4596 | 2628.336 | NORMAL
299.817 | 0.85 | 305.368 | 0.8 | 2 | 57226.51 | 22379.8945 | 4322.4304 | 5389.365 | NORMAL
299.817 | 0.85 | 305.368 | 0.8 | 2 | 79289.74 | 23645.2227 | 5815.1642 | 4563.965 | NORMAL
299.817 | 0.85 | 305.368 | 0.8 | 2 | 101352.97 | 23982.6202 | 7250.1859 | 4122.724 | NORMAL
299.817 | 0.85 | 305.368 | 0.8 | 2 | 106868.78 | 23814.2732 | 7584.2506 | 4034.698 | NORMAL
299.817 | 0.85 | 305.368 | 1.11 | 1 | 57226.51 | 18131.3892 | 1004.43 | 3437.19 | NORMAL
299.817 | 0.85 | 305.368 | 1.11 | 1 | 79289.74 | 19113.2474 | 4272.9576 | 2950.14 | NORMAL
299.817 | 0.85 | 305.368 | 1.11 | 1 | 101352.97 | 19506.8582 | 6482.6166 | 2682.882 | NORMAL
299.817 | 0.85 | 305.368 | 1.11 | 1 | 106868.78 | 19371.0434 | 6102.1886 | 2633.158 | NORMAL
299.817 | 0.85 | 305.368 | 1.11 | 2 | 57226.51 | 22719.5487 | 5650.17 | 5438.27 | NORMAL
299.817 | 0.85 | 305.368 | 1.11 | 2 | 79289.74 | 24264.7421 | 6986.8869 | 4620.562 | NORMAL
299.817 | 0.85 | 305.368 | 1.11 | 2 | 101352.97 | 24866.9988 | 8074.4637 | 4182.677 | NORMAL
299.817 | 0.85 | 305.368 | 1.11 | 2 | 106868.78 | 24737.9836 | 8133.4285 | 4092.109 | NORMAL
299.817 | 0.85 | 305.368 | 1.42 | 1 | 57226.51 | 18287.4853 | 578.4972 | 3449.17 | NORMAL
299.817 | 0.85 | 305.368 | 1.42 | 1 | 79289.74 | 19356.2134 | 4039.1772 | 2957.45 | NORMAL
299.817 | 0.85 | 305.368 | 1.42 | 1 | 101352.97 | 19838.8042 | 5080.7773 | 2687.072 | NORMAL
299.817 | 0.85 | 305.368 | 1.42 | 1 | 106868.78 | 19728.898 | 6470.2302 | 2636.34 | NORMAL
299.817 | 0.85 | 305.368 | 1.42 | 2 | 57226.51 | 22917.1161 | 1328.2233 | 5468.15 | NORMAL
299.817 | 0.85 | 305.368 | 1.42 | 2 | 79289.74 | 24631.8875 | 5145.1087 | 4655.59 | NORMAL
299.817 | 0.85 | 305.368 | 1.42 | 2 | 101352.97 | 25392.0867 | 8250.1429 | 4218.834 | NORMAL
299.817 | 0.85 | 305.368 | 1.42 | 2 | 106868.78 | 25287.3388 | 7475.2408 | 4127.253 | NORMAL
299.817 | 0.95 | 288.706 | 0.5 | 1 | 57226.51 | 11241.2075 | 3426.0053 | 3061.507 | NORMAL
299.817 | 0.95 | 288.706 | 0.5 | 1 | 79289.74 | 11123.5932 | 4288.8126 | 2783.526 | NORMAL
299.817 | 0.95 | 288.706 | 0.5 | 1 | 101352.97 | 10897.0692 | 4926.5759 | 2647.465 | NORMAL
299.817 | 0.95 | 288.706 | 0.5 | 1 | 106868.78 | 10776.4654 | 5040.3037 | 2625.8326 | NORMAL
299.817 | 0.95 | 288.706 | 0.5 | 2 | 57226.51 | 14351.6999 | 4438.4211 | 4309.659 | NORMAL
299.817 | 0.95 | 288.706 | 0.5 | 2 | 79289.74 | 14165.1817 | 5611.8625 | 3801.629 | NORMAL
299.817 | 0.95 | 288.706 | 0.5 | 2 | 101352.97 | 13779.8652 | 6438.3388 | 3550.838 | NORMAL
299.817 | 0.95 | 288.706 | 0.5 | 2 | 106868.78 | 13641.6471 | 6616.3489 | 3506.026 | NORMAL
299.817 | 0.95 | 288.706 | 0.8 | 1 | 57226.51 | 11861.1079 | 3530.1622 | 3088.292 | NORMAL
299.817 | 0.95 | 288.706 | 0.8 | 1 | 79289.74 | 12003.0774 | 4515.6777 | 2794.832 | NORMAL
299.817 | 0.95 | 288.706 | 0.8 | 1 | 101352.97 | 11942.7608 | 5228.5885 | 2644.371 | NORMAL
299.817 | 0.95 | 288.706 | 0.8 | 1 | 106868.78 | 11834.0856 | 5352.6042 | 2619.432 | NORMAL
299.817 | 0.95 | 288.706 | 0.8 | 2 | 57226.51 | 15366.6764 | 4604.4709 | 4425.876 | NORMAL
299.817 | 0.95 | 288.706 | 0.8 | 2 | 79289.74 | 15579.6014 | 5928.7083 | 3901.998 | NORMAL
299.817 | 0.95 | 288.706 | 0.8 | 2 | 101352.97 | 15473.2708 | 6887.0291 | 3634.449 | NORMAL
299.817 | 0.95 | 288.706 | 0.8 | 2 | 106868.78 | 15346.6295 | 7073.3229 | 3583.934 | NORMAL
299.817 | 0.95 | 288.706 | 1.11 | 1 | 57226.51 | 12125.4982 | 3631.4897 | 3100.56 | NORMAL
299.817 | 0.95 | 288.706 | 1.11 | 1 | 79289.74 | 12412.1043 | 4680.6914 | 2799.621 | NORMAL
299.817 | 0.95 | 288.706 | 1.11 | 1 | 101352.97 | 12450.4103 | 5423.0252 | 2643.662 | NORMAL
299.817 | 0.95 | 288.706 | 1.11 | 1 | 106868.78 | 12351.7292 | 5543.1596 | 2616.636 | NORMAL
299.817 | 0.95 | 288.706 | 1.11 | 2 | 57226.51 | 15821.0727 | 4595.2147 | 4482.57 | NORMAL
299.817 | 0.95 | 288.706 | 1.11 | 2 | 79289.74 | 16264.8593 | 6116.0913 | 3952.229 | NORMAL
299.817 | 0.95 | 288.706 | 1.11 | 2 | 101352.97 | 16313.1594 | 7138.1981 | 3677.246 | NORMAL
299.817 | 0.95 | 288.706 | 1.11 | 2 | 106868.78 | 16200.7327 | 7323.7194 | 3624.317 | NORMAL
299.817 | 0.95 | 288.706 | 1.42 | 1 | 57226.51 | 12268.7866 | 3873.1946 | 3106.85 | NORMAL
299.817 | 0.95 | 288.706 | 1.42 | 1 | 79289.74 | 12635.9613 | 4820.0633 | 2803.47 | NORMAL
299.817 | 0.95 | 288.706 | 1.42 | 1 | 101352.97 | 12751.6706 | 5584.0331 | 2643.505 | NORMAL
299.817 | 0.95 | 288.706 | 1.42 | 1 | 106868.78 | 12659.8769 | 5697.3497 | 2615.6 | NORMAL
299.817 | 0.95 | 288.706 | 1.42 | 2 | 57226.51 | 16080.6858 | 4653.2359 | 4514.07 | NORMAL
299.817 | 0.95 | 288.706 | 1.42 | 2 | 79289.74 | 16676.7585 | 6267.2426 | 3981.51 | NORMAL
299.817 | 0.95 | 288.706 | 1.42 | 2 | 101352.97 | 16830.4513 | 7330.5199 | 3704.549 | NORMAL
299.817 | 0.95 | 288.706 | 1.42 | 2 | 106868.78 | 16728.0774 | 7511.8937 | 3649.72 | NORMAL
299.817 | 0.95 | 291.483 | 0.5 | 1 | 57226.51 | 12294.1383 | 3333.7892 | 3107.933 | NORMAL
299.817 | 0.95 | 291.483 | 0.5 | 1 | 79289.74 | 12211.2544 | 4241.8112 | 2797.841 | NORMAL
299.817 | 0.95 | 291.483 | 0.5 | 1 | 101352.97 | 11970.6331 | 4933.852 | 2644.337 | NORMAL
299.817 | 0.95 | 291.483 | 0.5 | 1 | 106868.78 | 11833.0598 | 5061.8753 | 2619.3917 | NORMAL
299.817 | 0.95 | 291.483 | 0.5 | 2 | 57226.51 | 15618.4935 | 4288.5728 | 4459 | NORMAL
299.817 | 0.95 | 291.483 | 0.5 | 2 | 79289.74 | 15481.9168 | 5509.9677 | 3894.733 | NORMAL
299.817 | 0.95 | 291.483 | 0.5 | 2 | 101352.97 | 15103.5756 | 6449.257 | 3615.89 | NORMAL
299.817 | 0.95 | 291.483 | 0.5 | 2 | 106868.78 | 14934.2028 | 6634.2359 | 3564.9009 | NORMAL
299.817 | 0.95 | 291.483 | 0.8 | 1 | 57226.51 | 12907.5909 | 3318.3351 | 3136.684 | NORMAL
299.817 | 0.95 | 291.483 | 0.8 | 1 | 79289.74 | 13118.5522 | 4452.2005 | 2811.659 | NORMAL
299.817 | 0.95 | 291.483 | 0.8 | 1 | 101352.97 | 13072.626 | 5214.2391 | 2643.601 | NORMAL
299.817 | 0.95 | 291.483 | 0.8 | 1 | 106868.78 | 12952.1102 | 5350.7499 | 2614.719 | NORMAL
299.817 | 0.95 | 291.483 | 0.8 | 2 | 57226.51 | 16614.2438 | 4306.4785 | 4579.777 | NORMAL
299.817 | 0.95 | 291.483 | 0.8 | 2 | 79289.74 | 16940.2403 | 5806.1827 | 4001.929 | NORMAL
299.817 | 0.95 | 291.483 | 0.8 | 2 | 101352.97 | 16858.3529 | 6837.4108 | 3705.337 | NORMAL
299.817 | 0.95 | 291.483 | 0.8 | 2 | 106868.78 | 16716.2954 | 7036.9252 | 3648.954 | NORMAL
299.817 | 0.95 | 291.483 | 1.11 | 1 | 57226.51 | 13167.4384 | 3376.6711 | 3149.64 | NORMAL
299.817 | 0.95 | 291.483 | 1.11 | 1 | 79289.74 | 13537.6026 | 4607.9292 | 2817.615 | NORMAL
299.817 | 0.95 | 291.483 | 1.11 | 1 | 101352.97 | 13602.1395 | 5401.6952 | 2644.032 | NORMAL
299.817 | 0.95 | 291.483 | 1.11 | 1 | 106868.78 | 13492.1454 | 5530.7002 | 2613.451 | NORMAL
299.817 | 0.95 | 291.483 | 1.11 | 2 | 57226.51 | 17052.8136 | 4178.7067 | 4637.51 | NORMAL
299.817 | 0.95 | 291.483 | 1.11 | 2 | 79289.74 | 17633.3529 | 5982.2031 | 4054.983 | NORMAL
299.817 | 0.95 | 291.483 | 1.11 | 2 | 101352.97 | 17728.898 | 7066.7565 | 3751.647 | NORMAL
299.817 | 0.95 | 291.483 | 1.11 | 2 | 106868.78 | 17605.6565 | 7266.6467 | 3692.686 | NORMAL
299.817 | 0.95 | 291.483 | 1.42 | 1 | 57226.51 | 13307.4736 | 3787.4401 | 3156.34 | NORMAL
299.817 | 0.95 | 291.483 | 1.42 | 1 | 79289.74 | 13764.6542 | 4757.4637 | 2821.85 | NORMAL
299.817 | 0.95 | 291.483 | 1.42 | 1 | 101352.97 | 13923.476 | 5565.8538 | 2644.05 | NORMAL
299.817 | 0.95 | 291.483 | 1.42 | 1 | 106868.78 | 13813.5698 | 5680.9549 | 2613.148 | NORMAL
299.817 | 0.95 | 291.483 | 1.42 | 2 | 57226.51 | 17303.4877 | 4233.9385 | 4669.28 | NORMAL
299.817 | 0.95 | 291.483 | 1.42 | 2 | 79289.74 | 18046.6588 | 6075.4799 | 4085.64 | NORMAL
299.817 | 0.95 | 291.483 | 1.42 | 2 | 101352.97 | 18260.7268 | 7249.6364 | 3780.998 | NORMAL
299.817 | 0.95 | 291.483 | 1.42 | 2 | 106868.78 | 18150.5569 | 7443.3256 | 3720.122 | NORMAL
299.817 | 0.95 | 294.26 | 0.5 | 1 | 57226.51 | 13390.1231 | 3219.2266 | 3160.325 | NORMAL
299.817 | 0.95 | 294.26 | 0.5 | 1 | 79289.74 | 13365.3869 | 4160.2974 | 2815.582 | NORMAL
299.817 | 0.95 | 294.26 | 0.5 | 1 | 101352.97 | 13120.6917 | 4904.6851 | 2643.626 | NORMAL
299.817 | 0.95 | 294.26 | 0.5 | 1 | 106868.78 | 12967.4091 | 5047.0064 | 2614.6805 | NORMAL
299.817 | 0.95 | 294.26 | 0.5 | 2 | 57226.51 | 16928.898 | 4071.6878 | 4622.434 | NORMAL
299.817 | 0.95 | 294.26 | 0.5 | 2 | 79289.74 | 16888.1301 | 5386.5873 | 3997.037 | NORMAL
299.817 | 0.95 | 294.26 | 0.5 | 2 | 101352.97 | 16498.5346 | 6390.2289 | 3686.7 | NORMAL
299.817 | 0.95 | 294.26 | 0.5 | 2 | 106868.78 | 16309.7597 | 6596.7596 | 3629.5081 | NORMAL
299.817 | 0.95 | 294.26 | 0.8 | 1 | 57226.51 | 13988.7456 | 3072.6839 | 3190.587 | NORMAL
299.817 | 0.95 | 294.26 | 0.8 | 1 | 79289.74 | 14289.4197 | 4361.1738 | 2832.042 | NORMAL
299.817 | 0.95 | 294.26 | 0.8 | 1 | 101352.97 | 14270.3986 | 5163.4155 | 2645.162 | NORMAL
299.817 | 0.95 | 294.26 | 0.8 | 1 | 106868.78 | 14137.2802 | 5311.0086 | 2612.662 | NORMAL
299.817 | 0.95 | 294.26 | 0.8 | 2 | 57226.51 | 17889.9473 | 3948.1146 | 4744.086 | NORMAL
299.817 | 0.95 | 294.26 | 0.8 | 2 | 79289.74 | 18362.8664 | 5647.7015 | 4110.96 | NORMAL
299.817 | 0.95 | 294.26 | 0.8 | 2 | 101352.97 | 18324.619 | 6735.6902 | 3783.755 | NORMAL
299.817 | 0.95 | 294.26 | 0.8 | 2 | 106868.78 | 18170.0176 | 6953.1206 | 3720.893 | NORMAL
299.817 | 0.95 | 294.26 | 1.11 | 1 | 57226.51 | 14240.9144 | 3081.6627 | 3204 | NORMAL
299.817 | 0.95 | 294.26 | 1.11 | 1 | 79289.74 | 14710.6975 | 4420.0792 | 2838.834 | NORMAL
299.817 | 0.95 | 294.26 | 1.11 | 1 | 101352.97 | 14816.8816 | 5345.5012 | 2646.973 | NORMAL
299.817 | 0.95 | 294.26 | 1.11 | 1 | 106868.78 | 14696.483 | 5480.8917 | 2612.517 | NORMAL
299.817 | 0.95 | 294.26 | 1.11 | 2 | 57226.51 | 18304.748 | 3762.7972 | 4797.35 | NORMAL
299.817 | 0.95 | 294.26 | 1.11 | 2 | 79289.74 | 19054.0739 | 5815.189 | 4166.171 | NORMAL
299.817 | 0.95 | 294.26 | 1.11 | 2 | 101352.97 | 19215.4748 | 6945.5487 | 3833.396 | NORMAL
299.817 | 0.95 | 294.26 | 1.11 | 2 | 106868.78 | 19083.8218 | 7157.1584 | 3768.061 | NORMAL
299.817 | 0.95 | 294.26 | 1.42 | 1 | 57226.51 | 14377.6377 | 3472.1708 | 3211.15 | NORMAL
299.817 | 0.95 | 294.26 | 1.42 | 1 | 79289.74 | 14941.4713 | 4685.75 | 2843.93 | NORMAL
299.817 | 0.95 | 294.26 | 1.42 | 1 | 101352.97 | 15139.3904 | 5513.4178 | 2648.036 | NORMAL
299.817 | 0.95 | 294.26 | 1.42 | 1 | 106868.78 | 15030.4807 | 5627.2466 | 2612.676 | NORMAL
299.817 | 0.95 | 294.26 | 1.42 | 2 | 57226.51 | 18547.8312 | 3761.0179 | 4834.21 | NORMAL
299.817 | 0.95 | 294.26 | 1.42 | 2 | 79289.74 | 19464.1266 | 5685.6271 | 4198.29 | NORMAL
299.817 | 0.95 | 294.26 | 1.42 | 2 | 101352.97 | 19756.7116 | 7123.6577 | 3864.727 | NORMAL
299.817 | 0.95 | 294.26 | 1.42 | 2 | 106868.78 | 19639.5662 | 7325.4207 | 3797.449 | NORMAL
299.817 | 0.95 | 297.037 | 0.5 | 1 | 57226.51 | 14535.3751 | 3093.3168 | 3219.401 | NORMAL
299.817 | 0.95 | 297.037 | 0.5 | 1 | 79289.74 | 14593.8159 | 4038.824 | 2837.673 | NORMAL
299.817 | 0.95 | 297.037 | 0.5 | 1 | 101352.97 | 14357.6495 | 4844.0699 | 2645.377 | NORMAL
299.817 | 0.95 | 297.037 | 0.5 | 1 | 106868.78 | 14186.6647 | 4999.2246 | 2612.647 | NORMAL
299.817 | 0.95 | 297.037 | 0.5 | 2 | 57226.51 | 18283.3822 | 3820.0933 | 4801.248 | NORMAL
299.817 | 0.95 | 297.037 | 0.5 | 2 | 79289.74 | 18381.0668 | 5183.1851 | 4111.206 | NORMAL
299.817 | 0.95 | 297.037 | 0.5 | 2 | 101352.97 | 18004.6014 | 6274.6756 | 3765.97 | NORMAL
299.817 | 0.95 | 297.037 | 0.5 | 2 | 106868.78 | 17792.204 | 6514.4732 | 3702.0332 | NORMAL
299.817 | 0.95 | 297.037 | 0.8 | 1 | 57226.51 | 15112.1923 | 2734.6419 | 3250.868 | NORMAL
299.817 | 0.95 | 297.037 | 0.8 | 1 | 79289.74 | 15524.5018 | 4249.941 | 2856.771 | NORMAL
299.817 | 0.95 | 297.037 | 0.8 | 1 | 101352.97 | 15544.6952 | 5083.3174 | 2649.546 | NORMAL
299.817 | 0.95 | 297.037 | 0.8 | 1 | 106868.78 | 15399.5604 | 5236.9593 | 2613.131 | NORMAL
299.817 | 0.95 | 297.037 | 0.8 | 2 | 57226.51 | 19201.3482 | 3595.6829 | 4921.128 | NORMAL
299.817 | 0.95 | 297.037 | 0.8 | 2 | 79289.74 | 19855.129 | 5461.7489 | 4229.736 | NORMAL
299.817 | 0.95 | 297.037 | 0.8 | 2 | 101352.97 | 19879.9238 | 6593.9123 | 3870.905 | NORMAL
299.817 | 0.95 | 297.037 | 0.8 | 2 | 106868.78 | 19712.9836 | 6824.2012 | 3801.18 | NORMAL
299.817 | 0.95 | 297.037 | 1.11 | 1 | 57226.51 | 15348.8277 | 2814.0387 | 3263.97 | NORMAL
299.817 | 0.95 | 297.037 | 1.11 | 1 | 79289.74 | 15943.0246 | 4223.9609 | 2865.787 | NORMAL
299.817 | 0.95 | 297.037 | 1.11 | 1 | 101352.97 | 16104.279 | 5262.9589 | 2652.472 | NORMAL
299.817 | 0.95 | 297.037 | 1.11 | 1 | 106868.78 | 15973.3294 | 5401.4452 | 2614.206 | NORMAL
299.817 | 0.95 | 297.037 | 1.11 | 2 | 57226.51 | 19592.7315 | 3217.7143 | 4973.67 | NORMAL
299.817 | 0.95 | 297.037 | 1.11 | 2 | 79289.74 | 20532.8253 | 5484.5846 | 4287.629 | NORMAL
299.817 | 0.95 | 297.037 | 1.11 | 2 | 101352.97 | 20781.3013 | 6788.8771 | 3923.848 | NORMAL
299.817 | 0.95 | 297.037 | 1.11 | 2 | 106868.78 | 20642.6143 | 7006.2065 | 3851.469 | NORMAL
299.817 | 0.95 | 297.037 | 1.42 | 1 | 57226.51 | 15485.0528 | 3274.3918 | 3272.02 | NORMAL
299.817 | 0.95 | 297.037 | 1.42 | 1 | 79289.74 | 16174.8535 | 4401.679 | 2870.57 | NORMAL
299.817 | 0.95 | 297.037 | 1.42 | 1 | 101352.97 | 16434.2028 | 5437.371 | 2654.428 | NORMAL
299.817 | 0.95 | 297.037 | 1.42 | 1 | 106868.78 | 16314.5956 | 5542.6554 | 2615.168 | NORMAL
299.817 | 0.95 | 297.037 | 1.42 | 2 | 57226.51 | 19815.2696 | 3479.4623 | 5004.24 | NORMAL
299.817 | 0.95 | 297.037 | 1.42 | 2 | 79289.74 | 20936.1665 | 5407.5606 | 4322.46 | NORMAL
299.817 | 0.95 | 297.037 | 1.42 | 2 | 101352.97 | 21324.4431 | 6934.7942 | 3957.052 | NORMAL
299.817 | 0.95 | 297.037 | 1.42 | 2 | 106868.78 | 21203.8101 | 7169.2838 | 3882.792 | NORMAL
299.817 | 0.95 | 299.814 | 0.5 | 1 | 57226.51 | 15708.8218 | 2896.2198 | 3284.723 | NORMAL
299.817 | 0.95 | 299.814 | 0.5 | 1 | 79289.74 | 15879.3669 | 3889.8256 | 2864.4 | NORMAL
299.817 | 0.95 | 299.814 | 0.5 | 1 | 101352.97 | 15668.4349 | 4747.3948 | 2650.154 | NORMAL
299.817 | 0.95 | 299.814 | 0.5 | 1 | 106868.78 | 15481.653 | 4918.8308 | 2613.247 | NORMAL
299.817 | 0.95 | 299.814 | 0.5 | 2 | 57226.51 | 19681.5358 | 3512.1307 | 4981.258 | NORMAL
299.817 | 0.95 | 299.814 | 0.5 | 2 | 79289.74 | 19936.9578 | 4950.7254 | 4236.2 | NORMAL
299.817 | 0.95 | 299.814 | 0.5 | 2 | 101352.97 | 19598.9742 | 6119.7405 | 3854.511 | NORMAL
299.817 | 0.95 | 299.814 | 0.5 | 2 | 106868.78 | 19370.8675 | 6391.7858 | 3782.867 | NORMAL
299.817 | 0.95 | 299.814 | 0.8 | 1 | 57226.51 | 16256.0668 | 2308.8817 | 3316.991 | NORMAL
299.817 | 0.95 | 299.814 | 0.8 | 1 | 79289.74 | 16805.5686 | 4120.1204 | 2886.259 | NORMAL
299.817 | 0.95 | 299.814 | 0.8 | 1 | 101352.97 | 16881.7995 | 4973.9521 | 2657.391 | NORMAL
299.817 | 0.95 | 299.814 | 0.8 | 1 | 106868.78 | 16726.3482 | 5133.9853 | 2616.628 | NORMAL
299.817 | 0.95 | 299.814 | 0.8 | 2 | 57226.51 | 20517.1161 | 3192.3402 | 5111.432 | NORMAL
299.817 | 0.95 | 299.814 | 0.8 | 2 | 79289.74 | 21388.0715 | 5222.1329 | 4358.978 | NORMAL
299.817 | 0.95 | 299.814 | 0.8 | 2 | 101352.97 | 21504.1618 | 6414.1539 | 3966.647 | NORMAL
299.817 | 0.95 | 299.814 | 0.8 | 2 | 106868.78 | 21328.7222 | 6654.6466 | 3889.471 | NORMAL
299.817 | 0.95 | 299.814 | 1.11 | 1 | 57226.51 | 16480.9203 | 2229.0609 | 3330.37 | NORMAL
299.817 | 0.95 | 299.814 | 1.11 | 1 | 79289.74 | 17218.0539 | 3826.7297 | 2896.487 | NORMAL
299.817 | 0.95 | 299.814 | 1.11 | 1 | 101352.97 | 17447.7433 | 5154.517 | 2661.831 | NORMAL
299.817 | 0.95 | 299.814 | 1.11 | 1 | 106868.78 | 17309.3787 | 5293.0176 | 2619.196 | NORMAL
299.817 | 0.95 | 299.814 | 1.11 | 2 | 57226.51 | 20885.7855 | 2486.7034 | 5158.65 | NORMAL
299.817 | 0.95 | 299.814 | 1.11 | 2 | 79289.74 | 22045.4865 | 5123.0183 | 4418.232 | NORMAL
299.817 | 0.95 | 299.814 | 1.11 | 2 | 101352.97 | 22404.0445 | 6594.3393 | 4022.562 | NORMAL
299.817 | 0.95 | 299.814 | 1.11 | 2 | 106868.78 | 22262.6026 | 6816.3637 | 3942.95 | NORMAL
299.817 | 0.95 | 299.814 | 1.42 | 1 | 57226.51 | 16610.1993 | 2612.4189 | 3338.2 | NORMAL
299.817 | 0.95 | 299.814 | 1.42 | 1 | 79289.74 | 17446.6002 | 4197.3205 | 2901.81 | NORMAL
299.817 | 0.95 | 299.814 | 1.42 | 1 | 101352.97 | 17780.2462 | 5116.1058 | 2664.667 | NORMAL
299.817 | 0.95 | 299.814 | 1.42 | 1 | 106868.78 | 17654.8652 | 5434.1322 | 2620.976 | NORMAL
299.817 | 0.95 | 299.814 | 1.42 | 2 | 57226.51 | 21095.4279 | 2641.5906 | 5188.7 | NORMAL
299.817 | 0.95 | 299.814 | 1.42 | 2 | 79289.74 | 22433.9683 | 4840.7793 | 4453.83 | NORMAL
299.817 | 0.95 | 299.814 | 1.42 | 2 | 101352.97 | 22943.3177 | 6625.1583 | 4057.819 | NORMAL
299.817 | 0.95 | 299.814 | 1.42 | 2 | 106868.78 | 22823.3294 | 6978.3699 | 3976.016 | NORMAL
299.817 | 0.95 | 302.591 | 0.5 | 1 | 57226.51 | 16919.0797 | 2578.7723 | 3357.207 | NORMAL
299.817 | 0.95 | 302.591 | 0.5 | 1 | 79289.74 | 17229.0445 | 3734.3093 | 2896.704 | NORMAL
299.817 | 0.95 | 302.591 | 0.5 | 1 | 101352.97 | 17063.4232 | 4599.7529 | 2658.671 | NORMAL
299.817 | 0.95 | 302.591 | 0.5 | 1 | 106868.78 | 16862.0164 | 4811.6944 | 2617.199 | NORMAL
299.817 | 0.95 | 302.591 | 0.5 | 2 | 57226.51 | 21061.1665 | 3204.6039 | 5192.2 | NORMAL
299.817 | 0.95 | 302.591 | 0.5 | 2 | 79289.74 | 21559.1442 | 4641.425 | 4373.425 | NORMAL
299.817 | 0.95 | 302.591 | 0.5 | 2 | 101352.97 | 21290.9437 | 5877.2373 | 3953.592 | NORMAL
299.817 | 0.95 | 302.591 | 0.5 | 2 | 106868.78 | 21047.6553 | 6228.8642 | 3873.683 | NORMAL
299.817 | 0.95 | 302.591 | 0.8 | 1 | 57226.51 | 17431.653 | 1871.9678 | 3389.557 | NORMAL
299.817 | 0.95 | 302.591 | 0.8 | 1 | 79289.74 | 18140.2403 | 3861.7669 | 2921.683 | NORMAL
299.817 | 0.95 | 302.591 | 0.8 | 1 | 101352.97 | 18289.449 | 4843.924 | 2669.364 | NORMAL
299.817 | 0.95 | 302.591 | 0.8 | 1 | 106868.78 | 18126.231 | 5004.5255 | 2623.712 | NORMAL
299.817 | 0.95 | 302.591 | 0.8 | 2 | 57226.51 | 21856.3013 | 2636.919 | 5308.62 | NORMAL
299.817 | 0.95 | 302.591 | 0.8 | 2 | 79289.74 | 22968.3763 | 4952.694 | 4499.377 | NORMAL
299.817 | 0.95 | 302.591 | 0.8 | 2 | 101352.97 | 23200.8499 | 6204.9977 | 4072.559 | NORMAL
299.817 | 0.95 | 302.591 | 0.8 | 2 | 106868.78 | 23022.5674 | 6447.424 | 3987.306 | NORMAL
299.817 | 0.95 | 302.591 | 1.11 | 1 | 57226.51 | 17642.1161 | 2004.9736 | 3403.52 | NORMAL
299.817 | 0.95 | 302.591 | 1.11 | 1 | 79289.74 | 18542.2919 | 3504.5859 | 2932.775 | NORMAL
299.817 | 0.95 | 302.591 | 1.11 | 1 | 101352.97 | 18856.3306 | 4903.6642 | 2675.429 | NORMAL
299.817 | 0.95 | 302.591 | 1.11 | 1 | 106868.78 | 18712.9836 | 5167.7401 | 2627.785 | NORMAL
299.817 | 0.95 | 302.591 | 1.11 | 2 | 57226.51 | 22200.0293 | 1829.3313 | 5359.24 | NORMAL
299.817 | 0.95 | 302.591 | 1.11 | 2 | 79289.74 | 23600.9672 | 4518.0748 | 4558.336 | NORMAL
299.817 | 0.95 | 302.591 | 1.11 | 2 | 101352.97 | 24092.2919 | 6284.3057 | 4131.054 | NORMAL
299.817 | 0.95 | 302.591 | 1.11 | 2 | 106868.78 | 23950.0293 | 6599.5024 | 4043.72 | NORMAL
299.817 | 0.95 | 302.591 | 1.42 | 1 | 57226.51 | 17757.8839 | 2706.781 | 3410.83 | NORMAL
299.817 | 0.95 | 302.591 | 1.42 | 1 | 79289.74 | 18764.4197 | 3854.3056 | 2938.44 | NORMAL
299.817 | 0.95 | 302.591 | 1.42 | 1 | 101352.97 | 19188.9508 | 4906.4996 | 2679.159 | NORMAL
299.817 | 0.95 | 302.591 | 1.42 | 1 | 106868.78 | 19059.8769 | 5308.4616 | 2630.538 | NORMAL
299.817 | 0.95 | 302.591 | 1.42 | 2 | 57226.51 | 22398.1243 | 2310.7025 | 5382.16 | NORMAL
299.817 | 0.95 | 302.591 | 1.42 | 2 | 79289.74 | 23972.2743 | 4253.4486 | 4595.15 | NORMAL
299.817 | 0.95 | 302.591 | 1.42 | 2 | 101352.97 | 24620.9261 | 6026.3656 | 4167.978 | NORMAL
299.817 | 0.95 | 302.591 | 1.42 | 2 | 106868.78 | 24504.1911 | 6769.6013 | 4078.451 | NORMAL
299.817 | 0.95 | 305.368 | 0.5 | 1 | 57226.51 | 18156.0961 | 2200.8638 | 3437.024 | NORMAL
299.817 | 0.95 | 305.368 | 0.5 | 1 | 79289.74 | 18639.7714 | 3471.7506 | 2935.579 | NORMAL
299.817 | 0.95 | 305.368 | 0.5 | 1 | 101352.97 | 18539.5076 | 4462.1072 | 2672.086 | NORMAL
299.817 | 0.95 | 305.368 | 0.5 | 1 | 106868.78 | 18325.2638 | 4679.2645 | 2625.004 | NORMAL
299.817 | 0.95 | 305.368 | 0.5 | 2 | 57226.51 | 22480.422 | 2843.616 | 5404.382 | NORMAL
299.817 | 0.95 | 305.368 | 0.5 | 2 | 79289.74 | 23237.1336 | 4352.7334 | 4523.476 | NORMAL
299.817 | 0.95 | 305.368 | 0.5 | 2 | 101352.97 | 23071.7468 | 5591.4609 | 4064.269 | NORMAL
299.817 | 0.95 | 305.368 | 0.5 | 2 | 106868.78 | 22818.9918 | 6030.9226 | 3975.464 | NORMAL
299.817 | 0.95 | 305.368 | 0.8 | 1 | 57226.51 | 18629.9531 | 1220.1949 | 3469.434 | NORMAL
299.817 | 0.95 | 305.368 | 0.8 | 1 | 79289.74 | 19523.5053 | 3566.6906 | 2963.069 | NORMAL
299.817 | 0.95 | 305.368 | 0.8 | 1 | 101352.97 | 19765.211 | 4697.8151 | 2686.058 | NORMAL
299.817 | 0.95 | 305.368 | 0.8 | 1 | 106868.78 | 19596.3072 | 4858.3361 | 2635.181 | NORMAL
299.817 | 0.95 | 305.368 | 0.8 | 2 | 57226.51 | 23208.177 | 1986.1767 | 5514.646 | NORMAL
299.817 | 0.95 | 305.368 | 0.8 | 2 | 79289.74 | 24587.1043 | 4556.6789 | 4651.142 | NORMAL
299.817 | 0.95 | 305.368 | 0.8 | 2 | 101352.97 | 24964.068 | 5921.2273 | 4189.284 | NORMAL
299.817 | 0.95 | 305.368 | 0.8 | 2 | 106868.78 | 24786.1665 | 6212.5783 | 4095.61 | NORMAL
299.817 | 0.95 | 305.368 | 1.11 | 1 | 57226.51 | 18826.231 | 1242.9567 | 3481.98 | NORMAL
299.817 | 0.95 | 305.368 | 1.11 | 1 | 79289.74 | 19912.1043 | 3086.0178 | 2975.054 | NORMAL
299.817 | 0.95 | 305.368 | 1.11 | 1 | 101352.97 | 20327.4619 | 4604.2718 | 2693.773 | NORMAL
299.817 | 0.95 | 305.368 | 1.11 | 1 | 106868.78 | 20181.2427 | 5027.7328 | 2640.865 | NORMAL
299.817 | 0.95 | 305.368 | 1.11 | 2 | 57226.51 | 23526.1137 | 952.5747 | 5562.93 | NORMAL
299.817 | 0.95 | 305.368 | 1.11 | 2 | 79289.74 | 25189.1852 | 3979.9165 | 4712.758 | NORMAL
299.817 | 0.95 | 305.368 | 1.11 | 2 | 101352.97 | 25835.7268 | 5839.6752 | 4249.999 | NORMAL
299.817 | 0.95 | 305.368 | 1.11 | 2 | 106868.78 | 25699.5604 | 6295.5956 | 4154.617 | NORMAL
299.817 | 0.95 | 305.368 | 1.42 | 1 | 57226.51 | 18934.0856 | 1718.0089 | 3490.48 | NORMAL
299.817 | 0.95 | 305.368 | 1.42 | 1 | 79289.74 | 20127.0223 | 3607.2253 | 2980.77 | NORMAL
299.817 | 0.95 | 305.368 | 1.42 | 1 | 101352.97 | 20657.2392 | 4419.0173 | 2698.375 | NORMAL
299.817 | 0.95 | 305.368 | 1.42 | 1 | 106868.78 | 20526.5827 | 5169.8046 | 2644.545 | NORMAL
299.817 | 0.95 | 305.368 | 1.42 | 2 | 57226.51 | 23713.8628 | 1083.2137 | 5591.99 | NORMAL
299.817 | 0.95 | 305.368 | 1.42 | 2 | 79289.74 | 25540.973 | 3658.6422 | 4747.16 | NORMAL
299.817 | 0.95 | 305.368 | 1.42 | 2 | 101352.97 | 26350.4689 | 5506.5892 | 4288.675 | NORMAL
299.817 | 0.95 | 305.368 | 1.42 | 2 | 106868.78 | 26241.7057 | 6545.836 | 4190.898 | NORMAL
313.706 | 0.05 | 288.706 | 0.5 | 1 | 57226.51 | 7112.4853 | 7084.9387 | 3982.676 | NORMAL
313.706 | 0.05 | 288.706 | 0.5 | 1 | 79289.74 | 7347.8019 | 7345.3551 | 3744.794 | NORMAL
313.706 | 0.05 | 288.706 | 0.5 | 1 | 101352.97 | 7453.8394 | 7447.8912 | 3627.31 | NORMAL
313.706 | 0.05 | 288.706 | 0.5 | 1 | 106868.78 | 7466.1782 | 7463.7666 | 3612.3692 | NORMAL
313.706 | 0.05 | 288.706 | 0.5 | 2 | 57226.51 | 9060.9906 | 9057.475 | 5118.244 | NORMAL
313.706 | 0.05 | 288.706 | 0.5 | 2 | 79289.74 | 9361.6647 | 9335.3397 | 4715.185 | NORMAL
313.706 | 0.05 | 288.706 | 0.5 | 2 | 101352.97 | 9505.0117 | 9502.8731 | 4526.1622 | NORMAL
313.706 | 0.05 | 288.706 | 0.5 | 2 | 106868.78 | 9513.6577 | 9511.5171 | 4490.2826 | NORMAL
313.706 | 0.05 | 288.706 | 0.8 | 1 | 57226.51 | 8091.1196 | 8087.3329 | 4034.929 | NORMAL
313.706 | 0.05 | 288.706 | 0.8 | 1 | 79289.74 | 8409.0563 | 8405.2049 | 3758.936 | NORMAL
313.706 | 0.05 | 288.706 | 0.8 | 1 | 101352.97 | 8568.3177 | 8564.4448 | 3619.432 | NORMAL
313.706 | 0.05 | 288.706 | 0.8 | 1 | 106868.78 | 8597.9191 | 8594.0414 | 3593.663 | NORMAL
313.706 | 0.05 | 288.706 | 0.8 | 2 | 57226.51 | 10388.4818 | 10346.7825 | 5322.711 | NORMAL
313.706 | 0.05 | 288.706 | 0.8 | 2 | 79289.74 | 10818.6401 | 10805.7659 | 4866.196 | NORMAL
313.706 | 0.05 | 288.706 | 0.8 | 2 | 101352.97 | 11051.3775 | 11005.1827 | 4623.969 | NORMAL
313.706 | 0.05 | 288.706 | 0.8 | 2 | 106868.78 | 11088.9801 | 11085.0102 | 4585.635 | NORMAL
313.706 | 0.05 | 288.706 | 1.11 | 1 | 57226.51 | 8622.7433 | 8618.0611 | 4065.79 | NORMAL
313.706 | 0.05 | 288.706 | 1.11 | 1 | 79289.74 | 8996.2192 | 8991.4242 | 3770.175 | NORMAL
313.706 | 0.05 | 288.706 | 1.11 | 1 | 101352.97 | 9190.2403 | 9185.3971 | 3616.85 | NORMAL
313.706 | 0.05 | 288.706 | 1.11 | 1 | 106868.78 | 9223.9156 | 9219.0638 | 3590.243 | NORMAL
313.706 | 0.05 | 288.706 | 1.11 | 2 | 57226.51 | 11136.8406 | 11131.6174 | 5437.63 | NORMAL
313.706 | 0.05 | 288.706 | 1.11 | 2 | 79289.74 | 11658.2356 | 11652.9078 | 4945.88 | NORMAL
313.706 | 0.05 | 288.706 | 1.11 | 2 | 101352.97 | 11945.1934 | 11939.83 | 4682.829 | NORMAL
313.706 | 0.05 | 288.706 | 1.11 | 2 | 106868.78 | 11998.2708 | 11992.9076 | 4635.028 | NORMAL
313.706 | 0.05 | 288.706 | 1.42 | 1 | 57226.51 | 8964.2732 | 8958.9663 | 4085.76 | NORMAL
313.706 | 0.05 | 288.706 | 1.42 | 1 | 79289.74 | 9378.3118 | 9360.2023 | 3778.02 | NORMAL
313.706 | 0.05 | 288.706 | 1.42 | 1 | 101352.97 | 9596.8054 | 9591.268 | 3616.367 | NORMAL
313.706 | 0.05 | 288.706 | 1.42 | 1 | 106868.78 | 9635.1114 | 9629.5519 | 3588.047 | NORMAL
313.706 | 0.05 | 288.706 | 1.42 | 2 | 57226.51 | 11628.0481 | 11621.9201 | 5513.3 | NORMAL
313.706 | 0.05 | 288.706 | 1.42 | 2 | 79289.74 | 12217.1161 | 12210.812 | 4999.18 | NORMAL
313.706 | 0.05 | 288.706 | 1.42 | 2 | 101352.97 | 12544.959 | 12536.0646 | 4722.579 | NORMAL
313.706 | 0.05 | 288.706 | 1.42 | 2 | 106868.78 | 12605.8324 | 12599.4412 | 4672.217 | NORMAL
313.706 | 0.05 | 291.483 | 0.5 | 1 | 57226.51 | 7625.5862 | 7614.9714 | 4008.55 | NORMAL
313.706 | 0.05 | 291.483 | 0.5 | 1 | 79289.74 | 7869.4021 | 7852.8606 | 3753.055 | NORMAL
313.706 | 0.05 | 291.483 | 0.5 | 1 | 101352.97 | 7996.6002 | 7988.0519 | 3621.668 | NORMAL
313.706 | 0.05 | 291.483 | 0.5 | 1 | 106868.78 | 8015.4162 | 8012.2501 | 3602.2007 | NORMAL
313.706 | 0.05 | 291.483 | 0.5 | 2 | 57226.51 | 9585.17 | 9582.189 | 5199.226 | NORMAL
313.706 | 0.05 | 291.483 | 0.5 | 2 | 79289.74 | 9908.1477 | 9889.7681 | 4779.615 | NORMAL
313.706 | 0.05 | 291.483 | 0.5 | 2 | 101352.97 | 10074.2966 | 10071.4153 | 4563.6879 | NORMAL
313.706 | 0.05 | 291.483 | 0.5 | 2 | 106868.78 | 10085.7268 | 10082.8928 | 4523.9955 | NORMAL
313.706 | 0.05 | 291.483 | 0.8 | 1 | 57226.51 | 8687.0164 | 8673.0477 | 4068.226 | NORMAL
313.706 | 0.05 | 291.483 | 0.8 | 1 | 79289.74 | 9035.4631 | 9030.4574 | 3770.992 | NORMAL
313.706 | 0.05 | 291.483 | 0.8 | 1 | 101352.97 | 9216.5299 | 9211.4885 | 3616.697 | NORMAL
313.706 | 0.05 | 291.483 | 0.8 | 1 | 106868.78 | 9248.0363 | 9242.9962 | 3589.872 | NORMAL
313.706 | 0.05 | 291.483 | 0.8 | 2 | 57226.51 | 11023.3001 | 11018.0861 | 5420.13 | NORMAL
313.706 | 0.05 | 291.483 | 0.8 | 2 | 79289.74 | 11496.864 | 11469.4555 | 4930.536 | NORMAL
313.706 | 0.05 | 291.483 | 0.8 | 2 | 101352.97 | 11755.2755 | 11750.0444 | 4670.383 | NORMAL
313.706 | 0.05 | 291.483 | 0.8 | 2 | 106868.78 | 11802.9015 | 11797.6728 | 4623.152 | NORMAL
313.706 | 0.05 | 291.483 | 1.11 | 1 | 57226.51 | 9266.8816 | 9260.8025 | 4102.94 | NORMAL
313.706 | 0.05 | 291.483 | 1.11 | 1 | 79289.74 | 9681.0668 | 9674.2514 | 3784.696 | NORMAL
313.706 | 0.05 | 291.483 | 1.11 | 1 | 101352.97 | 9900.1172 | 9893.8307 | 3616.525 | NORMAL
313.706 | 0.05 | 291.483 | 1.11 | 1 | 106868.78 | 9938.8921 | 9932.5909 | 3586.836 | NORMAL
313.706 | 0.05 | 291.483 | 1.11 | 2 | 57226.51 | 11834.1149 | 11827.3221 | 5545.19 | NORMAL
313.706 | 0.05 | 291.483 | 1.11 | 2 | 79289.74 | 12411.1958 | 12404.2951 | 5017.735 | NORMAL
313.706 | 0.05 | 291.483 | 1.11 | 2 | 101352.97 | 12730.9203 | 12723.9565 | 4734.912 | NORMAL
313.706 | 0.05 | 291.483 | 1.11 | 2 | 106868.78 | 12790.2403 | 12783.2697 | 4683.476 | NORMAL
313.706 | 0.05 | 291.483 | 1.42 | 1 | 57226.51 | 9641.354 | 9634.4894 | 4125.73 | NORMAL
313.706 | 0.05 | 291.483 | 1.42 | 1 | 79289.74 | 10101.9343 | 10078.6999 | 3794.33 | NORMAL
313.706 | 0.05 | 291.483 | 1.42 | 1 | 101352.97 | 10347.3916 | 10340.2001 | 3618.238 | NORMAL
313.706 | 0.05 | 291.483 | 1.42 | 1 | 106868.78 | 10392.9074 | 10385.6947 | 3585.999 | NORMAL
313.706 | 0.05 | 291.483 | 1.42 | 2 | 57226.51 | 12367.7608 | 12358.5221 | 5628.21 | NORMAL
313.706 | 0.05 | 291.483 | 1.42 | 2 | 79289.74 | 13021.1313 | 13012.9801 | 5076.21 | NORMAL
313.706 | 0.05 | 291.483 | 1.42 | 2 | 101352.97 | 13386.8992 | 13378.6395 | 4778.506 | NORMAL
313.706 | 0.05 | 291.483 | 1.42 | 2 | 106868.78 | 13454.7186 | 13446.444 | 4724.439 | NORMAL
313.706 | 0.05 | 294.26 | 0.5 | 1 | 57226.51 | 8133.0598 | 8125.3171 | 4036.612 | NORMAL
313.706 | 0.05 | 294.26 | 0.5 | 1 | 79289.74 | 8407.8253 | 8403.7139 | 3758.59 | NORMAL
313.706 | 0.05 | 294.26 | 0.5 | 1 | 101352.97 | 8544.7245 | 8540.623 | 3619.205 | NORMAL
313.706 | 0.05 | 294.26 | 0.5 | 1 | 106868.78 | 8569.7538 | 8565.6575 | 3594.0106 | NORMAL
313.706 | 0.05 | 294.26 | 0.5 | 2 | 57226.51 | 10117.4091 | 10113.5443 | 5281.257 | NORMAL
313.706 | 0.05 | 294.26 | 0.5 | 2 | 79289.74 | 10475.0879 | 10471.2959 | 4833.673 | NORMAL
313.706 | 0.05 | 294.26 | 0.5 | 2 | 101352.97 | 10658.4115 | 10654.6597 | 4597.751 | NORMAL
313.706 | 0.05 | 294.26 | 0.5 | 2 | 106868.78 | 10688.8335 | 10685.1459 | 4560.4567 | NORMAL
313.706 | 0.05 | 294.26 | 0.8 | 1 | 57226.51 | 9287.6026 | 9275.12 | 4104.163 | NORMAL
313.706 | 0.05 | 294.26 | 0.8 | 1 | 79289.74 | 9672.6553 | 9666.2037 | 3784.547 | NORMAL
313.706 | 0.05 | 294.26 | 0.8 | 1 | 101352.97 | 9874.9121 | 9868.5033 | 3616.473 | NORMAL
313.706 | 0.05 | 294.26 | 0.8 | 1 | 106868.78 | 9910.6975 | 9904.2853 | 3586.979 | NORMAL
313.706 | 0.05 | 294.26 | 0.8 | 2 | 57226.51 | 11669.1969 | 11662.5455 | 5519.69 | NORMAL
313.706 | 0.05 | 294.26 | 0.8 | 2 | 79289.74 | 12188.8921 | 12182.2126 | 4996.555 | NORMAL
313.706 | 0.05 | 294.26 | 0.8 | 2 | 101352.97 | 12474.2087 | 12467.5225 | 4717.972 | NORMAL
313.706 | 0.05 | 294.26 | 0.8 | 2 | 106868.78 | 12526.993 | 12520.3161 | 4667.405 | NORMAL
313.706 | 0.05 | 294.26 | 1.11 | 1 | 57226.51 | 9920.3693 | 9905.6375 | 4142.18 | NORMAL
313.706 | 0.05 | 294.26 | 1.11 | 1 | 79289.74 | 10377.7843 | 10369.8868 | 3800.911 | NORMAL
313.706 | 0.05 | 294.26 | 1.11 | 1 | 101352.97 | 10621.6002 | 10608.1745 | 3619.879 | NORMAL
313.706 | 0.05 | 294.26 | 1.11 | 1 | 106868.78 | 10666.2075 | 10658.1972 | 3586.996 | NORMAL
313.706 | 0.05 | 294.26 | 1.11 | 2 | 57226.51 | 12544.4021 | 12527.3041 | 5655.78 | NORMAL
313.706 | 0.05 | 294.26 | 1.11 | 2 | 79289.74 | 13180.129 | 13171.3642 | 5091.541 | NORMAL
313.706 | 0.05 | 294.26 | 1.11 | 2 | 101352.97 | 13534.2028 | 13525.365 | 4788.395 | NORMAL
313.706 | 0.05 | 294.26 | 1.11 | 2 | 106868.78 | 13599.7362 | 13590.8828 | 4733.407 | NORMAL
313.706 | 0.05 | 294.26 | 1.42 | 1 | 57226.51 | 10329.4256 | 10292.6735 | 4167.76 | NORMAL
313.706 | 0.05 | 294.26 | 1.42 | 1 | 79289.74 | 10839.5662 | 10809.8442 | 3812.31 | NORMAL
313.706 | 0.05 | 294.26 | 1.42 | 1 | 101352.97 | 11119.5487 | 11110.4195 | 3619.067 | NORMAL
313.706 | 0.05 | 294.26 | 1.42 | 1 | 106868.78 | 11166.2075 | 11157.0512 | 3586.77 | NORMAL
313.706 | 0.05 | 294.26 | 1.42 | 2 | 57226.51 | 13119.2263 | 13100.4395 | 5747.67 | NORMAL
313.706 | 0.05 | 294.26 | 1.42 | 2 | 79289.74 | 13841.6178 | 13831.3058 | 5155.68 | NORMAL
313.706 | 0.05 | 294.26 | 1.42 | 2 | 101352.97 | 14248.007 | 14237.549 | 4836.543 | NORMAL
313.706 | 0.05 | 294.26 | 1.42 | 2 | 106868.78 | 14323.6518 | 14313.1669 | 4778.489 | NORMAL
313.706 | 0.05 | 297.037 | 0.5 | 1 | 57226.51 | 8649.6776 | 8643.8823 | 4065.898 | NORMAL
313.706 | 0.05 | 297.037 | 0.5 | 1 | 79289.74 | 8948.476 | 8943.3216 | 3769.229 | NORMAL
313.706 | 0.05 | 297.037 | 0.5 | 1 | 101352.97 | 9100.6155 | 9095.4736 | 3617.078 | NORMAL
313.706 | 0.05 | 297.037 | 0.5 | 1 | 106868.78 | 9127.1102 | 9121.9625 | 3590.8131 | NORMAL
313.706 | 0.05 | 297.037 | 0.5 | 2 | 57226.51 | 10661.3423 | 10656.4381 | 5364.303 | NORMAL
313.706 | 0.05 | 297.037 | 0.5 | 2 | 79289.74 | 11044.3435 | 11007.6542 | 4887.663 | NORMAL
313.706 | 0.05 | 297.037 | 0.5 | 2 | 101352.97 | 11249.4138 | 11219.6029 | 4637.071 | NORMAL
313.706 | 0.05 | 297.037 | 0.5 | 2 | 106868.78 | 11287.0457 | 11282.3277 | 4591.9725 | NORMAL
313.706 | 0.05 | 297.037 | 0.8 | 1 | 57226.51 | 9898.2122 | 9887.047 | 4140.113 | NORMAL
313.706 | 0.05 | 297.037 | 0.8 | 1 | 79289.74 | 10319.6073 | 10311.6508 | 3799.493 | NORMAL
313.706 | 0.05 | 297.037 | 0.8 | 1 | 101352.97 | 10543.728 | 10535.7148 | 3618.555 | NORMAL
313.706 | 0.05 | 297.037 | 0.8 | 1 | 106868.78 | 10582.8546 | 10574.8328 | 3587.073 | NORMAL
313.706 | 0.05 | 297.037 | 0.8 | 2 | 57226.51 | 12325.762 | 12313.3253 | 5621.626 | NORMAL
313.706 | 0.05 | 297.037 | 0.8 | 2 | 79289.74 | 12894.4607 | 12886.1051 | 5064.083 | NORMAL
313.706 | 0.05 | 297.037 | 0.8 | 2 | 101352.97 | 13207.3271 | 13198.9536 | 4766.607 | NORMAL
313.706 | 0.05 | 297.037 | 0.8 | 2 | 106868.78 | 13265.2696 | 13256.8993 | 4712.775 | NORMAL
313.706 | 0.05 | 297.037 | 1.11 | 1 | 57226.51 | 10583.4701 | 10573.8603 | 4183.25 | NORMAL
313.706 | 0.05 | 297.037 | 1.11 | 1 | 79289.74 | 11087.6612 | 11077.8154 | 3818.689 | NORMAL
313.706 | 0.05 | 297.037 | 1.11 | 1 | 101352.97 | 11363.1301 | 11353.1533 | 3620.745 | NORMAL
313.706 | 0.05 | 297.037 | 1.11 | 1 | 106868.78 | 11409.2614 | 11399.2555 | 3587.592 | NORMAL
313.706 | 0.05 | 297.037 | 1.11 | 2 | 57226.51 | 13265.1817 | 13254.4767 | 5770.41 | NORMAL
313.706 | 0.05 | 297.037 | 1.11 | 2 | 79289.74 | 13963.3646 | 13948.5634 | 5167.516 | NORMAL
313.706 | 0.05 | 297.037 | 1.11 | 2 | 101352.97 | 14353.4877 | 14342.4642 | 4843.745 | NORMAL
313.706 | 0.05 | 297.037 | 1.11 | 2 | 106868.78 | 14426.5533 | 14415.5026 | 4784.929 | NORMAL
313.706 | 0.05 | 297.037 | 1.42 | 1 | 57226.51 | 11028.2239 | 10995.7348 | 4211.65 | NORMAL
313.706 | 0.05 | 297.037 | 1.42 | 1 | 79289.74 | 11591.7644 | 11554.01 | 3832.21 | NORMAL
313.706 | 0.05 | 297.037 | 1.42 | 1 | 101352.97 | 11902.9601 | 11891.5571 | 3624.796 | NORMAL
313.706 | 0.05 | 297.037 | 1.42 | 1 | 106868.78 | 11958.3529 | 11943.6561 | 3588.025 | NORMAL
313.706 | 0.05 | 297.037 | 1.42 | 2 | 57226.51 | 13885.6389 | 13854.1185 | 5868.21 | NORMAL
313.706 | 0.05 | 297.037 | 1.42 | 2 | 79289.74 | 14677.6084 | 14663.2391 | 5237.68 | NORMAL
313.706 | 0.05 | 297.037 | 1.42 | 2 | 101352.97 | 15126.9637 | 15107.3137 | 4896.532 | NORMAL
313.706 | 0.05 | 297.037 | 1.42 | 2 | 106868.78 | 15210.5217 | 15197.4711 | 4834.649 | NORMAL
313.706 | 0.05 | 299.814 | 0.5 | 1 | 57226.51 | 9172.9191 | 9166.5439 | 4096.355 | NORMAL
313.706 | 0.05 | 299.814 | 0.5 | 1 | 79289.74 | 9496.4537 | 9490.0911 | 3780.684 | NORMAL
313.706 | 0.05 | 299.814 | 0.5 | 1 | 101352.97 | 9664.0973 | 9657.748 | 3616.386 | NORMAL
313.706 | 0.05 | 299.814 | 0.5 | 1 | 106868.78 | 9693.5229 | 9687.1736 | 3587.7037 | NORMAL
313.706 | 0.05 | 299.814 | 0.5 | 2 | 57226.51 | 11213.3646 | 11207.2533 | 5449.315 | NORMAL
313.706 | 0.05 | 299.814 | 0.5 | 2 | 79289.74 | 11627.9601 | 11621.9601 | 4943.09 | NORMAL
313.706 | 0.05 | 299.814 | 0.5 | 2 | 101352.97 | 11850.9086 | 11844.9831 | 4676.724 | NORMAL
313.706 | 0.05 | 299.814 | 0.5 | 2 | 106868.78 | 11891.9402 | 11886.0299 | 4628.5901 | NORMAL
313.706 | 0.05 | 299.814 | 0.8 | 1 | 57226.51 | 10516.2661 | 10506.4544 | 4178.378 | NORMAL
313.706 | 0.05 | 299.814 | 0.8 | 1 | 79289.74 | 10976.5827 | 10966.8025 | 3815.847 | NORMAL
313.706 | 0.05 | 299.814 | 0.8 | 1 | 101352.97 | 11227.3154 | 11217.4578 | 3619.863 | NORMAL
313.706 | 0.05 | 299.814 | 0.8 | 1 | 106868.78 | 11268.1125 | 11258.2304 | 3587.798 | NORMAL
313.706 | 0.05 | 299.814 | 0.8 | 2 | 57226.51 | 12990.4455 | 12980.222 | 5727.466 | NORMAL
313.706 | 0.05 | 299.814 | 0.8 | 2 | 79289.74 | 13611.4889 | 13601.1986 | 5133.306 | NORMAL
313.706 | 0.05 | 299.814 | 0.8 | 2 | 101352.97 | 13954.0152 | 13943.7032 | 4816.777 | NORMAL
313.706 | 0.05 | 299.814 | 0.8 | 2 | 106868.78 | 14017.585 | 14007.2681 | 4759.37 | NORMAL
313.706 | 0.05 | 299.814 | 1.11 | 1 | 57226.51 | 11256.3599 | 11244.5632 | 4226.01 | NORMAL
313.706 | 0.05 | 299.814 | 1.11 | 1 | 79289.74 | 11809.3201 | 11780.9777 | 3838.249 | NORMAL
313.706 | 0.05 | 299.814 | 1.11 | 1 | 101352.97 | 12114.2732 | 12101.9893 | 3626.659 | NORMAL
313.706 | 0.05 | 299.814 | 1.11 | 1 | 106868.78 | 12168.6108 | 12156.3083 | 3589.071 | NORMAL
313.706 | 0.05 | 299.814 | 1.11 | 2 | 57226.51 | 13998.857 | 13974.107 | 5886.16 | NORMAL
313.706 | 0.05 | 299.814 | 1.11 | 2 | 79289.74 | 14759.6424 | 14746.2407 | 5245.745 | NORMAL
313.706 | 0.05 | 299.814 | 1.11 | 2 | 101352.97 | 15188.9214 | 15175.3881 | 4900.817 | NORMAL
313.706 | 0.05 | 299.814 | 1.11 | 2 | 106868.78 | 15268.6401 | 15255.0815 | 4838.385 | NORMAL
313.706 | 0.05 | 299.814 | 1.42 | 1 | 57226.51 | 11738.0422 | 11713.2867 | 4257.98 | NORMAL
313.706 | 0.05 | 299.814 | 1.42 | 1 | 79289.74 | 12357.7667 | 12343.9878 | 3853.92 | NORMAL
313.706 | 0.05 | 299.814 | 1.42 | 1 | 101352.97 | 12702.5498 | 12684.9822 | 3632.219 | NORMAL
313.706 | 0.05 | 299.814 | 1.42 | 1 | 106868.78 | 12764.2732 | 12736.8172 | 3592.676 | NORMAL
313.706 | 0.05 | 299.814 | 1.42 | 2 | 57226.51 | 14665.5334 | 14617.8411 | 5991.63 | NORMAL
313.706 | 0.05 | 299.814 | 1.42 | 2 | 79289.74 | 15528.7222 | 15513.0071 | 5321.9 | NORMAL
313.706 | 0.05 | 299.814 | 1.42 | 2 | 101352.97 | 16022.3623 | 16006.404 | 4958.767 | NORMAL
313.706 | 0.05 | 299.814 | 1.42 | 2 | 106868.78 | 16112.4267 | 16096.4271 | 4894.063 | NORMAL
313.706 | 0.05 | 302.591 | 0.5 | 1 | 57226.51 | 9701.612 | 9693.8604 | 4127.939 | NORMAL
313.706 | 0.05 | 302.591 | 0.5 | 1 | 79289.74 | 10051.2309 | 10043.4814 | 3793.247 | NORMAL
313.706 | 0.05 | 302.591 | 0.5 | 1 | 101352.97 | 10233.6166 | 10225.8903 | 3618.088 | NORMAL
313.706 | 0.05 | 302.591 | 0.5 | 1 | 106868.78 | 10267.6729 | 10259.9414 | 3586.1193 | NORMAL
313.706 | 0.05 | 302.591 | 0.5 | 2 | 57226.51 | 11772.6553 | 11765.1797 | 5535.563 | NORMAL
313.706 | 0.05 | 302.591 | 0.5 | 2 | 79289.74 | 12220.4865 | 12213.142 | 4999.581 | NORMAL
313.706 | 0.05 | 302.591 | 0.5 | 2 | 101352.97 | 12462.2802 | 12455.0147 | 4717.194 | NORMAL
313.706 | 0.05 | 302.591 | 0.5 | 2 | 106868.78 | 12506.8875 | 12499.6335 | 4666.1974 | NORMAL
313.706 | 0.05 | 302.591 | 0.8 | 1 | 57226.51 | 11141.9695 | 11130.2816 | 4218.029 | NORMAL
313.706 | 0.05 | 302.591 | 0.8 | 1 | 79289.74 | 11644.109 | 11632.232 | 3833.677 | NORMAL
313.706 | 0.05 | 302.591 | 0.8 | 1 | 101352.97 | 11918.6694 | 11906.6911 | 3624.943 | NORMAL
313.706 | 0.05 | 302.591 | 0.8 | 1 | 106868.78 | 11967.0281 | 11955.0372 | 3588.082 | NORMAL
313.706 | 0.05 | 302.591 | 0.8 | 2 | 57226.51 | 13666.5006 | 13654.1051 | 5833.667 | NORMAL
313.706 | 0.05 | 302.591 | 0.8 | 2 | 79289.74 | 14339.3904 | 14326.9008 | 5204.387 | NORMAL
313.706 | 0.05 | 302.591 | 0.8 | 2 | 101352.97 | 14713.0422 | 14700.5067 | 4868.237 | NORMAL
313.706 | 0.05 | 302.591 | 0.8 | 2 | 106868.78 | 14782.7667 | 14770.2309 | 4807.46 | NORMAL
313.706 | 0.05 | 302.591 | 1.11 | 1 | 57226.51 | 11939.3611 | 11925.0697 | 4270.98 | NORMAL
313.706 | 0.05 | 302.591 | 1.11 | 1 | 79289.74 | 12543.9918 | 12529.3028 | 3859.461 | NORMAL
313.706 | 0.05 | 302.591 | 1.11 | 1 | 101352.97 | 12879.2204 | 12864.3191 | 3634.075 | NORMAL
313.706 | 0.05 | 302.591 | 1.11 | 1 | 106868.78 | 12939.3611 | 12924.4291 | 3593.904 | NORMAL
313.706 | 0.05 | 302.591 | 1.11 | 2 | 57226.51 | 14744.109 | 14728.2444 | 6004.15 | NORMAL
313.706 | 0.05 | 302.591 | 1.11 | 2 | 79289.74 | 15569.1676 | 15552.9446 | 5325.899 | NORMAL
313.706 | 0.05 | 302.591 | 1.11 | 2 | 101352.97 | 16038.3646 | 16021.9574 | 4959.905 | NORMAL
313.706 | 0.05 | 302.591 | 1.11 | 2 | 106868.78 | 16123.8863 | 16107.4399 | 4894.782 | NORMAL
313.706 | 0.05 | 302.591 | 1.42 | 1 | 57226.51 | 12458.558 | 12442.4242 | 4306.6 | NORMAL
313.706 | 0.05 | 302.591 | 1.42 | 1 | 79289.74 | 13138.2474 | 13121.5355 | 3877.65 | NORMAL
313.706 | 0.05 | 302.591 | 1.42 | 1 | 101352.97 | 13518.2005 | 13485.8109 | 3641.434 | NORMAL
313.706 | 0.05 | 302.591 | 1.42 | 1 | 106868.78 | 13587.1336 | 13570.0682 | 3599.097 | NORMAL
313.706 | 0.05 | 302.591 | 1.42 | 2 | 57226.51 | 15456.9168 | 15438.5385 | 6118.32 | NORMAL
313.706 | 0.05 | 302.591 | 1.42 | 2 | 79289.74 | 16392.8488 | 16373.8495 | 5408.93 | NORMAL
313.706 | 0.05 | 302.591 | 1.42 | 2 | 101352.97 | 16934.0563 | 16914.7345 | 5023.298 | NORMAL
313.706 | 0.05 | 302.591 | 1.42 | 2 | 106868.78 | 17033.265 | 17004.8024 | 4954.425 | NORMAL
313.706 | 0.05 | 305.368 | 0.5 | 1 | 57226.51 | 10235.1993 | 10225.8853 | 4160.686 | NORMAL
313.706 | 0.05 | 305.368 | 0.5 | 1 | 79289.74 | 10612.925 | 10603.6174 | 3806.677 | NORMAL
313.706 | 0.05 | 305.368 | 0.5 | 1 | 101352.97 | 10812.5146 | 10803.2267 | 3619.575 | NORMAL
313.706 | 0.05 | 305.368 | 0.5 | 1 | 106868.78 | 10848.0363 | 10838.7504 | 3586.7582 | NORMAL
313.706 | 0.05 | 305.368 | 0.5 | 2 | 57226.51 | 12339.2439 | 12330.2239 | 5623.67 | NORMAL
313.706 | 0.05 | 305.368 | 0.5 | 2 | 79289.74 | 12821.1899 | 12812.3177 | 5057.122 | NORMAL
313.706 | 0.05 | 305.368 | 0.5 | 2 | 101352.97 | 13082.5029 | 13073.7246 | 4758.361 | NORMAL
313.706 | 0.05 | 305.368 | 0.5 | 2 | 106868.78 | 13130.6565 | 13121.8984 | 4704.4713 | NORMAL
313.706 | 0.05 | 305.368 | 0.8 | 1 | 57226.51 | 11775.2638 | 11761.2748 | 4259.909 | NORMAL
313.706 | 0.05 | 305.368 | 0.8 | 1 | 79289.74 | 12321.6882 | 12307.4443 | 3852.898 | NORMAL
313.706 | 0.05 | 305.368 | 0.8 | 1 | 101352.97 | 12621.2192 | 12606.8563 | 3631.421 | NORMAL
313.706 | 0.05 | 305.368 | 0.8 | 1 | 106868.78 | 12675.0879 | 12660.7017 | 3592.054 | NORMAL
313.706 | 0.05 | 305.368 | 0.8 | 2 | 57226.51 | 14352.1688 | 14337.3143 | 5942.193 | NORMAL
313.706 | 0.05 | 305.368 | 0.8 | 2 | 79289.74 | 15077.9308 | 15062.9585 | 5277.354 | NORMAL
313.706 | 0.05 | 305.368 | 0.8 | 2 | 101352.97 | 15484.408 | 15469.3726 | 4921.316 | NORMAL
313.706 | 0.05 | 305.368 | 0.8 | 2 | 106868.78 | 15559.6717 | 15544.6411 | 4857.049 | NORMAL
313.706 | 0.05 | 305.368 | 1.11 | 1 | 57226.51 | 12631.2134 | 12601.4037 | 4318.21 | NORMAL
313.706 | 0.05 | 305.368 | 1.11 | 1 | 79289.74 | 13291.1782 | 13265.8053 | 3882.444 | NORMAL
313.706 | 0.05 | 305.368 | 1.11 | 1 | 101352.97 | 13658.4115 | 13640.5326 | 3643.142 | NORMAL
313.706 | 0.05 | 305.368 | 1.11 | 1 | 106868.78 | 13724.8535 | 13706.9288 | 3600.256 | NORMAL
313.706 | 0.05 | 305.368 | 1.11 | 2 | 57226.51 | 15500.381 | 15463.1956 | 6125.18 | NORMAL
313.706 | 0.05 | 305.368 | 1.11 | 2 | 79289.74 | 16390.2696 | 16370.8636 | 5408.676 | NORMAL
313.706 | 0.05 | 305.368 | 1.11 | 2 | 101352.97 | 16901.0551 | 16881.4161 | 5020.973 | NORMAL
313.706 | 0.05 | 305.368 | 1.11 | 2 | 106868.78 | 16994.49 | 16974.8104 | 4951.876 | NORMAL
313.706 | 0.05 | 305.368 | 1.42 | 1 | 57226.51 | 13189.6542 | 13170.3313 | 4357.56 | NORMAL
313.706 | 0.05 | 305.368 | 1.42 | 1 | 79289.74 | 13932.0633 | 13912.029 | 3903.39 | NORMAL
313.706 | 0.05 | 305.368 | 1.42 | 1 | 101352.97 | 14350.8499 | 14330.443 | 3652.397 | NORMAL
313.706 | 0.05 | 305.368 | 1.42 | 1 | 106868.78 | 14426.612 | 14406.1262 | 3607.309 | NORMAL
313.706 | 0.05 | 305.368 | 1.42 | 2 | 57226.51 | 16265.6213 | 16243.6627 | 6244.44 | NORMAL
313.706 | 0.05 | 305.368 | 1.42 | 2 | 79289.74 | 17268.7573 | 17246.0662 | 5498.74 | NORMAL
313.706 | 0.05 | 305.368 | 1.42 | 2 | 101352.97 | 17860.2579 | 17837.1646 | 5090.105 | NORMAL
313.706 | 0.05 | 305.368 | 1.42 | 2 | 106868.78 | 17969.0211 | 17945.859 | 5017.123 | NORMAL
313.706 | 0.15 | 288.706 | 0.5 | 1 | 57226.51 | 7122.2743 | 7119.8243 | 3982.628 | NORMAL
313.706 | 0.15 | 288.706 | 0.5 | 1 | 79289.74 | 7347.9777 | 7345.5308 | 3744.808 | NORMAL
313.706 | 0.15 | 288.706 | 0.5 | 1 | 101352.97 | 7458.4701 | 7456.0312 | 3627.26 | NORMAL
313.706 | 0.15 | 288.706 | 0.5 | 1 | 106868.78 | 7472.4795 | 7470.036 | 3612.2838 | NORMAL
313.706 | 0.15 | 288.706 | 0.5 | 2 | 57226.51 | 9072.245 | 9070.0042 | 5119.966 | NORMAL
313.706 | 0.15 | 288.706 | 0.5 | 2 | 79289.74 | 9374.7948 | 9341.6549 | 4715.438 | NORMAL
313.706 | 0.15 | 288.706 | 0.5 | 2 | 101352.97 | 9512.2216 | 9496.2506 | 4526.5661 | NORMAL
313.706 | 0.15 | 288.706 | 0.5 | 2 | 106868.78 | 9522.4502 | 9520.3267 | 4490.7961 | NORMAL
313.706 | 0.15 | 288.706 | 0.8 | 1 | 57226.51 | 8098.9449 | 8091.6316 | 4035.267 | NORMAL
313.706 | 0.15 | 288.706 | 0.8 | 1 | 79289.74 | 8414.0094 | 8410.1642 | 3758.872 | NORMAL
313.706 | 0.15 | 288.706 | 0.8 | 1 | 101352.97 | 8572.5674 | 8568.7012 | 3619.177 | NORMAL
313.706 | 0.15 | 288.706 | 0.8 | 1 | 106868.78 | 8601.3775 | 8597.5069 | 3593.831 | NORMAL
313.706 | 0.15 | 288.706 | 0.8 | 2 | 57226.51 | 10397.9191 | 10393.3128 | 5324.16 | NORMAL
313.706 | 0.15 | 288.706 | 0.8 | 2 | 79289.74 | 10825.4103 | 10821.4049 | 4866.849 | NORMAL
313.706 | 0.15 | 288.706 | 0.8 | 2 | 101352.97 | 11057.0047 | 11053.002 | 4624.339 | NORMAL
313.706 | 0.15 | 288.706 | 0.8 | 2 | 106868.78 | 11094.4607 | 11090.4667 | 4585.772 | NORMAL
313.706 | 0.15 | 288.706 | 1.11 | 1 | 57226.51 | 8627.7257 | 8621.16 | 4066.06 | NORMAL
313.706 | 0.15 | 288.706 | 1.11 | 1 | 79289.74 | 9000.1758 | 8986.3606 | 3770.253 | NORMAL
313.706 | 0.15 | 288.706 | 1.11 | 1 | 101352.97 | 9193.6401 | 9188.8042 | 3616.747 | NORMAL
313.706 | 0.15 | 288.706 | 1.11 | 1 | 106868.78 | 9227.0223 | 9222.1781 | 3590.227 | NORMAL
313.706 | 0.15 | 288.706 | 1.11 | 2 | 57226.51 | 11144.0797 | 11138.842 | 5438.67 | NORMAL
313.706 | 0.15 | 288.706 | 1.11 | 2 | 79289.74 | 11663.9801 | 11658.6496 | 4946.431 | NORMAL
313.706 | 0.15 | 288.706 | 1.11 | 2 | 101352.97 | 11950 | 11944.6464 | 4683.157 | NORMAL
313.706 | 0.15 | 288.706 | 1.11 | 2 | 106868.78 | 12002.8429 | 11997.4776 | 4635.288 | NORMAL
313.706 | 0.15 | 288.706 | 1.42 | 1 | 57226.51 | 8968.4642 | 8963.1729 | 4086 | NORMAL
313.706 | 0.15 | 288.706 | 1.42 | 1 | 79289.74 | 9381.8581 | 9376.3979 | 3778.1 | NORMAL
313.706 | 0.15 | 288.706 | 1.42 | 1 | 101352.97 | 9599.619 | 9594.0896 | 3616.369 | NORMAL
313.706 | 0.15 | 288.706 | 1.42 | 1 | 106868.78 | 9637.9836 | 9632.4417 | 3587.89 | NORMAL
313.706 | 0.15 | 288.706 | 1.42 | 2 | 57226.51 | 11634.1735 | 11623.9587 | 5514.19 | NORMAL
313.706 | 0.15 | 288.706 | 1.42 | 2 | 79289.74 | 12222.0985 | 12207.322 | 4999.66 | NORMAL
313.706 | 0.15 | 288.706 | 1.42 | 2 | 101352.97 | 12549.1501 | 12542.7751 | 4722.864 | NORMAL
313.706 | 0.15 | 288.706 | 1.42 | 2 | 106868.78 | 12609.8183 | 12603.4251 | 4672.45 | NORMAL
313.706 | 0.15 | 291.483 | 0.5 | 1 | 57226.51 | 7632.1512 | 7628.9228 | 4008.944 | NORMAL
313.706 | 0.15 | 291.483 | 0.5 | 1 | 79289.74 | 7877.2274 | 7874.0135 | 3753.163 | NORMAL
313.706 | 0.15 | 291.483 | 0.5 | 1 | 101352.97 | 8002.9601 | 7999.759 | 3621.645 | NORMAL
313.706 | 0.15 | 291.483 | 0.5 | 1 | 106868.78 | 8021.7468 | 8018.5461 | 3601.7835 | NORMAL
313.706 | 0.15 | 291.483 | 0.5 | 2 | 57226.51 | 9597.0399 | 9594.036 | 5201.161 | NORMAL
313.706 | 0.15 | 291.483 | 0.5 | 2 | 79289.74 | 9927.0223 | 9904.3688 | 4767.693 | NORMAL
313.706 | 0.15 | 291.483 | 0.5 | 2 | 101352.97 | 10083.0305 | 10080.1467 | 4564.2185 | NORMAL
313.706 | 0.15 | 291.483 | 0.5 | 2 | 106868.78 | 10113.1887 | 10110.3368 | 4525.4604 | NORMAL
313.706 | 0.15 | 291.483 | 0.8 | 1 | 57226.51 | 8694.8124 | 8689.8825 | 4068.714 | NORMAL
313.706 | 0.15 | 291.483 | 0.8 | 1 | 79289.74 | 9041.7644 | 9036.7733 | 3771.126 | NORMAL
313.706 | 0.15 | 291.483 | 0.8 | 1 | 101352.97 | 9221.7175 | 9216.6824 | 3616.751 | NORMAL
313.706 | 0.15 | 291.483 | 0.8 | 1 | 106868.78 | 9252.6377 | 9247.5951 | 3590.061 | NORMAL
313.706 | 0.15 | 291.483 | 0.8 | 2 | 57226.51 | 11034.2907 | 11029.0715 | 5421.801 | NORMAL
313.706 | 0.15 | 291.483 | 0.8 | 2 | 79289.74 | 11505.6858 | 11500.4622 | 4931.384 | NORMAL
313.706 | 0.15 | 291.483 | 0.8 | 2 | 101352.97 | 11762.6319 | 11757.3975 | 4670.879 | NORMAL
313.706 | 0.15 | 291.483 | 0.8 | 2 | 106868.78 | 11809.8183 | 11804.5865 | 4623.55 | NORMAL
313.706 | 0.15 | 291.483 | 1.11 | 1 | 57226.51 | 9273.3587 | 9267.3032 | 4103.32 | NORMAL
313.706 | 0.15 | 291.483 | 1.11 | 1 | 79289.74 | 9686.2837 | 9680.0748 | 3784.823 | NORMAL
313.706 | 0.15 | 291.483 | 1.11 | 1 | 101352.97 | 9904.4549 | 9898.1754 | 3616.537 | NORMAL
313.706 | 0.15 | 291.483 | 1.11 | 1 | 106868.78 | 9942.8195 | 9936.5257 | 3586.938 | NORMAL
313.706 | 0.15 | 291.483 | 1.11 | 2 | 57226.51 | 11843.2884 | 11836.5022 | 5546.62 | NORMAL
313.706 | 0.15 | 291.483 | 1.11 | 2 | 79289.74 | 12418.6987 | 12411.8063 | 5018.457 | NORMAL
313.706 | 0.15 | 291.483 | 1.11 | 2 | 101352.97 | 12737.2216 | 12730.2671 | 4735.326 | NORMAL
313.706 | 0.15 | 291.483 | 1.11 | 2 | 106868.78 | 12796.2192 | 12789.2581 | 4683.829 | NORMAL
313.706 | 0.15 | 291.483 | 1.42 | 1 | 57226.51 | 9646.864 | 9615.4442 | 4126.06 | NORMAL
313.706 | 0.15 | 291.483 | 1.42 | 1 | 79289.74 | 10106.4185 | 10098.3031 | 3794.44 | NORMAL
313.706 | 0.15 | 291.483 | 1.42 | 1 | 101352.97 | 10351.1723 | 10343.999 | 3618.212 | NORMAL
313.706 | 0.15 | 291.483 | 1.42 | 1 | 106868.78 | 10394.2263 | 10387.0335 | 3587.373 | NORMAL
313.706 | 0.15 | 291.483 | 1.42 | 2 | 57226.51 | 12375.6448 | 12349.2228 | 5629.45 | NORMAL
313.706 | 0.15 | 291.483 | 1.42 | 2 | 79289.74 | 13027.6377 | 13019.4955 | 5076.84 | NORMAL
313.706 | 0.15 | 291.483 | 1.42 | 2 | 101352.97 | 13392.4384 | 13384.2021 | 4778.872 | NORMAL
313.706 | 0.15 | 291.483 | 1.42 | 2 | 106868.78 | 13459.9648 | 13451.7004 | 4724.754 | NORMAL
313.706 | 0.15 | 294.26 | 0.5 | 1 | 57226.51 | 8145.9555 | 8141.8336 | 4037.35 | NORMAL
313.706 | 0.15 | 294.26 | 0.5 | 1 | 79289.74 | 8418.1419 | 8414.0338 | 3758.524 | NORMAL
313.706 | 0.15 | 294.26 | 0.5 | 1 | 101352.97 | 8552.6671 | 8548.5703 | 3619.416 | NORMAL
313.706 | 0.15 | 294.26 | 0.5 | 1 | 106868.78 | 8577.6671 | 8573.5669 | 3593.7522 | NORMAL
313.706 | 0.15 | 294.26 | 0.5 | 2 | 57226.51 | 10135.0235 | 10131.1417 | 5284.028 | NORMAL
313.706 | 0.15 | 294.26 | 0.5 | 2 | 79289.74 | 10483.7046 | 10479.9095 | 4834.488 | NORMAL
313.706 | 0.15 | 294.26 | 0.5 | 2 | 101352.97 | 10669.6366 | 10665.8915 | 4598.2 | NORMAL
313.706 | 0.15 | 294.26 | 0.5 | 2 | 106868.78 | 10699.6776 | 10695.9327 | 4560.9172 | NORMAL
313.706 | 0.15 | 294.26 | 0.8 | 1 | 57226.51 | 9298.1243 | 9291.8573 | 4104.757 | NORMAL
313.706 | 0.15 | 294.26 | 0.8 | 1 | 79289.74 | 9680.7737 | 9671.8771 | 3784.727 | NORMAL
313.706 | 0.15 | 294.26 | 0.8 | 1 | 101352.97 | 9881.6823 | 9875.279 | 3616.469 | NORMAL
313.706 | 0.15 | 294.26 | 0.8 | 1 | 106868.78 | 9917.1747 | 9910.7583 | 3586.854 | NORMAL
313.706 | 0.15 | 294.26 | 0.8 | 2 | 57226.51 | 11683.2356 | 11676.5879 | 5521.863 | NORMAL
313.706 | 0.15 | 294.26 | 0.8 | 2 | 79289.74 | 12200.2345 | 12193.5609 | 4997.65 | NORMAL
313.706 | 0.15 | 294.26 | 0.8 | 2 | 101352.97 | 12483.646 | 12476.9672 | 4718.602 | NORMAL
313.706 | 0.15 | 294.26 | 0.8 | 2 | 106868.78 | 12535.932 | 12529.2504 | 4667.927 | NORMAL
313.706 | 0.15 | 294.26 | 1.11 | 1 | 57226.51 | 9928.7515 | 9921.0567 | 4142.7 | NORMAL
313.706 | 0.15 | 294.26 | 1.11 | 1 | 79289.74 | 10384.5838 | 10376.6915 | 3801.073 | NORMAL
313.706 | 0.15 | 294.26 | 1.11 | 1 | 101352.97 | 10627.4326 | 10619.4514 | 3619.764 | NORMAL
313.706 | 0.15 | 294.26 | 1.11 | 1 | 106868.78 | 10671.6002 | 10662.0598 | 3586.959 | NORMAL
313.706 | 0.15 | 294.26 | 1.11 | 2 | 57226.51 | 12556.1841 | 12547.5956 | 5657.62 | NORMAL
313.706 | 0.15 | 294.26 | 1.11 | 2 | 79289.74 | 13189.7714 | 13178.5205 | 5092.479 | NORMAL
313.706 | 0.15 | 294.26 | 1.11 | 2 | 101352.97 | 13542.3212 | 13533.4916 | 4788.942 | NORMAL
313.706 | 0.15 | 294.26 | 1.11 | 2 | 106868.78 | 13607.4736 | 13598.6288 | 4733.865 | NORMAL
313.706 | 0.15 | 294.26 | 1.42 | 1 | 57226.51 | 10336.5768 | 10327.8941 | 4168.2 | NORMAL
313.706 | 0.15 | 294.26 | 1.42 | 1 | 79289.74 | 10845.3986 | 10832.7962 | 3812.47 | NORMAL
313.706 | 0.15 | 294.26 | 1.42 | 1 | 101352.97 | 11124.5018 | 11115.3797 | 3619.016 | NORMAL
313.706 | 0.15 | 294.26 | 1.42 | 1 | 106868.78 | 11170.8089 | 11155.8065 | 3586.776 | NORMAL
313.706 | 0.15 | 294.26 | 1.42 | 2 | 57226.51 | 13129.4256 | 13119.4209 | 5749.27 | NORMAL
313.706 | 0.15 | 294.26 | 1.42 | 2 | 79289.74 | 13850.0586 | 13839.768 | 5156.49 | NORMAL
313.706 | 0.15 | 294.26 | 1.42 | 2 | 101352.97 | 14255.0997 | 14244.6507 | 4837.024 | NORMAL
313.706 | 0.15 | 294.26 | 1.42 | 2 | 106868.78 | 14330.422 | 14319.0724 | 4778.905 | NORMAL
313.706 | 0.15 | 297.037 | 0.5 | 1 | 57226.51 | 8666.2368 | 8661.0717 | 4066.854 | NORMAL
313.706 | 0.15 | 297.037 | 0.5 | 1 | 79289.74 | 8961.3716 | 8956.2099 | 3769.504 | NORMAL
313.706 | 0.15 | 297.037 | 0.5 | 1 | 101352.97 | 9111.5768 | 9106.4287 | 3616.925 | NORMAL
313.706 | 0.15 | 297.037 | 0.5 | 1 | 106868.78 | 9137.0457 | 9131.9016 | 3590.7584 | NORMAL
313.706 | 0.15 | 297.037 | 0.5 | 2 | 57226.51 | 10683.0891 | 10678.1642 | 5367.795 | NORMAL
313.706 | 0.15 | 297.037 | 0.5 | 2 | 79289.74 | 11061.7526 | 11056.9297 | 4889.288 | NORMAL
313.706 | 0.15 | 297.037 | 0.5 | 2 | 101352.97 | 11266.9695 | 11262.2036 | 4633.944 | NORMAL
313.706 | 0.15 | 297.037 | 0.5 | 2 | 106868.78 | 11300.8206 | 11296.063 | 4592.0126 | NORMAL
313.706 | 0.15 | 297.037 | 0.8 | 1 | 57226.51 | 9911.4009 | 9903.5808 | 4140.923 | NORMAL
313.706 | 0.15 | 297.037 | 0.8 | 1 | 79289.74 | 10329.9824 | 10322.0283 | 3799.751 | NORMAL
313.706 | 0.15 | 297.037 | 0.8 | 1 | 101352.97 | 10552.4912 | 10544.4819 | 3618.555 | NORMAL
313.706 | 0.15 | 297.037 | 0.8 | 1 | 106868.78 | 10591.0903 | 10583.0728 | 3587.088 | NORMAL
313.706 | 0.15 | 297.037 | 0.8 | 2 | 57226.51 | 12343.6694 | 12335.3621 | 5624.428 | NORMAL
313.706 | 0.15 | 297.037 | 0.8 | 2 | 79289.74 | 12908.9977 | 12900.6455 | 5065.488 | NORMAL
313.706 | 0.15 | 297.037 | 0.8 | 2 | 101352.97 | 13219.6659 | 13211.2978 | 4767.43 | NORMAL
313.706 | 0.15 | 297.037 | 0.8 | 2 | 106868.78 | 13276.7292 | 13268.3648 | 4713.443 | NORMAL
313.706 | 0.15 | 297.037 | 1.11 | 1 | 57226.51 | 10594.5487 | 10581.8564 | 4183.92 | NORMAL
313.706 | 0.15 | 297.037 | 1.11 | 1 | 79289.74 | 11096.4537 | 11086.6111 | 3818.92 | NORMAL
313.706 | 0.15 | 297.037 | 1.11 | 1 | 101352.97 | 11370.4572 | 11355.6188 | 3620.794 | NORMAL
313.706 | 0.15 | 297.037 | 1.11 | 1 | 106868.78 | 11416.3247 | 11406.324 | 3587.523 | NORMAL
313.706 | 0.15 | 297.037 | 1.11 | 2 | 57226.51 | 13280.1876 | 13269.497 | 5772.79 | NORMAL
313.706 | 0.15 | 297.037 | 1.11 | 2 | 79289.74 | 13975.762 | 13964.8469 | 5168.735 | NORMAL
313.706 | 0.15 | 297.037 | 1.11 | 2 | 101352.97 | 14364.068 | 14353.0508 | 4844.458 | NORMAL
313.706 | 0.15 | 297.037 | 1.11 | 2 | 106868.78 | 14435.9027 | 14424.8737 | 4785.555 | NORMAL
313.706 | 0.15 | 297.037 | 1.42 | 1 | 57226.51 | 11037.4854 | 11026.6686 | 4212.24 | NORMAL
313.706 | 0.15 | 297.037 | 1.42 | 1 | 79289.74 | 11599.6483 | 11581.3209 | 3832.42 | NORMAL
313.706 | 0.15 | 297.037 | 1.42 | 1 | 101352.97 | 11909.2907 | 11893.3085 | 3624.851 | NORMAL
313.706 | 0.15 | 297.037 | 1.42 | 1 | 106868.78 | 11964.3611 | 11952.9471 | 3588.046 | NORMAL
313.706 | 0.15 | 297.037 | 1.42 | 2 | 57226.51 | 13898.6811 | 13886.2696 | 5870.27 | NORMAL
313.706 | 0.15 | 297.037 | 1.42 | 2 | 79289.74 | 14688.2767 | 14662.5722 | 5238.68 | NORMAL
313.706 | 0.15 | 297.037 | 1.42 | 2 | 101352.97 | 15136.1665 | 15123.1796 | 4897.151 | NORMAL
313.706 | 0.15 | 297.037 | 1.42 | 2 | 106868.78 | 15219.2556 | 15206.2127 | 4835.195 | NORMAL
313.706 | 0.15 | 299.814 | 0.5 | 1 | 57226.51 | 9193.8453 | 9187.4647 | 4097.617 | NORMAL
313.706 | 0.15 | 299.814 | 0.5 | 1 | 79289.74 | 9512.7491 | 9506.3851 | 3781.053 | NORMAL
313.706 | 0.15 | 299.814 | 0.5 | 1 | 101352.97 | 9677.7843 | 9671.426 | 3616.309 | NORMAL
313.706 | 0.15 | 299.814 | 0.5 | 1 | 106868.78 | 9706.3013 | 9699.9534 | 3587.5334 | NORMAL
313.706 | 0.15 | 299.814 | 0.5 | 2 | 57226.51 | 11240.6506 | 11234.5357 | 5453.508 | NORMAL
313.706 | 0.15 | 299.814 | 0.5 | 2 | 79289.74 | 11649.7069 | 11643.7073 | 4945.174 | NORMAL
313.706 | 0.15 | 299.814 | 0.5 | 2 | 101352.97 | 11868.6401 | 11862.7058 | 4677.9 | NORMAL
313.706 | 0.15 | 299.814 | 0.5 | 2 | 106868.78 | 11908.4994 | 11902.5809 | 4629.5854 | NORMAL
313.706 | 0.15 | 299.814 | 0.8 | 1 | 57226.51 | 10533.0305 | 10523.4138 | 4179.417 | NORMAL
313.706 | 0.15 | 299.814 | 0.8 | 1 | 79289.74 | 10990.0938 | 10980.3236 | 3816.181 | NORMAL
313.706 | 0.15 | 299.814 | 0.8 | 1 | 101352.97 | 11238.4525 | 11228.5964 | 3619.933 | NORMAL
313.706 | 0.15 | 299.814 | 0.8 | 1 | 106868.78 | 11278.6635 | 11268.806 | 3587.793 | NORMAL
313.706 | 0.15 | 299.814 | 0.8 | 2 | 57226.51 | 13013.1008 | 13002.8855 | 5731.01 | NORMAL
313.706 | 0.15 | 299.814 | 0.8 | 2 | 79289.74 | 13629.8652 | 13619.5883 | 5135.107 | NORMAL
313.706 | 0.15 | 299.814 | 0.8 | 2 | 101352.97 | 13969.4021 | 13959.0927 | 4817.821 | NORMAL
313.706 | 0.15 | 299.814 | 0.8 | 2 | 106868.78 | 14032.1512 | 14021.8376 | 4760.245 | NORMAL
313.706 | 0.15 | 299.814 | 1.11 | 1 | 57226.51 | 11270.2814 | 11258.5265 | 4226.9 | NORMAL
313.706 | 0.15 | 299.814 | 1.11 | 1 | 79289.74 | 11820.6038 | 11808.5113 | 3838.562 | NORMAL
313.706 | 0.15 | 299.814 | 1.11 | 1 | 101352.97 | 12123.7104 | 12111.4534 | 3626.738 | NORMAL
313.706 | 0.15 | 299.814 | 1.11 | 1 | 106868.78 | 12177.5205 | 12160.4598 | 3589.11 | NORMAL
313.706 | 0.15 | 299.814 | 1.11 | 2 | 57226.51 | 14017.9953 | 14001.0896 | 5889.18 | NORMAL
313.706 | 0.15 | 299.814 | 1.11 | 2 | 79289.74 | 14775.4103 | 14762.0386 | 5247.317 | NORMAL
313.706 | 0.15 | 299.814 | 1.11 | 2 | 101352.97 | 15202.1981 | 15188.6682 | 4901.73 | NORMAL
313.706 | 0.15 | 299.814 | 1.11 | 2 | 106868.78 | 15281.2134 | 15267.6589 | 4839.173 | NORMAL
313.706 | 0.15 | 299.814 | 1.42 | 1 | 57226.51 | 11749.6483 | 11692.357 | 4258.79 | NORMAL
313.706 | 0.15 | 299.814 | 1.42 | 1 | 79289.74 | 12367.2626 | 12340.4504 | 3854.2 | NORMAL
313.706 | 0.15 | 299.814 | 1.42 | 1 | 101352.97 | 12710.7561 | 12696.7743 | 3632.294 | NORMAL
313.706 | 0.15 | 299.814 | 1.42 | 1 | 106868.78 | 12772.0399 | 12758.0034 | 3592.727 | NORMAL
313.706 | 0.15 | 299.814 | 1.42 | 2 | 57226.51 | 14682.034 | 14666.8528 | 5994.21 | NORMAL
313.706 | 0.15 | 299.814 | 1.42 | 2 | 79289.74 | 15542.5264 | 15526.8595 | 5323.24 | NORMAL
313.706 | 0.15 | 299.814 | 1.42 | 2 | 101352.97 | 16034.0856 | 16018.1637 | 4959.598 | NORMAL
313.706 | 0.15 | 299.814 | 1.42 | 2 | 106868.78 | 16123.5346 | 16107.5562 | 4894.789 | NORMAL
313.706 | 0.15 | 302.591 | 0.5 | 1 | 57226.51 | 9728.0188 | 9720.2655 | 4129.52 | NORMAL
313.706 | 0.15 | 302.591 | 0.5 | 1 | 79289.74 | 10071.9519 | 10064.2066 | 3793.741 | NORMAL
313.706 | 0.15 | 302.591 | 0.5 | 1 | 101352.97 | 10250.7034 | 10242.9641 | 3618.047 | NORMAL
313.706 | 0.15 | 302.591 | 0.5 | 1 | 106868.78 | 10283.6753 | 10275.9419 | 3586.0737 | NORMAL
313.706 | 0.15 | 302.591 | 0.5 | 2 | 57226.51 | 11806.8582 | 11799.3608 | 5540.868 | NORMAL
313.706 | 0.15 | 302.591 | 0.5 | 2 | 79289.74 | 12247.5967 | 12240.2359 | 5002.181 | NORMAL
313.706 | 0.15 | 302.591 | 0.5 | 2 | 101352.97 | 12484.5252 | 12477.2467 | 4718.727 | NORMAL
313.706 | 0.15 | 302.591 | 0.5 | 2 | 106868.78 | 12527.8722 | 12520.6061 | 4667.4369 | NORMAL
313.706 | 0.15 | 302.591 | 0.8 | 1 | 57226.51 | 11163.5991 | 11151.9443 | 4219.414 | NORMAL
313.706 | 0.15 | 302.591 | 0.8 | 1 | 79289.74 | 11661.1665 | 11649.3071 | 3834.155 | NORMAL
313.706 | 0.15 | 302.591 | 0.8 | 1 | 101352.97 | 11932.8546 | 11920.8979 | 3625.057 | NORMAL
313.706 | 0.15 | 302.591 | 0.8 | 1 | 106868.78 | 11980.6565 | 11968.6758 | 3588.144 | NORMAL
313.706 | 0.15 | 302.591 | 0.8 | 2 | 57226.51 | 13694.9883 | 13682.608 | 5838.161 | NORMAL
313.706 | 0.15 | 302.591 | 0.8 | 2 | 79289.74 | 14362.5733 | 14350.0922 | 5206.675 | NORMAL
313.706 | 0.15 | 302.591 | 0.8 | 2 | 101352.97 | 14732.4736 | 14719.951 | 4869.557 | NORMAL
313.706 | 0.15 | 302.591 | 0.8 | 2 | 106868.78 | 14801.0258 | 14788.4893 | 4808.647 | NORMAL
313.706 | 0.15 | 302.591 | 1.11 | 1 | 57226.51 | 11957.0047 | 11906.9885 | 4272.21 | NORMAL
313.706 | 0.15 | 302.591 | 1.11 | 1 | 79289.74 | 12558.3529 | 12543.6973 | 3859.893 | NORMAL
313.706 | 0.15 | 302.591 | 1.11 | 1 | 101352.97 | 12891.4127 | 12871.547 | 3634.203 | NORMAL
313.706 | 0.15 | 302.591 | 1.11 | 1 | 106868.78 | 12950.7327 | 12935.8264 | 3593.988 | NORMAL
313.706 | 0.15 | 302.591 | 1.11 | 2 | 57226.51 | 14768.1125 | 14752.2811 | 6008.03 | NORMAL
313.706 | 0.15 | 302.591 | 1.11 | 2 | 79289.74 | 15589.0387 | 15572.8417 | 5327.893 | NORMAL
313.706 | 0.15 | 302.591 | 1.11 | 2 | 101352.97 | 16055.1876 | 16038.8113 | 4961.088 | NORMAL
313.706 | 0.15 | 302.591 | 1.11 | 2 | 106868.78 | 16142.2626 | 16125.8459 | 4894.605 | NORMAL
313.706 | 0.15 | 302.591 | 1.42 | 1 | 57226.51 | 12473.9156 | 12457.8492 | 4307.62 | NORMAL
313.706 | 0.15 | 302.591 | 1.42 | 1 | 79289.74 | 13150.6741 | 13114.3125 | 3878.04 | NORMAL
313.706 | 0.15 | 302.591 | 1.42 | 1 | 101352.97 | 13528.6928 | 13511.7143 | 3641.571 | NORMAL
313.706 | 0.15 | 302.591 | 1.42 | 1 | 106868.78 | 13597.0399 | 13572.7283 | 3599.181 | NORMAL
313.706 | 0.15 | 302.591 | 1.42 | 2 | 57226.51 | 15477.9308 | 15459.605 | 6121.58 | NORMAL
313.706 | 0.15 | 302.591 | 1.42 | 2 | 79289.74 | 16410.17 | 16391.2327 | 5410.7 | NORMAL
313.706 | 0.15 | 302.591 | 1.42 | 2 | 101352.97 | 16948.9742 | 16929.7032 | 5024.382 | NORMAL
313.706 | 0.15 | 302.591 | 1.42 | 2 | 106868.78 | 17047.2743 | 17027.9427 | 4955.376 | NORMAL
313.706 | 0.15 | 305.368 | 0.5 | 1 | 57226.51 | 10268.5522 | 10259.2386 | 4162.723 | NORMAL
313.706 | 0.15 | 305.368 | 0.5 | 1 | 79289.74 | 10638.9801 | 10629.671 | 3807.342 | NORMAL
313.706 | 0.15 | 305.368 | 0.5 | 1 | 101352.97 | 10834.027 | 10824.7314 | 3619.538 | NORMAL
313.706 | 0.15 | 305.368 | 0.5 | 1 | 106868.78 | 10868.0539 | 10858.7617 | 3586.7964 | NORMAL
313.706 | 0.15 | 305.368 | 0.5 | 2 | 57226.51 | 12381.8875 | 12372.8487 | 5630.304 | NORMAL
313.706 | 0.15 | 305.368 | 0.5 | 2 | 79289.74 | 12855.0117 | 12846.1161 | 5060.375 | NORMAL
313.706 | 0.15 | 305.368 | 0.5 | 2 | 101352.97 | 13110.3751 | 13101.5781 | 4760.218 | NORMAL
313.706 | 0.15 | 305.368 | 0.5 | 2 | 106868.78 | 13156.9461 | 13148.1704 | 4706.0438 | NORMAL
313.706 | 0.15 | 305.368 | 0.8 | 1 | 57226.51 | 11802.1102 | 11788.1601 | 4261.696 | NORMAL
313.706 | 0.15 | 305.368 | 0.8 | 1 | 79289.74 | 12343.2298 | 12329.0104 | 3853.542 | NORMAL
313.706 | 0.15 | 305.368 | 0.8 | 1 | 101352.97 | 12639.2145 | 12624.869 | 3631.609 | NORMAL
313.706 | 0.15 | 305.368 | 0.8 | 1 | 106868.78 | 12691.7937 | 12677.4266 | 3592.186 | NORMAL
313.706 | 0.15 | 305.368 | 0.8 | 2 | 57226.51 | 14387.7491 | 14372.9153 | 5947.804 | NORMAL
313.706 | 0.15 | 305.368 | 0.8 | 2 | 79289.74 | 15106.9461 | 15091.9751 | 5280.22 | NORMAL
313.706 | 0.15 | 305.368 | 0.8 | 2 | 101352.97 | 15508.7339 | 15493.7059 | 4923.021 | NORMAL
313.706 | 0.15 | 305.368 | 0.8 | 2 | 106868.78 | 15582.5909 | 15567.5537 | 4858.493 | NORMAL
313.706 | 0.15 | 305.368 | 1.11 | 1 | 57226.51 | 12653.7515 | 12636.7069 | 4319.76 | NORMAL
313.706 | 0.15 | 305.368 | 1.11 | 1 | 79289.74 | 13309.3787 | 13288.7758 | 3883.019 | NORMAL
313.706 | 0.15 | 305.368 | 1.11 | 1 | 101352.97 | 13673.7397 | 13655.9092 | 3643.339 | NORMAL
313.706 | 0.15 | 305.368 | 1.11 | 1 | 106868.78 | 13739.2145 | 13721.3261 | 3600.394 | NORMAL
313.706 | 0.15 | 305.368 | 1.11 | 2 | 57226.51 | 15530.7444 | 15511.8435 | 6129.83 | NORMAL
313.706 | 0.15 | 305.368 | 1.11 | 2 | 79289.74 | 16415.1231 | 16395.7533 | 5411.206 | NORMAL
313.706 | 0.15 | 305.368 | 1.11 | 2 | 101352.97 | 16922.2157 | 16902.6029 | 5022.498 | NORMAL
313.706 | 0.15 | 305.368 | 1.11 | 2 | 106868.78 | 17014.449 | 16994.7973 | 4953.211 | NORMAL
313.706 | 0.15 | 305.368 | 1.42 | 1 | 57226.51 | 13208.5873 | 13189.3688 | 4358.94 | NORMAL
313.706 | 0.15 | 305.368 | 1.42 | 1 | 79289.74 | 13947.8312 | 13901.9986 | 3903.93 | NORMAL
313.706 | 0.15 | 305.368 | 1.42 | 1 | 101352.97 | 14364.1852 | 14343.8312 | 3652.594 | NORMAL
313.706 | 0.15 | 305.368 | 1.42 | 1 | 106868.78 | 14439.2439 | 14418.8123 | 3607.447 | NORMAL
313.706 | 0.15 | 305.368 | 1.42 | 2 | 57226.51 | 16292.204 | 16270.3561 | 6248.49 | NORMAL
313.706 | 0.15 | 305.368 | 1.42 | 2 | 79289.74 | 17290.592 | 17250.7545 | 5500.97 | NORMAL
313.706 | 0.15 | 305.368 | 1.42 | 2 | 101352.97 | 17878.898 | 17855.8521 | 5091.481 | NORMAL
313.706 | 0.15 | 305.368 | 1.42 | 2 | 106868.78 | 17986.6354 | 17963.5046 | 5018.321 | NORMAL
313.706 | 0.25 | 288.706 | 0.5 | 1 | 57226.51 | 7129.8359 | 7127.3761 | 3983.125 | NORMAL
313.706 | 0.25 | 288.706 | 0.5 | 1 | 79289.74 | 7353.9859 | 7351.5371 | 3744.886 | NORMAL
313.706 | 0.25 | 288.706 | 0.5 | 1 | 101352.97 | 7463.6284 | 7461.1878 | 3626.965 | NORMAL
313.706 | 0.25 | 288.706 | 0.5 | 1 | 106868.78 | 7477.286 | 7474.841 | 3612.0992 | NORMAL
313.706 | 0.25 | 288.706 | 0.5 | 2 | 57226.51 | 9059.9355 | 9057.7068 | 5116.277 | NORMAL
313.706 | 0.25 | 288.706 | 0.5 | 2 | 79289.74 | 9407.7374 | 9272.4259 | 4731.84 | NORMAL
313.706 | 0.25 | 288.706 | 0.5 | 2 | 101352.97 | 9577.755 | 9392.4254 | 4530.6349 | NORMAL
313.706 | 0.25 | 288.706 | 0.5 | 2 | 106868.78 | 9577.3154 | 9511.8257 | 4493.8864 | NORMAL
313.706 | 0.25 | 288.706 | 0.8 | 1 | 57226.51 | 8105.0703 | 8101.2772 | 4035.607 | NORMAL
313.706 | 0.25 | 288.706 | 0.8 | 1 | 79289.74 | 8418.9625 | 8411.4191 | 3758.815 | NORMAL
313.706 | 0.25 | 288.706 | 0.8 | 1 | 101352.97 | 8576.3775 | 8572.5095 | 3619.21 | NORMAL
313.706 | 0.25 | 288.706 | 0.8 | 1 | 106868.78 | 8605.1583 | 8601.2859 | 3593.808 | NORMAL
313.706 | 0.25 | 288.706 | 0.8 | 2 | 57226.51 | 10406.3599 | 10402.3639 | 5325.463 | NORMAL
313.706 | 0.25 | 288.706 | 0.8 | 2 | 79289.74 | 10832.2098 | 10828.2019 | 4867.505 | NORMAL
313.706 | 0.25 | 288.706 | 0.8 | 2 | 101352.97 | 11062.6319 | 11058.6383 | 4624.713 | NORMAL
313.706 | 0.25 | 288.706 | 0.8 | 2 | 106868.78 | 11099.9414 | 11095.9454 | 4586.011 | NORMAL
313.706 | 0.25 | 288.706 | 1.11 | 1 | 57226.51 | 8632.4736 | 8616.5381 | 4066.34 | NORMAL
313.706 | 0.25 | 288.706 | 1.11 | 1 | 79289.74 | 9004.1618 | 8999.3806 | 3770.334 | NORMAL
313.706 | 0.25 | 288.706 | 1.11 | 1 | 101352.97 | 9196.9226 | 9192.085 | 3616.751 | NORMAL
313.706 | 0.25 | 288.706 | 1.11 | 1 | 106868.78 | 9230.1583 | 9225.3124 | 3590.218 | NORMAL
313.706 | 0.25 | 288.706 | 1.11 | 2 | 57226.51 | 11150.7327 | 11145.503 | 5439.78 | NORMAL
313.706 | 0.25 | 288.706 | 1.11 | 2 | 79289.74 | 11669.7538 | 11664.4441 | 4946.976 | NORMAL
313.706 | 0.25 | 288.706 | 1.11 | 2 | 101352.97 | 11954.8359 | 11949.4801 | 4683.473 | NORMAL
313.706 | 0.25 | 288.706 | 1.11 | 2 | 106868.78 | 12007.4736 | 12002.1063 | 4635.555 | NORMAL
313.706 | 0.25 | 288.706 | 1.42 | 1 | 57226.51 | 8972.6553 | 8967.3704 | 4086.24 | NORMAL
313.706 | 0.25 | 288.706 | 1.42 | 1 | 79289.74 | 9385.4045 | 9379.9609 | 3778.17 | NORMAL
313.706 | 0.25 | 288.706 | 1.42 | 1 | 101352.97 | 9602.4033 | 9596.8819 | 3616.377 | NORMAL
313.706 | 0.25 | 288.706 | 1.42 | 1 | 106868.78 | 9640.68 | 9635.1366 | 3587.886 | NORMAL
313.706 | 0.25 | 288.706 | 1.42 | 2 | 57226.51 | 11640.2403 | 11634.1059 | 5515.15 | NORMAL
313.706 | 0.25 | 288.706 | 1.42 | 2 | 79289.74 | 12227.1102 | 12220.8255 | 5000.13 | NORMAL
313.706 | 0.25 | 288.706 | 1.42 | 2 | 101352.97 | 12553.3705 | 12547.0059 | 4723.143 | NORMAL
313.706 | 0.25 | 288.706 | 1.42 | 2 | 106868.78 | 12613.8921 | 12607.5095 | 4672.699 | NORMAL
313.706 | 0.25 | 291.483 | 0.5 | 1 | 57226.51 | 7641.9402 | 7638.7153 | 4009.593 | NORMAL
313.706 | 0.25 | 291.483 | 0.5 | 1 | 79289.74 | 7885.1114 | 7881.9021 | 3753.237 | NORMAL
313.706 | 0.25 | 291.483 | 0.5 | 1 | 101352.97 | 8009.32 | 8006.1163 | 3621.62 | NORMAL
313.706 | 0.25 | 291.483 | 0.5 | 1 | 106868.78 | 8027.8429 | 8024.6398 | 3601.7155 | NORMAL
313.706 | 0.25 | 291.483 | 0.5 | 2 | 57226.51 | 9627.0516 | 9555.2819 | 5204.733 | NORMAL
313.706 | 0.25 | 291.483 | 0.5 | 2 | 79289.74 | 10016.0023 | 9754.5346 | 4789.856 | NORMAL
313.706 | 0.25 | 291.483 | 0.5 | 2 | 101352.97 | 10201.905 | 9912.0689 | 4571.617 | NORMAL
313.706 | 0.25 | 291.483 | 0.5 | 2 | 106868.78 | 10201.5827 | 9983.4728 | 4530.4796 | NORMAL
313.706 | 0.25 | 291.483 | 0.8 | 1 | 57226.51 | 8702.7257 | 8697.7999 | 4069.12 | NORMAL
313.706 | 0.25 | 291.483 | 0.8 | 1 | 79289.74 | 9048.095 | 9043.0914 | 3771.255 | NORMAL
313.706 | 0.25 | 291.483 | 0.8 | 1 | 101352.97 | 9226.9343 | 9221.9057 | 3616.753 | NORMAL
313.706 | 0.25 | 291.483 | 0.8 | 1 | 106868.78 | 9257.6202 | 9252.584 | 3590.048 | NORMAL
313.706 | 0.25 | 291.483 | 0.8 | 2 | 57226.51 | 11045.252 | 11040.0387 | 5423.497 | NORMAL
313.706 | 0.25 | 291.483 | 0.8 | 2 | 79289.74 | 11514.5076 | 11509.28 | 4932.227 | NORMAL
313.706 | 0.25 | 291.483 | 0.8 | 2 | 101352.97 | 11769.5193 | 11764.2937 | 4671.373 | NORMAL
313.706 | 0.25 | 291.483 | 0.8 | 2 | 106868.78 | 11816.8523 | 11811.6174 | 4623.975 | NORMAL
313.706 | 0.25 | 291.483 | 1.11 | 1 | 57226.51 | 9279.8652 | 9258.837 | 4103.7 | NORMAL
313.706 | 0.25 | 291.483 | 1.11 | 1 | 79289.74 | 9691.4713 | 9685.2687 | 3784.941 | NORMAL
313.706 | 0.25 | 291.483 | 1.11 | 1 | 101352.97 | 9908.8804 | 9902.6081 | 3616.465 | NORMAL
313.706 | 0.25 | 291.483 | 1.11 | 1 | 106868.78 | 9947.1278 | 9940.8412 | 3586.828 | NORMAL
313.706 | 0.25 | 291.483 | 1.11 | 2 | 57226.51 | 11852.5205 | 11845.7409 | 5548.04 | NORMAL
313.706 | 0.25 | 291.483 | 1.11 | 2 | 79289.74 | 12426.2016 | 12419.3051 | 5019.189 | NORMAL
313.706 | 0.25 | 291.483 | 1.11 | 2 | 101352.97 | 12743.4935 | 12736.5356 | 4735.747 | NORMAL
313.706 | 0.25 | 291.483 | 1.11 | 2 | 106868.78 | 12802.2567 | 12795.2923 | 4684.189 | NORMAL
313.706 | 0.25 | 291.483 | 1.42 | 1 | 57226.51 | 9652.3447 | 9645.5012 | 4126.4 | NORMAL
313.706 | 0.25 | 291.483 | 1.42 | 1 | 79289.74 | 10110.8734 | 10103.8059 | 3794.55 | NORMAL
313.706 | 0.25 | 291.483 | 1.42 | 1 | 101352.97 | 10355.129 | 10337.898 | 3618.226 | NORMAL
313.706 | 0.25 | 291.483 | 1.42 | 1 | 106868.78 | 10397.8312 | 10390.6463 | 3587.378 | NORMAL
313.706 | 0.25 | 291.483 | 1.42 | 2 | 57226.51 | 12383.5873 | 12374.5102 | 5630.67 | NORMAL
313.706 | 0.25 | 291.483 | 1.42 | 2 | 79289.74 | 13034.1735 | 13026.0402 | 5077.47 | NORMAL
313.706 | 0.25 | 291.483 | 1.42 | 2 | 101352.97 | 13397.9191 | 13389.6794 | 4779.251 | NORMAL
313.706 | 0.25 | 291.483 | 1.42 | 2 | 106868.78 | 13465.2696 | 13457.0154 | 4725.082 | NORMAL
313.706 | 0.25 | 294.26 | 0.5 | 1 | 57226.51 | 8159.027 | 8154.9067 | 4038.187 | NORMAL
313.706 | 0.25 | 294.26 | 0.5 | 1 | 79289.74 | 8428.0188 | 8423.9059 | 3759.023 | NORMAL
313.706 | 0.25 | 294.26 | 0.5 | 1 | 101352.97 | 8561.1665 | 8557.0657 | 3619.145 | NORMAL
313.706 | 0.25 | 294.26 | 0.5 | 1 | 106868.78 | 8585.5217 | 8581.4264 | 3593.6937 | NORMAL
313.706 | 0.25 | 294.26 | 0.5 | 2 | 57226.51 | 10226.3189 | 9999.3048 | 5294.476 | NORMAL
313.706 | 0.25 | 294.26 | 0.5 | 2 | 79289.74 | 10650.2345 | 10243.2038 | 4850.27 | NORMAL
313.706 | 0.25 | 294.26 | 0.5 | 2 | 101352.97 | 10857.5322 | 10432.8833 | 4610.88 | NORMAL
313.706 | 0.25 | 294.26 | 0.5 | 2 | 106868.78 | 10850.7913 | 10514.3951 | 4569.3682 | NORMAL
313.706 | 0.25 | 294.26 | 0.8 | 1 | 57226.51 | 9308.3236 | 9302.0591 | 4105.385 | NORMAL
313.706 | 0.25 | 294.26 | 0.8 | 1 | 79289.74 | 9688.9215 | 9682.5655 | 3784.909 | NORMAL
313.706 | 0.25 | 294.26 | 0.8 | 1 | 101352.97 | 9888.8042 | 9882.3963 | 3616.493 | NORMAL
313.706 | 0.25 | 294.26 | 0.8 | 1 | 106868.78 | 9923.7104 | 9917.2997 | 3586.848 | NORMAL
313.706 | 0.25 | 294.26 | 0.8 | 2 | 57226.51 | 11697.3623 | 11690.7182 | 5523.991 | NORMAL
313.706 | 0.25 | 294.26 | 0.8 | 2 | 79289.74 | 12211.6061 | 12204.9386 | 4998.738 | NORMAL
313.706 | 0.25 | 294.26 | 0.8 | 2 | 101352.97 | 12493.0832 | 12486.3994 | 4719.228 | NORMAL
313.706 | 0.25 | 294.26 | 0.8 | 2 | 106868.78 | 12545.0176 | 12538.3311 | 4668.465 | NORMAL
313.706 | 0.25 | 294.26 | 1.11 | 1 | 57226.51 | 9937.163 | 9912.4592 | 4143.21 | NORMAL
313.706 | 0.25 | 294.26 | 1.11 | 1 | 79289.74 | 10391.3834 | 10380.5971 | 3801.24 | NORMAL
313.706 | 0.25 | 294.26 | 1.11 | 1 | 101352.97 | 10633.1184 | 10625.1329 | 3619.763 | NORMAL
313.706 | 0.25 | 294.26 | 1.11 | 1 | 106868.78 | 10676.993 | 10669.0066 | 3586.967 | NORMAL
313.706 | 0.25 | 294.26 | 1.11 | 2 | 57226.51 | 12567.9953 | 12559.4114 | 5659.47 | NORMAL
313.706 | 0.25 | 294.26 | 1.11 | 2 | 79289.74 | 13199.4724 | 13190.7344 | 5093.422 | NORMAL
313.706 | 0.25 | 294.26 | 1.11 | 2 | 101352.97 | 13550.4689 | 13541.634 | 4789.494 | NORMAL
313.706 | 0.25 | 294.26 | 1.11 | 2 | 106868.78 | 13615.2989 | 13606.4626 | 4734.347 | NORMAL
313.706 | 0.25 | 294.26 | 1.42 | 1 | 57226.51 | 10343.728 | 10300.8119 | 4168.64 | NORMAL
313.706 | 0.25 | 294.26 | 1.42 | 1 | 79289.74 | 10851.2603 | 10842.308 | 3812.62 | NORMAL
313.706 | 0.25 | 294.26 | 1.42 | 1 | 101352.97 | 11129.5135 | 11120.4095 | 3619.013 | NORMAL
313.706 | 0.25 | 294.26 | 1.42 | 1 | 106868.78 | 11175.762 | 11162.8428 | 3586.782 | NORMAL
313.706 | 0.25 | 294.26 | 1.42 | 2 | 57226.51 | 13139.4783 | 13117.2069 | 5750.92 | NORMAL
313.706 | 0.25 | 294.26 | 1.42 | 2 | 79289.74 | 13858.4701 | 13848.201 | 5157.34 | NORMAL
313.706 | 0.25 | 294.26 | 1.42 | 2 | 101352.97 | 14262.2509 | 14251.8109 | 4837.514 | NORMAL
313.706 | 0.25 | 294.26 | 1.42 | 2 | 106868.78 | 14337.3095 | 14326.8433 | 4779.33 | NORMAL
313.706 | 0.25 | 297.037 | 0.5 | 1 | 57226.51 | 8682.8839 | 8677.7089 | 4067.786 | NORMAL
313.706 | 0.25 | 297.037 | 0.5 | 1 | 79289.74 | 8974.2673 | 8969.1071 | 3769.764 | NORMAL
313.706 | 0.25 | 297.037 | 0.5 | 1 | 101352.97 | 9122.2743 | 9117.1202 | 3616.89 | NORMAL
313.706 | 0.25 | 297.037 | 0.5 | 1 | 106868.78 | 9147.0399 | 9141.8901 | 3590.7016 | NORMAL
313.706 | 0.25 | 297.037 | 0.5 | 2 | 57226.51 | 10830.3048 | 10576.9298 | 5391.17 | NORMAL
313.706 | 0.25 | 297.037 | 0.5 | 2 | 79289.74 | 11312.8371 | 10790.184 | 4913.151 | NORMAL
313.706 | 0.25 | 297.037 | 0.5 | 2 | 101352.97 | 11536.313 | 10951.6411 | 4655.986 | NORMAL
313.706 | 0.25 | 297.037 | 0.5 | 2 | 106868.78 | 11529.279 | 11021.1606 | 4608.2595 | NORMAL
313.706 | 0.25 | 297.037 | 0.8 | 1 | 57226.51 | 9924.2087 | 9914.5524 | 4142.001 | NORMAL
313.706 | 0.25 | 297.037 | 0.8 | 1 | 79289.74 | 10340.8558 | 10332.3556 | 3800.008 | NORMAL
313.706 | 0.25 | 297.037 | 0.8 | 1 | 101352.97 | 10561.2837 | 10553.2782 | 3618.55 | NORMAL
313.706 | 0.25 | 297.037 | 0.8 | 1 | 106868.78 | 10599.4431 | 10591.43 | 3587.099 | NORMAL
313.706 | 0.25 | 297.037 | 0.8 | 2 | 57226.51 | 12361.6354 | 12350.7324 | 5627.233 | NORMAL
313.706 | 0.25 | 297.037 | 0.8 | 2 | 79289.74 | 12923.5053 | 12915.1567 | 5066.891 | NORMAL
313.706 | 0.25 | 297.037 | 0.8 | 2 | 101352.97 | 13231.7702 | 13223.4077 | 4768.248 | NORMAL
313.706 | 0.25 | 297.037 | 0.8 | 2 | 106868.78 | 13288.3939 | 13280.0222 | 4714.137 | NORMAL
313.706 | 0.25 | 297.037 | 1.11 | 1 | 57226.51 | 10605.4807 | 10582.8061 | 4184.6 | NORMAL
313.706 | 0.25 | 297.037 | 1.11 | 1 | 79289.74 | 11105.2462 | 11095.4291 | 3819.149 | NORMAL
313.706 | 0.25 | 297.037 | 1.11 | 1 | 101352.97 | 11377.8136 | 11367.858 | 3620.844 | NORMAL
313.706 | 0.25 | 297.037 | 1.11 | 1 | 106868.78 | 11423.4173 | 11413.4447 | 3587.515 | NORMAL
313.706 | 0.25 | 297.037 | 1.11 | 2 | 57226.51 | 13295.2814 | 13284.6185 | 5775.11 | NORMAL
313.706 | 0.25 | 297.037 | 1.11 | 2 | 79289.74 | 13988.1594 | 13977.2627 | 5169.962 | NORMAL
313.706 | 0.25 | 297.037 | 1.11 | 2 | 101352.97 | 14374.5018 | 14363.4909 | 4845.181 | NORMAL
313.706 | 0.25 | 297.037 | 1.11 | 2 | 106868.78 | 14446.0141 | 14434.9918 | 4786.174 | NORMAL
313.706 | 0.25 | 297.037 | 1.42 | 1 | 57226.51 | 11046.5416 | 11035.7602 | 4212.89 | NORMAL
313.706 | 0.25 | 297.037 | 1.42 | 1 | 79289.74 | 11606.9461 | 11595.7802 | 3832.63 | NORMAL
313.706 | 0.25 | 297.037 | 1.42 | 1 | 101352.97 | 11915.6213 | 11904.2658 | 3624.899 | NORMAL
313.706 | 0.25 | 297.037 | 1.42 | 1 | 106868.78 | 11970.4572 | 11959.0613 | 3588.074 | NORMAL
313.706 | 0.25 | 297.037 | 1.42 | 2 | 57226.51 | 13911.782 | 13877.8929 | 5872.31 | NORMAL
313.706 | 0.25 | 297.037 | 1.42 | 2 | 79289.74 | 14699.2087 | 14686.4351 | 5239.76 | NORMAL
313.706 | 0.25 | 297.037 | 1.42 | 2 | 101352.97 | 15145.2814 | 15132.3018 | 4897.802 | NORMAL
313.706 | 0.25 | 297.037 | 1.42 | 2 | 106868.78 | 15228.1067 | 15215.0866 | 4835.757 | NORMAL
313.706 | 0.25 | 299.814 | 0.5 | 1 | 57226.51 | 9214.7128 | 9208.3362 | 4099.018 | NORMAL
313.706 | 0.25 | 299.814 | 0.5 | 1 | 79289.74 | 9529.2204 | 9522.8549 | 3781.416 | NORMAL
313.706 | 0.25 | 299.814 | 0.5 | 1 | 101352.97 | 9626.905 | 9620.6187 | 3616.25 | NORMAL
313.706 | 0.25 | 299.814 | 0.5 | 1 | 106868.78 | 9719.1676 | 9712.8113 | 3587.66 | NORMAL
313.706 | 0.25 | 299.814 | 0.5 | 2 | 57226.51 | 11547.8898 | 10850.0855 | 5500.371 | NORMAL
313.706 | 0.25 | 299.814 | 0.5 | 2 | 79289.74 | 12054.279 | 11155.4638 | 4980.24 | NORMAL
313.706 | 0.25 | 299.814 | 0.5 | 2 | 101352.97 | 12287.2802 | 11404.7831 | 4705.428 | NORMAL
313.706 | 0.25 | 299.814 | 0.5 | 2 | 106868.78 | 12257.9132 | 11562.8651 | 4653.1489 | NORMAL
313.706 | 0.25 | 299.814 | 0.8 | 1 | 57226.51 | 10549.3259 | 10529.1978 | 4180.788 | NORMAL
313.706 | 0.25 | 299.814 | 0.8 | 1 | 79289.74 | 11003.5756 | 10993.8154 | 3816.538 | NORMAL
313.706 | 0.25 | 299.814 | 0.8 | 1 | 101352.97 | 11249.6483 | 11239.8049 | 3620.016 | NORMAL
313.706 | 0.25 | 299.814 | 0.8 | 1 | 106868.78 | 11289.4197 | 11279.564 | 3587.802 | NORMAL
313.706 | 0.25 | 299.814 | 0.8 | 2 | 57226.51 | 13035.8441 | 13025.6501 | 5734.533 | NORMAL
313.706 | 0.25 | 299.814 | 0.8 | 2 | 79289.74 | 13648.2708 | 13637.9937 | 5136.902 | NORMAL
313.706 | 0.25 | 299.814 | 0.8 | 2 | 101352.97 | 13984.789 | 13974.4822 | 4818.869 | NORMAL
313.706 | 0.25 | 299.814 | 0.8 | 2 | 106868.78 | 14046.9812 | 14036.6708 | 4761.154 | NORMAL
313.706 | 0.25 | 299.814 | 1.11 | 1 | 57226.51 | 11284.2028 | 11270.8875 | 4227.82 | NORMAL
313.706 | 0.25 | 299.814 | 1.11 | 1 | 79289.74 | 11831.9461 | 11819.8893 | 3838.854 | NORMAL
313.706 | 0.25 | 299.814 | 1.11 | 1 | 101352.97 | 12133.1477 | 12120.9054 | 3626.824 | NORMAL
313.706 | 0.25 | 299.814 | 1.11 | 1 | 106868.78 | 12186.6061 | 12174.3342 | 3589.168 | NORMAL
313.706 | 0.25 | 299.814 | 1.11 | 2 | 57226.51 | 14037.2216 | 14024.167 | 5892.2 | NORMAL
313.706 | 0.25 | 299.814 | 1.11 | 2 | 79289.74 | 14791.2661 | 14777.9096 | 5248.898 | NORMAL
313.706 | 0.25 | 299.814 | 1.11 | 2 | 101352.97 | 15215.5041 | 15201.9927 | 4902.652 | NORMAL
313.706 | 0.25 | 299.814 | 1.11 | 2 | 106868.78 | 15294.0211 | 15280.4859 | 4839.989 | NORMAL
313.706 | 0.25 | 299.814 | 1.42 | 1 | 57226.51 | 11761.4889 | 11748.2689 | 4259.56 | NORMAL
313.706 | 0.25 | 299.814 | 1.42 | 1 | 79289.74 | 12377.0223 | 12363.3333 | 3854.5 | NORMAL
313.706 | 0.25 | 299.814 | 1.42 | 1 | 101352.97 | 12719.109 | 12705.1434 | 3632.385 | NORMAL
313.706 | 0.25 | 299.814 | 1.42 | 1 | 106868.78 | 12779.9238 | 12765.9298 | 3592.779 | NORMAL
313.706 | 0.25 | 299.814 | 1.42 | 2 | 57226.51 | 14698.6811 | 14658.7595 | 5996.79 | NORMAL
313.706 | 0.25 | 299.814 | 1.42 | 2 | 79289.74 | 15556.272 | 15540.6224 | 5324.61 | NORMAL
313.706 | 0.25 | 299.814 | 1.42 | 2 | 101352.97 | 16045.8089 | 16022.1734 | 4960.428 | NORMAL
313.706 | 0.25 | 299.814 | 1.42 | 2 | 106868.78 | 16134.8476 | 16118.8902 | 4895.537 | NORMAL
313.706 | 0.25 | 302.591 | 0.5 | 1 | 57226.51 | 9754.1032 | 9746.3487 | 4131.451 | NORMAL
313.706 | 0.25 | 302.591 | 0.5 | 1 | 79289.74 | 9994.7245 | 9987.1085 | 3790.437 | NORMAL
313.706 | 0.25 | 302.591 | 0.5 | 1 | 101352.97 | 10216.2368 | 10208.5338 | 3618.1 | NORMAL
313.706 | 0.25 | 302.591 | 0.5 | 1 | 106868.78 | 10218.6401 | 10210.9863 | 3586.1696 | NORMAL
313.706 | 0.25 | 302.591 | 0.5 | 2 | 57226.51 | 12267.2333 | 11264.4851 | 5610.008 | NORMAL
313.706 | 0.25 | 302.591 | 0.5 | 2 | 79289.74 | 12816.0317 | 11592.4467 | 5052.766 | NORMAL
313.706 | 0.25 | 302.591 | 0.5 | 2 | 101352.97 | 13057.4736 | 11855.2981 | 4756.541 | NORMAL
313.706 | 0.25 | 302.591 | 0.5 | 2 | 106868.78 | 13036.0492 | 11967.0932 | 4700.1824 | NORMAL
313.706 | 0.25 | 302.591 | 0.8 | 1 | 57226.51 | 11184.1442 | 11156.3292 | 4221.168 | NORMAL
313.706 | 0.25 | 302.591 | 0.8 | 1 | 79289.74 | 11678.2825 | 11665.4131 | 3834.631 | NORMAL
313.706 | 0.25 | 302.591 | 0.8 | 1 | 101352.97 | 11946.8054 | 11934.8586 | 3625.173 | NORMAL
313.706 | 0.25 | 302.591 | 0.8 | 1 | 106868.78 | 11994.3142 | 11982.3558 | 3588.208 | NORMAL
313.706 | 0.25 | 302.591 | 0.8 | 2 | 57226.51 | 13723.5346 | 13711.156 | 5842.662 | NORMAL
313.706 | 0.25 | 302.591 | 0.8 | 2 | 79289.74 | 14193.0539 | 14181.004 | 5191.468 | NORMAL
313.706 | 0.25 | 302.591 | 0.8 | 2 | 101352.97 | 14551.8757 | 14539.7977 | 4856.878 | NORMAL
313.706 | 0.25 | 302.591 | 0.8 | 2 | 106868.78 | 14656.4478 | 14644.2097 | 4799.858 | NORMAL
313.706 | 0.25 | 302.591 | 1.11 | 1 | 57226.51 | 11975.0293 | 11960.8389 | 4273.25 | NORMAL
313.706 | 0.25 | 302.591 | 1.11 | 1 | 79289.74 | 12572.7139 | 12558.0919 | 3860.333 | NORMAL
313.706 | 0.25 | 302.591 | 1.11 | 1 | 101352.97 | 12903.517 | 12888.665 | 3634.313 | NORMAL
313.706 | 0.25 | 302.591 | 1.11 | 1 | 106868.78 | 12962.3974 | 12947.5166 | 3594.066 | NORMAL
313.706 | 0.25 | 302.591 | 1.11 | 2 | 57226.51 | 14792.2626 | 14776.4793 | 6011.86 | NORMAL
313.706 | 0.25 | 302.591 | 1.11 | 2 | 79289.74 | 15608.9097 | 15592.7389 | 5329.894 | NORMAL
313.706 | 0.25 | 302.591 | 1.11 | 2 | 101352.97 | 16072.0106 | 16055.6492 | 4962.285 | NORMAL
313.706 | 0.25 | 302.591 | 1.11 | 2 | 106868.78 | 16157.796 | 16141.3959 | 4895.671 | NORMAL
313.706 | 0.25 | 302.591 | 1.42 | 1 | 57226.51 | 12489.0094 | 12449.0695 | 4308.66 | NORMAL
313.706 | 0.25 | 302.591 | 1.42 | 1 | 79289.74 | 13163.1008 | 13146.5022 | 3878.43 | NORMAL
313.706 | 0.25 | 302.591 | 1.42 | 1 | 101352.97 | 13539.2439 | 13522.3062 | 3641.698 | NORMAL
313.706 | 0.25 | 302.591 | 1.42 | 1 | 106868.78 | 13607.1512 | 13590.1559 | 3599.268 | NORMAL
313.706 | 0.25 | 302.591 | 1.42 | 2 | 57226.51 | 15498.9742 | 15467.8368 | 6124.77 | NORMAL
313.706 | 0.25 | 302.591 | 1.42 | 2 | 79289.74 | 16426.5533 | 16407.6792 | 5412.49 | NORMAL
313.706 | 0.25 | 302.591 | 1.42 | 2 | 101352.97 | 16963.8042 | 16944.5673 | 5025.457 | NORMAL
313.706 | 0.25 | 302.591 | 1.42 | 2 | 106868.78 | 17061.6061 | 17039.1872 | 4956.331 | NORMAL
313.706 | 0.25 | 305.368 | 0.5 | 1 | 57226.51 | 10148.6518 | 10139.6804 | 4155.698 | NORMAL
313.706 | 0.25 | 305.368 | 0.5 | 1 | 79289.74 | 10617.6436 | 10608.3744 | 3805.391 | NORMAL
313.706 | 0.25 | 305.368 | 0.5 | 1 | 101352.97 | 10873.7397 | 10769.1779 | 3619.899 | NORMAL
313.706 | 0.25 | 305.368 | 0.5 | 1 | 106868.78 | 10851.1137 | 10841.8252 | 3586.985 | NORMAL
313.706 | 0.25 | 305.368 | 0.5 | 2 | 57226.51 | 13008.9097 | 11652.7049 | 5726.709 | NORMAL
313.706 | 0.25 | 305.368 | 0.5 | 2 | 79289.74 | 13605.0997 | 11998.1605 | 5131.675 | NORMAL
313.706 | 0.25 | 305.368 | 0.5 | 2 | 101352.97 | 13874.9414 | 12303.6459 | 4808.667 | NORMAL
313.706 | 0.25 | 305.368 | 0.5 | 2 | 106868.78 | 13844.7831 | 12426.8697 | 4749.9695 | NORMAL
313.706 | 0.25 | 305.368 | 0.8 | 1 | 57226.51 | 11828.5756 | 11801.7839 | 4263.591 | NORMAL
313.706 | 0.25 | 305.368 | 0.8 | 1 | 79289.74 | 12364.8886 | 12350.7061 | 3854.175 | NORMAL
313.706 | 0.25 | 305.368 | 0.8 | 1 | 101352.97 | 12657.2392 | 12642.9238 | 3631.794 | NORMAL
313.706 | 0.25 | 305.368 | 0.8 | 1 | 106868.78 | 12709.1149 | 12694.7663 | 3592.297 | NORMAL
313.706 | 0.25 | 305.368 | 0.8 | 2 | 57226.51 | 14424.0328 | 14409.2193 | 5953.144 | NORMAL
313.706 | 0.25 | 305.368 | 0.8 | 2 | 79289.74 | 14870.5451 | 14856.2545 | 5257.798 | NORMAL
313.706 | 0.25 | 305.368 | 0.8 | 2 | 101352.97 | 15410.2286 | 15395.5581 | 4914.058 | NORMAL
313.706 | 0.25 | 305.368 | 0.8 | 2 | 106868.78 | 15413.5698 | 15399.0193 | 4849.743 | NORMAL
313.706 | 0.25 | 305.368 | 1.11 | 1 | 57226.51 | 12676.7585 | 12659.797 | 4321.12 | NORMAL
313.706 | 0.25 | 305.368 | 1.11 | 1 | 79289.74 | 13327.6377 | 13301.8354 | 3883.605 | NORMAL
313.706 | 0.25 | 305.368 | 1.11 | 1 | 101352.97 | 13689.0973 | 13671.3015 | 3643.542 | NORMAL
313.706 | 0.25 | 305.368 | 1.11 | 1 | 106868.78 | 13753.9859 | 13736.147 | 3600.539 | NORMAL
313.706 | 0.25 | 305.368 | 1.11 | 2 | 57226.51 | 15560.6682 | 15541.8243 | 6134.55 | NORMAL
313.706 | 0.25 | 305.368 | 1.11 | 2 | 79289.74 | 16440.0645 | 16420.7474 | 5413.746 | NORMAL
313.706 | 0.25 | 305.368 | 1.11 | 2 | 101352.97 | 16943.5815 | 16924.0116 | 5024.038 | NORMAL
313.706 | 0.25 | 305.368 | 1.11 | 2 | 106868.78 | 17034.8476 | 17015.2235 | 4954.574 | NORMAL
313.706 | 0.25 | 305.368 | 1.42 | 1 | 57226.51 | 13227.6964 | 13157.9864 | 4360.27 | NORMAL
313.706 | 0.25 | 305.368 | 1.42 | 1 | 79289.74 | 13963.6577 | 13901.2681 | 3904.46 | NORMAL
313.706 | 0.25 | 305.368 | 1.42 | 1 | 101352.97 | 14377.5498 | 14353.9131 | 3652.789 | NORMAL
313.706 | 0.25 | 305.368 | 1.42 | 1 | 106868.78 | 14452.1395 | 14431.762 | 3607.59 | NORMAL
313.706 | 0.25 | 305.368 | 1.42 | 2 | 57226.51 | 16318.6108 | 16296.8581 | 6252.56 | NORMAL
313.706 | 0.25 | 305.368 | 1.42 | 2 | 79289.74 | 17312.5147 | 17289.9565 | 5503.26 | NORMAL
313.706 | 0.25 | 305.368 | 1.42 | 2 | 101352.97 | 17897.5381 | 17874.5398 | 5092.866 | NORMAL
313.706 | 0.25 | 305.368 | 1.42 | 2 | 106868.78 | 18004.6307 | 17981.5668 | 5019.552 | NORMAL
313.706 | 0.35 | 288.706 | 0.5 | 1 | 57226.51 | 7103.6342 | 7101.1835 | 3980.71 | NORMAL
313.706 | 0.35 | 288.706 | 0.5 | 1 | 79289.74 | 7376.4361 | 7264.034 | 3747.604 | NORMAL
313.706 | 0.35 | 288.706 | 0.5 | 1 | 101352.97 | 7506.8581 | 7368.822 | 3628.894 | NORMAL
313.706 | 0.35 | 288.706 | 0.5 | 1 | 106868.78 | 7490.0352 | 7430.819 | 3611.9887 | NORMAL
313.706 | 0.35 | 288.706 | 0.5 | 2 | 57226.51 | 9564.2145 | 8356.8185 | 5193.123 | NORMAL
313.706 | 0.35 | 288.706 | 0.5 | 2 | 79289.74 | 9853.8394 | 8687.2138 | 4773.906 | NORMAL
313.706 | 0.35 | 288.706 | 0.5 | 2 | 101352.97 | 9968.6108 | 8913.214 | 4557.1182 | NORMAL
313.706 | 0.35 | 288.706 | 0.5 | 2 | 106868.78 | 9953.4291 | 8987.8668 | 4516.0357 | NORMAL
313.706 | 0.35 | 288.706 | 0.8 | 1 | 57226.51 | 8111.1958 | 8107.4079 | 4035.904 | NORMAL
313.706 | 0.35 | 288.706 | 0.8 | 1 | 79289.74 | 8423.8863 | 8420.045 | 3758.785 | NORMAL
313.706 | 0.35 | 288.706 | 0.8 | 1 | 101352.97 | 8580.3341 | 8576.473 | 3619.191 | NORMAL
313.706 | 0.35 | 288.706 | 0.8 | 1 | 106868.78 | 8609.32 | 8605.4459 | 3593.463 | NORMAL
313.706 | 0.35 | 288.706 | 0.8 | 2 | 57226.51 | 10339.449 | 10335.5924 | 5311.963 | NORMAL
313.706 | 0.35 | 288.706 | 0.8 | 2 | 79289.74 | 10853.898 | 10849.9038 | 4869.698 | NORMAL
313.706 | 0.35 | 288.706 | 0.8 | 2 | 101352.97 | 11126.2896 | 11033.1737 | 4629.013 | NORMAL
313.706 | 0.35 | 288.706 | 0.8 | 2 | 106868.78 | 11129.9238 | 11125.9282 | 4585.756 | NORMAL
313.706 | 0.35 | 288.706 | 1.11 | 1 | 57226.51 | 8637.4267 | 8629.2212 | 4066.61 | NORMAL
313.706 | 0.35 | 288.706 | 1.11 | 1 | 79289.74 | 9008.1184 | 9003.3351 | 3770.419 | NORMAL
313.706 | 0.35 | 288.706 | 1.11 | 1 | 101352.97 | 9200.2052 | 9195.3751 | 3616.751 | NORMAL
313.706 | 0.35 | 288.706 | 1.11 | 1 | 106868.78 | 9233.3236 | 9228.4853 | 3590.197 | NORMAL
313.706 | 0.35 | 288.706 | 1.11 | 2 | 57226.51 | 11158.177 | 11141.6629 | 5440.87 | NORMAL
313.706 | 0.35 | 288.706 | 1.11 | 2 | 79289.74 | 11675.4982 | 11668.2127 | 4947.534 | NORMAL
313.706 | 0.35 | 288.706 | 1.11 | 2 | 101352.97 | 11959.6717 | 11954.3138 | 4683.795 | NORMAL
313.706 | 0.35 | 288.706 | 1.11 | 2 | 106868.78 | 12012.1043 | 12006.7469 | 4635.82 | NORMAL
313.706 | 0.35 | 288.706 | 1.42 | 1 | 57226.51 | 8976.8757 | 8959.0746 | 4086.49 | NORMAL
313.706 | 0.35 | 288.706 | 1.42 | 1 | 79289.74 | 9388.6284 | 9379.8594 | 3778.24 | NORMAL
313.706 | 0.35 | 288.706 | 1.42 | 1 | 101352.97 | 9605.2169 | 9599.7035 | 3616.389 | NORMAL
313.706 | 0.35 | 288.706 | 1.42 | 1 | 106868.78 | 9643.3763 | 9637.841 | 3587.878 | NORMAL
313.706 | 0.35 | 288.706 | 1.42 | 2 | 57226.51 | 11646.3365 | 11640.1988 | 5516.09 | NORMAL
313.706 | 0.35 | 288.706 | 1.42 | 2 | 79289.74 | 12232.1219 | 12216.3669 | 5000.62 | NORMAL
313.706 | 0.35 | 288.706 | 1.42 | 2 | 101352.97 | 12557.5909 | 12551.2242 | 4723.428 | NORMAL
313.706 | 0.35 | 288.706 | 1.42 | 2 | 106868.78 | 12617.9367 | 12611.552 | 4672.943 | NORMAL
313.706 | 0.35 | 291.483 | 0.5 | 1 | 57226.51 | 7705.3634 | 7672.4923 | 4011.404 | NORMAL
313.706 | 0.35 | 291.483 | 0.5 | 1 | 79289.74 | 7973.3587 | 7823.8343 | 3754.473 | NORMAL
313.706 | 0.35 | 291.483 | 0.5 | 1 | 101352.97 | 8104.0739 | 7947.884 | 3620.723 | NORMAL
313.706 | 0.35 | 291.483 | 0.5 | 1 | 106868.78 | 8086.8992 | 7966.3478 | 3600.7732 | NORMAL
313.706 | 0.35 | 291.483 | 0.5 | 2 | 57226.51 | 10217.7608 | 8710.9885 | 5293.041 | NORMAL
313.706 | 0.35 | 291.483 | 0.5 | 2 | 79289.74 | 10541.9988 | 9108.3081 | 4839.686 | NORMAL
313.706 | 0.35 | 291.483 | 0.5 | 2 | 101352.97 | 10674.0035 | 9375.3936 | 4598.529 | NORMAL
313.706 | 0.35 | 291.483 | 0.5 | 2 | 106868.78 | 10649.2087 | 9455.0703 | 4557.8602 | NORMAL
313.706 | 0.35 | 291.483 | 0.8 | 1 | 57226.51 | 8710.6682 | 8699.9018 | 4069.584 | NORMAL
313.706 | 0.35 | 291.483 | 0.8 | 1 | 79289.74 | 9054.3962 | 9049.4073 | 3771.378 | NORMAL
313.706 | 0.35 | 291.483 | 0.8 | 1 | 101352.97 | 9231.8581 | 9226.8268 | 3616.712 | NORMAL
313.706 | 0.35 | 291.483 | 0.8 | 1 | 106868.78 | 9262.8077 | 9257.7688 | 3589.854 | NORMAL
313.706 | 0.35 | 291.483 | 0.8 | 2 | 57226.51 | 11057.034 | 11051.8704 | 5422.255 | NORMAL
313.706 | 0.35 | 291.483 | 0.8 | 2 | 79289.74 | 11571.9226 | 11462.3712 | 4937.624 | NORMAL
313.706 | 0.35 | 291.483 | 0.8 | 2 | 101352.97 | 11874.9707 | 11685.3749 | 4678.494 | NORMAL
313.706 | 0.35 | 291.483 | 0.8 | 2 | 106868.78 | 11887.544 | 11853.1414 | 4629.731 | NORMAL
313.706 | 0.35 | 291.483 | 1.11 | 1 | 57226.51 | 9286.1958 | 9280.1598 | 4104.2 | NORMAL
313.706 | 0.35 | 291.483 | 1.11 | 1 | 79289.74 | 9696.6882 | 9689.0957 | 3785.057 | NORMAL
313.706 | 0.35 | 291.483 | 1.11 | 1 | 101352.97 | 9913.2181 | 9906.943 | 3616.478 | NORMAL
313.706 | 0.35 | 291.483 | 1.11 | 1 | 106868.78 | 9951.2896 | 9945.0103 | 3586.823 | NORMAL
313.706 | 0.35 | 291.483 | 1.11 | 2 | 57226.51 | 11861.7233 | 11854.9621 | 5549.48 | NORMAL
313.706 | 0.35 | 291.483 | 1.11 | 2 | 79289.74 | 12433.7046 | 12426.8163 | 5019.91 | NORMAL
313.706 | 0.35 | 291.483 | 1.11 | 2 | 101352.97 | 12634.6717 | 12627.7732 | 4729.422 | NORMAL
313.706 | 0.35 | 291.483 | 1.11 | 2 | 106868.78 | 12806.8875 | 12799.9333 | 4685.658 | NORMAL
313.706 | 0.35 | 291.483 | 1.42 | 1 | 57226.51 | 9657.7374 | 9623.6939 | 4126.74 | NORMAL
313.706 | 0.35 | 291.483 | 1.42 | 1 | 79289.74 | 10115.3283 | 10108.288 | 3794.66 | NORMAL
313.706 | 0.35 | 291.483 | 1.42 | 1 | 101352.97 | 10358.8511 | 10351.6931 | 3618.235 | NORMAL
313.706 | 0.35 | 291.483 | 1.42 | 1 | 106868.78 | 10401.4068 | 10394.2194 | 3587.378 | NORMAL
313.706 | 0.35 | 291.483 | 1.42 | 2 | 57226.51 | 12391.4713 | 12383.5779 | 5631.9 | NORMAL
313.706 | 0.35 | 291.483 | 1.42 | 2 | 79289.74 | 13040.6799 | 13032.5556 | 5078.11 | NORMAL
313.706 | 0.35 | 291.483 | 1.42 | 2 | 101352.97 | 13403.4291 | 13395.186 | 4779.622 | NORMAL
313.706 | 0.35 | 291.483 | 1.42 | 2 | 106868.78 | 13470.6038 | 13460.622 | 4725.404 | NORMAL
313.706 | 0.35 | 294.26 | 0.5 | 1 | 57226.51 | 8312.8957 | 7931.6829 | 4046.637 | NORMAL
313.706 | 0.35 | 294.26 | 0.5 | 1 | 79289.74 | 8639.0973 | 8084.9079 | 3762.469 | NORMAL
313.706 | 0.35 | 294.26 | 0.5 | 1 | 101352.97 | 8781.3599 | 8223.3308 | 3617.92 | NORMAL
313.706 | 0.35 | 294.26 | 0.5 | 1 | 106868.78 | 8755.3341 | 8318.5743 | 3594.1242 | NORMAL
313.706 | 0.35 | 294.26 | 0.5 | 2 | 57226.51 | 10906.9461 | 9113.4842 | 5402.015 | NORMAL
313.706 | 0.35 | 294.26 | 0.5 | 2 | 79289.74 | 11264.0094 | 9549.7511 | 4908.261 | NORMAL
313.706 | 0.35 | 294.26 | 0.5 | 2 | 101352.97 | 11405.129 | 9745.0098 | 4648.059 | NORMAL
313.706 | 0.35 | 294.26 | 0.5 | 2 | 106868.78 | 11380.891 | 9842.3538 | 4599.2729 | NORMAL
313.706 | 0.35 | 294.26 | 0.8 | 1 | 57226.51 | 9318.6401 | 9312.3873 | 4105.958 | NORMAL
313.706 | 0.35 | 294.26 | 0.8 | 1 | 79289.74 | 9696.9812 | 9690.6297 | 3785.104 | NORMAL
313.706 | 0.35 | 294.26 | 0.8 | 1 | 101352.97 | 9895.5451 | 9889.1526 | 3616.503 | NORMAL
313.706 | 0.35 | 294.26 | 0.8 | 1 | 106868.78 | 9930.0703 | 9923.6654 | 3586.838 | NORMAL
313.706 | 0.35 | 294.26 | 0.8 | 2 | 57226.51 | 11777.6084 | 11698.3334 | 5537.058 | NORMAL
313.706 | 0.35 | 294.26 | 0.8 | 2 | 79289.74 | 12409.1442 | 11947.0401 | 5017.663 | NORMAL
313.706 | 0.35 | 294.26 | 0.8 | 2 | 101352.97 | 12736.3423 | 12201.8999 | 4734.925 | NORMAL
313.706 | 0.35 | 294.26 | 0.8 | 2 | 106868.78 | 12730.0703 | 12350.0777 | 4681.407 | NORMAL
313.706 | 0.35 | 294.26 | 1.11 | 1 | 57226.51 | 9945.1934 | 9937.5356 | 4143.91 | NORMAL
313.706 | 0.35 | 294.26 | 1.11 | 1 | 79289.74 | 10398.1829 | 10390.3219 | 3801.402 | NORMAL
313.706 | 0.35 | 294.26 | 1.11 | 1 | 101352.97 | 10638.8042 | 10630.8358 | 3619.775 | NORMAL
313.706 | 0.35 | 294.26 | 1.11 | 1 | 106868.78 | 10682.415 | 10674.4352 | 3586.979 | NORMAL
313.706 | 0.35 | 294.26 | 1.11 | 2 | 57226.51 | 12578.3118 | 12569.746 | 5662.92 | NORMAL
313.706 | 0.35 | 294.26 | 1.11 | 2 | 79289.74 | 13009.7304 | 13001.4041 | 5074.433 | NORMAL
313.706 | 0.35 | 294.26 | 1.11 | 2 | 101352.97 | 13445.7503 | 13437.1988 | 4782.241 | NORMAL
313.706 | 0.35 | 294.26 | 1.11 | 2 | 106868.78 | 13456.5651 | 13448.0605 | 4726.387 | NORMAL
313.706 | 0.35 | 294.26 | 1.42 | 1 | 57226.51 | 10349.1794 | 10340.5378 | 4170.02 | NORMAL
313.706 | 0.35 | 294.26 | 1.42 | 1 | 79289.74 | 10857.0633 | 10848.1279 | 3812.78 | NORMAL
313.706 | 0.35 | 294.26 | 1.42 | 1 | 101352.97 | 11134.4959 | 11118.7183 | 3618.97 | NORMAL
313.706 | 0.35 | 294.26 | 1.42 | 1 | 106868.78 | 11180.4513 | 11171.3281 | 3586.79 | NORMAL
313.706 | 0.35 | 294.26 | 1.42 | 2 | 57226.51 | 13149.7948 | 13139.8273 | 5752.46 | NORMAL
313.706 | 0.35 | 294.26 | 1.42 | 2 | 79289.74 | 13866.9402 | 13856.6787 | 5158.15 | NORMAL
313.706 | 0.35 | 294.26 | 1.42 | 2 | 101352.97 | 14269.4021 | 14258.9855 | 4838.003 | NORMAL
313.706 | 0.35 | 294.26 | 1.42 | 2 | 106868.78 | 14344.1969 | 14333.7544 | 4779.757 | NORMAL
313.706 | 0.35 | 297.037 | 0.5 | 1 | 57226.51 | 8958.4994 | 8294.3342 | 4083.697 | NORMAL
313.706 | 0.35 | 297.037 | 0.5 | 1 | 79289.74 | 9312.4267 | 8462.2115 | 3776.139 | NORMAL
313.706 | 0.35 | 297.037 | 0.5 | 1 | 101352.97 | 9459.9648 | 8630.7895 | 3619.304 | NORMAL
313.706 | 0.35 | 297.037 | 0.5 | 1 | 106868.78 | 9434.3787 | 8739.3669 | 3588.8113 | NORMAL
313.706 | 0.35 | 297.037 | 0.5 | 2 | 57226.51 | 11694.49 | 9388.8512 | 5520.878 | NORMAL
313.706 | 0.35 | 297.037 | 0.5 | 2 | 79289.74 | 12077.7257 | 9839.1555 | 4985.422 | NORMAL
313.706 | 0.35 | 297.037 | 0.5 | 2 | 101352.97 | 12215.7093 | 10217.0482 | 4700.829 | NORMAL
313.706 | 0.35 | 297.037 | 0.5 | 2 | 106868.78 | 12147.4209 | 10166.796 | 4645.8503 | NORMAL
313.706 | 0.35 | 297.037 | 0.8 | 1 | 57226.51 | 9936.9578 | 9918.2962 | 4143.21 | NORMAL
313.706 | 0.35 | 297.037 | 0.8 | 1 | 79289.74 | 10351.4947 | 10343.5655 | 3800.276 | NORMAL
313.706 | 0.35 | 297.037 | 0.8 | 1 | 101352.97 | 10462.0457 | 10454.1364 | 3618.224 | NORMAL
313.706 | 0.35 | 297.037 | 0.8 | 1 | 106868.78 | 10609.3201 | 10601.31 | 3585.922 | NORMAL
313.706 | 0.35 | 297.037 | 0.8 | 2 | 57226.51 | 12544.9297 | 12201.6126 | 5655.956 | NORMAL
313.706 | 0.35 | 297.037 | 0.8 | 2 | 79289.74 | 13243.8453 | 12466.4713 | 5097.758 | NORMAL
313.706 | 0.35 | 297.037 | 0.8 | 2 | 101352.97 | 13601.9637 | 12748.6717 | 4792.501 | NORMAL
313.706 | 0.35 | 297.037 | 0.8 | 2 | 106868.78 | 13592.1747 | 12919.1717 | 4734.286 | NORMAL
313.706 | 0.35 | 297.037 | 1.11 | 1 | 57226.51 | 10615.8851 | 10606.352 | 4185.56 | NORMAL
313.706 | 0.35 | 297.037 | 1.11 | 1 | 79289.74 | 11114.0387 | 11104.2361 | 3819.387 | NORMAL
313.706 | 0.35 | 297.037 | 1.11 | 1 | 101352.97 | 11385.17 | 11375.2307 | 3620.895 | NORMAL
313.706 | 0.35 | 297.037 | 1.11 | 1 | 106868.78 | 11430.5393 | 11420.5718 | 3587.511 | NORMAL
313.706 | 0.35 | 297.037 | 1.11 | 2 | 57226.51 | 12987.6026 | 12977.719 | 5727.61 | NORMAL
313.706 | 0.35 | 297.037 | 1.11 | 2 | 79289.74 | 13857.1219 | 13846.6044 | 5156.092 | NORMAL
313.706 | 0.35 | 297.037 | 1.11 | 2 | 101352.97 | 14336.4302 | 14325.6349 | 4842.328 | NORMAL
313.706 | 0.35 | 297.037 | 1.11 | 2 | 106868.78 | 14347.3916 | 14336.6741 | 4781.197 | NORMAL
313.706 | 0.35 | 297.037 | 1.42 | 1 | 57226.51 | 11056.5944 | 11015.2869 | 4213.28 | NORMAL
313.706 | 0.35 | 297.037 | 1.42 | 1 | 79289.74 | 11614.5076 | 11603.3693 | 3832.83 | NORMAL
313.706 | 0.35 | 297.037 | 1.42 | 1 | 101352.97 | 11922.0106 | 11910.6727 | 3624.954 | NORMAL
313.706 | 0.35 | 297.037 | 1.42 | 1 | 106868.78 | 11976.5533 | 11965.1756 | 3588.099 | NORMAL
313.706 | 0.35 | 297.037 | 1.42 | 2 | 57226.51 | 13924.8535 | 13882.6333 | 5874.37 | NORMAL
313.706 | 0.35 | 297.037 | 1.42 | 2 | 79289.74 | 14710.0528 | 14697.3139 | 5240.83 | NORMAL
313.706 | 0.35 | 297.037 | 1.42 | 2 | 101352.97 | 15154.5428 | 15139.07 | 4898.433 | NORMAL
313.706 | 0.35 | 297.037 | 1.42 | 2 | 106868.78 | 15237.0164 | 15224.004 | 4836.327 | NORMAL
313.706 | 0.35 | 299.814 | 0.5 | 1 | 57226.51 | 9640.0352 | 8661.774 | 4121.957 | NORMAL
313.706 | 0.35 | 299.814 | 0.5 | 1 | 79289.74 | 10018.6694 | 8829.7539 | 3792.738 | NORMAL
313.706 | 0.35 | 299.814 | 0.5 | 1 | 101352.97 | 10182.7667 | 9027.8679 | 3617.381 | NORMAL
313.706 | 0.35 | 299.814 | 0.5 | 1 | 106868.78 | 10138.5111 | 9143.5278 | 3588.5407 | NORMAL
313.706 | 0.35 | 299.814 | 0.5 | 2 | 57226.51 | 12479.2497 | 9706.7598 | 5645.508 | NORMAL
313.706 | 0.35 | 299.814 | 0.5 | 2 | 79289.74 | 12920.3693 | 10175.6952 | 5064.897 | NORMAL
313.706 | 0.35 | 299.814 | 0.5 | 2 | 101352.97 | 13065.0352 | 10564.4528 | 4757.766 | NORMAL
313.706 | 0.35 | 299.814 | 0.5 | 2 | 106868.78 | 13021.9519 | 10611.3803 | 4699.3233 | NORMAL
313.706 | 0.35 | 299.814 | 0.8 | 1 | 57226.51 | 10565.5041 | 10555.9318 | 4182.323 | NORMAL
313.706 | 0.35 | 299.814 | 0.8 | 1 | 79289.74 | 10813.1301 | 10803.7768 | 3812.289 | NORMAL
313.706 | 0.35 | 299.814 | 0.8 | 1 | 101352.97 | 11128.6635 | 11119.104 | 3619.969 | NORMAL
313.706 | 0.35 | 299.814 | 0.8 | 1 | 106868.78 | 11146.7761 | 11137.1787 | 3586.731 | NORMAL
313.706 | 0.35 | 299.814 | 0.8 | 2 | 57226.51 | 13345.1934 | 12687.2487 | 5780.13 | NORMAL
313.706 | 0.35 | 299.814 | 0.8 | 2 | 79289.74 | 14110.7268 | 12961.2388 | 5182.016 | NORMAL
313.706 | 0.35 | 299.814 | 0.8 | 2 | 101352.97 | 14505.2755 | 13288.1088 | 4853.519 | NORMAL
313.706 | 0.35 | 299.814 | 0.8 | 2 | 106868.78 | 14491.823 | 13498.7853 | 4790.252 | NORMAL
313.706 | 0.35 | 299.814 | 1.11 | 1 | 57226.51 | 11297.3916 | 11285.7101 | 4229.08 | NORMAL
313.706 | 0.35 | 299.814 | 1.11 | 1 | 79289.74 | 11843.2591 | 11831.2263 | 3839.176 | NORMAL
313.706 | 0.35 | 299.814 | 1.11 | 1 | 101352.97 | 12142.6143 | 12129.8888 | 3626.898 | NORMAL
313.706 | 0.35 | 299.814 | 1.11 | 1 | 106868.78 | 12195.6624 | 12183.4179 | 3589.206 | NORMAL
313.706 | 0.35 | 299.814 | 1.11 | 2 | 57226.51 | 13790.9144 | 13778.6681 | 5850.7 | NORMAL
313.706 | 0.35 | 299.814 | 1.11 | 2 | 79289.74 | 14726.5827 | 14713.5202 | 5243.562 | NORMAL
313.706 | 0.35 | 299.814 | 1.11 | 2 | 101352.97 | 15261.6354 | 15248.2052 | 4905.549 | NORMAL
313.706 | 0.35 | 299.814 | 1.11 | 2 | 106868.78 | 15264.83 | 15251.5191 | 4840.173 | NORMAL
313.706 | 0.35 | 299.814 | 1.42 | 1 | 57226.51 | 11773.3294 | 11755.1985 | 4260.27 | NORMAL
313.706 | 0.35 | 299.814 | 1.42 | 1 | 79289.74 | 12386.782 | 12373.1193 | 3854.78 | NORMAL
313.706 | 0.35 | 299.814 | 1.42 | 1 | 101352.97 | 12726.993 | 12713.0696 | 3632.469 | NORMAL
313.706 | 0.35 | 299.814 | 1.42 | 1 | 106868.78 | 12787.8371 | 12773.8599 | 3592.834 | NORMAL
313.706 | 0.35 | 299.814 | 1.42 | 2 | 57226.51 | 14715.3576 | 14700.2743 | 5999.37 | NORMAL
313.706 | 0.35 | 299.814 | 1.42 | 2 | 79289.74 | 15570.0762 | 15541.8476 | 5325.99 | NORMAL
313.706 | 0.35 | 299.814 | 1.42 | 2 | 101352.97 | 15745.8968 | 15730.8595 | 4941.145 | NORMAL
313.706 | 0.35 | 299.814 | 1.42 | 2 | 106868.78 | 15933.0012 | 15917.6258 | 4880.135 | NORMAL
313.706 | 0.35 | 302.591 | 0.5 | 1 | 57226.51 | 10329.8652 | 8994.4305 | 4165.791 | NORMAL
313.706 | 0.35 | 302.591 | 0.5 | 1 | 79289.74 | 10756.0082 | 9196.1719 | 3810.479 | NORMAL
313.706 | 0.35 | 302.591 | 0.5 | 1 | 101352.97 | 10935.6682 | 9410.9189 | 3618.979 | NORMAL
313.706 | 0.35 | 302.591 | 0.5 | 1 | 106868.78 | 10889.449 | 9544.8307 | 3586.203 | NORMAL
313.706 | 0.35 | 302.591 | 0.5 | 2 | 57226.51 | 13310.6682 | 10019.326 | 5774.944 | NORMAL
313.706 | 0.35 | 302.591 | 0.5 | 2 | 79289.74 | 13805.2755 | 10497.9733 | 5150.17 | NORMAL
313.706 | 0.35 | 302.591 | 0.5 | 2 | 101352.97 | 13962.8957 | 10928.186 | 4817.942 | NORMAL
313.706 | 0.35 | 302.591 | 0.5 | 2 | 106868.78 | 13912.7491 | 10934.0852 | 4754.3022 | NORMAL
313.706 | 0.35 | 302.591 | 0.8 | 1 | 57226.51 | 10925.8206 | 10914.9822 | 4202.475 | NORMAL
313.706 | 0.35 | 302.591 | 0.8 | 1 | 79289.74 | 11555.3048 | 11543.7957 | 3832.274 | NORMAL
313.706 | 0.35 | 302.591 | 0.8 | 1 | 101352.97 | 11915.211 | 11903.415 | 3623.589 | NORMAL
313.706 | 0.35 | 302.591 | 0.8 | 1 | 106868.78 | 11887.3095 | 11875.6362 | 3588.269 | NORMAL
313.706 | 0.35 | 302.591 | 0.8 | 2 | 57226.51 | 14171.0727 | 13159.8391 | 5910.786 | NORMAL
313.706 | 0.35 | 302.591 | 0.8 | 2 | 79289.74 | 15014.83 | 13473.1373 | 5271.219 | NORMAL
313.706 | 0.35 | 302.591 | 0.8 | 2 | 101352.97 | 15450.9672 | 13823.1614 | 4918.397 | NORMAL
313.706 | 0.35 | 302.591 | 0.8 | 2 | 106868.78 | 15428.5463 | 14027.7115 | 4850.573 | NORMAL
313.706 | 0.35 | 302.591 | 1.11 | 1 | 57226.51 | 11991.3834 | 11977.2455 | 4275.01 | NORMAL
313.706 | 0.35 | 302.591 | 1.11 | 1 | 79289.74 | 12587.1923 | 12561.464 | 3860.769 | NORMAL
313.706 | 0.35 | 302.591 | 1.11 | 1 | 101352.97 | 12915.7679 | 12895.4255 | 3634.455 | NORMAL
313.706 | 0.35 | 302.591 | 1.11 | 1 | 106868.78 | 12974.0328 | 12959.1776 | 3594.15 | NORMAL
313.706 | 0.35 | 302.591 | 1.11 | 2 | 57226.51 | 14602.4912 | 14587.5236 | 5982.12 | NORMAL
313.706 | 0.35 | 302.591 | 1.11 | 2 | 79289.74 | 15643.2005 | 15627.1662 | 5333.076 | NORMAL
313.706 | 0.35 | 302.591 | 1.11 | 2 | 101352.97 | 16223.857 | 16079.059 | 4972.572 | NORMAL
313.706 | 0.35 | 302.591 | 1.11 | 2 | 106868.78 | 16224.9121 | 16208.5574 | 4902.163 | NORMAL
313.706 | 0.35 | 302.591 | 1.42 | 1 | 57226.51 | 12503.898 | 12487.993 | 4309.77 | NORMAL
313.706 | 0.35 | 302.591 | 1.42 | 1 | 79289.74 | 13175.5569 | 13140.9183 | 3878.83 | NORMAL
313.706 | 0.35 | 302.591 | 1.42 | 1 | 101352.97 | 13549.7655 | 13532.869 | 3641.826 | NORMAL
313.706 | 0.35 | 302.591 | 1.42 | 1 | 106868.78 | 13617.2626 | 13600.2955 | 3599.362 | NORMAL
313.706 | 0.35 | 302.591 | 1.42 | 2 | 57226.51 | 15519.9297 | 15501.7403 | 6128.05 | NORMAL
313.706 | 0.35 | 302.591 | 1.42 | 2 | 79289.74 | 16041.354 | 16023.6765 | 5373.56 | NORMAL
313.706 | 0.35 | 302.591 | 1.42 | 2 | 101352.97 | 16728.6342 | 16710.2495 | 5006.072 | NORMAL
313.706 | 0.35 | 302.591 | 1.42 | 2 | 106868.78 | 16740.2696 | 16722.006 | 4935.904 | NORMAL
313.706 | 0.35 | 305.368 | 0.5 | 1 | 57226.51 | 11049.3552 | 9370.1295 | 4210.749 | NORMAL
313.706 | 0.35 | 305.368 | 0.5 | 1 | 79289.74 | 11527.3447 | 9529.2985 | 3830.644 | NORMAL
313.706 | 0.35 | 305.368 | 0.5 | 1 | 101352.97 | 11726.9637 | 9784.568 | 3622.115 | NORMAL
313.706 | 0.35 | 305.368 | 0.5 | 1 | 106868.78 | 11671.4244 | 9922.2864 | 3586.954 | NORMAL
313.706 | 0.35 | 305.368 | 0.5 | 2 | 57226.51 | 14165.6799 | 10275.0476 | 5912.576 | NORMAL
313.706 | 0.35 | 305.368 | 0.5 | 2 | 79289.74 | 14733.7339 | 10816.6381 | 5240.932 | NORMAL
313.706 | 0.35 | 305.368 | 0.5 | 2 | 101352.97 | 14910.4338 | 11244.316 | 4882.406 | NORMAL
313.706 | 0.35 | 305.368 | 0.5 | 2 | 106868.78 | 14852.6671 | 11229.7897 | 4813.1892 | NORMAL
313.706 | 0.35 | 305.368 | 0.8 | 1 | 57226.51 | 11636.2251 | 11623.0529 | 4249.812 | NORMAL
313.706 | 0.35 | 305.368 | 0.8 | 1 | 79289.74 | 12344.0797 | 12330.0445 | 3853.976 | NORMAL
313.706 | 0.35 | 305.368 | 0.8 | 1 | 101352.97 | 12719.0797 | 12625.5818 | 3631.543 | NORMAL
313.706 | 0.35 | 305.368 | 0.8 | 1 | 106868.78 | 12692.1747 | 12677.9467 | 3592.798 | NORMAL
313.706 | 0.35 | 305.368 | 0.8 | 2 | 57226.51 | 15015.211 | 13636.3492 | 6047.72 | NORMAL
313.706 | 0.35 | 305.368 | 0.8 | 2 | 79289.74 | 15954.0739 | 13923.6148 | 5365.074 | NORMAL
313.706 | 0.35 | 305.368 | 0.8 | 2 | 101352.97 | 16438.7749 | 14342.3051 | 4987.392 | NORMAL
313.706 | 0.35 | 305.368 | 0.8 | 2 | 106868.78 | 16410.3458 | 14539.2382 | 4914.228 | NORMAL
313.706 | 0.35 | 305.368 | 1.11 | 1 | 57226.51 | 12697.5088 | 12680.6211 | 4323.31 | NORMAL
313.706 | 0.35 | 305.368 | 1.11 | 1 | 79289.74 | 13345.9261 | 13304.0199 | 3884.199 | NORMAL
313.706 | 0.35 | 305.368 | 1.11 | 1 | 101352.97 | 13704.5135 | 13686.7661 | 3643.74 | NORMAL
313.706 | 0.35 | 305.368 | 1.11 | 1 | 106868.78 | 13768.7866 | 13750.9836 | 3600.675 | NORMAL
313.706 | 0.35 | 305.368 | 1.11 | 2 | 57226.51 | 15466.5006 | 15448.4202 | 6115.16 | NORMAL
313.706 | 0.35 | 305.368 | 1.11 | 2 | 79289.74 | 16586.5182 | 16519.1769 | 5428.063 | NORMAL
313.706 | 0.35 | 305.368 | 1.11 | 2 | 101352.97 | 17222.1278 | 16766.1375 | 5043.595 | NORMAL
313.706 | 0.35 | 305.368 | 1.11 | 2 | 106868.78 | 17220.7503 | 17012.0692 | 4967.768 | NORMAL
313.706 | 0.35 | 305.368 | 1.42 | 1 | 57226.51 | 13246.3072 | 13196.6865 | 4361.79 | NORMAL
313.706 | 0.35 | 305.368 | 1.42 | 1 | 79289.74 | 13979.5428 | 13959.7478 | 3904.99 | NORMAL
313.706 | 0.35 | 305.368 | 1.42 | 1 | 101352.97 | 14390.9437 | 14370.6957 | 3652.982 | NORMAL
313.706 | 0.35 | 305.368 | 1.42 | 1 | 106868.78 | 14465.0352 | 14444.7118 | 3607.729 | NORMAL
313.706 | 0.35 | 305.368 | 1.42 | 2 | 57226.51 | 15744.9883 | 15725.4015 | 6161.39 | NORMAL
313.706 | 0.35 | 305.368 | 1.42 | 2 | 79289.74 | 16992.4678 | 16971.1592 | 5470.68 | NORMAL
313.706 | 0.35 | 305.368 | 1.42 | 2 | 101352.97 | 17737.0164 | 17714.8274 | 5078.422 | NORMAL
313.706 | 0.35 | 305.368 | 1.42 | 2 | 106868.78 | 17752.1981 | 17730.1499 | 5002.641 | NORMAL
313.706 | 0.45 | 288.706 | 0.5 | 1 | 57226.51 | 7512.837 | 6536.5889 | 4002.514 | NORMAL
313.706 | 0.45 | 288.706 | 0.5 | 1 | 79289.74 | 7752.8429 | 6779.396 | 3749.748 | NORMAL
313.706 | 0.45 | 288.706 | 0.5 | 1 | 101352.97 | 7841.1782 | 6888.9298 | 3623.363 | NORMAL
313.706 | 0.45 | 288.706 | 0.5 | 1 | 106868.78 | 7810.3165 | 6957.141 | 3604.0561 | NORMAL
313.706 | 0.45 | 288.706 | 0.5 | 2 | 57226.51 | 10062.7491 | 7659.7143 | 5272.194 | NORMAL
313.706 | 0.45 | 288.706 | 0.5 | 2 | 79289.74 | 10305.4807 | 8106.6724 | 4817.116 | NORMAL
313.706 | 0.45 | 288.706 | 0.5 | 2 | 101352.97 | 10368.9039 | 8422.5466 | 4581.847 | NORMAL
313.706 | 0.45 | 288.706 | 0.5 | 2 | 106868.78 | 10334.2321 | 8478.4521 | 4540.1709 | NORMAL
313.706 | 0.45 | 288.706 | 0.8 | 1 | 57226.51 | 8074.9121 | 8071.2057 | 4034.375 | NORMAL
313.706 | 0.45 | 288.706 | 0.8 | 1 | 79289.74 | 8454.1618 | 8398.0261 | 3760.15 | NORMAL
313.706 | 0.45 | 288.706 | 0.8 | 1 | 101352.97 | 8637.3095 | 8512.4745 | 3618.987 | NORMAL
313.706 | 0.45 | 288.706 | 0.8 | 1 | 106868.78 | 8621.4537 | 8617.5913 | 3593.4 | NORMAL
313.706 | 0.45 | 288.706 | 0.8 | 2 | 57226.51 | 10806.1841 | 9763.852 | 5386.442 | NORMAL
313.706 | 0.45 | 288.706 | 0.8 | 2 | 79289.74 | 11309.6424 | 10242.6003 | 4909.126 | NORMAL
313.706 | 0.45 | 288.706 | 0.8 | 2 | 101352.97 | 11535.6096 | 10546.0273 | 4655.241 | NORMAL
313.706 | 0.45 | 288.706 | 0.8 | 2 | 106868.78 | 11522.1278 | 10629.5431 | 4607.849 | NORMAL
313.706 | 0.45 | 288.706 | 1.11 | 1 | 57226.51 | 8641.9988 | 8637.3408 | 4067.28 | NORMAL
313.706 | 0.45 | 288.706 | 1.11 | 1 | 79289.74 | 9012.075 | 9007.3076 | 3770.506 | NORMAL
313.706 | 0.45 | 288.706 | 1.11 | 1 | 101352.97 | 9203.4877 | 9195.9132 | 3616.749 | NORMAL
313.706 | 0.45 | 288.706 | 1.11 | 1 | 106868.78 | 9236.4009 | 9230.4435 | 3590.233 | NORMAL
313.706 | 0.45 | 288.706 | 1.11 | 2 | 57226.51 | 11262.3095 | 11206.5385 | 5454.93 | NORMAL
313.706 | 0.45 | 288.706 | 1.11 | 2 | 79289.74 | 11871.9519 | 11436.8211 | 4966.104 | NORMAL
313.706 | 0.45 | 288.706 | 1.11 | 2 | 101352.97 | 12181.7116 | 11675.9757 | 4698.379 | NORMAL
313.706 | 0.45 | 288.706 | 1.11 | 2 | 106868.78 | 12149.0035 | 11877.4733 | 4645.754 | NORMAL
313.706 | 0.45 | 288.706 | 1.42 | 1 | 57226.51 | 8980.5979 | 8975.3353 | 4087.02 | NORMAL
313.706 | 0.45 | 288.706 | 1.42 | 1 | 79289.74 | 9391.9988 | 9386.5703 | 3778.32 | NORMAL
313.706 | 0.45 | 288.706 | 1.42 | 1 | 101352.97 | 9608.0891 | 9602.5644 | 3616.347 | NORMAL
313.706 | 0.45 | 288.706 | 1.42 | 1 | 106868.78 | 9645.8968 | 9640.3601 | 3587.986 | NORMAL
313.706 | 0.45 | 288.706 | 1.42 | 2 | 57226.51 | 11526.6413 | 11520.8088 | 5495.97 | NORMAL
313.706 | 0.45 | 288.706 | 1.42 | 2 | 79289.74 | 12215.8558 | 12209.6868 | 4999.12 | NORMAL
313.706 | 0.45 | 288.706 | 1.42 | 2 | 101352.97 | 12598.6811 | 12592.3692 | 4726.188 | NORMAL
313.706 | 0.45 | 288.706 | 1.42 | 2 | 106868.78 | 12605.9496 | 12599.6844 | 4673.834 | NORMAL
313.706 | 0.45 | 291.483 | 0.5 | 1 | 57226.51 | 8211.6061 | 6784.1251 | 4039.412 | NORMAL
313.706 | 0.45 | 291.483 | 0.5 | 1 | 79289.74 | 8453.0481 | 7052.7837 | 3760.981 | NORMAL
313.706 | 0.45 | 291.483 | 0.5 | 1 | 101352.97 | 8536.2251 | 7326.3944 | 3619.348 | NORMAL
313.706 | 0.45 | 291.483 | 0.5 | 1 | 106868.78 | 8502.9308 | 7270.8391 | 3594.5896 | NORMAL
313.706 | 0.45 | 291.483 | 0.5 | 2 | 57226.51 | 10778.2532 | 7871.5631 | 5382.166 | NORMAL
313.706 | 0.45 | 291.483 | 0.5 | 2 | 79289.74 | 11067.5264 | 8425.7964 | 4889.888 | NORMAL
313.706 | 0.45 | 291.483 | 0.5 | 2 | 101352.97 | 11141.823 | 8783.6784 | 4630.713 | NORMAL
313.706 | 0.45 | 291.483 | 0.5 | 2 | 106868.78 | 11103.0774 | 8823.1382 | 4583.9588 | NORMAL
313.706 | 0.45 | 291.483 | 0.8 | 1 | 57226.51 | 8748.095 | 8743.1785 | 4072.707 | NORMAL
313.706 | 0.45 | 291.483 | 0.8 | 1 | 79289.74 | 9167.9367 | 8873.9943 | 3772.238 | NORMAL
313.706 | 0.45 | 291.483 | 0.8 | 1 | 101352.97 | 9363.306 | 9002.8562 | 3619.503 | NORMAL
313.706 | 0.45 | 291.483 | 0.8 | 1 | 106868.78 | 9346.1606 | 9148.6015 | 3589.424 | NORMAL
313.706 | 0.45 | 291.483 | 0.8 | 2 | 57226.51 | 11642.4091 | 10046.782 | 5514.181 | NORMAL
313.706 | 0.45 | 291.483 | 0.8 | 2 | 79289.74 | 12175.9965 | 10438.0434 | 4991.432 | NORMAL
313.706 | 0.45 | 291.483 | 0.8 | 2 | 101352.97 | 12419.7245 | 10773.1423 | 4713.44 | NORMAL
313.706 | 0.45 | 291.483 | 0.8 | 2 | 106868.78 | 12400.9672 | 10937.3058 | 4661.169 | NORMAL
313.706 | 0.45 | 291.483 | 1.11 | 1 | 57226.51 | 9291.7057 | 9275.2873 | 4105.12 | NORMAL
313.706 | 0.45 | 291.483 | 1.11 | 1 | 79289.74 | 9539.8593 | 9533.916 | 3781.125 | NORMAL
313.706 | 0.45 | 291.483 | 1.11 | 1 | 101352.97 | 9807.3564 | 9801.2954 | 3616.477 | NORMAL
313.706 | 0.45 | 291.483 | 1.11 | 1 | 106868.78 | 9878.7515 | 9872.5279 | 3587.007 | NORMAL
313.706 | 0.45 | 291.483 | 1.11 | 2 | 57226.51 | 12048.7397 | 11735.5689 | 5579.61 | NORMAL
313.706 | 0.45 | 291.483 | 1.11 | 2 | 79289.74 | 12728.6635 | 12015.7693 | 5048.088 | NORMAL
313.706 | 0.45 | 291.483 | 1.11 | 2 | 101352.97 | 13085.1114 | 12279.9845 | 4758.09 | NORMAL
313.706 | 0.45 | 291.483 | 1.11 | 2 | 106868.78 | 13078.4877 | 12465.0674 | 4702.819 | NORMAL
313.706 | 0.45 | 291.483 | 1.42 | 1 | 57226.51 | 9662.7198 | 9655.9173 | 4127.44 | NORMAL
313.706 | 0.45 | 291.483 | 1.42 | 1 | 79289.74 | 10119.8124 | 10106.4138 | 3794.77 | NORMAL
313.706 | 0.45 | 291.483 | 1.42 | 1 | 101352.97 | 10362.6026 | 10355.4524 | 3618.256 | NORMAL
313.706 | 0.45 | 291.483 | 1.42 | 1 | 106868.78 | 10407.2098 | 10400.0393 | 3585.991 | NORMAL
313.706 | 0.45 | 291.483 | 1.42 | 2 | 57226.51 | 12314.5076 | 12306.9096 | 5620.31 | NORMAL
313.706 | 0.45 | 291.483 | 1.42 | 2 | 79289.74 | 13087.3974 | 13079.3356 | 5082.8 | NORMAL
313.706 | 0.45 | 291.483 | 1.42 | 2 | 101352.97 | 13514.3904 | 13470.9146 | 4787.17 | NORMAL
313.706 | 0.45 | 291.483 | 1.42 | 2 | 106868.78 | 13522.5381 | 13514.3434 | 4729.996 | NORMAL
313.706 | 0.45 | 294.26 | 0.5 | 1 | 57226.51 | 8896.6295 | 7070.2494 | 4080.065 | NORMAL
313.706 | 0.45 | 294.26 | 0.5 | 1 | 79289.74 | 9168.8453 | 7357.1731 | 3774.4 | NORMAL
313.706 | 0.45 | 294.26 | 0.5 | 1 | 101352.97 | 9254.9238 | 7619.3289 | 3619.76 | NORMAL
313.706 | 0.45 | 294.26 | 0.5 | 1 | 106868.78 | 9215.9437 | 7651.9612 | 3590.1717 | NORMAL
313.706 | 0.45 | 294.26 | 0.5 | 2 | 57226.51 | 11626.7878 | 8092.721 | 5514.537 | NORMAL
313.706 | 0.45 | 294.26 | 0.5 | 2 | 79289.74 | 11927.4033 | 8680.9788 | 4971.661 | NORMAL
313.706 | 0.45 | 294.26 | 0.5 | 2 | 101352.97 | 11949.0914 | 9078.4895 | 4682.333 | NORMAL
313.706 | 0.45 | 294.26 | 0.5 | 2 | 106868.78 | 11908.1477 | 9100.1946 | 4632.1869 | NORMAL
313.706 | 0.45 | 294.26 | 0.8 | 1 | 57226.51 | 9445.2227 | 9234.3676 | 4112.436 | NORMAL
313.706 | 0.45 | 294.26 | 0.8 | 1 | 79289.74 | 9909.027 | 9340.7344 | 3788.413 | NORMAL
313.706 | 0.45 | 294.26 | 0.8 | 1 | 101352.97 | 10127.0516 | 9497.392 | 3618.415 | NORMAL
313.706 | 0.45 | 294.26 | 0.8 | 1 | 106868.78 | 10098.3001 | 9645.0076 | 3588.797 | NORMAL
313.706 | 0.45 | 294.26 | 0.8 | 2 | 57226.51 | 12461.4889 | 10412.9322 | 5641.491 | NORMAL
313.706 | 0.45 | 294.26 | 0.8 | 2 | 79289.74 | 13053.7222 | 10864.9132 | 5078.438 | NORMAL
313.706 | 0.45 | 294.26 | 0.8 | 2 | 101352.97 | 13330.2755 | 11238.4487 | 4774.108 | NORMAL
313.706 | 0.45 | 294.26 | 0.8 | 2 | 106868.78 | 13301.6706 | 11418.4866 | 4716.432 | NORMAL
313.706 | 0.45 | 294.26 | 1.11 | 1 | 57226.51 | 9730.422 | 9723.2702 | 4129.68 | NORMAL
313.706 | 0.45 | 294.26 | 1.11 | 1 | 79289.74 | 10285.4044 | 10277.8138 | 3798.556 | NORMAL
313.706 | 0.45 | 294.26 | 1.11 | 1 | 101352.97 | 10584.8476 | 10577.0572 | 3618.764 | NORMAL
313.706 | 0.45 | 294.26 | 1.11 | 1 | 106868.78 | 10565.7093 | 10557.9857 | 3587.401 | NORMAL
313.706 | 0.45 | 294.26 | 1.11 | 2 | 57226.51 | 12874.1794 | 12251.0305 | 5706.35 | NORMAL
313.706 | 0.45 | 294.26 | 1.11 | 2 | 79289.74 | 13627.8136 | 12547.0735 | 5134.792 | NORMAL
313.706 | 0.45 | 294.26 | 1.11 | 2 | 101352.97 | 14024.619 | 12862.0482 | 4821.093 | NORMAL
313.706 | 0.45 | 294.26 | 1.11 | 2 | 106868.78 | 14014.9472 | 13084.0464 | 4760.607 | NORMAL
313.706 | 0.45 | 294.26 | 1.42 | 1 | 57226.51 | 10357.0633 | 10348.4566 | 4170.02 | NORMAL
313.706 | 0.45 | 294.26 | 1.42 | 1 | 79289.74 | 10862.925 | 10854.0065 | 3812.93 | NORMAL
313.706 | 0.45 | 294.26 | 1.42 | 1 | 101352.97 | 11139.5076 | 11130.4289 | 3618.916 | NORMAL
313.706 | 0.45 | 294.26 | 1.42 | 1 | 106868.78 | 11184.8769 | 11175.7836 | 3586.799 | NORMAL
313.706 | 0.45 | 294.26 | 1.42 | 2 | 57226.51 | 13139.5076 | 13129.8238 | 5748 | NORMAL
313.706 | 0.45 | 294.26 | 1.42 | 2 | 79289.74 | 13993.1418 | 13901.6407 | 5170.66 | NORMAL
313.706 | 0.45 | 294.26 | 1.42 | 2 | 101352.97 | 14470.5158 | 14196.097 | 4851.451 | NORMAL
313.706 | 0.45 | 294.26 | 1.42 | 2 | 106868.78 | 14474.7069 | 14456.3096 | 4789.446 | NORMAL
313.706 | 0.45 | 297.037 | 0.5 | 1 | 57226.51 | 9624.5604 | 7349.6415 | 4121.787 | NORMAL
313.706 | 0.45 | 297.037 | 0.5 | 1 | 79289.74 | 9922.0985 | 7653.3114 | 3790.897 | NORMAL
313.706 | 0.45 | 297.037 | 0.5 | 1 | 101352.97 | 10024.0035 | 7950.8692 | 3617.105 | NORMAL
313.706 | 0.45 | 297.037 | 0.5 | 1 | 106868.78 | 9966.6764 | 7943.4511 | 3588.9134 | NORMAL
313.706 | 0.45 | 297.037 | 0.5 | 2 | 57226.51 | 12477.5205 | 8283.2519 | 5646.015 | NORMAL
313.706 | 0.45 | 297.037 | 0.5 | 2 | 79289.74 | 12818.3177 | 8918.5753 | 5057.396 | NORMAL
313.706 | 0.45 | 297.037 | 0.5 | 2 | 101352.97 | 12886.5475 | 9380.1952 | 4746.254 | NORMAL
313.706 | 0.45 | 297.037 | 0.5 | 2 | 106868.78 | 12828.5463 | 9398.7062 | 4687.5148 | NORMAL
313.706 | 0.45 | 297.037 | 0.8 | 1 | 57226.51 | 10169.6366 | 9636.5747 | 4156.528 | NORMAL
313.706 | 0.45 | 297.037 | 0.8 | 1 | 79289.74 | 10684.8769 | 9784.6012 | 3806.795 | NORMAL
313.706 | 0.45 | 297.037 | 0.8 | 1 | 101352.97 | 10925.0879 | 9978.1669 | 3620.501 | NORMAL
313.706 | 0.45 | 297.037 | 0.8 | 1 | 106868.78 | 10897.8019 | 10143.6958 | 3586.201 | NORMAL
313.706 | 0.45 | 297.037 | 0.8 | 2 | 57226.51 | 13309.2614 | 10764.6637 | 5776.6 | NORMAL
313.706 | 0.45 | 297.037 | 0.8 | 2 | 79289.74 | 13981.7116 | 11269.9307 | 5168.366 | NORMAL
313.706 | 0.45 | 297.037 | 0.8 | 2 | 101352.97 | 14291.6764 | 11691.8204 | 4838.793 | NORMAL
313.706 | 0.45 | 297.037 | 0.8 | 2 | 106868.78 | 14258.2356 | 11891.2117 | 4775.741 | NORMAL
313.706 | 0.45 | 297.037 | 1.11 | 1 | 57226.51 | 10460.7561 | 10451.7181 | 4173.47 | NORMAL
313.706 | 0.45 | 297.037 | 1.11 | 1 | 79289.74 | 11067.2919 | 11057.6855 | 3818.154 | NORMAL
313.706 | 0.45 | 297.037 | 1.11 | 1 | 101352.97 | 11397.8605 | 11387.9899 | 3620.962 | NORMAL
313.706 | 0.45 | 297.037 | 1.11 | 1 | 106868.78 | 11376.4654 | 11366.693 | 3588.242 | NORMAL
313.706 | 0.45 | 297.037 | 1.11 | 2 | 57226.51 | 13720.5158 | 12720.0021 | 5842.02 | NORMAL
313.706 | 0.45 | 297.037 | 1.11 | 2 | 79289.74 | 14567.3505 | 13075.7412 | 5226.607 | NORMAL
313.706 | 0.45 | 297.037 | 1.11 | 2 | 101352.97 | 15009.1149 | 13459.1086 | 4888.016 | NORMAL
313.706 | 0.45 | 297.037 | 1.11 | 2 | 106868.78 | 14996.2192 | 13696.047 | 4822.208 | NORMAL
313.706 | 0.45 | 297.037 | 1.42 | 1 | 57226.51 | 11064.2145 | 11053.5044 | 4214.57 | NORMAL
313.706 | 0.45 | 297.037 | 1.42 | 1 | 79289.74 | 11622.0692 | 11610.9701 | 3833.06 | NORMAL
313.706 | 0.45 | 297.037 | 1.42 | 1 | 101352.97 | 11702.7257 | 11691.9358 | 3623.715 | NORMAL
313.706 | 0.45 | 297.037 | 1.42 | 1 | 106868.78 | 11982.0047 | 11970.6457 | 3588.619 | NORMAL
313.706 | 0.45 | 297.037 | 1.42 | 2 | 57226.51 | 13986.8699 | 13974.7013 | 5886.14 | NORMAL
313.706 | 0.45 | 297.037 | 1.42 | 2 | 79289.74 | 14935.9613 | 14558.0068 | 5263.64 | NORMAL
313.706 | 0.45 | 297.037 | 1.42 | 2 | 101352.97 | 15467.2919 | 14889.0472 | 4919.853 | NORMAL
313.706 | 0.45 | 297.037 | 1.42 | 2 | 106868.78 | 15469.7831 | 15112.23 | 4852.522 | NORMAL
313.706 | 0.45 | 299.814 | 0.5 | 1 | 57226.51 | 10365.2696 | 7551.4306 | 4168.748 | NORMAL
313.706 | 0.45 | 299.814 | 0.5 | 1 | 79289.74 | 10715.4162 | 7943.5416 | 3809.008 | NORMAL
313.706 | 0.45 | 299.814 | 0.5 | 1 | 101352.97 | 10824.5311 | 8258.2837 | 3618.493 | NORMAL
313.706 | 0.45 | 299.814 | 0.5 | 1 | 106868.78 | 10758.8804 | 8205.5614 | 3587.1479 | NORMAL
313.706 | 0.45 | 299.814 | 0.5 | 2 | 57226.51 | 13361.7233 | 8479.0557 | 5784.871 | NORMAL
313.706 | 0.45 | 299.814 | 0.5 | 2 | 79289.74 | 13761.3716 | 9140.826 | 5148.516 | NORMAL
313.706 | 0.45 | 299.814 | 0.5 | 2 | 101352.97 | 13840.5334 | 9644.5681 | 4810.047 | NORMAL
313.706 | 0.45 | 299.814 | 0.5 | 2 | 106868.78 | 13773.4173 | 9657.6999 | 4745.7181 | NORMAL
313.706 | 0.45 | 299.814 | 0.8 | 1 | 57226.51 | 10924.6776 | 10045.0553 | 4202.937 | NORMAL
313.706 | 0.45 | 299.814 | 0.8 | 1 | 79289.74 | 11482.5029 | 10190.3998 | 3828.504 | NORMAL
313.706 | 0.45 | 299.814 | 0.8 | 1 | 101352.97 | 11758.0891 | 10443.7111 | 3624.011 | NORMAL
313.706 | 0.45 | 299.814 | 0.8 | 1 | 106868.78 | 11725.0293 | 10631.5531 | 3587.202 | NORMAL
313.706 | 0.45 | 299.814 | 0.8 | 2 | 57226.51 | 14189.6542 | 11163.228 | 5916.696 | NORMAL
313.706 | 0.45 | 299.814 | 0.8 | 2 | 79289.74 | 14946.8933 | 11633.7799 | 5263.262 | NORMAL
313.706 | 0.45 | 299.814 | 0.8 | 2 | 101352.97 | 15291.9109 | 12131.0729 | 4908.481 | NORMAL
313.706 | 0.45 | 299.814 | 0.8 | 2 | 106868.78 | 15258.5287 | 12359.3625 | 4838.857 | NORMAL
313.706 | 0.45 | 299.814 | 1.11 | 1 | 57226.51 | 11209.4666 | 11198.2347 | 4220.65 | NORMAL
313.706 | 0.45 | 299.814 | 1.11 | 1 | 79289.74 | 11879.6307 | 11867.6679 | 3839.64 | NORMAL
313.706 | 0.45 | 299.814 | 1.11 | 1 | 101352.97 | 12238.9801 | 12136.3929 | 3627.764 | NORMAL
313.706 | 0.45 | 299.814 | 1.11 | 1 | 106868.78 | 12219.959 | 12207.7879 | 3589.549 | NORMAL
313.706 | 0.45 | 299.814 | 1.11 | 2 | 57226.51 | 14608.8511 | 13212.2596 | 5980.43 | NORMAL
313.706 | 0.45 | 299.814 | 1.11 | 2 | 79289.74 | 15540.7093 | 13563.4337 | 5322.851 | NORMAL
313.706 | 0.45 | 299.814 | 1.11 | 2 | 101352.97 | 16033.265 | 13977.3034 | 4959.037 | NORMAL
313.706 | 0.45 | 299.814 | 1.11 | 2 | 106868.78 | 16017.2626 | 14254.0663 | 4887.707 | NORMAL
313.706 | 0.45 | 299.814 | 1.42 | 1 | 57226.51 | 11783.939 | 11770.8353 | 4261.68 | NORMAL
313.706 | 0.45 | 299.814 | 1.42 | 1 | 79289.74 | 12124.7069 | 12111.782 | 3848.28 | NORMAL
313.706 | 0.45 | 299.814 | 1.42 | 1 | 101352.97 | 12557.2978 | 12543.9117 | 3629.393 | NORMAL
313.706 | 0.45 | 299.814 | 1.42 | 1 | 106868.78 | 12541.7644 | 12528.4952 | 3591.31 | NORMAL
313.706 | 0.45 | 299.814 | 1.42 | 2 | 57226.51 | 14862.8664 | 14847.8103 | 6023.17 | NORMAL
313.706 | 0.45 | 299.814 | 1.42 | 2 | 79289.74 | 15914.1266 | 15170.173 | 5360.4 | NORMAL
313.706 | 0.45 | 299.814 | 1.42 | 2 | 101352.97 | 16500.6155 | 15545.8239 | 4992.234 | NORMAL
313.706 | 0.45 | 299.814 | 1.42 | 2 | 106868.78 | 16502.4033 | 15853.3473 | 4919.319 | NORMAL
313.706 | 0.45 | 302.591 | 0.5 | 1 | 57226.51 | 11150.4982 | 7713.9147 | 4217.226 | NORMAL
313.706 | 0.45 | 302.591 | 0.5 | 1 | 79289.74 | 11540.9437 | 8205.3109 | 3831.228 | NORMAL
313.706 | 0.45 | 302.591 | 0.5 | 1 | 101352.97 | 11666.9695 | 8510.6809 | 3623.491 | NORMAL
313.706 | 0.45 | 302.591 | 0.5 | 1 | 106868.78 | 11595.1348 | 8447.5775 | 3587.275 | NORMAL
313.706 | 0.45 | 302.591 | 0.5 | 2 | 57226.51 | 14283.2943 | 8574.7472 | 5931.618 | NORMAL
313.706 | 0.45 | 302.591 | 0.5 | 2 | 79289.74 | 14755.6565 | 9301.8478 | 5246.059 | NORMAL
313.706 | 0.45 | 302.591 | 0.5 | 2 | 101352.97 | 14854.1325 | 9848.0373 | 4878.866 | NORMAL
313.706 | 0.45 | 302.591 | 0.5 | 2 | 106868.78 | 14777.4912 | 9900.6679 | 4808.4815 | NORMAL
313.706 | 0.45 | 302.591 | 0.8 | 1 | 57226.51 | 11694.9297 | 10409.2008 | 4253.849 | NORMAL
313.706 | 0.45 | 302.591 | 0.8 | 1 | 79289.74 | 12319.7538 | 10573.0468 | 3852.049 | NORMAL
313.706 | 0.45 | 302.591 | 0.8 | 1 | 101352.97 | 12633.4408 | 10886.6781 | 3631.395 | NORMAL
313.706 | 0.45 | 302.591 | 0.8 | 1 | 106868.78 | 12589.2732 | 11089.8278 | 3591.708 | NORMAL
313.706 | 0.45 | 302.591 | 0.8 | 2 | 57226.51 | 15116.3247 | 11597.7885 | 6060.57 | NORMAL
313.706 | 0.45 | 302.591 | 0.8 | 2 | 79289.74 | 15954.7186 | 11989.9072 | 5363.615 | NORMAL
313.706 | 0.45 | 302.591 | 0.8 | 2 | 101352.97 | 16345.7503 | 12532.3358 | 4981.982 | NORMAL
313.706 | 0.45 | 302.591 | 0.8 | 2 | 106868.78 | 16307.9426 | 12791.9501 | 4906.585 | NORMAL
313.706 | 0.45 | 302.591 | 1.11 | 1 | 57226.51 | 11976.0258 | 11962.2534 | 4272.23 | NORMAL
313.706 | 0.45 | 302.591 | 1.11 | 1 | 79289.74 | 12711.2251 | 12477.8597 | 3864.946 | NORMAL
313.706 | 0.45 | 302.591 | 1.11 | 1 | 101352.97 | 13118.4935 | 12672.8977 | 3636.686 | NORMAL
313.706 | 0.45 | 302.591 | 1.11 | 1 | 106868.78 | 13090.5334 | 12968.6082 | 3595.45 | NORMAL
313.706 | 0.45 | 302.591 | 1.11 | 2 | 57226.51 | 15520.5451 | 13761.5241 | 6124.94 | NORMAL
313.706 | 0.45 | 302.591 | 1.11 | 2 | 79289.74 | 16549.9707 | 13994.4566 | 5424.666 | NORMAL
313.706 | 0.45 | 302.591 | 1.11 | 2 | 101352.97 | 17100.9379 | 14484.0668 | 5034.749 | NORMAL
313.706 | 0.45 | 302.591 | 1.11 | 2 | 106868.78 | 17076.7292 | 14800.0938 | 4958.006 | NORMAL
313.706 | 0.45 | 302.591 | 1.42 | 1 | 57226.51 | 12161.6061 | 12146.9635 | 4285.1 | NORMAL
313.706 | 0.45 | 302.591 | 1.42 | 1 | 79289.74 | 12968.5229 | 12952.6883 | 3873.38 | NORMAL
313.706 | 0.45 | 302.591 | 1.42 | 1 | 101352.97 | 13445.1348 | 13428.7318 | 3639.216 | NORMAL
313.706 | 0.45 | 302.591 | 1.42 | 1 | 106868.78 | 13416.2075 | 13399.9471 | 3598.094 | NORMAL
313.706 | 0.45 | 302.591 | 1.42 | 2 | 57226.51 | 15772.7726 | 15689.6816 | 6166.9 | NORMAL
313.706 | 0.45 | 302.591 | 1.42 | 2 | 79289.74 | 16921.3072 | 15713.1766 | 5463.25 | NORMAL
313.706 | 0.45 | 302.591 | 1.42 | 2 | 101352.97 | 17574.0914 | 16175.1059 | 5069.194 | NORMAL
313.706 | 0.45 | 302.591 | 1.42 | 2 | 106868.78 | 17569.959 | 16491.2513 | 4990.813 | NORMAL
313.706 | 0.45 | 305.368 | 0.5 | 1 | 57226.51 | 11949.7948 | 7845.6976 | 4271.411 | NORMAL
313.706 | 0.45 | 305.368 | 0.5 | 1 | 79289.74 | 12408.4994 | 8379.0005 | 3855.794 | NORMAL
313.706 | 0.45 | 305.368 | 0.5 | 1 | 101352.97 | 12553.2239 | 8740.3202 | 3631.153 | NORMAL
313.706 | 0.45 | 305.368 | 0.5 | 1 | 106868.78 | 12476.9343 | 8663.01 | 3591.037 | NORMAL
313.706 | 0.45 | 305.368 | 0.5 | 2 | 57226.51 | 15254.0446 | 8600.8405 | 6082.548 | NORMAL
313.706 | 0.45 | 305.368 | 0.5 | 2 | 79289.74 | 15802.2274 | 9415.2515 | 5349.356 | NORMAL
313.706 | 0.45 | 305.368 | 0.5 | 2 | 101352.97 | 15924.7362 | 10008.0438 | 4952.908 | NORMAL
313.706 | 0.45 | 305.368 | 0.5 | 2 | 106868.78 | 15839.6835 | 10127.2442 | 4876.359 | NORMAL
313.706 | 0.45 | 305.368 | 0.8 | 1 | 57226.51 | 12495.721 | 10858.5191 | 4308.066 | NORMAL
313.706 | 0.45 | 305.368 | 0.8 | 1 | 79289.74 | 13192.3505 | 10962.5267 | 3878.511 | NORMAL
313.706 | 0.45 | 305.368 | 0.8 | 1 | 101352.97 | 13542.5264 | 11296.4848 | 3641.599 | NORMAL
313.706 | 0.45 | 305.368 | 0.8 | 1 | 106868.78 | 13487.1629 | 11513.7348 | 3598.675 | NORMAL
313.706 | 0.45 | 305.368 | 0.8 | 2 | 57226.51 | 16057.8839 | 11937.5915 | 6211.64 | NORMAL
313.706 | 0.45 | 305.368 | 0.8 | 2 | 79289.74 | 17007.7374 | 12384.8643 | 5469.056 | NORMAL
313.706 | 0.45 | 305.368 | 0.8 | 2 | 101352.97 | 17446.5416 | 12903.4098 | 5060.544 | NORMAL
313.706 | 0.45 | 305.368 | 0.8 | 2 | 106868.78 | 17400.1172 | 13200.1987 | 4979.482 | NORMAL
313.706 | 0.45 | 305.368 | 1.11 | 1 | 57226.51 | 12771.9519 | 12755.2718 | 4326.88 | NORMAL
313.706 | 0.45 | 305.368 | 1.11 | 1 | 79289.74 | 13586.2251 | 12965.3482 | 3892.323 | NORMAL
313.706 | 0.45 | 305.368 | 1.11 | 1 | 101352.97 | 14039.2732 | 13208.9625 | 3647.996 | NORMAL
313.706 | 0.45 | 305.368 | 1.11 | 1 | 106868.78 | 14001.0551 | 13533.5179 | 3603.344 | NORMAL
313.706 | 0.45 | 305.368 | 1.11 | 2 | 57226.51 | 16460.8148 | 14314.6044 | 6274.52 | NORMAL
313.706 | 0.45 | 305.368 | 1.11 | 2 | 79289.74 | 17591.7644 | 14501.7885 | 5532.358 | NORMAL
313.706 | 0.45 | 305.368 | 1.11 | 2 | 101352.97 | 18210.8148 | 15030.3142 | 5115.282 | NORMAL
313.706 | 0.45 | 305.368 | 1.11 | 2 | 106868.78 | 18183.7925 | 15321.2817 | 5032.368 | NORMAL
313.706 | 0.45 | 305.368 | 1.42 | 1 | 57226.51 | 12951.1137 | 12933.4743 | 4339.39 | NORMAL
313.706 | 0.45 | 305.368 | 1.42 | 1 | 79289.74 | 13850.5569 | 13831.4015 | 3901.09 | NORMAL
313.706 | 0.45 | 305.368 | 1.42 | 1 | 101352.97 | 14358.646 | 14338.7449 | 3651.443 | NORMAL
313.706 | 0.45 | 305.368 | 1.42 | 1 | 106868.78 | 14342.1454 | 14322.4393 | 3606.571 | NORMAL
313.706 | 0.45 | 305.368 | 1.42 | 2 | 57226.51 | 16731.3599 | 16194.5677 | 6313.41 | NORMAL
313.706 | 0.45 | 305.368 | 1.42 | 2 | 79289.74 | 17967.4091 | 16363.1531 | 5571.28 | NORMAL
313.706 | 0.45 | 305.368 | 1.42 | 2 | 101352.97 | 18687.6612 | 16730.1661 | 5150.843 | NORMAL
313.706 | 0.45 | 305.368 | 1.42 | 2 | 106868.78 | 18681.9461 | 17152.1562 | 5066.461 | NORMAL
313.706 | 0.55 | 288.706 | 0.5 | 1 | 57226.51 | 7988.687 | 5766.1304 | 4026.946 | NORMAL
313.706 | 0.55 | 288.706 | 0.5 | 1 | 79289.74 | 8165.2696 | 6122.8009 | 3756.535 | NORMAL
313.706 | 0.55 | 288.706 | 0.5 | 1 | 101352.97 | 8170.721 | 6384.822 | 3621.961 | NORMAL
313.706 | 0.55 | 288.706 | 0.5 | 1 | 106868.78 | 8124.0914 | 6371.14 | 3600.2367 | NORMAL
313.706 | 0.55 | 288.706 | 0.5 | 2 | 57226.51 | 10551.4068 | 6709.1226 | 5347.479 | NORMAL
313.706 | 0.55 | 288.706 | 0.5 | 2 | 79289.74 | 10753.0774 | 7401.3969 | 4860.036 | NORMAL
313.706 | 0.55 | 288.706 | 0.5 | 2 | 101352.97 | 10770.1641 | 7862.6398 | 4605.913 | NORMAL
313.706 | 0.55 | 288.706 | 0.5 | 2 | 106868.78 | 10720.9848 | 7935.4049 | 4561.8553 | NORMAL
313.706 | 0.55 | 288.706 | 0.8 | 1 | 57226.51 | 8503.9859 | 7336.6778 | 4056.292 | NORMAL
313.706 | 0.55 | 288.706 | 0.8 | 1 | 79289.74 | 8844.959 | 7589.417 | 3765.585 | NORMAL
313.706 | 0.55 | 288.706 | 0.8 | 1 | 101352.97 | 8990.4748 | 7835.1628 | 3617.281 | NORMAL
313.706 | 0.55 | 288.706 | 0.8 | 1 | 106868.78 | 8956.8288 | 7979.3253 | 3592.393 | NORMAL
313.706 | 0.55 | 288.706 | 0.8 | 2 | 57226.51 | 11365.3869 | 8616.9522 | 5473.492 | NORMAL
313.706 | 0.55 | 288.706 | 0.8 | 2 | 79289.74 | 11809.027 | 9135.168 | 4960.294 | NORMAL
313.706 | 0.55 | 288.706 | 0.8 | 2 | 101352.97 | 11938.7163 | 9621.5786 | 4681.342 | NORMAL
313.706 | 0.55 | 288.706 | 0.8 | 2 | 106868.78 | 11920.3107 | 9580.0318 | 4631.609 | NORMAL
313.706 | 0.55 | 288.706 | 1.11 | 1 | 57226.51 | 8761.1665 | 8638.4576 | 4073.11 | NORMAL
313.706 | 0.55 | 288.706 | 1.11 | 1 | 79289.74 | 9184.2028 | 8733.2401 | 3773.428 | NORMAL
313.706 | 0.55 | 288.706 | 1.11 | 1 | 101352.97 | 9390.8851 | 8884.7258 | 3619.022 | NORMAL
313.706 | 0.55 | 288.706 | 1.11 | 1 | 106868.78 | 9372.4209 | 9041.5182 | 3589.338 | NORMAL
313.706 | 0.55 | 288.706 | 1.11 | 2 | 57226.51 | 11756.6823 | 9925.3674 | 5533.96 | NORMAL
313.706 | 0.55 | 288.706 | 1.11 | 2 | 79289.74 | 12342.3505 | 10369.1789 | 5007.961 | NORMAL
313.706 | 0.55 | 288.706 | 1.11 | 2 | 101352.97 | 12620.34 | 10782.137 | 4727.328 | NORMAL
313.706 | 0.55 | 288.706 | 1.11 | 2 | 106868.78 | 12599.2673 | 10990.7944 | 4673.522 | NORMAL
313.706 | 0.55 | 288.706 | 1.42 | 1 | 57226.51 | 8927.8429 | 8922.7362 | 4082.14 | NORMAL
313.706 | 0.55 | 288.706 | 1.42 | 1 | 79289.74 | 9409.4666 | 9404.075 | 3776.14 | NORMAL
313.706 | 0.55 | 288.706 | 1.42 | 1 | 101352.97 | 9650.4396 | 9644.9292 | 3618.589 | NORMAL
313.706 | 0.55 | 288.706 | 1.42 | 1 | 106868.78 | 9639.5662 | 9634.1102 | 3587.85 | NORMAL
313.706 | 0.55 | 288.706 | 1.42 | 2 | 57226.51 | 12003.0774 | 11107.6598 | 5571.99 | NORMAL
313.706 | 0.55 | 288.706 | 1.42 | 2 | 79289.74 | 12674.5604 | 11412.5037 | 5042.89 | NORMAL
313.706 | 0.55 | 288.706 | 1.42 | 2 | 101352.97 | 13025.3224 | 11728.3129 | 4754.242 | NORMAL
313.706 | 0.55 | 288.706 | 1.42 | 2 | 106868.78 | 13015.7679 | 11962.4538 | 4699.006 | NORMAL
313.706 | 0.55 | 291.483 | 0.5 | 1 | 57226.51 | 8710.8441 | 5948.0257 | 4067.858 | NORMAL
313.706 | 0.55 | 291.483 | 0.5 | 1 | 79289.74 | 8910.4924 | 6385.1252 | 3768.433 | NORMAL
313.706 | 0.55 | 291.483 | 0.5 | 1 | 101352.97 | 8947.5967 | 6682.0742 | 3617.271 | NORMAL
313.706 | 0.55 | 291.483 | 0.5 | 1 | 106868.78 | 8895.0469 | 6675.7505 | 3592.7815 | NORMAL
313.706 | 0.55 | 291.483 | 0.5 | 2 | 57226.51 | 11414.3904 | 6873.0382 | 5480.453 | NORMAL
313.706 | 0.55 | 291.483 | 0.5 | 2 | 79289.74 | 11576.1137 | 7574.2859 | 4940.327 | NORMAL
313.706 | 0.55 | 291.483 | 0.5 | 2 | 101352.97 | 11610.8734 | 8074.7819 | 4661.468 | NORMAL
313.706 | 0.55 | 291.483 | 0.5 | 2 | 106868.78 | 11555.5686 | 8192.147 | 4610.002 | NORMAL
313.706 | 0.55 | 291.483 | 0.8 | 1 | 57226.51 | 9236.9871 | 7669.9692 | 4098.999 | NORMAL
313.706 | 0.55 | 291.483 | 0.8 | 1 | 79289.74 | 9618.5229 | 7940.7543 | 3781.852 | NORMAL
313.706 | 0.55 | 291.483 | 0.8 | 1 | 101352.97 | 9778.6635 | 8219.084 | 3618.287 | NORMAL
313.706 | 0.55 | 291.483 | 0.8 | 1 | 106868.78 | 9740.4748 | 8402.3966 | 3589.937 | NORMAL
313.706 | 0.55 | 291.483 | 0.8 | 2 | 57226.51 | 12218.2591 | 8909.4812 | 5606.573 | NORMAL
313.706 | 0.55 | 291.483 | 0.8 | 2 | 79289.74 | 12728.6928 | 9464.5723 | 5044.613 | NORMAL
313.706 | 0.55 | 291.483 | 0.8 | 2 | 101352.97 | 12926.3775 | 9966.4826 | 4747.513 | NORMAL
313.706 | 0.55 | 291.483 | 0.8 | 2 | 106868.78 | 12887.0164 | 10055.4296 | 4691.055 | NORMAL
313.706 | 0.55 | 291.483 | 1.11 | 1 | 57226.51 | 9493.8453 | 9013.8459 | 4117.49 | NORMAL
313.706 | 0.55 | 291.483 | 1.11 | 1 | 79289.74 | 9968.2005 | 9167.5945 | 3790.791 | NORMAL
313.706 | 0.55 | 291.483 | 1.11 | 1 | 101352.97 | 10204.0739 | 9403.1765 | 3618.3 | NORMAL
313.706 | 0.55 | 291.483 | 1.11 | 1 | 106868.78 | 10175.1758 | 9596.7476 | 3588.18 | NORMAL
313.706 | 0.55 | 291.483 | 1.11 | 2 | 57226.51 | 12614.449 | 10331.5996 | 5667.97 | NORMAL
313.706 | 0.55 | 291.483 | 1.11 | 2 | 79289.74 | 13279.2497 | 10785.9511 | 5097.656 | NORMAL
313.706 | 0.55 | 291.483 | 1.11 | 2 | 101352.97 | 13593.0832 | 11239.672 | 4792.314 | NORMAL
313.706 | 0.55 | 291.483 | 1.11 | 2 | 106868.78 | 13569.1676 | 11487.0739 | 4733.087 | NORMAL
313.706 | 0.55 | 291.483 | 1.42 | 1 | 57226.51 | 9668.0832 | 9661.4123 | 4125.55 | NORMAL
313.706 | 0.55 | 291.483 | 1.42 | 1 | 79289.74 | 10201.2896 | 10161.5045 | 3794.15 | NORMAL
313.706 | 0.55 | 291.483 | 1.42 | 1 | 101352.97 | 10474.9707 | 10279.4554 | 3618.601 | NORMAL
313.706 | 0.55 | 291.483 | 1.42 | 1 | 106868.78 | 10453.9273 | 10446.7664 | 3587.426 | NORMAL
313.706 | 0.55 | 291.483 | 1.42 | 2 | 57226.51 | 12862.9543 | 11537.4654 | 5706.59 | NORMAL
313.706 | 0.55 | 291.483 | 1.42 | 2 | 79289.74 | 13620.0762 | 11938.6914 | 5134.09 | NORMAL
313.706 | 0.55 | 291.483 | 1.42 | 2 | 101352.97 | 14015.8558 | 12314.8355 | 4820.63 | NORMAL
313.706 | 0.55 | 291.483 | 1.42 | 2 | 106868.78 | 14002.5205 | 12573.8713 | 4760.016 | NORMAL
313.706 | 0.55 | 294.26 | 0.5 | 1 | 57226.51 | 9463.6284 | 6127.4344 | 4112.092 | NORMAL
313.706 | 0.55 | 294.26 | 0.5 | 1 | 79289.74 | 9692.8781 | 6583.3834 | 3785.117 | NORMAL
313.706 | 0.55 | 294.26 | 0.5 | 1 | 101352.97 | 9732.415 | 6925.1291 | 3618.402 | NORMAL
313.706 | 0.55 | 294.26 | 0.5 | 1 | 106868.78 | 9672.1864 | 6914.0561 | 3590.1829 | NORMAL
313.706 | 0.55 | 294.26 | 0.5 | 2 | 57226.51 | 12297.3623 | 6918.6559 | 5617.928 | NORMAL
313.706 | 0.55 | 294.26 | 0.5 | 2 | 79289.74 | 12554.6307 | 7741.9009 | 5031.615 | NORMAL
313.706 | 0.55 | 294.26 | 0.5 | 2 | 101352.97 | 12556.2134 | 8300.4606 | 4724.475 | NORMAL
313.706 | 0.55 | 294.26 | 0.5 | 2 | 106868.78 | 12489.3904 | 8429.2145 | 4666.7441 | NORMAL
313.706 | 0.55 | 294.26 | 0.8 | 1 | 57226.51 | 9995.9848 | 8031.4939 | 4144.53 | NORMAL
313.706 | 0.55 | 294.26 | 0.8 | 1 | 79289.74 | 10425.4982 | 8288.6047 | 3800.649 | NORMAL
313.706 | 0.55 | 294.26 | 0.8 | 1 | 101352.97 | 10603.6928 | 8603.4652 | 3621.854 | NORMAL
313.706 | 0.55 | 294.26 | 0.8 | 1 | 106868.78 | 10564.0094 | 8806.1477 | 3587.299 | NORMAL
313.706 | 0.55 | 294.26 | 0.8 | 2 | 57226.51 | 13112.8664 | 9250.3404 | 5744.301 | NORMAL
313.706 | 0.55 | 294.26 | 0.8 | 2 | 79289.74 | 13688.4232 | 9793.3003 | 5139.617 | NORMAL
313.706 | 0.55 | 294.26 | 0.8 | 2 | 101352.97 | 13921.0141 | 10309.2905 | 4814.02 | NORMAL
313.706 | 0.55 | 294.26 | 0.8 | 2 | 106868.78 | 13874.238 | 10359.1304 | 4752.041 | NORMAL
313.706 | 0.55 | 294.26 | 1.11 | 1 | 57226.51 | 10253.3412 | 9447.1722 | 4161.8 | NORMAL
313.706 | 0.55 | 294.26 | 1.11 | 1 | 79289.74 | 10788.3353 | 9603.5603 | 3809.619 | NORMAL
313.706 | 0.55 | 294.26 | 1.11 | 1 | 101352.97 | 11055.6565 | 9862.3532 | 3619.13 | NORMAL
313.706 | 0.55 | 294.26 | 1.11 | 1 | 106868.78 | 11016.8523 | 10105.1747 | 3586.801 | NORMAL
313.706 | 0.55 | 294.26 | 1.11 | 2 | 57226.51 | 13503.6635 | 10744.0008 | 5808.08 | NORMAL
313.706 | 0.55 | 294.26 | 1.11 | 2 | 79289.74 | 14256.5065 | 11192.5979 | 5192.667 | NORMAL
313.706 | 0.55 | 294.26 | 1.11 | 2 | 101352.97 | 14612.5733 | 11683.746 | 4861.27 | NORMAL
313.706 | 0.55 | 294.26 | 1.11 | 2 | 106868.78 | 14584.408 | 11974.0615 | 4796.501 | NORMAL
313.706 | 0.55 | 294.26 | 1.42 | 1 | 57226.51 | 10419.3435 | 10410.8101 | 4173.77 | NORMAL
313.706 | 0.55 | 294.26 | 1.42 | 1 | 79289.74 | 11022.1864 | 10736.0835 | 3814.66 | NORMAL
313.706 | 0.55 | 294.26 | 1.42 | 1 | 101352.97 | 11335.6096 | 10873.7062 | 3620.237 | NORMAL
313.706 | 0.55 | 294.26 | 1.42 | 1 | 106868.78 | 11302.6377 | 11148.255 | 3588.98 | NORMAL
313.706 | 0.55 | 294.26 | 1.42 | 2 | 57226.51 | 13752.0809 | 12018.081 | 5847.09 | NORMAL
313.706 | 0.55 | 294.26 | 1.42 | 2 | 79289.74 | 14603.6049 | 12392.3271 | 5230.29 | NORMAL
313.706 | 0.55 | 294.26 | 1.42 | 2 | 101352.97 | 15049.238 | 12864.4799 | 4890.941 | NORMAL
313.706 | 0.55 | 294.26 | 1.42 | 2 | 106868.78 | 15033.558 | 13173.4709 | 4824.897 | NORMAL
313.706 | 0.55 | 297.037 | 0.5 | 1 | 57226.51 | 10251.2016 | 6294.1455 | 4160.184 | NORMAL
313.706 | 0.55 | 297.037 | 0.5 | 1 | 79289.74 | 10519.4021 | 6791.7889 | 3804.574 | NORMAL
313.706 | 0.55 | 297.037 | 0.5 | 1 | 101352.97 | 10568.8453 | 7160.9739 | 3618.727 | NORMAL
313.706 | 0.55 | 297.037 | 0.5 | 1 | 106868.78 | 10499.1208 | 7137.1028 | 3587.3581 | NORMAL
313.706 | 0.55 | 297.037 | 0.5 | 2 | 57226.51 | 13220.9261 | 6898.4677 | 5766.672 | NORMAL
313.706 | 0.55 | 297.037 | 0.5 | 2 | 79289.74 | 13542.4091 | 7822.9216 | 5126.812 | NORMAL
313.706 | 0.55 | 297.037 | 0.5 | 2 | 101352.97 | 13555.3048 | 8460.7875 | 4790.492 | NORMAL
313.706 | 0.55 | 297.037 | 0.5 | 2 | 106868.78 | 13472.0692 | 8639.5841 | 4727.1949 | NORMAL
313.706 | 0.55 | 297.037 | 0.8 | 1 | 57226.51 | 10777.6377 | 8354.9541 | 4194.843 | NORMAL
313.706 | 0.55 | 297.037 | 0.8 | 1 | 79289.74 | 11271.2485 | 8647.3808 | 3822.116 | NORMAL
313.706 | 0.55 | 297.037 | 0.8 | 1 | 101352.97 | 11481.7702 | 8960.3505 | 3620.85 | NORMAL
313.706 | 0.55 | 297.037 | 0.8 | 1 | 106868.78 | 11429.66 | 9173.9709 | 3586.984 | NORMAL
313.706 | 0.55 | 297.037 | 0.8 | 2 | 57226.51 | 14041.5592 | 9490.5775 | 5890.922 | NORMAL
313.706 | 0.55 | 297.037 | 0.8 | 2 | 79289.74 | 14701.6999 | 10095.4074 | 5238.791 | NORMAL
313.706 | 0.55 | 297.037 | 0.8 | 2 | 101352.97 | 14971.6882 | 10663.4202 | 4885.419 | NORMAL
313.706 | 0.55 | 297.037 | 0.8 | 2 | 106868.78 | 14917.7902 | 10634.9374 | 4817.508 | NORMAL
313.706 | 0.55 | 297.037 | 1.11 | 1 | 57226.51 | 11042.0868 | 9877.3564 | 4211.37 | NORMAL
313.706 | 0.55 | 297.037 | 1.11 | 1 | 79289.74 | 11640.7093 | 10030.6944 | 3832.178 | NORMAL
313.706 | 0.55 | 297.037 | 1.11 | 1 | 101352.97 | 11936.5475 | 10276.2334 | 3625.311 | NORMAL
313.706 | 0.55 | 297.037 | 1.11 | 1 | 106868.78 | 11897.3623 | 10541.8839 | 3588.307 | NORMAL
313.706 | 0.55 | 297.037 | 1.11 | 2 | 57226.51 | 14434.9648 | 11168.8375 | 5953.55 | NORMAL
313.706 | 0.55 | 297.037 | 1.11 | 2 | 79289.74 | 15278.3705 | 11624.7621 | 5293.344 | NORMAL
313.706 | 0.55 | 297.037 | 1.11 | 2 | 101352.97 | 15683.0012 | 12117.7688 | 4935.003 | NORMAL
313.706 | 0.55 | 297.037 | 1.11 | 2 | 106868.78 | 15651.0258 | 12422.1253 | 4864.375 | NORMAL
313.706 | 0.55 | 297.037 | 1.42 | 1 | 57226.51 | 11209.4373 | 11198.6874 | 4222.64 | NORMAL
313.706 | 0.55 | 297.037 | 1.42 | 1 | 79289.74 | 11878.4877 | 11227.1665 | 3837.92 | NORMAL
313.706 | 0.55 | 297.037 | 1.42 | 1 | 101352.97 | 12228.4877 | 11489.2634 | 3627.326 | NORMAL
313.706 | 0.55 | 297.037 | 1.42 | 1 | 106868.78 | 12195.4865 | 11714.2892 | 3589.669 | NORMAL
313.706 | 0.55 | 297.037 | 1.42 | 2 | 57226.51 | 14681.3599 | 12560.887 | 5992.76 | NORMAL
313.706 | 0.55 | 297.037 | 1.42 | 2 | 79289.74 | 15628.9273 | 12878.2674 | 5331.69 | NORMAL
313.706 | 0.55 | 297.037 | 1.42 | 2 | 101352.97 | 16130.0703 | 13334.084 | 4966.124 | NORMAL
313.706 | 0.55 | 297.037 | 1.42 | 2 | 106868.78 | 16111.8699 | 13720.1111 | 4894.255 | NORMAL
313.706 | 0.55 | 299.814 | 0.5 | 1 | 57226.51 | 11059.8476 | 6357.9082 | 4212.565 | NORMAL
313.706 | 0.55 | 299.814 | 0.5 | 1 | 79289.74 | 11382.7374 | 6931.313 | 3826.748 | NORMAL
313.706 | 0.55 | 299.814 | 0.5 | 1 | 101352.97 | 11451.2896 | 7351.35 | 3621.838 | NORMAL
313.706 | 0.55 | 299.814 | 0.5 | 1 | 106868.78 | 11369.1383 | 7341.3255 | 3586.897 | NORMAL
313.706 | 0.55 | 299.814 | 0.5 | 2 | 57226.51 | 14193.3763 | 6836.8926 | 5916.009 | NORMAL
313.706 | 0.55 | 299.814 | 0.5 | 2 | 79289.74 | 14581.5358 | 7863.064 | 5228.267 | NORMAL
313.706 | 0.55 | 299.814 | 0.5 | 2 | 101352.97 | 14608.2063 | 8576.1858 | 4862.125 | NORMAL
313.706 | 0.55 | 299.814 | 0.5 | 2 | 106868.78 | 14515.2989 | 8823.7486 | 4792.2018 | NORMAL
313.706 | 0.55 | 299.814 | 0.8 | 1 | 57226.51 | 11595.9554 | 8695.7026 | 4246.52 | NORMAL
313.706 | 0.55 | 299.814 | 0.8 | 1 | 79289.74 | 12146.8347 | 8973.0854 | 3847.821 | NORMAL
313.706 | 0.55 | 299.814 | 0.8 | 1 | 101352.97 | 12388.3646 | 9305.5077 | 3628.482 | NORMAL
313.706 | 0.55 | 299.814 | 0.8 | 1 | 106868.78 | 12330.2755 | 9557.7391 | 3590.48 | NORMAL
313.706 | 0.55 | 299.814 | 0.8 | 2 | 57226.51 | 15000.5276 | 9650.7694 | 6042.616 | NORMAL
313.706 | 0.55 | 299.814 | 0.8 | 2 | 79289.74 | 15755.1583 | 10369.5568 | 5343.253 | NORMAL
313.706 | 0.55 | 299.814 | 0.8 | 2 | 101352.97 | 16070.8089 | 10899.6565 | 4961.728 | NORMAL
313.706 | 0.55 | 299.814 | 0.8 | 2 | 106868.78 | 16011.5182 | 10861.5575 | 4887.607 | NORMAL
313.706 | 0.55 | 299.814 | 1.11 | 1 | 57226.51 | 11859.2614 | 10400.2402 | 4263.95 | NORMAL
313.706 | 0.55 | 299.814 | 1.11 | 1 | 79289.74 | 12523.4467 | 10429.8395 | 3857.432 | NORMAL
313.706 | 0.55 | 299.814 | 1.11 | 1 | 101352.97 | 12855.1583 | 10720.4693 | 3633.996 | NORMAL
313.706 | 0.55 | 299.814 | 1.11 | 1 | 106868.78 | 12811.1958 | 11024.3286 | 3593.488 | NORMAL
313.706 | 0.55 | 299.814 | 1.11 | 2 | 57226.51 | 15389.1266 | 11531.5035 | 6104.4 | NORMAL
313.706 | 0.55 | 299.814 | 1.11 | 2 | 79289.74 | 16335.3751 | 12011.0093 | 5399.041 | NORMAL
313.706 | 0.55 | 299.814 | 1.11 | 2 | 101352.97 | 16797.8312 | 12567.3478 | 5013.186 | NORMAL
313.706 | 0.55 | 299.814 | 1.11 | 2 | 106868.78 | 16761.782 | 12875.898 | 4936.656 | NORMAL
313.706 | 0.55 | 299.814 | 1.42 | 1 | 57226.51 | 12017.7315 | 11660.204 | 4276.67 | NORMAL
313.706 | 0.55 | 299.814 | 1.42 | 1 | 79289.74 | 12764.1559 | 11714.8402 | 3863.89 | NORMAL
313.706 | 0.55 | 299.814 | 1.42 | 1 | 101352.97 | 13155.1876 | 11959.8151 | 3636.828 | NORMAL
313.706 | 0.55 | 299.814 | 1.42 | 1 | 106868.78 | 13116.9109 | 12305.0791 | 3595.58 | NORMAL
313.706 | 0.55 | 299.814 | 1.42 | 2 | 57226.51 | 15634.3787 | 13098.0134 | 6143.18 | NORMAL
313.706 | 0.55 | 299.814 | 1.42 | 2 | 79289.74 | 16685.17 | 13366.2227 | 5438.57 | NORMAL
313.706 | 0.55 | 299.814 | 1.42 | 2 | 101352.97 | 17251.2016 | 13854.0605 | 5045.88 | NORMAL
313.706 | 0.55 | 299.814 | 1.42 | 2 | 106868.78 | 17231.7116 | 14227.9141 | 4967.841 | NORMAL
313.706 | 0.55 | 302.591 | 0.5 | 1 | 57226.51 | 11904.1618 | 6365.3577 | 4268.399 | NORMAL
313.706 | 0.55 | 302.591 | 0.5 | 1 | 79289.74 | 12292.9074 | 7002.7407 | 3852.038 | NORMAL
313.706 | 0.55 | 302.591 | 0.5 | 1 | 101352.97 | 12377.3154 | 7474.7845 | 3629.411 | NORMAL
313.706 | 0.55 | 302.591 | 0.5 | 1 | 106868.78 | 12286.5768 | 7531.5733 | 3590.363 | NORMAL
313.706 | 0.55 | 302.591 | 0.5 | 2 | 57226.51 | 15201.7878 | 6682.9187 | 6074.488 | NORMAL
313.706 | 0.55 | 302.591 | 0.5 | 2 | 79289.74 | 15674.9121 | 7845.074 | 5336.488 | NORMAL
313.706 | 0.55 | 302.591 | 0.5 | 2 | 101352.97 | 15728.3998 | 8667.0246 | 4939.222 | NORMAL
313.706 | 0.55 | 302.591 | 0.5 | 2 | 106868.78 | 15625.4396 | 8939.3453 | 4862.83 | NORMAL
313.706 | 0.55 | 302.591 | 0.8 | 1 | 57226.51 | 12438.7456 | 8968.9948 | 4303.103 | NORMAL
313.706 | 0.55 | 302.591 | 0.8 | 1 | 79289.74 | 13062.456 | 9270.7908 | 3875.305 | NORMAL
313.706 | 0.55 | 302.591 | 0.8 | 1 | 101352.97 | 13336.4595 | 9674.0277 | 3639.555 | NORMAL
313.706 | 0.55 | 302.591 | 0.8 | 1 | 106868.78 | 13273.7104 | 9811.5153 | 3596.929 | NORMAL
313.706 | 0.55 | 302.591 | 0.8 | 2 | 57226.51 | 15995.9554 | 9650.8718 | 6199.979 | NORMAL
313.706 | 0.55 | 302.591 | 0.8 | 2 | 79289.74 | 16851.4654 | 10552.7752 | 5454.233 | NORMAL
313.706 | 0.55 | 302.591 | 0.8 | 2 | 101352.97 | 17224.0621 | 11099.6507 | 5043.608 | NORMAL
313.706 | 0.55 | 302.591 | 0.8 | 2 | 106868.78 | 17159.5252 | 11035.8741 | 4962.987 | NORMAL
313.706 | 0.55 | 302.591 | 1.11 | 1 | 57226.51 | 12689.4783 | 10734.9814 | 4321.79 | NORMAL
313.706 | 0.55 | 302.591 | 1.11 | 1 | 79289.74 | 13442.3798 | 10847.4359 | 3885.791 | NORMAL
313.706 | 0.55 | 302.591 | 1.11 | 1 | 101352.97 | 13814.8593 | 11202.801 | 3645.247 | NORMAL
313.706 | 0.55 | 302.591 | 1.11 | 1 | 106868.78 | 13765.9144 | 11478.1433 | 3601.158 | NORMAL
313.706 | 0.55 | 302.591 | 1.11 | 2 | 57226.51 | 16383.4701 | 11884.3071 | 6259.8 | NORMAL
313.706 | 0.55 | 302.591 | 1.11 | 2 | 79289.74 | 17430.6272 | 12346.6013 | 5511.28 | NORMAL
313.706 | 0.55 | 302.591 | 1.11 | 2 | 101352.97 | 17959.6131 | 12975.0482 | 5097.091 | NORMAL
313.706 | 0.55 | 302.591 | 1.11 | 2 | 106868.78 | 17921.3072 | 13356.0334 | 5014.041 | NORMAL
313.706 | 0.55 | 302.591 | 1.42 | 1 | 57226.51 | 12855.51 | 12185.1465 | 4333.3 | NORMAL
313.706 | 0.55 | 302.591 | 1.42 | 1 | 79289.74 | 13684.8769 | 12141.1544 | 3893.13 | NORMAL
313.706 | 0.55 | 302.591 | 1.42 | 1 | 101352.97 | 14122.0692 | 12496.6472 | 3649.003 | NORMAL
313.706 | 0.55 | 302.591 | 1.42 | 1 | 106868.78 | 14077.6671 | 12815.4494 | 3604.056 | NORMAL
313.706 | 0.55 | 302.591 | 1.42 | 2 | 57226.51 | 16625.762 | 13557.86 | 6297.77 | NORMAL
313.706 | 0.55 | 302.591 | 1.42 | 2 | 79289.74 | 17778.0188 | 13859.4945 | 5551.38 | NORMAL
313.706 | 0.55 | 302.591 | 1.42 | 2 | 101352.97 | 18416.7937 | 14349.8684 | 5130.782 | NORMAL
313.706 | 0.55 | 302.591 | 1.42 | 2 | 106868.78 | 18397.5088 | 14771.0655 | 5046.448 | NORMAL
313.706 | 0.55 | 305.368 | 0.5 | 1 | 57226.51 | 12789.83 | 6288.0688 | 4327.436 | NORMAL
313.706 | 0.55 | 305.368 | 0.5 | 1 | 79289.74 | 13241.823 | 7053.1776 | 3880.867 | NORMAL
313.706 | 0.55 | 305.368 | 0.5 | 1 | 101352.97 | 13352.9894 | 7559.2876 | 3639.793 | NORMAL
313.706 | 0.55 | 305.368 | 0.5 | 1 | 106868.78 | 13252.3447 | 7715.8729 | 3596.765 | NORMAL
313.706 | 0.55 | 305.368 | 0.5 | 2 | 57226.51 | 16239.7128 | 6445.7856 | 6239.844 | NORMAL
313.706 | 0.55 | 305.368 | 0.5 | 2 | 79289.74 | 16818.7573 | 7756.424 | 5452.287 | NORMAL
313.706 | 0.55 | 305.368 | 0.5 | 2 | 101352.97 | 16912.2802 | 8713.3421 | 5022.615 | NORMAL
313.706 | 0.55 | 305.368 | 0.5 | 2 | 106868.78 | 16800.6448 | 8989.605 | 4939.36 | NORMAL
313.706 | 0.55 | 305.368 | 0.8 | 1 | 57226.51 | 13305.3048 | 9357.0088 | 4364.035 | NORMAL
313.706 | 0.55 | 305.368 | 0.8 | 1 | 79289.74 | 14007.8253 | 9536.0652 | 3906.693 | NORMAL
313.706 | 0.55 | 305.368 | 0.8 | 1 | 101352.97 | 14335.2579 | 9994.5418 | 3652.584 | NORMAL
313.706 | 0.55 | 305.368 | 0.8 | 1 | 106868.78 | 14268.8159 | 9993.3222 | 3605.821 | NORMAL
313.706 | 0.55 | 305.368 | 0.8 | 2 | 57226.51 | 17030.3048 | 9680.5532 | 6361.28 | NORMAL
313.706 | 0.55 | 305.368 | 0.8 | 2 | 79289.74 | 17987.0164 | 10695.2778 | 5571.69 | NORMAL
313.706 | 0.55 | 305.368 | 0.8 | 2 | 101352.97 | 18421.864 | 11324.4725 | 5131.581 | NORMAL
313.706 | 0.55 | 305.368 | 0.8 | 2 | 106868.78 | 18360.5217 | 11181.4475 | 5043.825 | NORMAL
313.706 | 0.55 | 305.368 | 1.11 | 1 | 57226.51 | 13553.2239 | 11097.4475 | 4382.87 | NORMAL
313.706 | 0.55 | 305.368 | 1.11 | 1 | 79289.74 | 14395.5744 | 11212.641 | 3917.68 | NORMAL
313.706 | 0.55 | 305.368 | 1.11 | 1 | 101352.97 | 14814.8886 | 11637.0061 | 3659.434 | NORMAL
313.706 | 0.55 | 305.368 | 1.11 | 1 | 106868.78 | 14770.0469 | 11969.3506 | 3611.34 | NORMAL
313.706 | 0.55 | 305.368 | 1.11 | 2 | 57226.51 | 17408.7925 | 12349.7452 | 6419.4 | NORMAL
313.706 | 0.55 | 305.368 | 1.11 | 2 | 79289.74 | 18555.4513 | 12689.3866 | 5632.597 | NORMAL
313.706 | 0.55 | 305.368 | 1.11 | 2 | 101352.97 | 19166.3247 | 13358.0467 | 5186.515 | NORMAL
313.706 | 0.55 | 305.368 | 1.11 | 2 | 106868.78 | 19127.4326 | 13732.1003 | 5096.843 | NORMAL
313.706 | 0.55 | 305.368 | 1.42 | 1 | 57226.51 | 13723.4467 | 12857.3599 | 4394.08 | NORMAL
313.706 | 0.55 | 305.368 | 1.42 | 1 | 79289.74 | 14639.1852 | 12667.975 | 3925.83 | NORMAL
313.706 | 0.55 | 305.368 | 1.42 | 1 | 101352.97 | 15128.5756 | 12966.4752 | 3664.228 | NORMAL
313.706 | 0.55 | 305.368 | 1.42 | 1 | 106868.78 | 15085.9613 | 13308.1864 | 3615.204 | NORMAL
313.706 | 0.55 | 305.368 | 1.42 | 2 | 57226.51 | 17652.9895 | 13880.1043 | 6455.98 | NORMAL
313.706 | 0.55 | 305.368 | 1.42 | 2 | 79289.74 | 18903.7222 | 14137.262 | 5670.05 | NORMAL
313.706 | 0.55 | 305.368 | 1.42 | 2 | 101352.97 | 19623.8277 | 14838.3414 | 5221.349 | NORMAL
313.706 | 0.55 | 305.368 | 1.42 | 2 | 106868.78 | 19605.9203 | 15259.3466 | 5130.307 | NORMAL
313.706 | 0.65 | 288.706 | 0.5 | 1 | 57226.51 | 8408.1184 | 4934.1698 | 4052.956 | NORMAL
313.706 | 0.65 | 288.706 | 0.5 | 1 | 79289.74 | 8552.8722 | 5481.3049 | 3761.363 | NORMAL
313.706 | 0.65 | 288.706 | 0.5 | 1 | 101352.97 | 8547.0692 | 5844.4004 | 3619.016 | NORMAL
313.706 | 0.65 | 288.706 | 0.5 | 1 | 106868.78 | 8492.4091 | 5879.074 | 3594.8683 | NORMAL
313.706 | 0.65 | 288.706 | 0.5 | 2 | 57226.51 | 11080.891 | 5855.2647 | 5429.017 | NORMAL
313.706 | 0.65 | 288.706 | 0.5 | 2 | 79289.74 | 11195.4865 | 6716.038 | 4902.492 | NORMAL
313.706 | 0.65 | 288.706 | 0.5 | 2 | 101352.97 | 11170.8675 | 7304.1499 | 4632.558 | NORMAL
313.706 | 0.65 | 288.706 | 0.5 | 2 | 106868.78 | 11106.5651 | 7401.6482 | 4583.9854 | NORMAL
313.706 | 0.65 | 288.706 | 0.8 | 1 | 57226.51 | 8916.2954 | 6442.7724 | 4081.086 | NORMAL
313.706 | 0.65 | 288.706 | 0.8 | 1 | 79289.74 | 9229.4549 | 6774.0415 | 3774.469 | NORMAL
313.706 | 0.65 | 288.706 | 0.8 | 1 | 101352.97 | 9341.9109 | 7105.5976 | 3618.839 | NORMAL
313.706 | 0.65 | 288.706 | 0.8 | 1 | 106868.78 | 9300.6155 | 7170.4583 | 3589.683 | NORMAL
313.706 | 0.65 | 288.706 | 0.8 | 2 | 57226.51 | 11863.1301 | 7482.3728 | 5549.03 | NORMAL
313.706 | 0.65 | 288.706 | 0.8 | 2 | 79289.74 | 12279.4256 | 8203.3439 | 5002.383 | NORMAL
313.706 | 0.65 | 288.706 | 0.8 | 2 | 101352.97 | 12418.6401 | 8734.3028 | 4713.896 | NORMAL
313.706 | 0.65 | 288.706 | 0.8 | 2 | 106868.78 | 12373.8863 | 8745.8876 | 4659.843 | NORMAL
313.706 | 0.65 | 288.706 | 1.11 | 1 | 57226.51 | 9164.449 | 7393.5842 | 4095.28 | NORMAL
313.706 | 0.65 | 288.706 | 1.11 | 1 | 79289.74 | 9568.6108 | 7680.8865 | 3779.706 | NORMAL
313.706 | 0.65 | 288.706 | 1.11 | 1 | 101352.97 | 9742.9367 | 7993.5729 | 3618.194 | NORMAL
313.706 | 0.65 | 288.706 | 1.11 | 1 | 106868.78 | 9710.6389 | 8232.5146 | 3587.693 | NORMAL
313.706 | 0.65 | 288.706 | 1.11 | 2 | 57226.51 | 12242.2626 | 8777.2248 | 5608.66 | NORMAL
313.706 | 0.65 | 288.706 | 1.11 | 2 | 79289.74 | 12805.1876 | 9285.7714 | 5055.612 | NORMAL
313.706 | 0.65 | 288.706 | 1.11 | 2 | 101352.97 | 13055.9203 | 9828.1051 | 4756.457 | NORMAL
313.706 | 0.65 | 288.706 | 1.11 | 2 | 106868.78 | 13022.0106 | 10035.6729 | 4699.513 | NORMAL
313.706 | 0.65 | 288.706 | 1.42 | 1 | 57226.51 | 9315.2989 | 8318.8787 | 4105.97 | NORMAL
313.706 | 0.65 | 288.706 | 1.42 | 1 | 79289.74 | 9776.2309 | 8441.5212 | 3784.63 | NORMAL
313.706 | 0.65 | 288.706 | 1.42 | 1 | 101352.97 | 9993.728 | 8692.6546 | 3618.152 | NORMAL
313.706 | 0.65 | 288.706 | 1.42 | 1 | 106868.78 | 9968.1712 | 8922.7293 | 3586.769 | NORMAL
313.706 | 0.65 | 288.706 | 1.42 | 2 | 57226.51 | 12478.136 | 9635.3795 | 5645.04 | NORMAL
313.706 | 0.65 | 288.706 | 1.42 | 2 | 79289.74 | 13134.2907 | 10148.5644 | 5087.24 | NORMAL
313.706 | 0.65 | 288.706 | 1.42 | 2 | 101352.97 | 13464.1266 | 10688.2142 | 4778.489 | NORMAL
313.706 | 0.65 | 288.706 | 1.42 | 2 | 106868.78 | 13434.0563 | 10998.65 | 4724.537 | NORMAL
313.706 | 0.65 | 291.483 | 0.5 | 1 | 57226.51 | 9189.9179 | 4979.5295 | 4095.552 | NORMAL
313.706 | 0.65 | 291.483 | 0.5 | 1 | 79289.74 | 9360.0528 | 5599.5299 | 3776.13 | NORMAL
313.706 | 0.65 | 291.483 | 0.5 | 1 | 101352.97 | 9354.3962 | 6027.7859 | 3616.202 | NORMAL
313.706 | 0.65 | 291.483 | 0.5 | 1 | 106868.78 | 9287.2802 | 6091.0348 | 3589.5756 | NORMAL
313.706 | 0.65 | 291.483 | 0.5 | 2 | 57226.51 | 11984.3787 | 5878.098 | 5569.153 | NORMAL
313.706 | 0.65 | 291.483 | 0.5 | 2 | 79289.74 | 12165.3576 | 6830.4468 | 4994.807 | NORMAL
313.706 | 0.65 | 291.483 | 0.5 | 2 | 101352.97 | 12086.8699 | 7475.028 | 4695.499 | NORMAL
313.706 | 0.65 | 291.483 | 0.5 | 2 | 106868.78 | 12001.7878 | 7569.1915 | 4637.3444 | NORMAL
313.706 | 0.65 | 291.483 | 0.8 | 1 | 57226.51 | 9699.7655 | 6681.7029 | 4127.52 | NORMAL
313.706 | 0.65 | 291.483 | 0.8 | 1 | 79289.74 | 10058.8511 | 7074.219 | 3792.927 | NORMAL
313.706 | 0.65 | 291.483 | 0.8 | 1 | 101352.97 | 10192.3798 | 7417.2904 | 3618.078 | NORMAL
313.706 | 0.65 | 291.483 | 0.8 | 1 | 106868.78 | 10140.2403 | 7433.293 | 3588.068 | NORMAL
313.706 | 0.65 | 291.483 | 0.8 | 2 | 57226.51 | 12773.5639 | 7620.3633 | 5692.839 | NORMAL
313.706 | 0.65 | 291.483 | 0.8 | 2 | 79289.74 | 13269.578 | 8384.9269 | 5097.294 | NORMAL
313.706 | 0.65 | 291.483 | 0.8 | 2 | 101352.97 | 13432.5616 | 8937.5966 | 4781.615 | NORMAL
313.706 | 0.65 | 291.483 | 0.8 | 2 | 106868.78 | 13376.7585 | 8991.2952 | 4721.335 | NORMAL
313.706 | 0.65 | 291.483 | 1.11 | 1 | 57226.51 | 9951.905 | 7756.883 | 4142.01 | NORMAL
313.706 | 0.65 | 291.483 | 1.11 | 1 | 79289.74 | 10409.7304 | 8033.1889 | 3799.274 | NORMAL
313.706 | 0.65 | 291.483 | 1.11 | 1 | 101352.97 | 10612.6319 | 8366.9459 | 3618.658 | NORMAL
313.706 | 0.65 | 291.483 | 1.11 | 1 | 106868.78 | 10570.7503 | 8605.7429 | 3587.11 | NORMAL
313.706 | 0.65 | 291.483 | 1.11 | 2 | 57226.51 | 13157.9132 | 8989.3679 | 5753.71 | NORMAL
313.706 | 0.65 | 291.483 | 1.11 | 2 | 79289.74 | 13809.0856 | 9669.7431 | 5152.582 | NORMAL
313.706 | 0.65 | 291.483 | 1.11 | 2 | 101352.97 | 14098.9156 | 10211.3229 | 4826.471 | NORMAL
313.706 | 0.65 | 291.483 | 1.11 | 2 | 106868.78 | 14060.0821 | 10340.6842 | 4763.717 | NORMAL
313.706 | 0.65 | 291.483 | 1.42 | 1 | 57226.51 | 10106.6237 | 8700.3982 | 4152.39 | NORMAL
313.706 | 0.65 | 291.483 | 1.42 | 1 | 79289.74 | 10623.9156 | 8860.5793 | 3804.73 | NORMAL
313.706 | 0.65 | 291.483 | 1.42 | 1 | 101352.97 | 10874.3845 | 9202.959 | 3620.053 | NORMAL
313.706 | 0.65 | 291.483 | 1.42 | 1 | 106868.78 | 10840.3576 | 9464.933 | 3586.784 | NORMAL
313.706 | 0.65 | 291.483 | 1.42 | 2 | 57226.51 | 13395.1055 | 10010.7249 | 5790.45 | NORMAL
313.706 | 0.65 | 291.483 | 1.42 | 2 | 79289.74 | 14145.6624 | 10481.7661 | 5185.46 | NORMAL
313.706 | 0.65 | 291.483 | 1.42 | 2 | 101352.97 | 14524.3259 | 11078.8072 | 4849.466 | NORMAL
313.706 | 0.65 | 291.483 | 1.42 | 2 | 106868.78 | 14489.3318 | 11412.3628 | 4790.213 | NORMAL
313.706 | 0.65 | 294.26 | 0.5 | 1 | 57226.51 | 9993.6694 | 4963.3559 | 4145.355 | NORMAL
313.706 | 0.65 | 294.26 | 0.5 | 1 | 79289.74 | 10205.5979 | 5672.7408 | 3795.174 | NORMAL
313.706 | 0.65 | 294.26 | 0.5 | 1 | 101352.97 | 10204.7773 | 6159.2974 | 3618.59 | NORMAL
313.706 | 0.65 | 294.26 | 0.5 | 1 | 106868.78 | 10126.905 | 6275.319 | 3588.1362 | NORMAL
313.706 | 0.65 | 294.26 | 0.5 | 2 | 57226.51 | 12936.694 | 5866.5449 | 5718.011 | NORMAL
313.706 | 0.65 | 294.26 | 0.5 | 2 | 79289.74 | 13175.2931 | 6910.9024 | 5091.605 | NORMAL
313.706 | 0.65 | 294.26 | 0.5 | 2 | 101352.97 | 13132.4443 | 7617.146 | 4762.451 | NORMAL
313.706 | 0.65 | 294.26 | 0.5 | 2 | 106868.78 | 13039.83 | 7744.7332 | 4700.8206 | NORMAL
313.706 | 0.65 | 294.26 | 0.8 | 1 | 57226.51 | 10510.0528 | 6820.9402 | 4177.642 | NORMAL
313.706 | 0.65 | 294.26 | 0.8 | 1 | 79289.74 | 10925.0586 | 7326.8687 | 3813.987 | NORMAL
313.706 | 0.65 | 294.26 | 0.8 | 1 | 101352.97 | 11089.0094 | 7693.1111 | 3618.286 | NORMAL
313.706 | 0.65 | 294.26 | 0.8 | 1 | 106868.78 | 11024.9707 | 7642.8625 | 3586.673 | NORMAL
313.706 | 0.65 | 294.26 | 0.8 | 2 | 57226.51 | 13728.9566 | 7591.4128 | 5842.557 | NORMAL
313.706 | 0.65 | 294.26 | 0.8 | 2 | 79289.74 | 14308.1477 | 8470.0514 | 5198.116 | NORMAL
313.706 | 0.65 | 294.26 | 0.8 | 2 | 101352.97 | 14504.3962 | 9107.3249 | 4853.989 | NORMAL
313.706 | 0.65 | 294.26 | 0.8 | 2 | 106868.78 | 14441.6764 | 9210.3524 | 4787.551 | NORMAL
313.706 | 0.65 | 294.26 | 1.11 | 1 | 57226.51 | 10764.2145 | 8150.857 | 4192.72 | NORMAL
313.706 | 0.65 | 294.26 | 1.11 | 1 | 79289.74 | 11284.9355 | 8397.4026 | 3821.542 | NORMAL
313.706 | 0.65 | 294.26 | 1.11 | 1 | 101352.97 | 11522.9777 | 8760.0788 | 3621.556 | NORMAL
313.706 | 0.65 | 294.26 | 1.11 | 1 | 106868.78 | 11474.0914 | 8999.3709 | 3587.123 | NORMAL
313.706 | 0.65 | 294.26 | 1.11 | 2 | 57226.51 | 14104.7773 | 9282.1847 | 5906.2 | NORMAL
313.706 | 0.65 | 294.26 | 1.11 | 2 | 79289.74 | 14856.5651 | 9954.5226 | 5255.427 | NORMAL
313.706 | 0.65 | 294.26 | 1.11 | 2 | 101352.97 | 15193.6108 | 10594.7783 | 4901.196 | NORMAL
313.706 | 0.65 | 294.26 | 1.11 | 2 | 106868.78 | 15149.7948 | 10575.7991 | 4832.345 | NORMAL
313.706 | 0.65 | 294.26 | 1.42 | 1 | 57226.51 | 10920.9848 | 9101.7562 | 4202.87 | NORMAL
313.706 | 0.65 | 294.26 | 1.42 | 1 | 79289.74 | 11503.9859 | 9226.4843 | 3827.76 | NORMAL
313.706 | 0.65 | 294.26 | 1.42 | 1 | 101352.97 | 11793.728 | 9587.8999 | 3623.658 | NORMAL
313.706 | 0.65 | 294.26 | 1.42 | 1 | 106868.78 | 11755.2169 | 9930.6074 | 3587.017 | NORMAL
313.706 | 0.65 | 294.26 | 1.42 | 2 | 57226.51 | 14341.735 | 10411.2105 | 5942.47 | NORMAL
313.706 | 0.65 | 294.26 | 1.42 | 2 | 79289.74 | 15197.5088 | 10902.4649 | 5289.31 | NORMAL
313.706 | 0.65 | 294.26 | 1.42 | 2 | 101352.97 | 15632.2978 | 11497.3205 | 4925.333 | NORMAL
313.706 | 0.65 | 294.26 | 1.42 | 2 | 106868.78 | 15592.7608 | 11831.9117 | 4860.411 | NORMAL
313.706 | 0.65 | 297.037 | 0.5 | 1 | 57226.51 | 10841.5299 | 4885.0199 | 4197.142 | NORMAL
313.706 | 0.65 | 297.037 | 0.5 | 1 | 79289.74 | 11096.5416 | 5703.1563 | 3818.74 | NORMAL
313.706 | 0.65 | 297.037 | 0.5 | 1 | 101352.97 | 11112.3388 | 6259.836 | 3619.558 | NORMAL
313.706 | 0.65 | 297.037 | 0.5 | 1 | 106868.78 | 11022.3623 | 6443.0557 | 3586.7176 | NORMAL
313.706 | 0.65 | 297.037 | 0.5 | 2 | 57226.51 | 13935.3458 | 5842.8257 | 5875.707 | NORMAL
313.706 | 0.65 | 297.037 | 0.5 | 2 | 79289.74 | 14249.619 | 6975.4735 | 5196.076 | NORMAL
313.706 | 0.65 | 297.037 | 0.5 | 2 | 101352.97 | 14218.2298 | 7737.3758 | 4835.416 | NORMAL
313.706 | 0.65 | 297.037 | 0.5 | 2 | 106868.78 | 14113.3353 | 7868.9607 | 4767.2525 | NORMAL
313.706 | 0.65 | 297.037 | 0.8 | 1 | 57226.51 | 11353.0774 | 6857.1225 | 4231.53 | NORMAL
313.706 | 0.65 | 297.037 | 0.8 | 1 | 79289.74 | 11832.9719 | 7526.6102 | 3838.359 | NORMAL
313.706 | 0.65 | 297.037 | 0.8 | 1 | 101352.97 | 12020.4572 | 7883.0399 | 3626.059 | NORMAL
313.706 | 0.65 | 297.037 | 0.8 | 1 | 106868.78 | 11959.1149 | 7814.0259 | 3588.007 | NORMAL
313.706 | 0.65 | 297.037 | 0.8 | 2 | 57226.51 | 14722.5381 | 7523.2759 | 5999.06 | NORMAL
313.706 | 0.65 | 297.037 | 0.8 | 2 | 79289.74 | 15397.9777 | 8488.5818 | 5305.765 | NORMAL
313.706 | 0.65 | 297.037 | 0.8 | 2 | 101352.97 | 15638.1008 | 9192.8263 | 4931.965 | NORMAL
313.706 | 0.65 | 297.037 | 0.8 | 2 | 106868.78 | 15567.6729 | 9409.8955 | 4859.138 | NORMAL
313.706 | 0.65 | 297.037 | 1.11 | 1 | 57226.51 | 11603.136 | 8404.9056 | 4247.87 | NORMAL
313.706 | 0.65 | 297.037 | 1.11 | 1 | 79289.74 | 12199.2087 | 8676.5774 | 3847.064 | NORMAL
313.706 | 0.65 | 297.037 | 1.11 | 1 | 101352.97 | 12472.245 | 9122.2624 | 3629.666 | NORMAL
313.706 | 0.65 | 297.037 | 1.11 | 1 | 106868.78 | 12420.0176 | 9429.7866 | 3590.51 | NORMAL
313.706 | 0.65 | 297.037 | 1.11 | 2 | 57226.51 | 15098.6518 | 9504.707 | 6059.35 | NORMAL
313.706 | 0.65 | 297.037 | 1.11 | 2 | 79289.74 | 15950 | 10196.2927 | 5364.261 | NORMAL
313.706 | 0.65 | 297.037 | 1.11 | 2 | 101352.97 | 16344.0797 | 10859.5459 | 4981.346 | NORMAL
313.706 | 0.65 | 297.037 | 1.11 | 2 | 106868.78 | 16295.9848 | 10765.1764 | 4906.24 | NORMAL
313.706 | 0.65 | 297.037 | 1.42 | 1 | 57226.51 | 11762.9836 | 9457.6388 | 4257.7 | NORMAL
313.706 | 0.65 | 297.037 | 1.42 | 1 | 79289.74 | 12421.8347 | 9589.4328 | 3853.82 | NORMAL
313.706 | 0.65 | 297.037 | 1.42 | 1 | 101352.97 | 12751.0844 | 9954.7206 | 3632.519 | NORMAL
313.706 | 0.65 | 297.037 | 1.42 | 1 | 106868.78 | 12707.8839 | 10344.7258 | 3592.42 | NORMAL
313.706 | 0.65 | 297.037 | 1.42 | 2 | 57226.51 | 15330.4807 | 10701.0434 | 6096.37 | NORMAL
313.706 | 0.65 | 297.037 | 1.42 | 2 | 79289.74 | 16292.4384 | 11241.2612 | 5398.89 | NORMAL
313.706 | 0.65 | 297.037 | 1.42 | 2 | 101352.97 | 16781.3892 | 11908.3087 | 5012.411 | NORMAL
313.706 | 0.65 | 297.037 | 1.42 | 2 | 106868.78 | 16748.8277 | 12288.7488 | 4935.907 | NORMAL
313.706 | 0.65 | 299.814 | 0.5 | 1 | 57226.51 | 11712.6905 | 4743.3117 | 4253.796 | NORMAL
313.706 | 0.65 | 299.814 | 0.5 | 1 | 79289.74 | 12029.8066 | 5692.4684 | 3844.191 | NORMAL
313.706 | 0.65 | 299.814 | 0.5 | 1 | 101352.97 | 12061.8699 | 6329.6471 | 3626.585 | NORMAL
313.706 | 0.65 | 299.814 | 0.5 | 1 | 106868.78 | 11963.7749 | 6570.0266 | 3588.584 | NORMAL
313.706 | 0.65 | 299.814 | 0.5 | 2 | 57226.51 | 14969.578 | 5825.6807 | 6039.585 | NORMAL
313.706 | 0.65 | 299.814 | 0.5 | 2 | 79289.74 | 15376.8171 | 7022.823 | 5307.424 | NORMAL
313.706 | 0.65 | 299.814 | 0.5 | 2 | 101352.97 | 15369.3142 | 7824.2105 | 4914.126 | NORMAL
313.706 | 0.65 | 299.814 | 0.5 | 2 | 106868.78 | 15251.4361 | 7957.33 | 4839.295 | NORMAL
313.706 | 0.65 | 299.814 | 0.8 | 1 | 57226.51 | 12219.0797 | 6874.0021 | 4289.261 | NORMAL
313.706 | 0.65 | 299.814 | 0.8 | 1 | 79289.74 | 12774.8828 | 7624.3566 | 3865.775 | NORMAL
313.706 | 0.65 | 299.814 | 0.8 | 1 | 101352.97 | 12997.2157 | 8070.4521 | 3635.549 | NORMAL
313.706 | 0.65 | 299.814 | 0.8 | 1 | 106868.78 | 12930.4513 | 7962.1064 | 3593.784 | NORMAL
313.706 | 0.65 | 299.814 | 0.8 | 2 | 57226.51 | 15740.7093 | 7392.1676 | 6160.844 | NORMAL
313.706 | 0.65 | 299.814 | 0.8 | 2 | 79289.74 | 16528.2239 | 8436.7493 | 5419.191 | NORMAL
313.706 | 0.65 | 299.814 | 0.8 | 2 | 101352.97 | 16822.5381 | 9212.6443 | 5015.381 | NORMAL
313.706 | 0.65 | 299.814 | 0.8 | 2 | 106868.78 | 16747.7433 | 9590.143 | 4935.902 | NORMAL
313.706 | 0.65 | 299.814 | 1.11 | 1 | 57226.51 | 12467.5264 | 8694.1921 | 4306.13 | NORMAL
313.706 | 0.65 | 299.814 | 1.11 | 1 | 79289.74 | 13139.0094 | 8967.9126 | 3876.737 | NORMAL
313.706 | 0.65 | 299.814 | 1.11 | 1 | 101352.97 | 13460.0528 | 9447.4764 | 3640.555 | NORMAL
313.706 | 0.65 | 299.814 | 1.11 | 1 | 106868.78 | 13403.0774 | 9745.4044 | 3597.62 | NORMAL
313.706 | 0.65 | 299.814 | 1.11 | 2 | 57226.51 | 16117.9367 | 9550.0064 | 6219.21 | NORMAL
313.706 | 0.65 | 299.814 | 1.11 | 2 | 79289.74 | 17077.0809 | 10489.7506 | 5478.976 | NORMAL
313.706 | 0.65 | 299.814 | 1.11 | 2 | 101352.97 | 17538.6577 | 11046.2675 | 5066.785 | NORMAL
313.706 | 0.65 | 299.814 | 1.11 | 2 | 106868.78 | 17488.7749 | 10941.6247 | 4984.967 | NORMAL
313.706 | 0.65 | 299.814 | 1.42 | 1 | 57226.51 | 12626.7292 | 9967.1233 | 4316.31 | NORMAL
313.706 | 0.65 | 299.814 | 1.42 | 1 | 79289.74 | 13371.0141 | 10032.2986 | 3883.01 | NORMAL
313.706 | 0.65 | 299.814 | 1.42 | 1 | 101352.97 | 13745.1055 | 10415.5874 | 3644.103 | NORMAL
313.706 | 0.65 | 299.814 | 1.42 | 1 | 106868.78 | 13698.7397 | 10741.7161 | 3600.163 | NORMAL
313.706 | 0.65 | 299.814 | 1.42 | 2 | 57226.51 | 16348.7691 | 11089.1085 | 6255.98 | NORMAL
313.706 | 0.65 | 299.814 | 1.42 | 2 | 79289.74 | 17419.0797 | 11493.9101 | 5514.44 | NORMAL
313.706 | 0.65 | 299.814 | 1.42 | 2 | 101352.97 | 17981.1841 | 12287.532 | 5099.07 | NORMAL
313.706 | 0.65 | 299.814 | 1.42 | 2 | 106868.78 | 17948.1829 | 12764.0477 | 5015.926 | NORMAL
313.706 | 0.65 | 302.591 | 0.5 | 1 | 57226.51 | 12615.7386 | 4577.9487 | 4314.991 | NORMAL
313.706 | 0.65 | 302.591 | 0.5 | 1 | 79289.74 | 13008.5287 | 5640.8103 | 3873.301 | NORMAL
313.706 | 0.65 | 302.591 | 0.5 | 1 | 101352.97 | 13066.0903 | 6380.9166 | 3636.483 | NORMAL
313.706 | 0.65 | 302.591 | 0.5 | 1 | 106868.78 | 12959.408 | 6626.2619 | 3594.461 | NORMAL
313.706 | 0.65 | 302.591 | 0.5 | 2 | 57226.51 | 16047.626 | 5827.2942 | 6209.088 | NORMAL
313.706 | 0.65 | 302.591 | 0.5 | 2 | 79289.74 | 16561.1079 | 7051.9847 | 5426.453 | NORMAL
313.706 | 0.65 | 302.591 | 0.5 | 2 | 101352.97 | 16591.2661 | 7908.4593 | 4999.578 | NORMAL
313.706 | 0.65 | 302.591 | 0.5 | 2 | 106868.78 | 16462.8077 | 8014.9509 | 4917.483 | NORMAL
313.706 | 0.65 | 302.591 | 0.8 | 1 | 57226.51 | 13114.068 | 7116.2047 | 4351.488 | NORMAL
313.706 | 0.65 | 302.591 | 0.8 | 1 | 79289.74 | 13757.0926 | 7710.7954 | 3896.805 | NORMAL
313.706 | 0.65 | 302.591 | 0.8 | 1 | 101352.97 | 14021.5123 | 8284.6807 | 3648.008 | NORMAL
313.706 | 0.65 | 302.591 | 0.8 | 1 | 106868.78 | 13945.3693 | 8084.0887 | 3602.672 | NORMAL
313.706 | 0.65 | 302.591 | 0.8 | 2 | 57226.51 | 16803.2239 | 7073.5187 | 6326.708 | NORMAL
313.706 | 0.65 | 302.591 | 0.8 | 2 | 79289.74 | 17696.0141 | 8328.7529 | 5542.746 | NORMAL
313.706 | 0.65 | 302.591 | 0.8 | 2 | 101352.97 | 18063.3353 | 9176.2827 | 5105.067 | NORMAL
313.706 | 0.65 | 302.591 | 0.8 | 2 | 106868.78 | 17984.3787 | 9697.123 | 5018.475 | NORMAL
313.706 | 0.65 | 302.591 | 1.11 | 1 | 57226.51 | 13359.0856 | 9162.5827 | 4368.73 | NORMAL
313.706 | 0.65 | 302.591 | 1.11 | 1 | 79289.74 | 14123.1536 | 9278.4882 | 3908.791 | NORMAL
313.706 | 0.65 | 302.591 | 1.11 | 1 | 101352.97 | 14493.0832 | 9713.2789 | 3654.37 | NORMAL
313.706 | 0.65 | 302.591 | 1.11 | 1 | 106868.78 | 14432.796 | 9994.8989 | 3607.461 | NORMAL
313.706 | 0.65 | 302.591 | 1.11 | 2 | 57226.51 | 17175.762 | 9622.1195 | 6382.83 | NORMAL
313.706 | 0.65 | 302.591 | 1.11 | 2 | 79289.74 | 18243.9918 | 10564.9315 | 5600.325 | NORMAL
313.706 | 0.65 | 302.591 | 1.11 | 2 | 101352.97 | 18784.1149 | 11197.7368 | 5158.163 | NORMAL
313.706 | 0.65 | 302.591 | 1.11 | 2 | 106868.78 | 18733.3822 | 11051.815 | 5069.643 | NORMAL
313.706 | 0.65 | 302.591 | 1.42 | 1 | 57226.51 | 13517.6143 | 10280.024 | 4379.16 | NORMAL
313.706 | 0.65 | 302.591 | 1.42 | 1 | 79289.74 | 14356.1254 | 10388.0349 | 3916.06 | NORMAL
313.706 | 0.65 | 302.591 | 1.42 | 1 | 101352.97 | 14782.8839 | 10866.1736 | 3658.813 | NORMAL
313.706 | 0.65 | 302.591 | 1.42 | 1 | 106868.78 | 14733.6166 | 11256.8367 | 3610.901 | NORMAL
313.706 | 0.65 | 302.591 | 1.42 | 2 | 57226.51 | 17407.7374 | 11663.01 | 6418.6 | NORMAL
313.706 | 0.65 | 302.591 | 1.42 | 2 | 79289.74 | 18581.2427 | 11847.3446 | 5636.17 | NORMAL
313.706 | 0.65 | 302.591 | 1.42 | 2 | 101352.97 | 19228.0188 | 12597.8326 | 5191.458 | NORMAL
313.706 | 0.65 | 302.591 | 1.42 | 2 | 106868.78 | 19196.1313 | 13076.0783 | 5101.616 | NORMAL
313.706 | 0.65 | 305.368 | 0.5 | 1 | 57226.51 | 13548.0363 | 4326.1319 | 4381.009 | NORMAL
313.706 | 0.65 | 305.368 | 0.5 | 1 | 79289.74 | 14030.6565 | 5545.9958 | 3906.39 | NORMAL
313.706 | 0.65 | 305.368 | 0.5 | 1 | 101352.97 | 14123.3294 | 6407.8111 | 3649.684 | NORMAL
313.706 | 0.65 | 305.368 | 0.5 | 1 | 106868.78 | 14008.0305 | 6650.9008 | 3603.297 | NORMAL
313.706 | 0.65 | 305.368 | 0.5 | 2 | 57226.51 | 17171.2778 | 5896.7198 | 6382.998 | NORMAL
313.706 | 0.65 | 305.368 | 0.5 | 2 | 79289.74 | 17795.1641 | 7099.701 | 5553.86 | NORMAL
313.706 | 0.65 | 305.368 | 0.5 | 2 | 101352.97 | 17881.7995 | 7925.8752 | 5092.201 | NORMAL
313.706 | 0.65 | 305.368 | 0.5 | 2 | 106868.78 | 17742.9367 | 8038.3665 | 5002.46 | NORMAL
313.706 | 0.65 | 305.368 | 0.8 | 1 | 57226.51 | 14034.2614 | 7346.6552 | 4417.598 | NORMAL
313.706 | 0.65 | 305.368 | 0.8 | 1 | 79289.74 | 14780.4513 | 7938.6395 | 3931.589 | NORMAL
313.706 | 0.65 | 305.368 | 0.8 | 1 | 101352.97 | 15091.6764 | 8414.334 | 3663.817 | NORMAL
313.706 | 0.65 | 305.368 | 0.8 | 1 | 106868.78 | 15011.6647 | 8219.637 | 3614.315 | NORMAL
313.706 | 0.65 | 305.368 | 0.8 | 2 | 57226.51 | 17912.2216 | 6764.7296 | 6494.852 | NORMAL
313.706 | 0.65 | 305.368 | 0.8 | 2 | 79289.74 | 18907.2685 | 8128.7263 | 5670.178 | NORMAL
313.706 | 0.65 | 305.368 | 0.8 | 2 | 101352.97 | 19356.653 | 9050.4935 | 5201.227 | NORMAL
313.706 | 0.65 | 305.368 | 0.8 | 2 | 106868.78 | 19275.7913 | 9640.6521 | 5107.219 | NORMAL
313.706 | 0.65 | 305.368 | 1.11 | 1 | 57226.51 | 14276.524 | 9390.4408 | 4435.17 | NORMAL
313.706 | 0.65 | 305.368 | 1.11 | 1 | 79289.74 | 15141.442 | 9597.2667 | 3944.812 | NORMAL
313.706 | 0.65 | 305.368 | 1.11 | 1 | 101352.97 | 15569.578 | 10055.8922 | 3671.809 | NORMAL
313.706 | 0.65 | 305.368 | 1.11 | 1 | 106868.78 | 15506.1547 | 10161.1677 | 3620.694 | NORMAL
313.706 | 0.65 | 305.368 | 1.11 | 2 | 57226.51 | 18285.2286 | 9364.853 | 6548.56 | NORMAL
313.706 | 0.65 | 305.368 | 1.11 | 2 | 79289.74 | 19444.1676 | 10738.6249 | 5727.841 | NORMAL
313.706 | 0.65 | 305.368 | 1.11 | 2 | 101352.97 | 20073.9742 | 11375.4193 | 5255.799 | NORMAL
313.706 | 0.65 | 305.368 | 1.11 | 2 | 106868.78 | 20024.619 | 11085.4088 | 5160.222 | NORMAL
313.706 | 0.65 | 305.368 | 1.42 | 1 | 57226.51 | 14428.517 | 10604.2241 | 4446.31 | NORMAL
313.706 | 0.65 | 305.368 | 1.42 | 1 | 79289.74 | 15374.0328 | 10590.5716 | 3953.06 | NORMAL
313.706 | 0.65 | 305.368 | 1.42 | 1 | 101352.97 | 15862.1629 | 11098.9458 | 3677.015 | NORMAL
313.706 | 0.65 | 305.368 | 1.42 | 1 | 106868.78 | 15811.0786 | 11610.7865 | 3624.914 | NORMAL
313.706 | 0.65 | 305.368 | 1.42 | 2 | 57226.51 | 18523.476 | 11886.0514 | 6582.08 | NORMAL
313.706 | 0.65 | 305.368 | 1.42 | 2 | 79289.74 | 19775.5275 | 12317.3455 | 5764.03 | NORMAL
313.706 | 0.65 | 305.368 | 1.42 | 2 | 101352.97 | 20516.1489 | 13016.286 | 5289.962 | NORMAL
313.706 | 0.65 | 305.368 | 1.42 | 2 | 106868.78 | 20486.6354 | 13272.9838 | 5193.358 | NORMAL
313.706 | 0.75 | 288.706 | 0.5 | 1 | 57226.51 | 8816.6764 | 4110.4051 | 4076.202 | NORMAL
313.706 | 0.75 | 288.706 | 0.5 | 1 | 79289.74 | 8935.932 | 4821.0425 | 3768.277 | NORMAL
313.706 | 0.75 | 288.706 | 0.5 | 1 | 101352.97 | 8896.5123 | 5295.6578 | 3617.292 | NORMAL
313.706 | 0.75 | 288.706 | 0.5 | 1 | 106868.78 | 8824.5311 | 5368.3329 | 3593.2179 | NORMAL
313.706 | 0.75 | 288.706 | 0.5 | 2 | 57226.51 | 11571.3951 | 5282.5501 | 5504.237 | NORMAL
313.706 | 0.75 | 288.706 | 0.5 | 2 | 79289.74 | 11648.9742 | 6142.7604 | 4949.906 | NORMAL
313.706 | 0.75 | 288.706 | 0.5 | 2 | 101352.97 | 11574.8535 | 6772.7014 | 4659.155 | NORMAL
313.706 | 0.75 | 288.706 | 0.5 | 2 | 106868.78 | 11497.626 | 6870.3259 | 4606.6841 | NORMAL
313.706 | 0.75 | 288.706 | 0.8 | 1 | 57226.51 | 9309.2321 | 5192.969 | 4105.378 | NORMAL
313.706 | 0.75 | 288.706 | 0.8 | 1 | 79289.74 | 9620.4279 | 5814.298 | 3773.909 | NORMAL
313.706 | 0.75 | 288.706 | 0.8 | 1 | 101352.97 | 9693.8159 | 6239.9384 | 3618.043 | NORMAL
313.706 | 0.75 | 288.706 | 0.8 | 1 | 106868.78 | 9641.1489 | 6256.1126 | 3587.897 | NORMAL
313.706 | 0.75 | 288.706 | 0.8 | 2 | 57226.51 | 12336.2837 | 5779.6846 | 5623.017 | NORMAL
313.706 | 0.75 | 288.706 | 0.8 | 2 | 79289.74 | 12741.7644 | 6906.3421 | 5049.017 | NORMAL
313.706 | 0.75 | 288.706 | 0.8 | 2 | 101352.97 | 12853.4877 | 7667.8766 | 4742.313 | NORMAL
313.706 | 0.75 | 288.706 | 0.8 | 2 | 106868.78 | 12789.5956 | 7910.0195 | 4685.317 | NORMAL
313.706 | 0.75 | 288.706 | 1.11 | 1 | 57226.51 | 9544.1383 | 6207.6412 | 4118.82 | NORMAL
313.706 | 0.75 | 288.706 | 1.11 | 1 | 79289.74 | 9935.6975 | 6690.5795 | 3788.725 | NORMAL
313.706 | 0.75 | 288.706 | 1.11 | 1 | 101352.97 | 10090.5041 | 7091.5962 | 3617.826 | NORMAL
313.706 | 0.75 | 288.706 | 1.11 | 1 | 106868.78 | 10047.0692 | 7098.7869 | 3586.49 | NORMAL
313.706 | 0.75 | 288.706 | 1.11 | 2 | 57226.51 | 12699.7362 | 7170.487 | 5682.35 | NORMAL
313.706 | 0.75 | 288.706 | 1.11 | 2 | 79289.74 | 13262.4267 | 8016.6993 | 5099.74 | NORMAL
313.706 | 0.75 | 288.706 | 1.11 | 2 | 101352.97 | 13491.5006 | 8637.6499 | 4784.661 | NORMAL
313.706 | 0.75 | 288.706 | 1.11 | 2 | 106868.78 | 13442.4678 | 8712.5742 | 4725.394 | NORMAL
313.706 | 0.75 | 288.706 | 1.42 | 1 | 57226.51 | 9687.8957 | 6912.1489 | 4127.61 | NORMAL
313.706 | 0.75 | 288.706 | 1.42 | 1 | 79289.74 | 10132.4736 | 7251.6695 | 3795.09 | NORMAL
313.706 | 0.75 | 288.706 | 1.42 | 1 | 101352.97 | 10334.9648 | 7694.7844 | 3618.145 | NORMAL
313.706 | 0.75 | 288.706 | 1.42 | 1 | 106868.78 | 10298.4173 | 7986.2785 | 3586.056 | NORMAL
313.706 | 0.75 | 288.706 | 1.42 | 2 | 57226.51 | 12924.0035 | 8118.3808 | 5717.16 | NORMAL
313.706 | 0.75 | 288.706 | 1.42 | 2 | 79289.74 | 13583.7632 | 8922.2096 | 5130.76 | NORMAL
313.706 | 0.75 | 288.706 | 1.42 | 2 | 101352.97 | 13888.0715 | 9562.465 | 4811.101 | NORMAL
313.706 | 0.75 | 288.706 | 1.42 | 2 | 106868.78 | 13850.8499 | 9531.4485 | 4750.531 | NORMAL
313.706 | 0.75 | 291.483 | 0.5 | 1 | 57226.51 | 9644.8124 | 4120.8329 | 4121.815 | NORMAL
313.706 | 0.75 | 291.483 | 0.5 | 1 | 79289.74 | 9794.6366 | 4914.8311 | 3786.74 | NORMAL
313.706 | 0.75 | 291.483 | 0.5 | 1 | 101352.97 | 9756.4771 | 5429.3429 | 3617.369 | NORMAL
313.706 | 0.75 | 291.483 | 0.5 | 1 | 106868.78 | 9677.7843 | 5514.0821 | 3587.5802 | NORMAL
313.706 | 0.75 | 291.483 | 0.5 | 2 | 57226.51 | 12544.6952 | 5254.9352 | 5655.721 | NORMAL
313.706 | 0.75 | 291.483 | 0.5 | 2 | 79289.74 | 12706.3013 | 6206.6597 | 5045.044 | NORMAL
313.706 | 0.75 | 291.483 | 0.5 | 2 | 101352.97 | 12610.551 | 6890.5942 | 4727.448 | NORMAL
313.706 | 0.75 | 291.483 | 0.5 | 2 | 106868.78 | 12514.1852 | 6996.5683 | 4668.5994 | NORMAL
313.706 | 0.75 | 291.483 | 0.8 | 1 | 57226.51 | 10137.5733 | 5169.544 | 4155.362 | NORMAL
313.706 | 0.75 | 291.483 | 0.8 | 1 | 79289.74 | 10488.7456 | 5860.7649 | 3803.581 | NORMAL
313.706 | 0.75 | 291.483 | 0.8 | 1 | 101352.97 | 10597.5967 | 6360.8577 | 3618.979 | NORMAL
313.706 | 0.75 | 291.483 | 0.8 | 1 | 106868.78 | 10534.1735 | 6446.714 | 3587.009 | NORMAL
313.706 | 0.75 | 291.483 | 0.8 | 2 | 57226.51 | 13304.3669 | 5612.9661 | 5776.534 | NORMAL
313.706 | 0.75 | 291.483 | 0.8 | 2 | 79289.74 | 13796.864 | 6874.9635 | 5150.804 | NORMAL
313.706 | 0.75 | 291.483 | 0.8 | 2 | 101352.97 | 13939.2145 | 7764.951 | 4814.888 | NORMAL
313.706 | 0.75 | 291.483 | 0.8 | 2 | 106868.78 | 13866.1196 | 8066.3239 | 4751.62 | NORMAL
313.706 | 0.75 | 291.483 | 1.11 | 1 | 57226.51 | 10374.7069 | 6327.8865 | 4169.6 | NORMAL
313.706 | 0.75 | 291.483 | 1.11 | 1 | 79289.74 | 10827.2274 | 6945.125 | 3810.318 | NORMAL
313.706 | 0.75 | 291.483 | 1.11 | 1 | 101352.97 | 11015.2403 | 7334.8062 | 3618.353 | NORMAL
313.706 | 0.75 | 291.483 | 1.11 | 1 | 106868.78 | 10960.3165 | 7284.5113 | 3586.619 | NORMAL
313.706 | 0.75 | 291.483 | 1.11 | 2 | 57226.51 | 13669.4021 | 7071.1407 | 5833.69 | NORMAL
313.706 | 0.75 | 291.483 | 1.11 | 2 | 79289.74 | 14328.3705 | 8037.9149 | 5203.486 | NORMAL
313.706 | 0.75 | 291.483 | 1.11 | 2 | 101352.97 | 14601.5827 | 8747.5453 | 4859.582 | NORMAL
313.706 | 0.75 | 291.483 | 1.11 | 2 | 106868.78 | 14546.864 | 8911.3362 | 4794.218 | NORMAL
313.706 | 0.75 | 291.483 | 1.42 | 1 | 57226.51 | 10519.7538 | 7278.5125 | 4179.01 | NORMAL
313.706 | 0.75 | 291.483 | 1.42 | 1 | 79289.74 | 11029.8359 | 7507.5571 | 3817.23 | NORMAL
313.706 | 0.75 | 291.483 | 1.42 | 1 | 101352.97 | 11269.9003 | 8015.2658 | 3620.078 | NORMAL
313.706 | 0.75 | 291.483 | 1.42 | 1 | 106868.78 | 11222.5674 | 8287.2263 | 3587.45 | NORMAL
313.706 | 0.75 | 291.483 | 1.42 | 2 | 57226.51 | 13891.4713 | 8212.5684 | 5869.88 | NORMAL
313.706 | 0.75 | 291.483 | 1.42 | 2 | 79289.74 | 14654.7773 | 9107.0648 | 5235.56 | NORMAL
313.706 | 0.75 | 291.483 | 1.42 | 2 | 101352.97 | 15010.4338 | 9754.8606 | 4888.657 | NORMAL
313.706 | 0.75 | 291.483 | 1.42 | 2 | 106868.78 | 14971.0141 | 9730.1561 | 4821.03 | NORMAL
313.706 | 0.75 | 294.26 | 0.5 | 1 | 57226.51 | 10502.3447 | 4175.6062 | 4174.337 | NORMAL
313.706 | 0.75 | 294.26 | 0.5 | 1 | 79289.74 | 10697.4502 | 4980.0054 | 3808.374 | NORMAL
313.706 | 0.75 | 294.26 | 0.5 | 1 | 101352.97 | 10670.7796 | 5548.7414 | 3618.212 | NORMAL
313.706 | 0.75 | 294.26 | 0.5 | 1 | 106868.78 | 10577.1688 | 5622.9499 | 3586.8626 | NORMAL
313.706 | 0.75 | 294.26 | 0.5 | 2 | 57226.51 | 13556.1547 | 5220.4481 | 5820.686 | NORMAL
313.706 | 0.75 | 294.26 | 0.5 | 2 | 79289.74 | 13793.8746 | 6218.0028 | 5149.987 | NORMAL
313.706 | 0.75 | 294.26 | 0.5 | 2 | 101352.97 | 13703.517 | 6962.8118 | 4800.401 | NORMAL
313.706 | 0.75 | 294.26 | 0.5 | 2 | 106868.78 | 13592.4678 | 7079.4329 | 4734.6968 | NORMAL
313.706 | 0.75 | 294.26 | 0.8 | 1 | 57226.51 | 10993.4935 | 5009.6581 | 4209.048 | NORMAL
313.706 | 0.75 | 294.26 | 0.8 | 1 | 79289.74 | 11413.0715 | 5883.7009 | 3825.418 | NORMAL
313.706 | 0.75 | 294.26 | 0.8 | 1 | 101352.97 | 11548.476 | 6439.153 | 3621.904 | NORMAL
313.706 | 0.75 | 294.26 | 0.8 | 1 | 106868.78 | 11476.6413 | 6612.3587 | 3586.936 | NORMAL
313.706 | 0.75 | 294.26 | 0.8 | 2 | 57226.51 | 14308.9683 | 5364.003 | 5935.766 | NORMAL
313.706 | 0.75 | 294.26 | 0.8 | 2 | 79289.74 | 14904.1911 | 6813.0187 | 5258.122 | NORMAL
313.706 | 0.75 | 294.26 | 0.8 | 2 | 101352.97 | 15086.7233 | 7818.1663 | 4893.107 | NORMAL
313.706 | 0.75 | 294.26 | 0.8 | 2 | 106868.78 | 15004.4256 | 8133.584 | 4823.085 | NORMAL
313.706 | 0.75 | 294.26 | 1.11 | 1 | 57226.51 | 11229.0152 | 6358.0818 | 4225.33 | NORMAL
313.706 | 0.75 | 294.26 | 1.11 | 1 | 79289.74 | 11754.66 | 7104.6693 | 3835.167 | NORMAL
313.706 | 0.75 | 294.26 | 1.11 | 1 | 101352.97 | 11983.177 | 7507.4364 | 3621.574 | NORMAL
313.706 | 0.75 | 294.26 | 1.11 | 1 | 106868.78 | 11919.6952 | 7416.2794 | 3587.573 | NORMAL
313.706 | 0.75 | 294.26 | 1.11 | 2 | 57226.51 | 14670.2227 | 6857.625 | 5992.66 | NORMAL
313.706 | 0.75 | 294.26 | 1.11 | 2 | 79289.74 | 15437.6905 | 7994.5933 | 5313.236 | NORMAL
313.706 | 0.75 | 294.26 | 1.11 | 2 | 101352.97 | 15766.6764 | 8779.2954 | 4939.769 | NORMAL
313.706 | 0.75 | 294.26 | 1.11 | 2 | 106868.78 | 15706.3892 | 9079.3296 | 4868.153 | NORMAL
313.706 | 0.75 | 294.26 | 1.42 | 1 | 57226.51 | 11377.3154 | 7609.3192 | 4233.59 | NORMAL
313.706 | 0.75 | 294.26 | 1.42 | 1 | 79289.74 | 11961.8113 | 7836.9122 | 3842.54 | NORMAL
313.706 | 0.75 | 294.26 | 1.42 | 1 | 101352.97 | 12239.9472 | 8309.2228 | 3627.748 | NORMAL
313.706 | 0.75 | 294.26 | 1.42 | 1 | 106868.78 | 12191.9988 | 8526.9377 | 3589.236 | NORMAL
313.706 | 0.75 | 294.26 | 1.42 | 2 | 57226.51 | 14891.9109 | 8255.033 | 6027.79 | NORMAL
313.706 | 0.75 | 294.26 | 1.42 | 2 | 79289.74 | 15767.3505 | 9268.7109 | 5345.98 | NORMAL
313.706 | 0.75 | 294.26 | 1.42 | 2 | 101352.97 | 16184.6131 | 9951.0932 | 4970.265 | NORMAL
313.706 | 0.75 | 294.26 | 1.42 | 2 | 106868.78 | 16141.735 | 9836.0147 | 4896.298 | NORMAL
313.706 | 0.75 | 297.037 | 0.5 | 1 | 57226.51 | 11392.585 | 4199.6828 | 4231.969 | NORMAL
313.706 | 0.75 | 297.037 | 0.5 | 1 | 79289.74 | 11650.8499 | 5044.6083 | 3833.381 | NORMAL
313.706 | 0.75 | 297.037 | 0.5 | 1 | 101352.97 | 11641.354 | 5637.3606 | 3623.122 | NORMAL
313.706 | 0.75 | 297.037 | 0.5 | 1 | 106868.78 | 11539.3318 | 5704.4917 | 3586.269 | NORMAL
313.706 | 0.75 | 297.037 | 0.5 | 2 | 57226.51 | 14626.6706 | 5171.6397 | 5984.606 | NORMAL
313.706 | 0.75 | 297.037 | 0.5 | 2 | 79289.74 | 14947.9191 | 6203.1921 | 5263.096 | NORMAL
313.706 | 0.75 | 297.037 | 0.5 | 2 | 101352.97 | 14874.5018 | 7000.5801 | 4879.981 | NORMAL
313.706 | 0.75 | 297.037 | 0.5 | 2 | 106868.78 | 14750.4689 | 7127.9429 | 4807.1511 | NORMAL
313.706 | 0.75 | 297.037 | 0.8 | 1 | 57226.51 | 11880.422 | 4823.8078 | 4267.16 | NORMAL
313.706 | 0.75 | 297.037 | 0.8 | 1 | 79289.74 | 12376.2896 | 5789.1208 | 3852.791 | NORMAL
313.706 | 0.75 | 297.037 | 0.8 | 1 | 101352.97 | 12545.721 | 6436.6825 | 3630.554 | NORMAL
313.706 | 0.75 | 297.037 | 0.8 | 1 | 106868.78 | 12469.1969 | 6766.2352 | 3590.778 | NORMAL
313.706 | 0.75 | 297.037 | 0.8 | 2 | 57226.51 | 15356.653 | 5008.8641 | 6100.065 | NORMAL
313.706 | 0.75 | 297.037 | 0.8 | 2 | 79289.74 | 16064.6835 | 6714.2666 | 5373.54 | NORMAL
313.706 | 0.75 | 297.037 | 0.8 | 2 | 101352.97 | 16301.993 | 7851.9364 | 4977.39 | NORMAL
313.706 | 0.75 | 297.037 | 0.8 | 2 | 106868.78 | 16209.408 | 8133.8971 | 4900.677 | NORMAL
313.706 | 0.75 | 297.037 | 1.11 | 1 | 57226.51 | 12114.449 | 6383.9633 | 4284.03 | NORMAL
313.706 | 0.75 | 297.037 | 1.11 | 1 | 79289.74 | 12719.2849 | 7187.8714 | 3864.751 | NORMAL
313.706 | 0.75 | 297.037 | 1.11 | 1 | 101352.97 | 12991.7057 | 7697.053 | 3631.655 | NORMAL
313.706 | 0.75 | 297.037 | 1.11 | 1 | 106868.78 | 12923.9449 | 7555.713 | 3593.611 | NORMAL
313.706 | 0.75 | 297.037 | 1.11 | 2 | 57226.51 | 15709.8476 | 6641.181 | 6155.83 | NORMAL
313.706 | 0.75 | 297.037 | 1.11 | 2 | 79289.74 | 16593.2884 | 7832.8286 | 5429.713 | NORMAL
313.706 | 0.75 | 297.037 | 1.11 | 2 | 101352.97 | 16989.8593 | 8699.6575 | 5025.904 | NORMAL
313.706 | 0.75 | 297.037 | 1.11 | 2 | 106868.78 | 16926.3189 | 9245.6124 | 4947.723 | NORMAL
313.706 | 0.75 | 297.037 | 1.42 | 1 | 57226.51 | 12264.0094 | 7886.8741 | 4292.51 | NORMAL
313.706 | 0.75 | 297.037 | 1.42 | 1 | 79289.74 | 12933.0012 | 8150.1575 | 3871.3 | NORMAL
313.706 | 0.75 | 297.037 | 1.42 | 1 | 101352.97 | 13256.0668 | 8678.5879 | 3638.246 | NORMAL
313.706 | 0.75 | 297.037 | 1.42 | 1 | 106868.78 | 13203.6928 | 8665.4516 | 3595.962 | NORMAL
313.706 | 0.75 | 297.037 | 1.42 | 2 | 57226.51 | 15928.5756 | 8301.655 | 6190.62 | NORMAL
313.706 | 0.75 | 297.037 | 1.42 | 2 | 79289.74 | 16921.7175 | 9375.4776 | 5463.18 | NORMAL
313.706 | 0.75 | 297.037 | 1.42 | 2 | 101352.97 | 17413.306 | 10182.3088 | 5057.822 | NORMAL
313.706 | 0.75 | 297.037 | 1.42 | 2 | 106868.78 | 17369.0797 | 9956.3039 | 4977.135 | NORMAL
313.706 | 0.75 | 299.814 | 0.5 | 1 | 57226.51 | 12312.7491 | 4300.0183 | 4293.32 | NORMAL
313.706 | 0.75 | 299.814 | 0.5 | 1 | 79289.74 | 12645.6038 | 5086.5424 | 3862.082 | NORMAL
313.706 | 0.75 | 299.814 | 0.5 | 1 | 101352.97 | 12662.0457 | 5675.4961 | 3632.201 | NORMAL
313.706 | 0.75 | 299.814 | 0.5 | 1 | 106868.78 | 12549.1501 | 5750.4598 | 3591.413 | NORMAL
313.706 | 0.75 | 299.814 | 0.5 | 2 | 57226.51 | 15728.898 | 5134.1168 | 6158.479 | NORMAL
313.706 | 0.75 | 299.814 | 0.5 | 2 | 79289.74 | 16152.9601 | 6166.231 | 5385.369 | NORMAL
313.706 | 0.75 | 299.814 | 0.5 | 2 | 101352.97 | 16114.449 | 7004.4837 | 4965.916 | NORMAL
313.706 | 0.75 | 299.814 | 0.5 | 2 | 106868.78 | 15978.0481 | 7137.2343 | 4885.736 | NORMAL
313.706 | 0.75 | 299.814 | 0.8 | 1 | 57226.51 | 12792.1161 | 4526.1193 | 4328.52 | NORMAL
313.706 | 0.75 | 299.814 | 0.8 | 1 | 79289.74 | 13375.2638 | 5665.1866 | 3883.484 | NORMAL
313.706 | 0.75 | 299.814 | 0.8 | 1 | 101352.97 | 13585.6682 | 6345.7705 | 3642.238 | NORMAL
313.706 | 0.75 | 299.814 | 0.8 | 1 | 106868.78 | 13502.6671 | 6883.8757 | 3598.535 | NORMAL
313.706 | 0.75 | 299.814 | 0.8 | 2 | 57226.51 | 16433.2063 | 4590.0082 | 6268.692 | NORMAL
313.706 | 0.75 | 299.814 | 0.8 | 2 | 79289.74 | 17260.2286 | 6582.7405 | 5498.271 | NORMAL
313.706 | 0.75 | 299.814 | 0.8 | 2 | 101352.97 | 17570.2227 | 7845.4383 | 5067.725 | NORMAL
313.706 | 0.75 | 299.814 | 0.8 | 2 | 106868.78 | 17473.3294 | 8119.8911 | 4984.11 | NORMAL
313.706 | 0.75 | 299.814 | 1.11 | 1 | 57226.51 | 13021.5709 | 6703.4526 | 4346.59 | NORMAL
313.706 | 0.75 | 299.814 | 1.11 | 1 | 79289.74 | 13719.49 | 7266.1712 | 3896.376 | NORMAL
313.706 | 0.75 | 299.814 | 1.11 | 1 | 101352.97 | 14034.3201 | 7889.9825 | 3648.052 | NORMAL
313.706 | 0.75 | 299.814 | 1.11 | 1 | 106868.78 | 13968.3177 | 7627.5815 | 3602.685 | NORMAL
313.706 | 0.75 | 299.814 | 1.11 | 2 | 57226.51 | 16781.2134 | 6181.1754 | 6322.5 | NORMAL
313.706 | 0.75 | 299.814 | 1.11 | 2 | 79289.74 | 17783.0891 | 7689.4255 | 5552.377 | NORMAL
313.706 | 0.75 | 299.814 | 1.11 | 2 | 101352.97 | 18259.5838 | 8566.8124 | 5117.659 | NORMAL
313.706 | 0.75 | 299.814 | 1.11 | 2 | 106868.78 | 18193.9039 | 9328.4148 | 5032.707 | NORMAL
313.706 | 0.75 | 299.814 | 1.42 | 1 | 57226.51 | 13159.0563 | 8091.1879 | 4360.71 | NORMAL
313.706 | 0.75 | 299.814 | 1.42 | 1 | 79289.74 | 13935.0528 | 8341.9128 | 3903.55 | NORMAL
313.706 | 0.75 | 299.814 | 1.42 | 1 | 101352.97 | 14310.8734 | 8918.4075 | 3651.858 | NORMAL
313.706 | 0.75 | 299.814 | 1.42 | 1 | 106868.78 | 14255.6565 | 8762.5814 | 3605.592 | NORMAL
313.706 | 0.75 | 299.814 | 1.42 | 2 | 57226.51 | 16999.7948 | 8593.0223 | 6356.14 | NORMAL
313.706 | 0.75 | 299.814 | 1.42 | 2 | 79289.74 | 18106.4185 | 9517.6389 | 5586.24 | NORMAL
313.706 | 0.75 | 299.814 | 1.42 | 2 | 101352.97 | 18683.2356 | 10229.987 | 5150.806 | NORMAL
313.706 | 0.75 | 299.814 | 1.42 | 2 | 106868.78 | 18639.5369 | 10026.6543 | 5063.249 | NORMAL
313.706 | 0.75 | 302.591 | 0.5 | 1 | 57226.51 | 13264.3611 | 4352.7134 | 4359.581 | NORMAL
313.706 | 0.75 | 302.591 | 0.5 | 1 | 79289.74 | 13689.449 | 5058.0461 | 3894.835 | NORMAL
313.706 | 0.75 | 302.591 | 0.5 | 1 | 101352.97 | 13740.8265 | 5681.8592 | 3644.607 | NORMAL
313.706 | 0.75 | 302.591 | 0.5 | 1 | 106868.78 | 13618.347 | 5764.4693 | 3599.563 | NORMAL
313.706 | 0.75 | 302.591 | 0.5 | 2 | 57226.51 | 16881.8875 | 5028.3208 | 6336.681 | NORMAL
313.706 | 0.75 | 302.591 | 0.5 | 2 | 79289.74 | 17416.823 | 6111.3542 | 5514.634 | NORMAL
313.706 | 0.75 | 302.591 | 0.5 | 2 | 101352.97 | 17429.3083 | 6978.3116 | 5059.517 | NORMAL
313.706 | 0.75 | 302.591 | 0.5 | 2 | 106868.78 | 17282.2098 | 7116.693 | 4971.505 | NORMAL
313.706 | 0.75 | 302.591 | 0.8 | 1 | 57226.51 | 13728.7515 | 3999.8168 | 4395.053 | NORMAL
313.706 | 0.75 | 302.591 | 0.8 | 1 | 79289.74 | 14414.5076 | 5447.8478 | 3918.331 | NORMAL
313.706 | 0.75 | 302.591 | 0.8 | 1 | 101352.97 | 14676.2309 | 6212.9329 | 3657.228 | NORMAL
313.706 | 0.75 | 302.591 | 0.8 | 1 | 106868.78 | 14588.9214 | 6799.2836 | 3609.252 | NORMAL
313.706 | 0.75 | 302.591 | 0.8 | 2 | 57226.51 | 17557.0633 | 3979.2908 | 6441.052 | NORMAL
313.706 | 0.75 | 302.591 | 0.8 | 2 | 79289.74 | 18505.6858 | 6371.156 | 5628.34 | NORMAL
313.706 | 0.75 | 302.591 | 0.8 | 2 | 101352.97 | 18898.8277 | 7830.9371 | 5165.295 | NORMAL
313.706 | 0.75 | 302.591 | 0.8 | 2 | 106868.78 | 18797.3329 | 8052.4767 | 5074.151 | NORMAL
313.706 | 0.75 | 302.591 | 1.11 | 1 | 57226.51 | 13956.7702 | 6855.6214 | 4412.01 | NORMAL
313.706 | 0.75 | 302.591 | 1.11 | 1 | 79289.74 | 14756.6237 | 7475.5727 | 3932.064 | NORMAL
313.706 | 0.75 | 302.591 | 1.11 | 1 | 101352.97 | 15129.7773 | 7910.7251 | 3664.419 | NORMAL
313.706 | 0.75 | 302.591 | 1.11 | 1 | 106868.78 | 15061.1665 | 7688.0025 | 3614.796 | NORMAL
313.706 | 0.75 | 302.591 | 1.11 | 2 | 57226.51 | 17900.9086 | 5693.7599 | 6492.03 | NORMAL
313.706 | 0.75 | 302.591 | 1.11 | 2 | 79289.74 | 19008.646 | 7341.1771 | 5681.69 | NORMAL
313.706 | 0.75 | 302.591 | 1.11 | 2 | 101352.97 | 19579.7773 | 8349.8548 | 5215.987 | NORMAL
313.706 | 0.75 | 302.591 | 1.11 | 2 | 106868.78 | 19513.8335 | 9227.7211 | 5124.061 | NORMAL
313.706 | 0.75 | 302.591 | 1.42 | 1 | 57226.51 | 14098.4173 | 7599.0047 | 4424.06 | NORMAL
313.706 | 0.75 | 302.591 | 1.42 | 1 | 79289.74 | 14972.2743 | 8601.871 | 3939.87 | NORMAL
313.706 | 0.75 | 302.591 | 1.42 | 1 | 101352.97 | 15409.8476 | 9148.6724 | 3669.059 | NORMAL
313.706 | 0.75 | 302.591 | 1.42 | 1 | 106868.78 | 15353.2532 | 8912.4714 | 3618.507 | NORMAL
313.706 | 0.75 | 302.591 | 1.42 | 2 | 57226.51 | 18119.7831 | 8920.2424 | 6524.45 | NORMAL
313.706 | 0.75 | 302.591 | 1.42 | 2 | 79289.74 | 19326.905 | 9688.7901 | 5715.7 | NORMAL
313.706 | 0.75 | 302.591 | 1.42 | 2 | 101352.97 | 19999.5897 | 10120.4924 | 5250.199 | NORMAL
313.706 | 0.75 | 302.591 | 1.42 | 2 | 106868.78 | 19958.646 | 10131.1085 | 5155.52 | NORMAL
313.706 | 0.75 | 305.368 | 0.5 | 1 | 57226.51 | 14240.4162 | 4308.1673 | 4430.459 | NORMAL
313.706 | 0.75 | 305.368 | 0.5 | 1 | 79289.74 | 14778.2532 | 5021.7834 | 3932.116 | NORMAL
313.706 | 0.75 | 305.368 | 0.5 | 1 | 101352.97 | 14877.755 | 5677.2472 | 3660.631 | NORMAL
313.706 | 0.75 | 305.368 | 0.5 | 1 | 106868.78 | 14746.6588 | 5750.2827 | 3611.089 | NORMAL
313.706 | 0.75 | 305.368 | 0.5 | 2 | 57226.51 | 18087.6319 | 4860.2371 | 6519.607 | NORMAL
313.706 | 0.75 | 305.368 | 0.5 | 2 | 79289.74 | 18731.4478 | 5975.1071 | 5652.286 | NORMAL
313.706 | 0.75 | 305.368 | 0.5 | 2 | 101352.97 | 18813.687 | 6932.3357 | 5161.019 | NORMAL
313.706 | 0.75 | 305.368 | 0.5 | 2 | 106868.78 | 18659.2321 | 7066.0833 | 5064.879 | NORMAL
313.706 | 0.75 | 305.368 | 0.8 | 1 | 57226.51 | 14690.4162 | 3552.5833 | 4465.426 | NORMAL
313.706 | 0.75 | 305.368 | 0.8 | 1 | 79289.74 | 15489.3611 | 5063.0229 | 3957.639 | NORMAL
313.706 | 0.75 | 305.368 | 0.8 | 1 | 101352.97 | 15814.0094 | 5973.7895 | 3676.198 | NORMAL
313.706 | 0.75 | 305.368 | 0.8 | 1 | 106868.78 | 15723.7104 | 6653.6453 | 3623.682 | NORMAL
313.706 | 0.75 | 305.368 | 0.8 | 2 | 57226.51 | 18745.6624 | 3260.6018 | 6612.936 | NORMAL
313.706 | 0.75 | 305.368 | 0.8 | 2 | 79289.74 | 19788.7749 | 6137.7458 | 5765.592 | NORMAL
313.706 | 0.75 | 305.368 | 0.8 | 2 | 101352.97 | 20280.0997 | 7788.8156 | 5270.355 | NORMAL
313.706 | 0.75 | 305.368 | 0.8 | 2 | 106868.78 | 20177.2274 | 7950.6347 | 5171.325 | NORMAL
313.706 | 0.75 | 305.368 | 1.11 | 1 | 57226.51 | 14913.8921 | 6582.7534 | 4482.37 | NORMAL
313.706 | 0.75 | 305.368 | 1.11 | 1 | 79289.74 | 15828.0188 | 7599.5066 | 3971.901 | NORMAL
313.706 | 0.75 | 305.368 | 1.11 | 1 | 101352.97 | 16269.0504 | 7839.6324 | 3684.612 | NORMAL
313.706 | 0.75 | 305.368 | 1.11 | 1 | 106868.78 | 16199.1208 | 7838.9975 | 3630.591 | NORMAL
313.706 | 0.75 | 305.368 | 1.11 | 2 | 57226.51 | 19085.8441 | 5025.4363 | 6662.48 | NORMAL
313.706 | 0.75 | 305.368 | 1.11 | 2 | 79289.74 | 20268.5229 | 6912.904 | 5817.419 | NORMAL
313.706 | 0.75 | 305.368 | 1.11 | 2 | 101352.97 | 20949.4431 | 7921.6548 | 5321.969 | NORMAL
313.706 | 0.75 | 305.368 | 1.11 | 2 | 106868.78 | 20880.8324 | 8957.9606 | 5222.217 | NORMAL
313.706 | 0.75 | 305.368 | 1.42 | 1 | 57226.51 | 15057.2978 | 7734.7532 | 4493.21 | NORMAL
313.706 | 0.75 | 305.368 | 1.42 | 1 | 79289.74 | 16042.5557 | 8908.8483 | 3980.1 | NORMAL
313.706 | 0.75 | 305.368 | 1.42 | 1 | 101352.97 | 16550.5569 | 9190.9711 | 3689.97 | NORMAL
313.706 | 0.75 | 305.368 | 1.42 | 1 | 106868.78 | 16494.1676 | 8919.7325 | 3634.98 | NORMAL
313.706 | 0.75 | 305.368 | 1.42 | 2 | 57226.51 | 19313.3939 | 8212.6538 | 6692.74 | NORMAL
313.706 | 0.75 | 305.368 | 1.42 | 2 | 79289.74 | 20579.6893 | 9753.2293 | 5851.35 | NORMAL
313.706 | 0.75 | 305.368 | 1.42 | 2 | 101352.97 | 21358.4994 | 10020.7244 | 5355.989 | NORMAL
313.706 | 0.75 | 305.368 | 1.42 | 2 | 106868.78 | 21323.0363 | 10248.8108 | 5254.226 | NORMAL
313.706 | 0.85 | 288.706 | 0.5 | 1 | 57226.51 | 9209.5545 | 3571.0692 | 4099.607 | NORMAL
313.706 | 0.85 | 288.706 | 0.5 | 1 | 79289.74 | 9316.1782 | 4275.6134 | 3776.649 | NORMAL
313.706 | 0.85 | 288.706 | 0.5 | 1 | 101352.97 | 9247.5381 | 4790.5022 | 3616.299 | NORMAL
313.706 | 0.85 | 288.706 | 0.5 | 1 | 106868.78 | 9162.163 | 4864.6413 | 3590.4429 | NORMAL
313.706 | 0.85 | 288.706 | 0.5 | 2 | 57226.51 | 12061.8699 | 4553.9107 | 5580.347 | NORMAL
313.706 | 0.85 | 288.706 | 0.5 | 2 | 79289.74 | 12143.4642 | 5539.4962 | 4991.112 | NORMAL
313.706 | 0.85 | 288.706 | 0.5 | 2 | 101352.97 | 11965.1231 | 6222.6417 | 4686.07 | NORMAL
313.706 | 0.85 | 288.706 | 0.5 | 2 | 106868.78 | 11885.0528 | 6351.9783 | 4630.3126 | NORMAL
313.706 | 0.85 | 288.706 | 0.8 | 1 | 57226.51 | 9674.8828 | 3712.2622 | 4127.558 | NORMAL
313.706 | 0.85 | 288.706 | 0.8 | 1 | 79289.74 | 9972.4795 | 4687.2349 | 3791.398 | NORMAL
313.706 | 0.85 | 288.706 | 0.8 | 1 | 101352.97 | 10042.5264 | 5313.3099 | 3617.666 | NORMAL
313.706 | 0.85 | 288.706 | 0.8 | 1 | 106868.78 | 9977.6377 | 5456.9996 | 3586.62 | NORMAL
313.706 | 0.85 | 288.706 | 0.8 | 2 | 57226.51 | 12796.8347 | 5089.6339 | 5697.313 | NORMAL
313.706 | 0.85 | 288.706 | 0.8 | 2 | 79289.74 | 13214.5076 | 6139.1695 | 5093.165 | NORMAL
313.706 | 0.85 | 288.706 | 0.8 | 2 | 101352.97 | 13294.4314 | 6924.2584 | 4773.847 | NORMAL
313.706 | 0.85 | 288.706 | 0.8 | 2 | 106868.78 | 13216.3834 | 7042.9843 | 4712.025 | NORMAL
313.706 | 0.85 | 288.706 | 1.11 | 1 | 57226.51 | 9884.9062 | 4105.8935 | 4142.6 | NORMAL
313.706 | 0.85 | 288.706 | 1.11 | 1 | 79289.74 | 10287.3095 | 5065.0083 | 3797.345 | NORMAL
313.706 | 0.85 | 288.706 | 1.11 | 1 | 101352.97 | 10430.422 | 5696.7106 | 3618.114 | NORMAL
313.706 | 0.85 | 288.706 | 1.11 | 1 | 106868.78 | 10376.8757 | 5924.48 | 3585.897 | NORMAL
313.706 | 0.85 | 288.706 | 1.11 | 2 | 57226.51 | 13133.2063 | 4913.3032 | 5749.41 | NORMAL
313.706 | 0.85 | 288.706 | 1.11 | 2 | 79289.74 | 13718.1418 | 6372.0906 | 5141.568 | NORMAL
313.706 | 0.85 | 288.706 | 1.11 | 2 | 101352.97 | 13930.1876 | 7324.7434 | 4815.243 | NORMAL
313.706 | 0.85 | 288.706 | 1.11 | 2 | 106868.78 | 13865.2403 | 7587.6973 | 4752.162 | NORMAL
313.706 | 0.85 | 288.706 | 1.42 | 1 | 57226.51 | 10010.932 | 5161.5665 | 4152.57 | NORMAL
313.706 | 0.85 | 288.706 | 1.42 | 1 | 79289.74 | 10472.1864 | 5865.7439 | 3803.12 | NORMAL
313.706 | 0.85 | 288.706 | 1.42 | 1 | 101352.97 | 10664.449 | 6319.6565 | 3619.375 | NORMAL
313.706 | 0.85 | 288.706 | 1.42 | 1 | 106868.78 | 10619.2849 | 6298.9881 | 3586.703 | NORMAL
313.706 | 0.85 | 288.706 | 1.42 | 2 | 57226.51 | 13339.2732 | 5152.5477 | 5781.47 | NORMAL
313.706 | 0.85 | 288.706 | 1.42 | 2 | 79289.74 | 14024.5604 | 6613.4497 | 5171.17 | NORMAL
313.706 | 0.85 | 288.706 | 1.42 | 2 | 101352.97 | 14317.2333 | 7599.7592 | 4840.088 | NORMAL
313.706 | 0.85 | 288.706 | 1.42 | 2 | 106868.78 | 14266.6471 | 8064.3222 | 4777.131 | NORMAL
313.706 | 0.85 | 291.483 | 0.5 | 1 | 57226.51 | 10081.6823 | 3555.9404 | 4149.316 | NORMAL
313.706 | 0.85 | 291.483 | 0.5 | 1 | 79289.74 | 10228.9273 | 4299.4943 | 3797.236 | NORMAL
313.706 | 0.85 | 291.483 | 0.5 | 1 | 101352.97 | 10163.306 | 4863.8432 | 3617.387 | NORMAL
313.706 | 0.85 | 291.483 | 0.5 | 1 | 106868.78 | 10068.6987 | 4948.413 | 3586.4023 | NORMAL
313.706 | 0.85 | 291.483 | 0.5 | 2 | 57226.51 | 13091.5885 | 4477.8077 | 5743.325 | NORMAL
313.706 | 0.85 | 291.483 | 0.5 | 2 | 79289.74 | 13236.9871 | 5519.9428 | 5095.939 | NORMAL
313.706 | 0.85 | 291.483 | 0.5 | 2 | 101352.97 | 13097.0106 | 6290.6251 | 4760.732 | NORMAL
313.706 | 0.85 | 291.483 | 0.5 | 2 | 106868.78 | 12983.8511 | 6424.072 | 4697.7552 | NORMAL
313.706 | 0.85 | 291.483 | 0.8 | 1 | 57226.51 | 10540.0352 | 3629.4927 | 4180.938 | NORMAL
313.706 | 0.85 | 291.483 | 0.8 | 1 | 79289.74 | 10904.0152 | 4716.9025 | 3812.696 | NORMAL
313.706 | 0.85 | 291.483 | 0.8 | 1 | 101352.97 | 11000.4982 | 5399.9576 | 3618.361 | NORMAL
313.706 | 0.85 | 291.483 | 0.8 | 1 | 106868.78 | 10922.3329 | 5551.5925 | 3586.554 | NORMAL
313.706 | 0.85 | 291.483 | 0.8 | 2 | 57226.51 | 13820.1934 | 5020.5722 | 5858.12 | NORMAL
313.706 | 0.85 | 291.483 | 0.8 | 2 | 79289.74 | 14335.1114 | 6117.8385 | 5202.151 | NORMAL
313.706 | 0.85 | 291.483 | 0.8 | 2 | 101352.97 | 14448.8277 | 6959.8702 | 4851.664 | NORMAL
313.706 | 0.85 | 291.483 | 0.8 | 2 | 106868.78 | 14361.2544 | 7090.2805 | 4783.088 | NORMAL
313.706 | 0.85 | 291.483 | 1.11 | 1 | 57226.51 | 10745.6917 | 3897.2797 | 4199.05 | NORMAL
313.706 | 0.85 | 291.483 | 1.11 | 1 | 79289.74 | 11223.5639 | 4969.4798 | 3820.88 | NORMAL
313.706 | 0.85 | 291.483 | 1.11 | 1 | 101352.97 | 11402.5205 | 5677.9763 | 3621.074 | NORMAL
313.706 | 0.85 | 291.483 | 1.11 | 1 | 106868.78 | 11339.5662 | 6064.4794 | 3587.093 | NORMAL
313.706 | 0.85 | 291.483 | 1.11 | 2 | 57226.51 | 14145.4865 | 4695.962 | 5908.76 | NORMAL
313.706 | 0.85 | 291.483 | 1.11 | 2 | 79289.74 | 14845.5451 | 6342.0466 | 5252.097 | NORMAL
313.706 | 0.85 | 291.483 | 1.11 | 2 | 101352.97 | 15109.4666 | 7368.5847 | 4894.464 | NORMAL
313.706 | 0.85 | 291.483 | 1.11 | 2 | 106868.78 | 15035.932 | 7661.2584 | 4825.701 | NORMAL
313.706 | 0.85 | 291.483 | 1.42 | 1 | 57226.51 | 10877.4033 | 4872.9353 | 4205.11 | NORMAL
313.706 | 0.85 | 291.483 | 1.42 | 1 | 79289.74 | 11413.1301 | 5869.8071 | 3827.32 | NORMAL
313.706 | 0.85 | 291.483 | 1.42 | 1 | 101352.97 | 11648.3294 | 6397.0529 | 3621.76 | NORMAL
313.706 | 0.85 | 291.483 | 1.42 | 1 | 106868.78 | 11596.483 | 6426.7825 | 3586.406 | NORMAL
313.706 | 0.85 | 291.483 | 1.42 | 2 | 57226.51 | 14350.2931 | 4802.6556 | 5940.3 | NORMAL
313.706 | 0.85 | 291.483 | 1.42 | 2 | 79289.74 | 15145.9261 | 6390.1571 | 5284.61 | NORMAL
313.706 | 0.85 | 291.483 | 1.42 | 2 | 101352.97 | 15504.66 | 7517.9151 | 4921.604 | NORMAL
313.706 | 0.85 | 291.483 | 1.42 | 2 | 106868.78 | 15448.7104 | 8189.7631 | 4852.027 | NORMAL
313.706 | 0.85 | 294.26 | 0.5 | 1 | 57226.51 | 10983.4408 | 3525.6406 | 4205.974 | NORMAL
313.706 | 0.85 | 294.26 | 0.5 | 1 | 79289.74 | 11189.8007 | 4297.7787 | 3821.198 | NORMAL
313.706 | 0.85 | 294.26 | 0.5 | 1 | 101352.97 | 11138.218 | 4903.879 | 3619.389 | NORMAL
313.706 | 0.85 | 294.26 | 0.5 | 1 | 106868.78 | 11028.9566 | 4995.7865 | 3586.4743 | NORMAL
313.706 | 0.85 | 294.26 | 0.5 | 2 | 57226.51 | 14167.6436 | 4335.6531 | 5913.446 | NORMAL
313.706 | 0.85 | 294.26 | 0.5 | 2 | 79289.74 | 14395.1641 | 5465.9878 | 5208.719 | NORMAL
313.706 | 0.85 | 294.26 | 0.5 | 2 | 101352.97 | 14264.83 | 6296.6814 | 4839.128 | NORMAL
313.706 | 0.85 | 294.26 | 0.5 | 2 | 106868.78 | 14137.2802 | 6443.744 | 4769.0699 | NORMAL
313.706 | 0.85 | 294.26 | 0.8 | 1 | 57226.51 | 11430.2169 | 3584.4131 | 4238.865 | NORMAL
313.706 | 0.85 | 294.26 | 0.8 | 1 | 79289.74 | 11872.8898 | 4742.7802 | 3838.831 | NORMAL
313.706 | 0.85 | 294.26 | 0.8 | 1 | 101352.97 | 12001.6999 | 5490.7417 | 3625.668 | NORMAL
313.706 | 0.85 | 294.26 | 0.8 | 1 | 106868.78 | 11918.3763 | 5610.1347 | 3587.962 | NORMAL
313.706 | 0.85 | 294.26 | 0.8 | 2 | 57226.51 | 14881.7702 | 4972.3864 | 6024.498 | NORMAL
313.706 | 0.85 | 294.26 | 0.8 | 2 | 79289.74 | 15508.2356 | 6065.2089 | 5318.102 | NORMAL
313.706 | 0.85 | 294.26 | 0.8 | 2 | 101352.97 | 15668.2884 | 6955.3099 | 4935.57 | NORMAL
313.706 | 0.85 | 294.26 | 0.8 | 2 | 106868.78 | 15572.7139 | 7093.2466 | 4859.979 | NORMAL
313.706 | 0.85 | 294.26 | 1.11 | 1 | 57226.51 | 11645.6624 | 3322.8336 | 4252.24 | NORMAL
313.706 | 0.85 | 294.26 | 1.11 | 1 | 79289.74 | 12193.9039 | 4809.2025 | 3849.242 | NORMAL
313.706 | 0.85 | 294.26 | 1.11 | 1 | 101352.97 | 12414.8886 | 5651.1828 | 3629.476 | NORMAL
313.706 | 0.85 | 294.26 | 1.11 | 1 | 106868.78 | 12349.4724 | 6177.2555 | 3590.189 | NORMAL
313.706 | 0.85 | 294.26 | 1.11 | 2 | 57226.51 | 15193.1712 | 4589.386 | 6073.79 | NORMAL
313.706 | 0.85 | 294.26 | 1.11 | 2 | 79289.74 | 16014.4783 | 6300.6723 | 5371.342 | NORMAL
313.706 | 0.85 | 294.26 | 1.11 | 2 | 101352.97 | 16344.7831 | 7413.9446 | 4980.397 | NORMAL
313.706 | 0.85 | 294.26 | 1.11 | 2 | 106868.78 | 16265.3869 | 7693.3979 | 4904.861 | NORMAL
313.706 | 0.85 | 294.26 | 1.42 | 1 | 57226.51 | 11774.4724 | 4627.662 | 4261.24 | NORMAL
313.706 | 0.85 | 294.26 | 1.42 | 1 | 79289.74 | 12388.8921 | 5664.0776 | 3854.85 | NORMAL
313.706 | 0.85 | 294.26 | 1.42 | 1 | 101352.97 | 12667.9953 | 6294.0301 | 3630.94 | NORMAL
313.706 | 0.85 | 294.26 | 1.42 | 1 | 106868.78 | 12613.4818 | 6543.8996 | 3591.503 | NORMAL
313.706 | 0.85 | 294.26 | 1.42 | 2 | 57226.51 | 15391.5592 | 3987.6144 | 6104.96 | NORMAL
313.706 | 0.85 | 294.26 | 1.42 | 2 | 79289.74 | 16313.9214 | 6109.8083 | 5401.64 | NORMAL
313.706 | 0.85 | 294.26 | 1.42 | 2 | 101352.97 | 16746.2778 | 7402.1562 | 5008.695 | NORMAL
313.706 | 0.85 | 294.26 | 1.42 | 2 | 106868.78 | 16683.4408 | 8104.2149 | 4932.303 | NORMAL
313.706 | 0.85 | 297.037 | 0.5 | 1 | 57226.51 | 11923.7691 | 3408.2782 | 4267.763 | NORMAL
313.706 | 0.85 | 297.037 | 0.5 | 1 | 79289.74 | 12203.6049 | 4274.1174 | 3849.292 | NORMAL
313.706 | 0.85 | 297.037 | 0.5 | 1 | 101352.97 | 12171.102 | 4912.3663 | 3627.304 | NORMAL
313.706 | 0.85 | 297.037 | 0.5 | 1 | 106868.78 | 12053.3705 | 5012.8642 | 3588.653 | NORMAL
313.706 | 0.85 | 297.037 | 0.5 | 2 | 57226.51 | 15295.8089 | 4154.2652 | 6088.973 | NORMAL
313.706 | 0.85 | 297.037 | 0.5 | 2 | 79289.74 | 15622.9777 | 5384.7249 | 5329.753 | NORMAL
313.706 | 0.85 | 297.037 | 0.5 | 2 | 101352.97 | 15516.3247 | 6267.5091 | 4925.052 | NORMAL
313.706 | 0.85 | 297.037 | 0.5 | 2 | 106868.78 | 15375.7327 | 6426.5027 | 4847.3627 | NORMAL
313.706 | 0.85 | 297.037 | 0.8 | 1 | 57226.51 | 12353.6049 | 3590.5629 | 4300.166 | NORMAL
313.706 | 0.85 | 297.037 | 0.8 | 1 | 79289.74 | 12886.782 | 4809.7079 | 3868.702 | NORMAL
313.706 | 0.85 | 297.037 | 0.8 | 1 | 101352.97 | 13058.8218 | 5548.4714 | 3636.086 | NORMAL
313.706 | 0.85 | 297.037 | 0.8 | 1 | 106868.78 | 12965.6213 | 5632.9401 | 3594.408 | NORMAL
313.706 | 0.85 | 297.037 | 0.8 | 2 | 57226.51 | 15985.6096 | 4898.87 | 6195.564 | NORMAL
313.706 | 0.85 | 297.037 | 0.8 | 2 | 79289.74 | 16734.6424 | 6012.004 | 5442.058 | NORMAL
313.706 | 0.85 | 297.037 | 0.8 | 2 | 101352.97 | 16957.5029 | 6921.6796 | 5026.441 | NORMAL
313.706 | 0.85 | 297.037 | 0.8 | 2 | 106868.78 | 16854.8652 | 7058.0254 | 4943.502 | NORMAL
313.706 | 0.85 | 297.037 | 1.11 | 1 | 57226.51 | 12564.449 | 2929.0746 | 4314.35 | NORMAL
313.706 | 0.85 | 297.037 | 1.11 | 1 | 79289.74 | 13207.3564 | 4458.9884 | 3879.921 | NORMAL
313.706 | 0.85 | 297.037 | 1.11 | 1 | 101352.97 | 13478.9273 | 5498.2566 | 3640.107 | NORMAL
313.706 | 0.85 | 297.037 | 1.11 | 1 | 106868.78 | 13407.5322 | 6126.183 | 3597.579 | NORMAL
313.706 | 0.85 | 297.037 | 1.11 | 2 | 57226.51 | 16282.0926 | 4081.6438 | 6242.54 | NORMAL
313.706 | 0.85 | 297.037 | 1.11 | 2 | 79289.74 | 17234.2321 | 6255.5265 | 5495.898 | NORMAL
313.706 | 0.85 | 297.037 | 1.11 | 2 | 101352.97 | 17642.9074 | 7454.9399 | 5073.258 | NORMAL
313.706 | 0.85 | 297.037 | 1.11 | 2 | 106868.78 | 17558.7339 | 7680.3131 | 4990.421 | NORMAL
313.706 | 0.85 | 297.037 | 1.42 | 1 | 57226.51 | 12693.4642 | 4330.5784 | 4323.61 | NORMAL
313.706 | 0.85 | 297.037 | 1.42 | 1 | 79289.74 | 13404.1325 | 5592.137 | 3886.05 | NORMAL
313.706 | 0.85 | 297.037 | 1.42 | 1 | 101352.97 | 13735.4924 | 6172.7303 | 3643.201 | NORMAL
313.706 | 0.85 | 297.037 | 1.42 | 1 | 106868.78 | 13677.1981 | 6689.9553 | 3599.821 | NORMAL
313.706 | 0.85 | 297.037 | 1.42 | 2 | 57226.51 | 16470.4572 | 3454.4972 | 6272.29 | NORMAL
313.706 | 0.85 | 297.037 | 1.42 | 2 | 79289.74 | 17525.6448 | 5553.1057 | 5525.67 | NORMAL
313.706 | 0.85 | 297.037 | 1.42 | 2 | 101352.97 | 18046.0141 | 7186.2296 | 5102.307 | NORMAL
313.706 | 0.85 | 297.037 | 1.42 | 2 | 106868.78 | 17978.6342 | 7911.516 | 5018.804 | NORMAL
313.706 | 0.85 | 299.814 | 0.5 | 1 | 57226.51 | 12888.3353 | 3281.3315 | 4334.002 | NORMAL
313.706 | 0.85 | 299.814 | 0.5 | 1 | 79289.74 | 13261.5182 | 4232.334 | 3880.793 | NORMAL
313.706 | 0.85 | 299.814 | 0.5 | 1 | 101352.97 | 13258.4701 | 4893.4892 | 3638.525 | NORMAL
313.706 | 0.85 | 299.814 | 0.5 | 1 | 106868.78 | 13130.0703 | 4997.6593 | 3595.477 | NORMAL
313.706 | 0.85 | 299.814 | 0.5 | 2 | 57226.51 | 16459.8183 | 3900.6313 | 6271.58 | NORMAL
313.706 | 0.85 | 299.814 | 0.5 | 2 | 79289.74 | 16902.9601 | 5277.0873 | 5459.302 | NORMAL
313.706 | 0.85 | 299.814 | 0.5 | 2 | 101352.97 | 16839.7128 | 6201.3926 | 5018.012 | NORMAL
313.706 | 0.85 | 299.814 | 0.5 | 2 | 106868.78 | 16686.4889 | 6370.9348 | 4932.507 | NORMAL
313.706 | 0.85 | 299.814 | 0.8 | 1 | 57226.51 | 13296.0727 | 3487.0014 | 4366.374 | NORMAL
313.706 | 0.85 | 299.814 | 0.8 | 1 | 79289.74 | 13937.6319 | 4852.4702 | 3902.449 | NORMAL
313.706 | 0.85 | 299.814 | 0.8 | 1 | 101352.97 | 14162.7784 | 5522.5064 | 3649.891 | NORMAL
313.706 | 0.85 | 299.814 | 0.8 | 1 | 106868.78 | 14061.4009 | 5624.94 | 3603.79 | NORMAL
313.706 | 0.85 | 299.814 | 0.8 | 2 | 57226.51 | 17125.8793 | 4776.3735 | 6372.002 | NORMAL
313.706 | 0.85 | 299.814 | 0.8 | 2 | 79289.74 | 17999.8242 | 5891.7204 | 5573.194 | NORMAL
313.706 | 0.85 | 299.814 | 0.8 | 2 | 101352.97 | 18300.6155 | 6856.655 | 5123.848 | NORMAL
313.706 | 0.85 | 299.814 | 0.8 | 2 | 106868.78 | 18193.9332 | 6984.2507 | 5033.225 | NORMAL
313.706 | 0.85 | 299.814 | 1.11 | 1 | 57226.51 | 13503.0481 | 2194.7584 | 4380.44 | NORMAL
313.706 | 0.85 | 299.814 | 1.11 | 1 | 79289.74 | 14252.8722 | 4186.8382 | 3914.391 | NORMAL
313.706 | 0.85 | 299.814 | 1.11 | 1 | 101352.97 | 14583.1477 | 5342.4778 | 3654.937 | NORMAL
313.706 | 0.85 | 299.814 | 1.11 | 1 | 106868.78 | 14508.6166 | 5900.1901 | 3608.282 | NORMAL
313.706 | 0.85 | 299.814 | 1.11 | 2 | 57226.51 | 17411.0492 | 3739.5626 | 6416.06 | NORMAL
313.706 | 0.85 | 299.814 | 1.11 | 2 | 79289.74 | 18487.3095 | 6162.7816 | 5626.85 | NORMAL
313.706 | 0.85 | 299.814 | 1.11 | 2 | 101352.97 | 18987.1336 | 7481.3104 | 5172.688 | NORMAL
313.706 | 0.85 | 299.814 | 1.11 | 2 | 106868.78 | 18902.0516 | 7591.8956 | 5081.948 | NORMAL
313.706 | 0.85 | 299.814 | 1.42 | 1 | 57226.51 | 13624.9414 | 3435.1747 | 4392.66 | NORMAL
313.706 | 0.85 | 299.814 | 1.42 | 1 | 79289.74 | 14449.4431 | 5302.5699 | 3921.2 | NORMAL
313.706 | 0.85 | 299.814 | 1.42 | 1 | 101352.97 | 14842.4384 | 6016.4566 | 3658.766 | NORMAL
313.706 | 0.85 | 299.814 | 1.42 | 1 | 106868.78 | 14782.5029 | 6769.9281 | 3611.421 | NORMAL
313.706 | 0.85 | 299.814 | 1.42 | 2 | 57226.51 | 17590.4748 | 2451.8483 | 6445.13 | NORMAL
313.706 | 0.85 | 299.814 | 1.42 | 2 | 79289.74 | 18770.9261 | 5136.1759 | 5656.47 | NORMAL
313.706 | 0.85 | 299.814 | 1.42 | 2 | 101352.97 | 19388.2767 | 6913.4523 | 5201.993 | NORMAL
313.706 | 0.85 | 299.814 | 1.42 | 2 | 106868.78 | 19320.4279 | 7517.849 | 5111.317 | NORMAL
313.706 | 0.85 | 302.591 | 0.5 | 1 | 57226.51 | 13885.1114 | 3209.0159 | 4402.762 | NORMAL
313.706 | 0.85 | 302.591 | 0.5 | 1 | 79289.74 | 14367.6436 | 4128.3269 | 3917.573 | NORMAL
313.706 | 0.85 | 302.591 | 0.5 | 1 | 101352.97 | 14408.1184 | 4850.1329 | 3653.542 | NORMAL
313.706 | 0.85 | 302.591 | 0.5 | 1 | 106868.78 | 14270.2227 | 4958.6884 | 3605.915 | NORMAL
313.706 | 0.85 | 302.591 | 0.5 | 2 | 57226.51 | 17678.6928 | 3581.88 | 6457.601 | NORMAL
313.706 | 0.85 | 302.591 | 0.5 | 2 | 79289.74 | 18239.3611 | 5153.0208 | 5597.81 | NORMAL
313.706 | 0.85 | 302.591 | 0.5 | 2 | 101352.97 | 18240.6213 | 6104.9536 | 5118.994 | NORMAL
313.706 | 0.85 | 302.591 | 0.5 | 2 | 106868.78 | 18077.8429 | 6280.803 | 5025.315 | NORMAL
313.706 | 0.85 | 302.591 | 0.8 | 1 | 57226.51 | 14262.9543 | 3617.456 | 4436.735 | NORMAL
313.706 | 0.85 | 302.591 | 0.8 | 1 | 79289.74 | 15029.8066 | 4788.7669 | 3940.828 | NORMAL
313.706 | 0.85 | 302.591 | 0.8 | 1 | 101352.97 | 15319.7831 | 5477.6957 | 3667.659 | NORMAL
313.706 | 0.85 | 302.591 | 0.8 | 1 | 106868.78 | 15212.3681 | 5575.1656 | 3616.855 | NORMAL
313.706 | 0.85 | 302.591 | 0.8 | 2 | 57226.51 | 18324.5018 | 4576.4344 | 6551.859 | NORMAL
313.706 | 0.85 | 302.591 | 0.8 | 2 | 79289.74 | 19308.4115 | 5644.6403 | 5712.008 | NORMAL
313.706 | 0.85 | 302.591 | 0.8 | 2 | 101352.97 | 19704.0739 | 6766.5366 | 5228.92 | NORMAL
313.706 | 0.85 | 302.591 | 0.8 | 2 | 106868.78 | 19596.0727 | 6892.2719 | 5130.258 | NORMAL
313.706 | 0.85 | 302.591 | 1.11 | 1 | 57226.51 | 14459.2321 | 960.3518 | 4453.02 | NORMAL
313.706 | 0.85 | 302.591 | 1.11 | 1 | 79289.74 | 15334.1735 | 3609.5418 | 3953.267 | NORMAL
313.706 | 0.85 | 302.591 | 1.11 | 1 | 101352.97 | 15734.7304 | 5145.7761 | 3673.833 | NORMAL
313.706 | 0.85 | 302.591 | 1.11 | 1 | 106868.78 | 15657.9426 | 5637.517 | 3622.736 | NORMAL
313.706 | 0.85 | 302.591 | 1.11 | 2 | 57226.51 | 18606.0375 | 4414.8592 | 6593.68 | NORMAL
313.706 | 0.85 | 302.591 | 1.11 | 2 | 79289.74 | 19779.1325 | 6214.3067 | 5765.032 | NORMAL
313.706 | 0.85 | 302.591 | 1.11 | 2 | 101352.97 | 20382.6495 | 7371.8132 | 5279.586 | NORMAL
313.706 | 0.85 | 302.591 | 1.11 | 2 | 106868.78 | 20299.0914 | 7548.9073 | 5180.5 | NORMAL
313.706 | 0.85 | 302.591 | 1.42 | 1 | 57226.51 | 14585.4044 | 2986.3178 | 4462.62 | NORMAL
313.706 | 0.85 | 302.591 | 1.42 | 1 | 79289.74 | 15529.279 | 4862.4347 | 3960.59 | NORMAL
313.706 | 0.85 | 302.591 | 1.42 | 1 | 101352.97 | 15993.9918 | 5531.746 | 3678.379 | NORMAL
313.706 | 0.85 | 302.591 | 1.42 | 1 | 106868.78 | 15934.0563 | 6881.5206 | 3626.658 | NORMAL
313.706 | 0.85 | 302.591 | 1.42 | 2 | 57226.51 | 18779.9824 | 1262.8843 | 6618.52 | NORMAL
313.706 | 0.85 | 302.591 | 1.42 | 2 | 79289.74 | 20054.3963 | 4373.8237 | 5794.89 | NORMAL
313.706 | 0.85 | 302.591 | 1.42 | 2 | 101352.97 | 20779.9238 | 6680.2468 | 5310.373 | NORMAL
313.706 | 0.85 | 302.591 | 1.42 | 2 | 106868.78 | 20714.0973 | 7112.7653 | 5210.703 | NORMAL
313.706 | 0.85 | 305.368 | 0.5 | 1 | 57226.51 | 14907.6202 | 3000.1138 | 4477.984 | NORMAL
313.706 | 0.85 | 305.368 | 0.5 | 1 | 79289.74 | 15517.9074 | 3948.097 | 3959.488 | NORMAL
313.706 | 0.85 | 305.368 | 0.5 | 1 | 101352.97 | 15616.5885 | 4794.4957 | 3673.045 | NORMAL
313.706 | 0.85 | 305.368 | 0.5 | 1 | 106868.78 | 15470.6038 | 4898.6739 | 3620.247 | NORMAL
313.706 | 0.85 | 305.368 | 0.5 | 2 | 57226.51 | 18975.2345 | 3192.2606 | 6643.972 | NORMAL
313.706 | 0.85 | 305.368 | 0.5 | 2 | 79289.74 | 19623.9156 | 4920.1474 | 5745.342 | NORMAL
313.706 | 0.85 | 305.368 | 0.5 | 2 | 101352.97 | 19710.8148 | 5981.5818 | 5229.303 | NORMAL
313.706 | 0.85 | 305.368 | 0.5 | 2 | 106868.78 | 19541.7057 | 6162.3987 | 5126.479 | NORMAL
313.706 | 0.85 | 305.368 | 0.8 | 1 | 57226.51 | 15257.1512 | 3208.4416 | 4510.616 | NORMAL
313.706 | 0.85 | 305.368 | 0.8 | 1 | 79289.74 | 16160.1993 | 4722.7536 | 3983.692 | NORMAL
313.706 | 0.85 | 305.368 | 0.8 | 1 | 101352.97 | 16525.6155 | 5438.0347 | 3689.67 | NORMAL
313.706 | 0.85 | 305.368 | 0.8 | 1 | 106868.78 | 16415.7386 | 5498.9113 | 3633.925 | NORMAL
313.706 | 0.85 | 305.368 | 0.8 | 2 | 57226.51 | 19616.1489 | 4338.3663 | 6732.161 | NORMAL
313.706 | 0.85 | 305.368 | 0.8 | 2 | 79289.74 | 20651.6706 | 5473.4981 | 5859.657 | NORMAL
313.706 | 0.85 | 305.368 | 0.8 | 2 | 101352.97 | 21161.7526 | 6516.3808 | 5342.036 | NORMAL
313.706 | 0.85 | 305.368 | 0.8 | 2 | 106868.78 | 21053.9273 | 6776.1644 | 5235.093 | NORMAL
313.706 | 0.85 | 305.368 | 1.11 | 1 | 57226.51 | 15454.3376 | 213.2822 | 4522.83 | NORMAL
313.706 | 0.85 | 305.368 | 1.11 | 1 | 79289.74 | 16448.6811 | 3054.7833 | 3996.147 | NORMAL
313.706 | 0.85 | 305.368 | 1.11 | 1 | 101352.97 | 16933.4994 | 4790.6733 | 3696.747 | NORMAL
313.706 | 0.85 | 305.368 | 1.11 | 1 | 106868.78 | 16853.0188 | 5199.4765 | 3640.916 | NORMAL
313.706 | 0.85 | 305.368 | 1.11 | 2 | 57226.51 | 19903.9859 | 3931.4751 | 6768.73 | NORMAL
313.706 | 0.85 | 305.368 | 1.11 | 2 | 79289.74 | 21108.7339 | 6072.3495 | 5909.225 | NORMAL
313.706 | 0.85 | 305.368 | 1.11 | 2 | 101352.97 | 21824.7362 | 7244.1756 | 5393.913 | NORMAL
313.706 | 0.85 | 305.368 | 1.11 | 2 | 106868.78 | 21746.6295 | 7467.8578 | 5286.467 | NORMAL
313.706 | 0.85 | 305.368 | 1.42 | 1 | 57226.51 | 15579.1325 | 1947.4383 | 4532.02 | NORMAL
313.706 | 0.85 | 305.368 | 1.42 | 1 | 79289.74 | 16640.2989 | 4718.7395 | 4003.92 | NORMAL
313.706 | 0.85 | 305.368 | 1.42 | 1 | 101352.97 | 17187.456 | 5233.546 | 3701.819 | NORMAL
313.706 | 0.85 | 305.368 | 1.42 | 1 | 106868.78 | 17128.8101 | 6595.3284 | 3645.816 | NORMAL
313.706 | 0.85 | 305.368 | 1.42 | 2 | 57226.51 | 20079.7186 | 3964.0577 | 6790.55 | NORMAL
313.706 | 0.85 | 305.368 | 1.42 | 2 | 79289.74 | 21371.1606 | 3557.999 | 5939.51 | NORMAL
313.706 | 0.85 | 305.368 | 1.42 | 2 | 101352.97 | 22212.456 | 6217.3331 | 5425.262 | NORMAL
313.706 | 0.85 | 305.368 | 1.42 | 2 | 106868.78 | 22153.3412 | 6569.0638 | 5317.001 | NORMAL
313.706 | 0.95 | 288.706 | 0.5 | 1 | 57226.51 | 9613.2474 | 2908.7956 | 4121.718 | NORMAL
313.706 | 0.95 | 288.706 | 0.5 | 1 | 79289.74 | 9695.7503 | 3693.4991 | 3785.435 | NORMAL
313.706 | 0.95 | 288.706 | 0.5 | 1 | 101352.97 | 9593.4936 | 4276.8754 | 3617.564 | NORMAL
313.706 | 0.95 | 288.706 | 0.5 | 1 | 106868.78 | 9499.4431 | 4380.7537 | 3588.5069 | NORMAL
313.706 | 0.95 | 288.706 | 0.5 | 2 | 57226.51 | 12535.5803 | 3852.8858 | 5656.454 | NORMAL
313.706 | 0.95 | 288.706 | 0.5 | 2 | 79289.74 | 12594.959 | 4912.6512 | 5037.25 | NORMAL
313.706 | 0.95 | 288.706 | 0.5 | 2 | 101352.97 | 12420.34 | 5716.5484 | 4715.97 | NORMAL
313.706 | 0.95 | 288.706 | 0.5 | 2 | 106868.78 | 12305.51 | 5864.3631 | 4656.5533 | NORMAL
313.706 | 0.95 | 288.706 | 0.8 | 1 | 57226.51 | 10035.1993 | 3052.2059 | 4146.829 | NORMAL
313.706 | 0.95 | 288.706 | 0.8 | 1 | 79289.74 | 10349.2673 | 3889.7618 | 3800.315 | NORMAL
313.706 | 0.95 | 288.706 | 0.8 | 1 | 101352.97 | 10403.7515 | 4535.9524 | 3617.882 | NORMAL
313.706 | 0.95 | 288.706 | 0.8 | 1 | 106868.78 | 10322.2157 | 4643.841 | 3585.942 | NORMAL
313.706 | 0.95 | 288.706 | 0.8 | 2 | 57226.51 | 13270.7503 | 3932.0304 | 5769.977 | NORMAL
313.706 | 0.95 | 288.706 | 0.8 | 2 | 79289.74 | 13676.8757 | 5165.9748 | 5142.123 | NORMAL
313.706 | 0.95 | 288.706 | 0.8 | 2 | 101352.97 | 13732.5909 | 6058.8328 | 4803.677 | NORMAL
313.706 | 0.95 | 288.706 | 0.8 | 2 | 106868.78 | 13642.3212 | 6225.2231 | 4738.508 | NORMAL
313.706 | 0.95 | 288.706 | 1.11 | 1 | 57226.51 | 10200.7913 | 3190.1139 | 4157.92 | NORMAL
313.706 | 0.95 | 288.706 | 1.11 | 1 | 79289.74 | 10630.0703 | 4034.9621 | 3806.561 | NORMAL
313.706 | 0.95 | 288.706 | 1.11 | 1 | 101352.97 | 10778.4584 | 4707.0067 | 3619.456 | NORMAL
313.706 | 0.95 | 288.706 | 1.11 | 1 | 106868.78 | 10707.2685 | 4809.0411 | 3586.727 | NORMAL
313.706 | 0.95 | 288.706 | 1.11 | 2 | 57226.51 | 13590.4748 | 4010.2365 | 5819.05 | NORMAL
313.706 | 0.95 | 288.706 | 1.11 | 2 | 79289.74 | 14189.5956 | 5334.0534 | 5187.665 | NORMAL
313.706 | 0.95 | 288.706 | 1.11 | 2 | 101352.97 | 14378.4291 | 6268.8513 | 4847.394 | NORMAL
313.706 | 0.95 | 288.706 | 1.11 | 2 | 106868.78 | 14301.3482 | 6434.4769 | 4779.723 | NORMAL
313.706 | 0.95 | 288.706 | 1.42 | 1 | 57226.51 | 10289.7714 | 3089.5553 | 4163.5 | NORMAL
313.706 | 0.95 | 288.706 | 1.42 | 1 | 79289.74 | 10786.1079 | 4146.6652 | 3811.08 | NORMAL
313.706 | 0.95 | 288.706 | 1.42 | 1 | 101352.97 | 10980.1876 | 4843.0423 | 3619.788 | NORMAL
313.706 | 0.95 | 288.706 | 1.42 | 1 | 106868.78 | 10930.041 | 4954.8062 | 3587.094 | NORMAL
313.706 | 0.95 | 288.706 | 1.42 | 2 | 57226.51 | 13767.2919 | 4192.2092 | 5845.85 | NORMAL
313.706 | 0.95 | 288.706 | 1.42 | 2 | 79289.74 | 14482.7667 | 5483.7982 | 5218.5 | NORMAL
313.706 | 0.95 | 288.706 | 1.42 | 2 | 101352.97 | 14767.3505 | 6438.1661 | 4872.224 | NORMAL
313.706 | 0.95 | 288.706 | 1.42 | 2 | 106868.78 | 14701.2896 | 6597.2772 | 4805.007 | NORMAL
313.706 | 0.95 | 291.483 | 0.5 | 1 | 57226.51 | 10527.9601 | 2830.4842 | 4175.803 | NORMAL
313.706 | 0.95 | 291.483 | 0.5 | 1 | 79289.74 | 10658.3236 | 3658.8639 | 3808.537 | NORMAL
313.706 | 0.95 | 291.483 | 0.5 | 1 | 101352.97 | 10565.3869 | 4293.3823 | 3617.789 | NORMAL
313.706 | 0.95 | 291.483 | 0.5 | 1 | 106868.78 | 10455.129 | 4407.7987 | 3587.0734 | NORMAL
313.706 | 0.95 | 291.483 | 0.5 | 2 | 57226.51 | 13622.7139 | 3702.0951 | 5825.701 | NORMAL
313.706 | 0.95 | 291.483 | 0.5 | 2 | 79289.74 | 13751.9637 | 4822.3186 | 5148.928 | NORMAL
313.706 | 0.95 | 291.483 | 0.5 | 2 | 101352.97 | 13577.0516 | 5696.3878 | 4793.194 | NORMAL
313.706 | 0.95 | 291.483 | 0.5 | 2 | 106868.78 | 13449.5897 | 5863.0662 | 4726.6043 | NORMAL
313.706 | 0.95 | 291.483 | 0.8 | 1 | 57226.51 | 10940.2989 | 2814.9608 | 4203.765 | NORMAL
313.706 | 0.95 | 291.483 | 0.8 | 1 | 79289.74 | 11331.0668 | 3846.6252 | 3823.8 | NORMAL
313.706 | 0.95 | 291.483 | 0.8 | 1 | 101352.97 | 11413.7456 | 4534.8752 | 3620.917 | NORMAL
313.706 | 0.95 | 291.483 | 0.8 | 1 | 106868.78 | 11319.6073 | 4651.4983 | 3587.134 | NORMAL
313.706 | 0.95 | 291.483 | 0.8 | 2 | 57226.51 | 14345.7796 | 3731.5525 | 5937.44 | NORMAL
313.706 | 0.95 | 291.483 | 0.8 | 2 | 79289.74 | 14857.0926 | 5058.9886 | 5258.115 | NORMAL
313.706 | 0.95 | 291.483 | 0.8 | 2 | 101352.97 | 14951.3482 | 6006.45 | 4886.681 | NORMAL
313.706 | 0.95 | 291.483 | 0.8 | 2 | 106868.78 | 14852.6377 | 6188.9605 | 4814.237 | NORMAL
313.706 | 0.95 | 291.483 | 1.11 | 1 | 57226.51 | 11101.9343 | 3137.6842 | 4214.66 | NORMAL
313.706 | 0.95 | 291.483 | 1.11 | 1 | 79289.74 | 11613.8921 | 3989.7901 | 3832.352 | NORMAL
313.706 | 0.95 | 291.483 | 1.11 | 1 | 101352.97 | 11802.5205 | 4701.5813 | 3624.038 | NORMAL
313.706 | 0.95 | 291.483 | 1.11 | 1 | 106868.78 | 11723.0363 | 4810.3369 | 3587.061 | NORMAL
313.706 | 0.95 | 291.483 | 1.11 | 2 | 57226.51 | 14652.3447 | 3617.9716 | 5984.53 | NORMAL
313.706 | 0.95 | 291.483 | 1.11 | 2 | 79289.74 | 15374.4431 | 5222.2064 | 5304.786 | NORMAL
313.706 | 0.95 | 291.483 | 1.11 | 2 | 101352.97 | 15617.9367 | 6204.116 | 4932.696 | NORMAL
313.706 | 0.95 | 291.483 | 1.11 | 2 | 106868.78 | 15535.1114 | 6381.9946 | 4858.062 | NORMAL
313.706 | 0.95 | 291.483 | 1.42 | 1 | 57226.51 | 11188.2767 | 3261.7854 | 4220.35 | NORMAL
313.706 | 0.95 | 291.483 | 1.42 | 1 | 79289.74 | 11742.5264 | 3951.912 | 3835.18 | NORMAL
313.706 | 0.95 | 291.483 | 1.42 | 1 | 101352.97 | 12013.5405 | 4848.2925 | 3625.421 | NORMAL
313.706 | 0.95 | 291.483 | 1.42 | 1 | 106868.78 | 11951.4068 | 4958.6984 | 3588.576 | NORMAL
313.706 | 0.95 | 291.483 | 1.42 | 2 | 57226.51 | 14826.6706 | 3923.4187 | 6014 | NORMAL
313.706 | 0.95 | 291.483 | 1.42 | 2 | 79289.74 | 15667.7608 | 5261.5161 | 5335.96 | NORMAL
313.706 | 0.95 | 291.483 | 1.42 | 2 | 101352.97 | 16017.585 | 6370.2576 | 4959.002 | NORMAL
313.706 | 0.95 | 291.483 | 1.42 | 2 | 106868.78 | 15946.7468 | 6537.7835 | 4884.795 | NORMAL
313.706 | 0.95 | 294.26 | 0.5 | 1 | 57226.51 | 11472.2157 | 2717.4123 | 4236.265 | NORMAL
313.706 | 0.95 | 294.26 | 0.5 | 1 | 79289.74 | 11670.9261 | 3597.3062 | 3835.116 | NORMAL
313.706 | 0.95 | 294.26 | 0.5 | 1 | 101352.97 | 11593.4935 | 4273.153 | 3623.238 | NORMAL
313.706 | 0.95 | 294.26 | 0.5 | 1 | 106868.78 | 11474.2966 | 4401.2533 | 3586.639 | NORMAL
313.706 | 0.95 | 294.26 | 0.5 | 2 | 57226.51 | 14754.6307 | 3566.7992 | 6001.904 | NORMAL
313.706 | 0.95 | 294.26 | 0.5 | 2 | 79289.74 | 14974.6483 | 4697.3825 | 5269.158 | NORMAL
313.706 | 0.95 | 294.26 | 0.5 | 2 | 101352.97 | 14816.0023 | 5635.5924 | 4877.225 | NORMAL
313.706 | 0.95 | 294.26 | 0.5 | 2 | 106868.78 | 14674.3259 | 5819.4121 | 4803.046 | NORMAL
313.706 | 0.95 | 294.26 | 0.8 | 1 | 57226.51 | 11872.0692 | 2655.4138 | 4264.645 | NORMAL
313.706 | 0.95 | 294.26 | 0.8 | 1 | 79289.74 | 12348.2122 | 3767.81 | 3853.777 | NORMAL
313.706 | 0.95 | 294.26 | 0.8 | 1 | 101352.97 | 12469.871 | 4496.86 | 3629.914 | NORMAL
313.706 | 0.95 | 294.26 | 0.8 | 1 | 106868.78 | 12370.252 | 4622.5158 | 3590.583 | NORMAL
313.706 | 0.95 | 294.26 | 0.8 | 2 | 57226.51 | 15454.0739 | 3390.2993 | 6112.175 | NORMAL
313.706 | 0.95 | 294.26 | 0.8 | 2 | 79289.74 | 16087.8957 | 4919.7428 | 5381.02 | NORMAL
313.706 | 0.95 | 294.26 | 0.8 | 2 | 101352.97 | 16237.3388 | 5914.6293 | 4976.163 | NORMAL
313.706 | 0.95 | 294.26 | 0.8 | 2 | 106868.78 | 16130.2755 | 6109.1644 | 4896.385 | NORMAL
313.706 | 0.95 | 294.26 | 1.11 | 1 | 57226.51 | 12027.9894 | 2967.4734 | 4275.8 | NORMAL
313.706 | 0.95 | 294.26 | 1.11 | 1 | 79289.74 | 12634.7011 | 3922.6704 | 3861.693 | NORMAL
313.706 | 0.95 | 294.26 | 1.11 | 1 | 101352.97 | 12871.1606 | 4665.8472 | 3633.07 | NORMAL
313.706 | 0.95 | 294.26 | 1.11 | 1 | 106868.78 | 12783.2943 | 4773.6017 | 3592.941 | NORMAL
313.706 | 0.95 | 294.26 | 1.11 | 2 | 57226.51 | 15749.8242 | 3301.1159 | 6157.62 | NORMAL
313.706 | 0.95 | 294.26 | 1.11 | 2 | 79289.74 | 16602.0809 | 4949.761 | 5428.338 | NORMAL
313.706 | 0.95 | 294.26 | 1.11 | 2 | 101352.97 | 16916.2661 | 6098.9737 | 5024.498 | NORMAL
313.706 | 0.95 | 294.26 | 1.11 | 2 | 106868.78 | 16829.4549 | 6285.0609 | 4942.381 | NORMAL
313.706 | 0.95 | 294.26 | 1.42 | 1 | 57226.51 | 12111.3423 | 3220.3938 | 4281.42 | NORMAL
313.706 | 0.95 | 294.26 | 1.42 | 1 | 79289.74 | 12765.1817 | 3877.5005 | 3864.75 | NORMAL
313.706 | 0.95 | 294.26 | 1.42 | 1 | 101352.97 | 13088.2474 | 4807.4049 | 3636.037 | NORMAL
313.706 | 0.95 | 294.26 | 1.42 | 1 | 106868.78 | 13018.9918 | 4924.0561 | 3594.691 | NORMAL
313.706 | 0.95 | 294.26 | 1.42 | 2 | 57226.51 | 15914.3904 | 3587.4219 | 6182.9 | NORMAL
313.706 | 0.95 | 294.26 | 1.42 | 2 | 79289.74 | 16892.4971 | 5036.3291 | 5460.22 | NORMAL
313.706 | 0.95 | 294.26 | 1.42 | 2 | 101352.97 | 17321.2485 | 6267.3474 | 5053.517 | NORMAL
313.706 | 0.95 | 294.26 | 1.42 | 2 | 106868.78 | 17247.0399 | 6435.2155 | 4970.351 | NORMAL
313.706 | 0.95 | 297.037 | 0.5 | 1 | 57226.51 | 12455.5979 | 2514.2994 | 4302.208 | NORMAL
313.706 | 0.95 | 297.037 | 0.5 | 1 | 79289.74 | 12740.1817 | 3505.8305 | 3866.04 | NORMAL
313.706 | 0.95 | 297.037 | 0.5 | 1 | 101352.97 | 12687.075 | 4222.119 | 3632.888 | NORMAL
313.706 | 0.95 | 297.037 | 0.5 | 1 | 106868.78 | 12557.0633 | 4360.8797 | 3591.74 | NORMAL
313.706 | 0.95 | 297.037 | 0.5 | 2 | 57226.51 | 15937.4267 | 3404.6487 | 6187.744 | NORMAL
313.706 | 0.95 | 297.037 | 0.5 | 2 | 79289.74 | 16273.1243 | 4521.1621 | 5395.887 | NORMAL
313.706 | 0.95 | 297.037 | 0.5 | 2 | 101352.97 | 16146.5709 | 5531.7829 | 4968.815 | NORMAL
313.706 | 0.95 | 297.037 | 0.5 | 2 | 106868.78 | 15988.0422 | 5737.0851 | 4887.199 | NORMAL
313.706 | 0.95 | 297.037 | 0.8 | 1 | 57226.51 | 12836.8699 | 2349.3911 | 4331.061 | NORMAL
313.706 | 0.95 | 297.037 | 0.8 | 1 | 79289.74 | 13417.1747 | 3621.9529 | 3886.564 | NORMAL
313.706 | 0.95 | 297.037 | 0.8 | 1 | 101352.97 | 13585.3165 | 4431.2042 | 3642.356 | NORMAL
313.706 | 0.95 | 297.037 | 0.8 | 1 | 106868.78 | 13477.6671 | 4563.1876 | 3598.543 | NORMAL
313.706 | 0.95 | 297.037 | 0.8 | 2 | 57226.51 | 16612.1336 | 3059.9218 | 6293.325 | NORMAL
313.706 | 0.95 | 297.037 | 0.8 | 2 | 79289.74 | 17373.6518 | 4759.0776 | 5512.82 | NORMAL
313.706 | 0.95 | 297.037 | 0.8 | 2 | 101352.97 | 17596.3951 | 5785.6771 | 5073.191 | NORMAL
313.706 | 0.95 | 297.037 | 0.8 | 2 | 106868.78 | 17482.6495 | 5991.4963 | 4985.64 | NORMAL
313.706 | 0.95 | 297.037 | 1.11 | 1 | 57226.51 | 12981.9168 | 2812.9737 | 4340.67 | NORMAL
313.706 | 0.95 | 297.037 | 1.11 | 1 | 79289.74 | 13701.524 | 3678.3934 | 3895.268 | NORMAL
313.706 | 0.95 | 297.037 | 1.11 | 1 | 101352.97 | 13993.2884 | 4601.1751 | 3646.565 | NORMAL
313.706 | 0.95 | 297.037 | 1.11 | 1 | 106868.78 | 13900.2345 | 4710.859 | 3602.31 | NORMAL
313.706 | 0.95 | 297.037 | 1.11 | 2 | 57226.51 | 16899.1207 | 2900.7679 | 6334.93 | NORMAL
313.706 | 0.95 | 297.037 | 1.11 | 2 | 79289.74 | 17875.2345 | 4726.1762 | 5563.068 | NORMAL
313.706 | 0.95 | 297.037 | 1.11 | 2 | 101352.97 | 18279.0445 | 5961.8932 | 5123.577 | NORMAL
313.706 | 0.95 | 297.037 | 1.11 | 2 | 106868.78 | 18190.0352 | 6153.6707 | 5033.659 | NORMAL
313.706 | 0.95 | 297.037 | 1.42 | 1 | 57226.51 | 13064.5956 | 3113.0188 | 4347.25 | NORMAL
313.706 | 0.95 | 297.037 | 1.42 | 1 | 79289.74 | 13832.5616 | 3786.3871 | 3898.53 | NORMAL
313.706 | 0.95 | 297.037 | 1.42 | 1 | 101352.97 | 14214.1559 | 4753.6828 | 3650.14 | NORMAL
313.706 | 0.95 | 297.037 | 1.42 | 1 | 106868.78 | 14139.7128 | 4856.1288 | 3604.409 | NORMAL
313.706 | 0.95 | 297.037 | 1.42 | 2 | 57226.51 | 17057.3857 | 3341.3372 | 6360.01 | NORMAL
313.706 | 0.95 | 297.037 | 1.42 | 2 | 79289.74 | 18163.3353 | 4661.9106 | 5592.12 | NORMAL
313.706 | 0.95 | 297.037 | 1.42 | 2 | 101352.97 | 18684.789 | 6118.222 | 5153.447 | NORMAL
313.706 | 0.95 | 297.037 | 1.42 | 2 | 106868.78 | 18609.9062 | 6302.4122 | 5062.732 | NORMAL
313.706 | 0.95 | 299.814 | 0.5 | 1 | 57226.51 | 13460.1993 | 2270.7087 | 4372.637 | NORMAL
313.706 | 0.95 | 299.814 | 0.5 | 1 | 79289.74 | 13851.0258 | 3401.2025 | 3901.477 | NORMAL
313.706 | 0.95 | 299.814 | 0.5 | 1 | 101352.97 | 13837.1629 | 4142.1686 | 3646.153 | NORMAL
313.706 | 0.95 | 299.814 | 0.5 | 1 | 106868.78 | 13696.7468 | 4290.6429 | 3600.402 | NORMAL
313.706 | 0.95 | 299.814 | 0.5 | 2 | 57226.51 | 17162.8664 | 3177.4473 | 6376.077 | NORMAL
313.706 | 0.95 | 299.814 | 0.5 | 2 | 79289.74 | 17620.1348 | 4358.869 | 5534.228 | NORMAL
313.706 | 0.95 | 299.814 | 0.5 | 2 | 101352.97 | 17547.7433 | 5383.1563 | 5068.65 | NORMAL
313.706 | 0.95 | 299.814 | 0.5 | 2 | 106868.78 | 17379.9238 | 5620.65 | 4978.217 | NORMAL
313.706 | 0.95 | 299.814 | 0.8 | 1 | 57226.51 | 13819.6366 | 1959.9147 | 4401.104 | NORMAL
313.706 | 0.95 | 299.814 | 0.8 | 1 | 79289.74 | 14520.2227 | 3369.258 | 3923.675 | NORMAL
313.706 | 0.95 | 299.814 | 0.8 | 1 | 101352.97 | 14746.3951 | 4338.9056 | 3658.751 | NORMAL
313.706 | 0.95 | 299.814 | 0.8 | 1 | 106868.78 | 14634.3787 | 4473.8466 | 3609.966 | NORMAL
313.706 | 0.95 | 299.814 | 0.8 | 2 | 57226.51 | 17809.6718 | 2586 | 6475.045 | NORMAL
313.706 | 0.95 | 299.814 | 0.8 | 2 | 79289.74 | 18699.9414 | 4569.7234 | 5648.943 | NORMAL
313.706 | 0.95 | 299.814 | 0.8 | 2 | 101352.97 | 19008.3236 | 5626.0646 | 5177.378 | NORMAL
313.706 | 0.95 | 299.814 | 0.8 | 2 | 106868.78 | 18891.9402 | 5835.7014 | 5081.736 | NORMAL
313.706 | 0.95 | 299.814 | 1.11 | 1 | 57226.51 | 13956.653 | 2330.2028 | 4411.16 | NORMAL
313.706 | 0.95 | 299.814 | 1.11 | 1 | 79289.74 | 14798.2122 | 3481.4718 | 3932.963 | NORMAL
313.706 | 0.95 | 299.814 | 1.11 | 1 | 101352.97 | 15157.2978 | 4372.1983 | 3663.848 | NORMAL
313.706 | 0.95 | 299.814 | 1.11 | 1 | 106868.78 | 15060.4631 | 4620.6856 | 3615.086 | NORMAL
313.706 | 0.95 | 299.814 | 1.11 | 2 | 57226.51 | 18087.2216 | 2235.4902 | 6515.45 | NORMAL
313.706 | 0.95 | 299.814 | 1.11 | 2 | 79289.74 | 19182.5029 | 4250.6892 | 5701.376 | NORMAL
313.706 | 0.95 | 299.814 | 1.11 | 2 | 101352.97 | 19686.9578 | 5795.3876 | 5229.266 | NORMAL
313.706 | 0.95 | 299.814 | 1.11 | 2 | 106868.78 | 19598.769 | 5988.7959 | 5131.377 | NORMAL
313.706 | 0.95 | 299.814 | 1.42 | 1 | 57226.51 | 14029.8945 | 2966.551 | 4416.49 | NORMAL
313.706 | 0.95 | 299.814 | 1.42 | 1 | 79289.74 | 14927.4033 | 3915.7564 | 3936.4 | NORMAL
313.706 | 0.95 | 299.814 | 1.42 | 1 | 101352.97 | 15380.3048 | 4683.3643 | 3668.205 | NORMAL
313.706 | 0.95 | 299.814 | 1.42 | 1 | 106868.78 | 15302.9308 | 4750.0603 | 3617.954 | NORMAL
313.706 | 0.95 | 299.814 | 1.42 | 2 | 57226.51 | 18246.0141 | 2589.4561 | 6538.01 | NORMAL
313.706 | 0.95 | 299.814 | 1.42 | 2 | 79289.74 | 19462.075 | 4313.7884 | 5730.24 | NORMAL
313.706 | 0.95 | 299.814 | 1.42 | 2 | 101352.97 | 20088.6577 | 5687.7217 | 5259.826 | NORMAL
313.706 | 0.95 | 299.814 | 1.42 | 2 | 106868.78 | 20016.3247 | 6136.5848 | 5161.446 | NORMAL
313.706 | 0.95 | 302.591 | 0.5 | 1 | 57226.51 | 14495.9554 | 1989.6859 | 4447.714 | NORMAL
313.706 | 0.95 | 302.591 | 0.5 | 1 | 79289.74 | 15011.4889 | 3206.9344 | 3941.987 | NORMAL
313.706 | 0.95 | 302.591 | 0.5 | 1 | 101352.97 | 15051.2309 | 4040.6836 | 3663.712 | NORMAL
313.706 | 0.95 | 302.591 | 0.5 | 1 | 106868.78 | 14902.2274 | 4193.8743 | 3613.107 | NORMAL
313.706 | 0.95 | 302.591 | 0.5 | 2 | 57226.51 | 18455.3048 | 2894.3455 | 6567.039 | NORMAL
313.706 | 0.95 | 302.591 | 0.5 | 2 | 79289.74 | 19020.4865 | 4155.5579 | 5681.126 | NORMAL
313.706 | 0.95 | 302.591 | 0.5 | 2 | 101352.97 | 19025.8793 | 5191.6107 | 5177.582 | NORMAL
313.706 | 0.95 | 302.591 | 0.5 | 2 | 106868.78 | 18851.2603 | 5469.1842 | 5078.154 | NORMAL
313.706 | 0.95 | 302.591 | 0.8 | 1 | 57226.51 | 14828.1067 | 1781.3005 | 4474.183 | NORMAL
313.706 | 0.95 | 302.591 | 0.8 | 1 | 79289.74 | 15663.6284 | 3171.7438 | 3965.643 | NORMAL
313.706 | 0.95 | 302.591 | 0.8 | 1 | 101352.97 | 15962.6319 | 4228.2139 | 3679.342 | NORMAL
313.706 | 0.95 | 302.591 | 0.8 | 1 | 106868.78 | 15846.7175 | 4364.7248 | 3625.532 | NORMAL
313.706 | 0.95 | 302.591 | 0.8 | 2 | 57226.51 | 19090.1524 | 2078.574 | 6657.956 | NORMAL
313.706 | 0.95 | 302.591 | 0.8 | 2 | 79289.74 | 20062.8957 | 4335.8726 | 5796.368 | NORMAL
313.706 | 0.95 | 302.591 | 0.8 | 2 | 101352.97 | 20484.4959 | 5441.6244 | 5288.981 | NORMAL
313.706 | 0.95 | 302.591 | 0.8 | 2 | 106868.78 | 20366.5006 | 5650.4005 | 5185.198 | NORMAL
313.706 | 0.95 | 302.591 | 1.11 | 1 | 57226.51 | 14960.3165 | 2340.5415 | 4485.44 | NORMAL
313.706 | 0.95 | 302.591 | 1.11 | 1 | 79289.74 | 15933.265 | 3231.0909 | 3975.409 | NORMAL
313.706 | 0.95 | 302.591 | 1.11 | 1 | 101352.97 | 16371.3951 | 4227.8964 | 3685.393 | NORMAL
313.706 | 0.95 | 302.591 | 1.11 | 1 | 106868.78 | 16272.0399 | 4515.9792 | 3631.871 | NORMAL
313.706 | 0.95 | 302.591 | 1.11 | 2 | 57226.51 | 19365.2403 | 1723.4076 | 6700.1 | NORMAL
313.706 | 0.95 | 302.591 | 1.11 | 2 | 79289.74 | 20528.7808 | 3876.8808 | 5847.132 | NORMAL
313.706 | 0.95 | 302.591 | 1.11 | 2 | 101352.97 | 21147.4502 | 5487.9325 | 5342.641 | NORMAL
313.706 | 0.95 | 302.591 | 1.11 | 2 | 106868.78 | 21061.8992 | 5803.4168 | 5236.898 | NORMAL
313.706 | 0.95 | 302.591 | 1.42 | 1 | 57226.51 | 15030.0997 | 2887.0266 | 4490.16 | NORMAL
313.706 | 0.95 | 302.591 | 1.42 | 1 | 79289.74 | 16076.3775 | 3816.6606 | 3980.77 | NORMAL
313.706 | 0.95 | 302.591 | 1.42 | 1 | 101352.97 | 16593.1712 | 4532.0597 | 3690.359 | NORMAL
313.706 | 0.95 | 302.591 | 1.42 | 1 | 106868.78 | 16514.2145 | 4629.5619 | 3635.695 | NORMAL
313.706 | 0.95 | 302.591 | 1.42 | 2 | 57226.51 | 19535.9613 | 2216.2962 | 6720.77 | NORMAL
313.706 | 0.95 | 302.591 | 1.42 | 2 | 79289.74 | 20799.0035 | 3817.4075 | 5875.57 | NORMAL
313.706 | 0.95 | 302.591 | 1.42 | 2 | 101352.97 | 21542.4385 | 5377.5312 | 5373.924 | NORMAL
313.706 | 0.95 | 302.591 | 1.42 | 2 | 106868.78 | 21474.3552 | 5958.747 | 5267.684 | NORMAL
313.706 | 0.95 | 305.368 | 0.5 | 1 | 57226.51 | 15559.6717 | 1650.3521 | 4526.914 | NORMAL
313.706 | 0.95 | 305.368 | 0.5 | 1 | 79289.74 | 16217.204 | 3004.5776 | 3987.648 | NORMAL
313.706 | 0.95 | 305.368 | 0.5 | 1 | 101352.97 | 16326.2896 | 3889.0201 | 3686.244 | NORMAL
313.706 | 0.95 | 305.368 | 0.5 | 1 | 106868.78 | 16170.7796 | 4077.5753 | 3630.25 | NORMAL
313.706 | 0.95 | 305.368 | 0.5 | 2 | 57226.51 | 19840.7386 | 2710.3838 | 6760.64 | NORMAL
313.706 | 0.95 | 305.368 | 0.5 | 2 | 79289.74 | 20466.2075 | 3885.489 | 5838.657 | NORMAL
313.706 | 0.95 | 305.368 | 0.5 | 2 | 101352.97 | 20575.4689 | 4931.014 | 5295.795 | NORMAL
313.706 | 0.95 | 305.368 | 0.5 | 2 | 106868.78 | 20395.9848 | 5289.7802 | 5187.317 | NORMAL
313.706 | 0.95 | 305.368 | 0.8 | 1 | 57226.51 | 15866.2661 | 1269.5361 | 4552.223 | NORMAL
313.706 | 0.95 | 305.368 | 0.8 | 1 | 79289.74 | 16845.4865 | 2793.386 | 4012.253 | NORMAL
313.706 | 0.95 | 305.368 | 0.8 | 1 | 101352.97 | 17230.6565 | 4105.6002 | 3704.421 | NORMAL
313.706 | 0.95 | 305.368 | 0.8 | 1 | 106868.78 | 17112.7198 | 4240.2239 | 3645.521 | NORMAL
313.706 | 0.95 | 305.368 | 0.8 | 2 | 57226.51 | 20484.1442 | 1554.7097 | 6843.442 | NORMAL
313.706 | 0.95 | 305.368 | 0.8 | 2 | 79289.74 | 21469.871 | 3886.519 | 5949.889 | NORMAL
313.706 | 0.95 | 305.368 | 0.8 | 2 | 101352.97 | 22009.9648 | 5238.9439 | 5410.06 | NORMAL
313.706 | 0.95 | 305.368 | 0.8 | 2 | 106868.78 | 21896.4537 | 5444.7284 | 5297.607 | NORMAL
313.706 | 0.95 | 305.368 | 1.11 | 1 | 57226.51 | 15992.6436 | 1601.8232 | 4561.84 | NORMAL
313.706 | 0.95 | 305.368 | 1.11 | 1 | 79289.74 | 17104.1032 | 2991.0971 | 4022.287 | NORMAL
313.706 | 0.95 | 305.368 | 1.11 | 1 | 101352.97 | 17633.3822 | 3825.2801 | 3711.43 | NORMAL
313.706 | 0.95 | 305.368 | 1.11 | 1 | 106868.78 | 17532.8546 | 4395.2587 | 3653.073 | NORMAL
313.706 | 0.95 | 305.368 | 1.11 | 2 | 57226.51 | 20793.7866 | 950.5277 | 6875.61 | NORMAL
313.706 | 0.95 | 305.368 | 1.11 | 2 | 79289.74 | 21910.1114 | 3344.0746 | 5999.94 | NORMAL
313.706 | 0.95 | 305.368 | 1.11 | 2 | 101352.97 | 22654.3669 | 5161.0273 | 5464.752 | NORMAL
313.706 | 0.95 | 305.368 | 1.11 | 2 | 106868.78 | 22578.1653 | 5594.8242 | 5349.674 | NORMAL
313.706 | 0.95 | 305.368 | 1.42 | 1 | 57226.51 | 16058.1477 | 2340.5714 | 4566.72 | NORMAL
313.706 | 0.95 | 305.368 | 1.42 | 1 | 79289.74 | 17228.8394 | 3534.7893 | 4026.01 | NORMAL
313.706 | 0.95 | 305.368 | 1.42 | 1 | 101352.97 | 17852.4326 | 4224.0998 | 3716.983 | NORMAL
313.706 | 0.95 | 305.368 | 1.42 | 1 | 106868.78 | 17772.6553 | 4501.2982 | 3657.335 | NORMAL
313.706 | 0.95 | 305.368 | 1.42 | 2 | 57226.51 | 20976.8464 | 1254.5685 | 6895.87 | NORMAL
313.706 | 0.95 | 305.368 | 1.42 | 2 | 79289.74 | 22170.8968 | 3452.7181 | 6028.15 | NORMAL
313.706 | 0.95 | 305.368 | 1.42 | 2 | 101352.97 | 23037.837 | 4803.9419 | 5496.414 | NORMAL
313.706 | 0.95 | 305.368 | 1.42 | 2 | 106868.78 | 22978.4291 | 5763.2198 | 5381.61 | NORMAL
324.817 | 0.05 | 288.706 | 0.5 | 1 | 57226.51 | 5873.7397 | 5871.3021 | 5307.805 | NORMAL
324.817 | 0.05 | 288.706 | 0.5 | 1 | 79289.74 | 6352.1981 | 6349.7335 | 4781.692 | NORMAL
324.817 | 0.05 | 288.706 | 0.5 | 1 | 101352.97 | 6438.9508 | 6434.5787 | 4687.911 | NORMAL
324.817 | 0.05 | 288.706 | 0.5 | 1 | 106868.78 | 6447.8605 | 6445.4168 | 4678.5979 | NORMAL
324.817 | 0.05 | 288.706 | 0.5 | 2 | 57226.51 | 8258.1184 | 8239.6698 | 7126.983 | NORMAL
324.817 | 0.05 | 288.706 | 0.5 | 2 | 79289.74 | 8439.5662 | 8419.5054 | 5965.334 | NORMAL
324.817 | 0.05 | 288.706 | 0.5 | 2 | 101352.97 | 8605.422 | 8585.8017 | 5734.1464 | NORMAL
324.817 | 0.05 | 288.706 | 0.5 | 2 | 106868.78 | 8616.3247 | 8614.0328 | 5694.0829 | NORMAL
324.817 | 0.05 | 288.706 | 0.8 | 1 | 57226.51 | 6607.3564 | 6603.8743 | 5377.823 | NORMAL
324.817 | 0.05 | 288.706 | 0.8 | 1 | 79289.74 | 7240.9437 | 7237.3015 | 4787.896 | NORMAL
324.817 | 0.05 | 288.706 | 0.8 | 1 | 101352.97 | 7391.6178 | 7387.9442 | 4651.417 | NORMAL
324.817 | 0.05 | 288.706 | 0.8 | 1 | 106868.78 | 7414.068 | 7410.3906 | 4631.142 | NORMAL
324.817 | 0.05 | 288.706 | 0.8 | 2 | 57226.51 | 9159.9355 | 9115.8396 | 7119.077 | NORMAL
324.817 | 0.05 | 288.706 | 0.8 | 2 | 79289.74 | 9683.0598 | 9634.8382 | 6108.063 | NORMAL
324.817 | 0.05 | 288.706 | 0.8 | 2 | 101352.97 | 9917.2626 | 9913.2759 | 5838.172 | NORMAL
324.817 | 0.05 | 288.706 | 0.8 | 2 | 106868.78 | 9960.932 | 9956.9377 | 5789.482 | NORMAL
324.817 | 0.05 | 288.706 | 1.11 | 1 | 57226.51 | 6996.2485 | 6970.5303 | 5416.25 | NORMAL
324.817 | 0.05 | 288.706 | 1.11 | 1 | 79289.74 | 7719.2849 | 7707.073 | 4794.642 | NORMAL
324.817 | 0.05 | 288.706 | 1.11 | 1 | 101352.97 | 7906.5358 | 7902.0686 | 4640.08 | NORMAL
324.817 | 0.05 | 288.706 | 1.11 | 1 | 106868.78 | 7937.4853 | 7933.0007 | 4614.707 | NORMAL
324.817 | 0.05 | 288.706 | 1.11 | 2 | 57226.51 | 9505.51 | 9500.5956 | 7108.83 | NORMAL
324.817 | 0.05 | 288.706 | 1.11 | 2 | 79289.74 | 10385.0821 | 10379.9622 | 6185.657 | NORMAL
324.817 | 0.05 | 288.706 | 1.11 | 2 | 101352.97 | 10672.1278 | 10666.9625 | 5890.096 | NORMAL
324.817 | 0.05 | 288.706 | 1.11 | 2 | 106868.78 | 10719.959 | 10714.7812 | 5842.639 | NORMAL
324.817 | 0.05 | 288.706 | 1.42 | 1 | 57226.51 | 7242.6729 | 7219.844 | 5439.46 | NORMAL
324.817 | 0.05 | 288.706 | 1.42 | 1 | 79289.74 | 8025.5569 | 8020.6131 | 4799.38 | NORMAL
324.817 | 0.05 | 288.706 | 1.42 | 1 | 101352.97 | 8234.8476 | 8228.935 | 4636.87 | NORMAL
324.817 | 0.05 | 288.706 | 1.42 | 1 | 106868.78 | 8273.5639 | 8264.3223 | 4606.852 | NORMAL
324.817 | 0.05 | 288.706 | 1.42 | 2 | 57226.51 | 9658.2356 | 9652.6725 | 7100.51 | NORMAL
324.817 | 0.05 | 288.706 | 1.42 | 2 | 79289.74 | 10844.8417 | 10826.2103 | 6241.2 | NORMAL
324.817 | 0.05 | 288.706 | 1.42 | 2 | 101352.97 | 11171.1606 | 11165.1282 | 5926.303 | NORMAL
324.817 | 0.05 | 288.706 | 1.42 | 2 | 106868.78 | 11228.4877 | 11219.3926 | 5871.844 | NORMAL
324.817 | 0.05 | 291.483 | 0.5 | 1 | 57226.51 | 6344.9297 | 6320.4065 | 5351.507 | NORMAL
324.817 | 0.05 | 291.483 | 0.5 | 1 | 79289.74 | 6870.4865 | 6867.2643 | 4784.143 | NORMAL
324.817 | 0.05 | 291.483 | 0.5 | 1 | 101352.97 | 6983.4701 | 6980.2437 | 4664.237 | NORMAL
324.817 | 0.05 | 291.483 | 0.5 | 1 | 106868.78 | 6998.769 | 6995.5426 | 4648.2472 | NORMAL
324.817 | 0.05 | 291.483 | 0.5 | 2 | 57226.51 | 8688.1594 | 8685.023 | 7124.674 | NORMAL
324.817 | 0.05 | 291.483 | 0.5 | 2 | 79289.74 | 8967.7315 | 8964.6466 | 6026.002 | NORMAL
324.817 | 0.05 | 291.483 | 0.5 | 2 | 101352.97 | 9145.34 | 9120.4921 | 5777.977 | NORMAL
324.817 | 0.05 | 291.483 | 0.5 | 2 | 106868.78 | 9174.5311 | 9171.4943 | 5732.8172 | NORMAL
324.817 | 0.05 | 291.483 | 0.8 | 1 | 57226.51 | 7158.1477 | 7153.6023 | 5430.128 | NORMAL
324.817 | 0.05 | 291.483 | 0.8 | 1 | 79289.74 | 7843.9332 | 7839.1876 | 4796.634 | NORMAL
324.817 | 0.05 | 291.483 | 0.8 | 1 | 101352.97 | 8023.388 | 8018.5981 | 4637.945 | NORMAL
324.817 | 0.05 | 291.483 | 0.8 | 1 | 106868.78 | 8053.1946 | 8048.3949 | 4611.777 | NORMAL
324.817 | 0.05 | 291.483 | 0.8 | 2 | 57226.51 | 9497.4795 | 9492.4173 | 7108.336 | NORMAL
324.817 | 0.05 | 291.483 | 0.8 | 2 | 79289.74 | 10322.7726 | 10317.6009 | 6178.789 | NORMAL
324.817 | 0.05 | 291.483 | 0.8 | 2 | 101352.97 | 10584.6424 | 10579.4454 | 5885.213 | NORMAL
324.817 | 0.05 | 291.483 | 0.8 | 2 | 106868.78 | 10629.0739 | 10623.8762 | 5836.848 | NORMAL
324.817 | 0.05 | 291.483 | 1.11 | 1 | 57226.51 | 7590.0645 | 7584.6604 | 5474.6 | NORMAL
324.817 | 0.05 | 291.483 | 1.11 | 1 | 79289.74 | 8372.8312 | 8367.0874 | 4805.441 | NORMAL
324.817 | 0.05 | 291.483 | 1.11 | 1 | 101352.97 | 8586.5475 | 8580.7172 | 4633.583 | NORMAL
324.817 | 0.05 | 291.483 | 1.11 | 1 | 106868.78 | 8626.2603 | 8616.4695 | 4602.141 | NORMAL
324.817 | 0.05 | 291.483 | 1.11 | 2 | 57226.51 | 9752.8722 | 9733.0056 | 7093.91 | NORMAL
324.817 | 0.05 | 291.483 | 1.11 | 2 | 79289.74 | 11090.6799 | 11084.0588 | 6266.387 | NORMAL
324.817 | 0.05 | 291.483 | 1.11 | 2 | 101352.97 | 11410.2872 | 11403.5894 | 5945.14 | NORMAL
324.817 | 0.05 | 291.483 | 1.11 | 2 | 106868.78 | 11466.9109 | 11460.1913 | 5890.283 | NORMAL
324.817 | 0.05 | 291.483 | 1.42 | 1 | 57226.51 | 7869.3435 | 7861.2538 | 5498.84 | NORMAL
324.817 | 0.05 | 291.483 | 1.42 | 1 | 79289.74 | 8713.1008 | 8706.6706 | 4811.76 | NORMAL
324.817 | 0.05 | 291.483 | 1.42 | 1 | 101352.97 | 8954.1325 | 8946.5662 | 4629.547 | NORMAL
324.817 | 0.05 | 291.483 | 1.42 | 1 | 106868.78 | 8996.6002 | 8984.7517 | 4597.647 | NORMAL
324.817 | 0.05 | 291.483 | 1.42 | 2 | 57226.51 | 9881.7702 | 9874.7838 | 7083.97 | NORMAL
324.817 | 0.05 | 291.483 | 1.42 | 2 | 79289.74 | 11600.4689 | 11592.7894 | 6322.99 | NORMAL
324.817 | 0.05 | 291.483 | 1.42 | 2 | 101352.97 | 11956.8288 | 11942.6839 | 5987.606 | NORMAL
324.817 | 0.05 | 291.483 | 1.42 | 2 | 106868.78 | 12021.4537 | 12013.6277 | 5930.005 | NORMAL
324.817 | 0.05 | 294.26 | 0.5 | 1 | 57226.51 | 6822.0985 | 6814.6419 | 5399.696 | NORMAL
324.817 | 0.05 | 294.26 | 0.5 | 1 | 79289.74 | 7390.7386 | 7386.6219 | 4790.003 | NORMAL
324.817 | 0.05 | 294.26 | 0.5 | 1 | 101352.97 | 7527.1102 | 7522.9853 | 4647.825 | NORMAL
324.817 | 0.05 | 294.26 | 0.5 | 1 | 106868.78 | 7548.1243 | 7544.003 | 4626.0687 | NORMAL
324.817 | 0.05 | 294.26 | 0.5 | 2 | 57226.51 | 9092.5264 | 9088.4893 | 7120.569 | NORMAL
324.817 | 0.05 | 294.26 | 0.5 | 2 | 79289.74 | 9502.6964 | 9487.5871 | 6086.805 | NORMAL
324.817 | 0.05 | 294.26 | 0.5 | 2 | 101352.97 | 9699.8828 | 9695.9349 | 5819.381 | NORMAL
324.817 | 0.05 | 294.26 | 0.5 | 2 | 106868.78 | 9734.1149 | 9730.2212 | 5773.9213 | NORMAL
324.817 | 0.05 | 294.26 | 0.8 | 1 | 57226.51 | 7716.9402 | 7698.5199 | 5485.415 | NORMAL
324.817 | 0.05 | 294.26 | 0.8 | 1 | 79289.74 | 8454.1911 | 8448.1463 | 4807.01 | NORMAL
324.817 | 0.05 | 294.26 | 0.8 | 1 | 101352.97 | 8656.5064 | 8650.395 | 4632.47 | NORMAL
324.817 | 0.05 | 294.26 | 0.8 | 1 | 106868.78 | 8695.8382 | 8689.7163 | 4598.957 | NORMAL
324.817 | 0.05 | 294.26 | 0.8 | 2 | 57226.51 | 9753.136 | 9746.7477 | 7094.431 | NORMAL
324.817 | 0.05 | 294.26 | 0.8 | 2 | 79289.74 | 10975.1172 | 10968.5322 | 6254.364 | NORMAL
324.817 | 0.05 | 294.26 | 0.8 | 2 | 101352.97 | 11266.5592 | 11259.9457 | 5933.999 | NORMAL
324.817 | 0.05 | 294.26 | 0.8 | 2 | 106868.78 | 11317.7608 | 11311.14 | 5879.712 | NORMAL
324.817 | 0.05 | 294.26 | 1.11 | 1 | 57226.51 | 8203.1946 | 8196.3039 | 5530.78 | NORMAL
324.817 | 0.05 | 294.26 | 1.11 | 1 | 79289.74 | 9036.0785 | 9028.7684 | 4818.193 | NORMAL
324.817 | 0.05 | 294.26 | 1.11 | 1 | 101352.97 | 9280.129 | 9272.7049 | 4627.069 | NORMAL
324.817 | 0.05 | 294.26 | 1.11 | 1 | 106868.78 | 9323.7691 | 9316.3194 | 4593.31 | NORMAL
324.817 | 0.05 | 294.26 | 1.11 | 2 | 57226.51 | 9917.6729 | 9904.4427 | 7075.96 | NORMAL
324.817 | 0.05 | 294.26 | 1.11 | 2 | 79289.74 | 11822.1571 | 11813.7515 | 6339.478 | NORMAL
324.817 | 0.05 | 294.26 | 1.11 | 2 | 101352.97 | 12164.3025 | 12155.7996 | 6003.585 | NORMAL
324.817 | 0.05 | 294.26 | 1.11 | 2 | 106868.78 | 12227.0223 | 12218.5 | 5944.745 | NORMAL
324.817 | 0.05 | 294.26 | 1.42 | 1 | 57226.51 | 8519.0211 | 8511.3881 | 5558.86 | NORMAL
324.817 | 0.05 | 294.26 | 1.42 | 1 | 79289.74 | 9411.3423 | 9403.145 | 4826.58 | NORMAL
324.817 | 0.05 | 294.26 | 1.42 | 1 | 101352.97 | 9685.8441 | 9676.1679 | 4624.909 | NORMAL
324.817 | 0.05 | 294.26 | 1.42 | 1 | 106868.78 | 9734.9648 | 9719.4765 | 4589.237 | NORMAL
324.817 | 0.05 | 294.26 | 1.42 | 2 | 57226.51 | 10012.6612 | 10004.1204 | 7063.91 | NORMAL
324.817 | 0.05 | 294.26 | 1.42 | 2 | 79289.74 | 12375.7034 | 12365.9761 | 6406.56 | NORMAL
324.817 | 0.05 | 294.26 | 1.42 | 2 | 101352.97 | 12762.5146 | 12752.6237 | 6050.387 | NORMAL
324.817 | 0.05 | 294.26 | 1.42 | 2 | 106868.78 | 12834.0856 | 12824.1648 | 5988.326 | NORMAL
324.817 | 0.05 | 297.037 | 0.5 | 1 | 57226.51 | 7306.9754 | 7301.8824 | 5446.599 | NORMAL
324.817 | 0.05 | 297.037 | 0.5 | 1 | 79289.74 | 7914.9472 | 7909.7946 | 4797.838 | NORMAL
324.817 | 0.05 | 297.037 | 0.5 | 1 | 101352.97 | 8072.1864 | 8067.0202 | 4637.062 | NORMAL
324.817 | 0.05 | 297.037 | 0.5 | 1 | 106868.78 | 8098.5346 | 8093.3677 | 4610.3414 | NORMAL
324.817 | 0.05 | 297.037 | 0.5 | 2 | 57226.51 | 9416.5885 | 9392.6421 | 7111.204 | NORMAL
324.817 | 0.05 | 297.037 | 0.5 | 2 | 79289.74 | 10050.6155 | 10045.5902 | 6148.382 | NORMAL
324.817 | 0.05 | 297.037 | 0.5 | 2 | 101352.97 | 10264.3611 | 10259.3726 | 5862.518 | NORMAL
324.817 | 0.05 | 297.037 | 0.5 | 2 | 106868.78 | 10302.8136 | 10297.827 | 5812.677 | NORMAL
324.817 | 0.05 | 297.037 | 0.8 | 1 | 57226.51 | 8293.1125 | 8285.8644 | 5539.3 | NORMAL
324.817 | 0.05 | 297.037 | 0.8 | 1 | 79289.74 | 9073.007 | 9065.4401 | 4819 | NORMAL
324.817 | 0.05 | 297.037 | 0.8 | 1 | 101352.97 | 9300.5276 | 9292.8732 | 4626.945 | NORMAL
324.817 | 0.05 | 297.037 | 0.8 | 1 | 106868.78 | 9341.1196 | 9333.4505 | 4593.034 | NORMAL
324.817 | 0.05 | 297.037 | 0.8 | 2 | 57226.51 | 9932.9426 | 9912.8383 | 7077.579 | NORMAL
324.817 | 0.05 | 297.037 | 0.8 | 2 | 79289.74 | 11649.5604 | 11641.3358 | 6321.894 | NORMAL
324.817 | 0.05 | 297.037 | 0.8 | 2 | 101352.97 | 11959.4959 | 11951.2199 | 5987.763 | NORMAL
324.817 | 0.05 | 297.037 | 0.8 | 2 | 106868.78 | 12016.1489 | 12007.8698 | 5929.707 | NORMAL
324.817 | 0.05 | 297.037 | 1.11 | 1 | 57226.51 | 8841.0023 | 8832.3735 | 5590.43 | NORMAL
324.817 | 0.05 | 297.037 | 1.11 | 1 | 79289.74 | 9711.7819 | 9702.6334 | 4831.226 | NORMAL
324.817 | 0.05 | 297.037 | 1.11 | 1 | 101352.97 | 9983.9097 | 9974.6047 | 4623.825 | NORMAL
324.817 | 0.05 | 297.037 | 1.11 | 1 | 106868.78 | 10033.177 | 10023.8462 | 4586.858 | NORMAL
324.817 | 0.05 | 297.037 | 1.11 | 2 | 57226.51 | 10050.5569 | 10041.2299 | 7055.79 | NORMAL
324.817 | 0.05 | 297.037 | 1.11 | 2 | 79289.74 | 12560.7855 | 12550.3223 | 6426.584 | NORMAL
324.817 | 0.05 | 297.037 | 1.11 | 2 | 101352.97 | 12934.8769 | 12924.2703 | 6063.844 | NORMAL
324.817 | 0.05 | 297.037 | 1.11 | 2 | 106868.78 | 13004.1618 | 12993.5374 | 6000.57 | NORMAL
324.817 | 0.05 | 297.037 | 1.42 | 1 | 57226.51 | 9427.4033 | 9397.3676 | 5713.58 | NORMAL
324.817 | 0.05 | 297.037 | 1.42 | 1 | 79289.74 | 10121.8347 | 10111.5813 | 4843.59 | NORMAL
324.817 | 0.05 | 297.037 | 1.42 | 1 | 101352.97 | 10427.9894 | 10415.9034 | 4624.681 | NORMAL
324.817 | 0.05 | 297.037 | 1.42 | 1 | 106868.78 | 10485.6096 | 10465.5821 | 4584.21 | NORMAL
324.817 | 0.05 | 297.037 | 1.42 | 2 | 57226.51 | 10145.0469 | 10134.7801 | 7043.9 | NORMAL
324.817 | 0.05 | 297.037 | 1.42 | 2 | 79289.74 | 13170.5744 | 13158.4839 | 6492.38 | NORMAL
324.817 | 0.05 | 297.037 | 1.42 | 2 | 101352.97 | 13587.2216 | 13574.9116 | 6114.463 | NORMAL
324.817 | 0.05 | 297.037 | 1.42 | 2 | 106868.78 | 13665.6799 | 13653.3262 | 6048.112 | NORMAL
324.817 | 0.05 | 299.814 | 0.5 | 1 | 57226.51 | 8091.4713 | 8085.1518 | 5889.776 | NORMAL
324.817 | 0.05 | 299.814 | 0.5 | 1 | 79289.74 | 8439.5369 | 8433.182 | 4812.329 | NORMAL
324.817 | 0.05 | 299.814 | 0.5 | 1 | 101352.97 | 8621.6002 | 8615.2375 | 4629.9 | NORMAL
324.817 | 0.05 | 299.814 | 0.5 | 1 | 106868.78 | 8652.1688 | 8645.8008 | 4599.5059 | NORMAL
324.817 | 0.05 | 299.814 | 0.5 | 2 | 57226.51 | 9676.6413 | 9670.2934 | 7097.705 | NORMAL
324.817 | 0.05 | 299.814 | 0.5 | 2 | 79289.74 | 10607.2978 | 10601.0713 | 6212.378 | NORMAL
324.817 | 0.05 | 299.814 | 0.5 | 2 | 101352.97 | 10842.8488 | 10836.6683 | 5901.607 | NORMAL
324.817 | 0.05 | 299.814 | 0.5 | 2 | 106868.78 | 10879.8359 | 10873.6561 | 5855.2141 | NORMAL
324.817 | 0.05 | 299.814 | 0.8 | 1 | 57226.51 | 9164.7714 | 9155.6983 | 5751.74 | NORMAL
324.817 | 0.05 | 299.814 | 0.8 | 1 | 79289.74 | 9696.1313 | 9686.8133 | 4835.251 | NORMAL
324.817 | 0.05 | 299.814 | 0.8 | 1 | 101352.97 | 9953.3705 | 9943.9446 | 4623.877 | NORMAL
324.817 | 0.05 | 299.814 | 0.8 | 1 | 106868.78 | 9998.857 | 9989.4081 | 4586.998 | NORMAL
324.817 | 0.05 | 299.814 | 0.8 | 2 | 57226.51 | 10045.6038 | 10036.1408 | 7057.24 | NORMAL
324.817 | 0.05 | 299.814 | 0.8 | 2 | 79289.74 | 12329.8359 | 12319.7131 | 6401.08 | NORMAL
324.817 | 0.05 | 299.814 | 0.8 | 2 | 101352.97 | 12666.3247 | 12656.141 | 6042.981 | NORMAL
324.817 | 0.05 | 299.814 | 0.8 | 2 | 106868.78 | 12728.136 | 12717.9535 | 5980.838 | NORMAL
324.817 | 0.05 | 299.814 | 1.11 | 1 | 57226.51 | 9631.3599 | 9600.058 | 5680.2 | NORMAL
324.817 | 0.05 | 299.814 | 1.11 | 1 | 79289.74 | 10394.578 | 10365.8785 | 4849.766 | NORMAL
324.817 | 0.05 | 299.814 | 1.11 | 1 | 101352.97 | 10695.7796 | 10681.0087 | 4625.554 | NORMAL
324.817 | 0.05 | 299.814 | 1.11 | 1 | 106868.78 | 10751.1137 | 10739.61 | 4585.093 | NORMAL
324.817 | 0.05 | 299.814 | 1.11 | 2 | 57226.51 | 10186.8406 | 10175.7064 | 7036.36 | NORMAL
324.817 | 0.05 | 299.814 | 1.11 | 2 | 79289.74 | 13322.3916 | 13309.5488 | 6508.605 | NORMAL
324.817 | 0.05 | 299.814 | 1.11 | 2 | 101352.97 | 13722.3623 | 13709.3397 | 6124.986 | NORMAL
324.817 | 0.05 | 299.814 | 1.11 | 2 | 106868.78 | 13798.007 | 13784.9541 | 6057.643 | NORMAL
324.817 | 0.05 | 299.814 | 1.42 | 1 | 57226.51 | 9859.0856 | 9847.2645 | 5633.85 | NORMAL
324.817 | 0.05 | 299.814 | 1.42 | 1 | 79289.74 | 10849.0328 | 10836.3937 | 4860.64 | NORMAL
324.817 | 0.05 | 299.814 | 1.42 | 1 | 101352.97 | 11190.8851 | 11174.3674 | 4622.556 | NORMAL
324.817 | 0.05 | 299.814 | 1.42 | 1 | 106868.78 | 11246.0727 | 11220.949 | 4584.825 | NORMAL
324.817 | 0.05 | 299.814 | 1.42 | 2 | 57226.51 | 10269.4314 | 10210.8032 | 7022.07 | NORMAL
324.817 | 0.05 | 299.814 | 1.42 | 2 | 79289.74 | 13986.3716 | 13971.5321 | 6581.45 | NORMAL
324.817 | 0.05 | 299.814 | 1.42 | 2 | 101352.97 | 14429.748 | 14414.64 | 6179.942 | NORMAL
324.817 | 0.05 | 299.814 | 1.42 | 2 | 106868.78 | 14515.0352 | 14499.8815 | 6109.257 | NORMAL
324.817 | 0.05 | 302.591 | 0.5 | 1 | 57226.51 | 8605.7444 | 8598.0595 | 5826.269 | NORMAL
324.817 | 0.05 | 302.591 | 0.5 | 1 | 79289.74 | 8976.524 | 8968.7952 | 4820.953 | NORMAL
324.817 | 0.05 | 302.591 | 0.5 | 1 | 101352.97 | 9172.3916 | 9164.6501 | 4627.649 | NORMAL
324.817 | 0.05 | 302.591 | 0.5 | 1 | 106868.78 | 9209.1442 | 9201.3993 | 4592.0327 | NORMAL
324.817 | 0.05 | 302.591 | 0.5 | 2 | 57226.51 | 9865.0938 | 9857.3398 | 7084.438 | NORMAL
324.817 | 0.05 | 302.591 | 0.5 | 2 | 79289.74 | 11173.3587 | 11165.7497 | 6277.405 | NORMAL
324.817 | 0.05 | 302.591 | 0.5 | 2 | 101352.97 | 11427.1981 | 11419.6447 | 5946.568 | NORMAL
324.817 | 0.05 | 302.591 | 0.5 | 2 | 106868.78 | 11471.6882 | 11464.1513 | 5890.8199 | NORMAL
324.817 | 0.05 | 302.591 | 0.8 | 1 | 57226.51 | 9616.1782 | 9605.235 | 5678.914 | NORMAL
324.817 | 0.05 | 302.591 | 0.8 | 1 | 79289.74 | 10335.932 | 10315.6529 | 4848.656 | NORMAL
324.817 | 0.05 | 302.591 | 0.8 | 1 | 101352.97 | 10614.0973 | 10602.6341 | 4624.157 | NORMAL
324.817 | 0.05 | 302.591 | 0.8 | 1 | 106868.78 | 10662.8371 | 10651.3532 | 4585.524 | NORMAL
324.817 | 0.05 | 302.591 | 0.8 | 2 | 57226.51 | 10184.2907 | 10173.0473 | 7036.303 | NORMAL
324.817 | 0.05 | 302.591 | 0.8 | 2 | 79289.74 | 13027.6671 | 13015.382 | 6477.032 | NORMAL
324.817 | 0.05 | 302.591 | 0.8 | 2 | 101352.97 | 13386.1079 | 13373.7525 | 6098.929 | NORMAL
324.817 | 0.05 | 302.591 | 0.8 | 2 | 106868.78 | 13453.0774 | 13440.714 | 6032.933 | NORMAL
324.817 | 0.05 | 302.591 | 1.11 | 1 | 57226.51 | 9988.7456 | 9975.9101 | 5600.49 | NORMAL
324.817 | 0.05 | 302.591 | 1.11 | 1 | 79289.74 | 11094.1969 | 11080.4845 | 4866.617 | NORMAL
324.817 | 0.05 | 302.591 | 1.11 | 1 | 101352.97 | 11431.0082 | 11417.051 | 4622.761 | NORMAL
324.817 | 0.05 | 302.591 | 1.11 | 1 | 106868.78 | 11486.5475 | 11472.5454 | 4583.164 | NORMAL
324.817 | 0.05 | 302.591 | 1.11 | 2 | 57226.51 | 10326.7292 | 10313.6246 | 7013.46 | NORMAL
324.817 | 0.05 | 302.591 | 1.11 | 2 | 79289.74 | 14102.4033 | 14086.8342 | 6593.353 | NORMAL
324.817 | 0.05 | 302.591 | 1.11 | 2 | 101352.97 | 14525.2052 | 14509.4308 | 6187.415 | NORMAL
324.817 | 0.05 | 302.591 | 1.11 | 2 | 106868.78 | 14606.9461 | 14591.1267 | 6115.91 | NORMAL
324.817 | 0.05 | 302.591 | 1.42 | 1 | 57226.51 | 10177.0223 | 10162.9983 | 5553.69 | NORMAL
324.817 | 0.05 | 302.591 | 1.42 | 1 | 79289.74 | 11590.3576 | 11574.9772 | 4879.66 | NORMAL
324.817 | 0.05 | 302.591 | 1.42 | 1 | 101352.97 | 11963.8042 | 11942.2933 | 4626.454 | NORMAL
324.817 | 0.05 | 302.591 | 1.42 | 1 | 106868.78 | 12030.5686 | 11996.9191 | 4581.936 | NORMAL
324.817 | 0.05 | 302.591 | 1.42 | 2 | 57226.51 | 10433.7339 | 10383.6937 | 7000.94 | NORMAL
324.817 | 0.05 | 302.591 | 1.42 | 2 | 79289.74 | 14828.4877 | 14810.5007 | 6667.09 | NORMAL
324.817 | 0.05 | 302.591 | 1.42 | 2 | 101352.97 | 15290.4748 | 15272.0192 | 6246.954 | NORMAL
324.817 | 0.05 | 302.591 | 1.42 | 2 | 106868.78 | 15382.6202 | 15364.2533 | 6172.016 | NORMAL
324.817 | 0.05 | 305.368 | 0.5 | 1 | 57226.51 | 9086.694 | 9077.4801 | 5765.217 | NORMAL
324.817 | 0.05 | 305.368 | 0.5 | 1 | 79289.74 | 9518.8159 | 9509.5446 | 4831 | NORMAL
324.817 | 0.05 | 305.368 | 0.5 | 1 | 101352.97 | 9731.7116 | 9722.4178 | 4624.603 | NORMAL
324.817 | 0.05 | 305.368 | 0.5 | 1 | 106868.78 | 9769.4021 | 9760.1016 | 4588.649 | NORMAL
324.817 | 0.05 | 305.368 | 0.5 | 2 | 57226.51 | 10001.4068 | 9992.0955 | 7066.37 | NORMAL
324.817 | 0.05 | 305.368 | 0.5 | 2 | 79289.74 | 11755.2755 | 11746.1181 | 6332.379 | NORMAL
324.817 | 0.05 | 305.368 | 0.5 | 2 | 101352.97 | 12020.6917 | 12011.592 | 5992.614 | NORMAL
324.817 | 0.05 | 305.368 | 0.5 | 2 | 106868.78 | 12069.0211 | 12059.9331 | 5933.6093 | NORMAL
324.817 | 0.05 | 305.368 | 0.8 | 1 | 57226.51 | 9978.7515 | 9965.7691 | 5604.237 | NORMAL
324.817 | 0.05 | 305.368 | 0.8 | 1 | 79289.74 | 10986.1079 | 10962.8283 | 4863.031 | NORMAL
324.817 | 0.05 | 305.368 | 0.8 | 1 | 101352.97 | 11290.6213 | 11276.8468 | 4622.856 | NORMAL
324.817 | 0.05 | 305.368 | 0.8 | 1 | 106868.78 | 11340.592 | 11326.8019 | 4584.075 | NORMAL
324.817 | 0.05 | 305.368 | 0.8 | 2 | 57226.51 | 10311.5768 | 10296.8828 | 7015.134 | NORMAL
324.817 | 0.05 | 305.368 | 0.8 | 2 | 79289.74 | 13740.8558 | 13726.1393 | 6553.179 | NORMAL
324.817 | 0.05 | 305.368 | 0.8 | 2 | 101352.97 | 14118.7866 | 14103.976 | 6155.797 | NORMAL
324.817 | 0.05 | 305.368 | 0.8 | 2 | 106868.78 | 14191.0023 | 14176.1727 | 6086 | NORMAL
324.817 | 0.05 | 305.368 | 1.11 | 1 | 57226.51 | 10259.9062 | 10244.8447 | 5519.98 | NORMAL
324.817 | 0.05 | 305.368 | 1.11 | 1 | 79289.74 | 11805.9496 | 11789.4803 | 4885.967 | NORMAL
324.817 | 0.05 | 305.368 | 1.11 | 1 | 101352.97 | 12169.4314 | 12152.6498 | 4628.181 | NORMAL
324.817 | 0.05 | 305.368 | 1.11 | 1 | 106868.78 | 12234.9062 | 12216.3703 | 4582.85 | NORMAL
324.817 | 0.05 | 305.368 | 1.11 | 2 | 57226.51 | 10469.4314 | 10418.3301 | 6993.21 | NORMAL
324.817 | 0.05 | 305.368 | 1.11 | 2 | 79289.74 | 14903.5756 | 14884.9312 | 6678.336 | NORMAL
324.817 | 0.05 | 305.368 | 1.11 | 2 | 101352.97 | 15343.4642 | 15324.5611 | 6251.158 | NORMAL
324.817 | 0.05 | 305.368 | 1.11 | 2 | 106868.78 | 15431.4478 | 15410.7543 | 6175.579 | NORMAL
324.817 | 0.05 | 305.368 | 1.42 | 1 | 57226.51 | 10397.0399 | 10380.6853 | 5473.88 | NORMAL
324.817 | 0.05 | 305.368 | 1.42 | 1 | 79289.74 | 12345.721 | 12284.0541 | 4900.96 | NORMAL
324.817 | 0.05 | 305.368 | 1.42 | 1 | 101352.97 | 12748.095 | 12720.7885 | 4633.825 | NORMAL
324.817 | 0.05 | 305.368 | 1.42 | 1 | 106868.78 | 12822.1864 | 12779.3859 | 4586.298 | NORMAL
324.817 | 0.05 | 305.368 | 1.42 | 2 | 57226.51 | 11055.7444 | 11038.6412 | 6984.84 | NORMAL
324.817 | 0.05 | 305.368 | 1.42 | 2 | 79289.74 | 15696.4244 | 15653.5104 | 6754.03 | NORMAL
324.817 | 0.05 | 305.368 | 1.42 | 2 | 101352.97 | 16168.2005 | 16146.2926 | 6315.425 | NORMAL
324.817 | 0.05 | 305.368 | 1.42 | 2 | 106868.78 | 16267.1454 | 16245.1685 | 6236.312 | NORMAL
324.817 | 0.15 | 288.706 | 0.5 | 1 | 57226.51 | 5873.2122 | 5870.7689 | 5309.467 | NORMAL
324.817 | 0.15 | 288.706 | 0.5 | 1 | 79289.74 | 6357.2685 | 6354.8018 | 4781.694 | NORMAL
324.817 | 0.15 | 288.706 | 0.5 | 1 | 101352.97 | 6443.1125 | 6440.6448 | 4687.783 | NORMAL
324.817 | 0.15 | 288.706 | 0.5 | 1 | 106868.78 | 6474.5604 | 6472.0936 | 4654.9955 | NORMAL
324.817 | 0.15 | 288.706 | 0.5 | 2 | 57226.51 | 7908.558 | 7884.3816 | 6821.539 | NORMAL
324.817 | 0.15 | 288.706 | 0.5 | 2 | 79289.74 | 8452.8722 | 8441.0636 | 5958.916 | NORMAL
324.817 | 0.15 | 288.706 | 0.5 | 2 | 101352.97 | 8609.9941 | 8589.8123 | 5734.5215 | NORMAL
324.817 | 0.15 | 288.706 | 0.5 | 2 | 106868.78 | 8637.544 | 8635.255 | 5695.6754 | NORMAL
324.817 | 0.15 | 288.706 | 0.8 | 1 | 57226.51 | 6612.0164 | 6596.4385 | 5378.298 | NORMAL
324.817 | 0.15 | 288.706 | 0.8 | 1 | 79289.74 | 7244.871 | 7237.8942 | 4787.951 | NORMAL
324.817 | 0.15 | 288.706 | 0.8 | 1 | 101352.97 | 7394.9004 | 7389.3246 | 4651.36 | NORMAL
324.817 | 0.15 | 288.706 | 0.8 | 1 | 106868.78 | 7417.1747 | 7413.4958 | 4631.07 | NORMAL
324.817 | 0.15 | 288.706 | 0.8 | 2 | 57226.51 | 9167.4385 | 9163.5056 | 7119.048 | NORMAL
324.817 | 0.15 | 288.706 | 0.8 | 2 | 79289.74 | 9689.3611 | 9685.3884 | 6107.849 | NORMAL
324.817 | 0.15 | 288.706 | 0.8 | 2 | 101352.97 | 9922.1571 | 9918.1783 | 5838.377 | NORMAL
324.817 | 0.15 | 288.706 | 0.8 | 2 | 106868.78 | 9965.5041 | 9961.5179 | 5789.691 | NORMAL
324.817 | 0.15 | 288.706 | 1.11 | 1 | 57226.51 | 6999.8242 | 6975.8428 | 5416.59 | NORMAL
324.817 | 0.15 | 288.706 | 1.11 | 1 | 79289.74 | 7722.4795 | 7718.0777 | 4794.689 | NORMAL
324.817 | 0.15 | 288.706 | 1.11 | 1 | 101352.97 | 7909.2321 | 7904.7634 | 4640.056 | NORMAL
324.817 | 0.15 | 288.706 | 1.11 | 1 | 106868.78 | 7939.7128 | 7935.2348 | 4614.889 | NORMAL
324.817 | 0.15 | 288.706 | 1.11 | 2 | 57226.51 | 9508.3529 | 9503.4466 | 7108.72 | NORMAL
324.817 | 0.15 | 288.706 | 1.11 | 2 | 79289.74 | 10389.83 | 10384.7182 | 6186.256 | NORMAL
324.817 | 0.15 | 288.706 | 1.11 | 2 | 101352.97 | 10676.2309 | 10671.0637 | 5890.334 | NORMAL
324.817 | 0.15 | 288.706 | 1.11 | 2 | 106868.78 | 10723.7691 | 10718.5895 | 5842.894 | NORMAL
324.817 | 0.15 | 288.706 | 1.42 | 1 | 57226.51 | 7245.6624 | 7241.0759 | 5439.74 | NORMAL
324.817 | 0.15 | 288.706 | 1.42 | 1 | 79289.74 | 8028.1653 | 8008.1993 | 4799.44 | NORMAL
324.817 | 0.15 | 288.706 | 1.42 | 1 | 101352.97 | 8237.075 | 8232.0504 | 4636.851 | NORMAL
324.817 | 0.15 | 288.706 | 1.42 | 1 | 106868.78 | 8275.7034 | 8270.6635 | 4606.823 | NORMAL
324.817 | 0.15 | 288.706 | 1.42 | 2 | 57226.51 | 9659.9941 | 9654.4493 | 7100.41 | NORMAL
324.817 | 0.15 | 288.706 | 1.42 | 2 | 79289.74 | 10848.857 | 10842.2934 | 6241.73 | NORMAL
324.817 | 0.15 | 288.706 | 1.42 | 2 | 101352.97 | 11174.619 | 11168.5959 | 5926.596 | NORMAL
324.817 | 0.15 | 288.706 | 1.42 | 2 | 106868.78 | 11231.9168 | 11225.874 | 5871.957 | NORMAL
324.817 | 0.15 | 291.483 | 0.5 | 1 | 57226.51 | 6352.8722 | 6349.6831 | 5352.25 | NORMAL
324.817 | 0.15 | 291.483 | 0.5 | 1 | 79289.74 | 6877.1981 | 6873.9796 | 4784.129 | NORMAL
324.817 | 0.15 | 291.483 | 0.5 | 1 | 101352.97 | 6989.0973 | 6985.8683 | 4664.123 | NORMAL
324.817 | 0.15 | 291.483 | 0.5 | 1 | 106868.78 | 7003.7808 | 7000.552 | 4648.1195 | NORMAL
324.817 | 0.15 | 291.483 | 0.5 | 2 | 57226.51 | 8698.857 | 8695.7254 | 7125.041 | NORMAL
324.817 | 0.15 | 291.483 | 0.5 | 2 | 79289.74 | 8975.0879 | 8971.9915 | 6026.887 | NORMAL
324.817 | 0.15 | 291.483 | 0.5 | 2 | 101352.97 | 9152.3447 | 9149.2786 | 5778.539 | NORMAL
324.817 | 0.15 | 291.483 | 0.5 | 2 | 106868.78 | 9185.2286 | 9182.1699 | 5733.4971 | NORMAL
324.817 | 0.15 | 291.483 | 0.8 | 1 | 57226.51 | 7164.1266 | 7158.9971 | 5430.699 | NORMAL
324.817 | 0.15 | 291.483 | 0.8 | 1 | 79289.74 | 7849.1208 | 7844.3799 | 4796.717 | NORMAL
324.817 | 0.15 | 291.483 | 0.8 | 1 | 101352.97 | 8027.6671 | 8021.3091 | 4637.908 | NORMAL
324.817 | 0.15 | 291.483 | 0.8 | 1 | 106868.78 | 8057.4443 | 8052.6501 | 4611.556 | NORMAL
324.817 | 0.15 | 291.483 | 0.8 | 2 | 57226.51 | 9502.0223 | 9496.9482 | 7108.166 | NORMAL
324.817 | 0.15 | 291.483 | 0.8 | 2 | 79289.74 | 10330.2462 | 10325.0707 | 6179.615 | NORMAL
324.817 | 0.15 | 291.483 | 0.8 | 2 | 101352.97 | 10591.0023 | 10585.8127 | 5885.538 | NORMAL
324.817 | 0.15 | 291.483 | 0.8 | 2 | 106868.78 | 10634.9355 | 10629.7457 | 5837.248 | NORMAL
324.817 | 0.15 | 291.483 | 1.11 | 1 | 57226.51 | 7594.8417 | 7589.4494 | 5475.08 | NORMAL
324.817 | 0.15 | 291.483 | 1.11 | 1 | 79289.74 | 8377.0516 | 8371.3217 | 4805.516 | NORMAL
324.817 | 0.15 | 291.483 | 1.11 | 1 | 101352.97 | 8590.0938 | 8584.2697 | 4633.564 | NORMAL
324.817 | 0.15 | 291.483 | 1.11 | 1 | 106868.78 | 8629.6307 | 8623.7971 | 4602.103 | NORMAL
324.817 | 0.15 | 291.483 | 1.11 | 2 | 57226.51 | 9755.4513 | 9749.2176 | 7093.7 | NORMAL
324.817 | 0.15 | 291.483 | 1.11 | 2 | 79289.74 | 11098.2122 | 11091.5977 | 6266.464 | NORMAL
324.817 | 0.15 | 291.483 | 1.11 | 2 | 101352.97 | 11415.5334 | 11408.8325 | 5945.553 | NORMAL
324.817 | 0.15 | 291.483 | 1.11 | 2 | 106868.78 | 11471.8347 | 11465.1237 | 5890.677 | NORMAL
324.817 | 0.15 | 291.483 | 1.42 | 1 | 57226.51 | 7873.388 | 7828.431 | 5499.2 | NORMAL
324.817 | 0.15 | 291.483 | 1.42 | 1 | 79289.74 | 8716.6764 | 8708.2038 | 4811.83 | NORMAL
324.817 | 0.15 | 291.483 | 1.42 | 1 | 101352.97 | 8957.1219 | 8950.5743 | 4629.539 | NORMAL
324.817 | 0.15 | 291.483 | 1.42 | 1 | 106868.78 | 8999.5604 | 8992.9997 | 4597.619 | NORMAL
324.817 | 0.15 | 291.483 | 1.42 | 2 | 57226.51 | 9882.1219 | 9875.155 | 7083.83 | NORMAL
324.817 | 0.15 | 291.483 | 1.42 | 2 | 79289.74 | 11610.1993 | 11602.5366 | 6317.87 | NORMAL
324.817 | 0.15 | 291.483 | 1.42 | 2 | 101352.97 | 11961.8992 | 11954.1 | 5987.831 | NORMAL
324.817 | 0.15 | 291.483 | 1.42 | 2 | 106868.78 | 12025.762 | 12012.0286 | 5930.309 | NORMAL
324.817 | 0.15 | 294.26 | 0.5 | 1 | 57226.51 | 6832.2392 | 6822.8107 | 5400.571 | NORMAL
324.817 | 0.15 | 294.26 | 0.5 | 1 | 79289.74 | 7399.2966 | 7395.1826 | 4790.124 | NORMAL
324.817 | 0.15 | 294.26 | 0.5 | 1 | 101352.97 | 7534.1735 | 7530.0523 | 4647.725 | NORMAL
324.817 | 0.15 | 294.26 | 0.5 | 1 | 106868.78 | 7554.7479 | 7550.6306 | 4625.9207 | NORMAL
324.817 | 0.15 | 294.26 | 0.5 | 2 | 57226.51 | 9091.2075 | 9087.1528 | 7119.474 | NORMAL
324.817 | 0.15 | 294.26 | 0.5 | 2 | 79289.74 | 9514.3025 | 9510.3065 | 6088.112 | NORMAL
324.817 | 0.15 | 294.26 | 0.5 | 2 | 101352.97 | 9709.5252 | 9705.5637 | 5820.082 | NORMAL
324.817 | 0.15 | 294.26 | 0.5 | 2 | 106868.78 | 9743.1125 | 9739.1666 | 5774.5745 | NORMAL
324.817 | 0.15 | 294.26 | 0.8 | 1 | 57226.51 | 7724.8242 | 7719.046 | 5486.183 | NORMAL
324.817 | 0.15 | 294.26 | 0.8 | 1 | 79289.74 | 8460.9906 | 8454.9495 | 4807.138 | NORMAL
324.817 | 0.15 | 294.26 | 0.8 | 1 | 101352.97 | 8662.1336 | 8654.9614 | 4632.435 | NORMAL
324.817 | 0.15 | 294.26 | 0.8 | 1 | 106868.78 | 8701.2896 | 8695.1726 | 4598.801 | NORMAL
324.817 | 0.15 | 294.26 | 0.8 | 2 | 57226.51 | 9757.0047 | 9750.6334 | 7094.158 | NORMAL
324.817 | 0.15 | 294.26 | 0.8 | 2 | 79289.74 | 10984.8183 | 10978.2384 | 6255.407 | NORMAL
324.817 | 0.15 | 294.26 | 0.8 | 2 | 101352.97 | 11274.6483 | 11268.0414 | 5934.577 | NORMAL
324.817 | 0.15 | 294.26 | 0.8 | 2 | 106868.78 | 11325.381 | 11318.767 | 5880.239 | NORMAL
324.817 | 0.15 | 294.26 | 1.11 | 1 | 57226.51 | 8209.7597 | 8202.8963 | 5531.28 | NORMAL
324.817 | 0.15 | 294.26 | 1.11 | 1 | 79289.74 | 9041.4713 | 9034.1658 | 4818.302 | NORMAL
324.817 | 0.15 | 294.26 | 1.11 | 1 | 101352.97 | 9284.6717 | 9277.2533 | 4627.142 | NORMAL
324.817 | 0.15 | 294.26 | 1.11 | 1 | 106868.78 | 9328.1653 | 9320.7308 | 4593.282 | NORMAL
324.817 | 0.15 | 294.26 | 1.11 | 2 | 57226.51 | 9919.3435 | 9890.2203 | 7075.72 | NORMAL
324.817 | 0.15 | 294.26 | 1.11 | 2 | 79289.74 | 11828.6049 | 11820.2066 | 6342.522 | NORMAL
324.817 | 0.15 | 294.26 | 1.11 | 2 | 101352.97 | 12171.102 | 12162.6066 | 6004.161 | NORMAL
324.817 | 0.15 | 294.26 | 1.11 | 2 | 106868.78 | 12233.4994 | 12224.9849 | 5945.23 | NORMAL
324.817 | 0.15 | 294.26 | 1.42 | 1 | 57226.51 | 8524.4138 | 8516.8015 | 5559.59 | NORMAL
324.817 | 0.15 | 294.26 | 1.42 | 1 | 79289.74 | 9416.0023 | 9407.8198 | 4826.72 | NORMAL
324.817 | 0.15 | 294.26 | 1.42 | 1 | 101352.97 | 9689.8007 | 9681.4578 | 4624.904 | NORMAL
324.817 | 0.15 | 294.26 | 1.42 | 1 | 106868.78 | 9738.687 | 9730.3117 | 4589.221 | NORMAL
324.817 | 0.15 | 294.26 | 1.42 | 2 | 57226.51 | 10013.8042 | 9998.393 | 7063.83 | NORMAL
324.817 | 0.15 | 294.26 | 1.42 | 2 | 79289.74 | 12382.7667 | 12373.0586 | 6407.33 | NORMAL
324.817 | 0.15 | 294.26 | 1.42 | 2 | 101352.97 | 12768.5229 | 12758.6528 | 6050.806 | NORMAL
324.817 | 0.15 | 294.26 | 1.42 | 2 | 106868.78 | 12839.7128 | 12829.8134 | 5988.733 | NORMAL
324.817 | 0.15 | 297.037 | 0.5 | 1 | 57226.51 | 7320.3693 | 7315.2816 | 5447.78 | NORMAL
324.817 | 0.15 | 297.037 | 0.5 | 1 | 79289.74 | 7925.9965 | 7920.8446 | 4798.021 | NORMAL
324.817 | 0.15 | 297.037 | 0.5 | 1 | 101352.97 | 8081.4185 | 8076.2545 | 4636.888 | NORMAL
324.817 | 0.15 | 297.037 | 0.5 | 1 | 106868.78 | 8107.0926 | 8101.9284 | 4610.1959 | NORMAL
324.817 | 0.15 | 297.037 | 0.5 | 2 | 57226.51 | 9427.1688 | 9422.0404 | 7110.872 | NORMAL
324.817 | 0.15 | 297.037 | 0.5 | 2 | 79289.74 | 10065.7679 | 10060.735 | 6150.038 | NORMAL
324.817 | 0.15 | 297.037 | 0.5 | 2 | 101352.97 | 10274.9414 | 10269.9478 | 5865.355 | NORMAL
324.817 | 0.15 | 297.037 | 0.5 | 2 | 106868.78 | 10314.4197 | 10309.4378 | 5813.4437 | NORMAL
324.817 | 0.15 | 297.037 | 0.8 | 1 | 57226.51 | 8303.5756 | 8296.3432 | 5540.232 | NORMAL
324.817 | 0.15 | 297.037 | 0.8 | 1 | 79289.74 | 9081.7995 | 9074.2435 | 4819.186 | NORMAL
324.817 | 0.15 | 297.037 | 0.8 | 1 | 101352.97 | 9307.8546 | 9296.9458 | 4626.923 | NORMAL
324.817 | 0.15 | 297.037 | 0.8 | 1 | 106868.78 | 9348.0363 | 9340.3803 | 4592.988 | NORMAL
324.817 | 0.15 | 297.037 | 0.8 | 2 | 57226.51 | 9935.7562 | 9927.9168 | 7077.137 | NORMAL
324.817 | 0.15 | 297.037 | 0.8 | 2 | 79289.74 | 11662.2216 | 11653.9997 | 6323.146 | NORMAL
324.817 | 0.15 | 297.037 | 0.8 | 2 | 101352.97 | 11969.9297 | 11961.6584 | 5988.524 | NORMAL
324.817 | 0.15 | 297.037 | 0.8 | 2 | 106868.78 | 12025.9086 | 12017.6347 | 5930.413 | NORMAL
324.817 | 0.15 | 297.037 | 1.11 | 1 | 57226.51 | 9156.4478 | 9147.6576 | 5755.56 | NORMAL
324.817 | 0.15 | 297.037 | 1.11 | 1 | 79289.74 | 9712.4267 | 9700.7815 | 4835.378 | NORMAL
324.817 | 0.15 | 297.037 | 1.11 | 1 | 101352.97 | 9989.9766 | 9980.6859 | 4623.822 | NORMAL
324.817 | 0.15 | 297.037 | 1.11 | 1 | 106868.78 | 10038.8921 | 10029.576 | 4586.847 | NORMAL
324.817 | 0.15 | 297.037 | 1.11 | 2 | 57226.51 | 10067.7022 | 10058.3896 | 7056.06 | NORMAL
324.817 | 0.15 | 297.037 | 1.11 | 2 | 79289.74 | 12571.3658 | 12557.7887 | 6427.728 | NORMAL
324.817 | 0.15 | 297.037 | 1.11 | 2 | 101352.97 | 12943.8159 | 12933.2279 | 6064.534 | NORMAL
324.817 | 0.15 | 297.037 | 1.11 | 2 | 106868.78 | 13012.5146 | 13001.8964 | 6001.182 | NORMAL
324.817 | 0.15 | 297.037 | 1.42 | 1 | 57226.51 | 9432.7667 | 9423.0415 | 5712.7 | NORMAL
324.817 | 0.15 | 297.037 | 1.42 | 1 | 79289.74 | 10128.0481 | 10117.8187 | 4843.72 | NORMAL
324.817 | 0.15 | 297.037 | 1.42 | 1 | 101352.97 | 10433.2063 | 10422.7523 | 4624.673 | NORMAL
324.817 | 0.15 | 297.037 | 1.42 | 1 | 106868.78 | 10490.592 | 10480.1014 | 4584.17 | NORMAL
324.817 | 0.15 | 297.037 | 1.42 | 2 | 57226.51 | 10145.9848 | 10135.7576 | 7043.7 | NORMAL
324.817 | 0.15 | 297.037 | 1.42 | 2 | 79289.74 | 13179.8359 | 13167.75 | 6493.37 | NORMAL
324.817 | 0.15 | 297.037 | 1.42 | 2 | 101352.97 | 13594.959 | 13582.6691 | 6115.079 | NORMAL
324.817 | 0.15 | 297.037 | 1.42 | 2 | 106868.78 | 13672.9484 | 13660.6154 | 6048.645 | NORMAL
324.817 | 0.15 | 299.814 | 0.5 | 1 | 57226.51 | 8110.2286 | 8103.9107 | 5887.655 | NORMAL
324.817 | 0.15 | 299.814 | 0.5 | 1 | 79289.74 | 8453.2825 | 8446.9257 | 4812.526 | NORMAL
324.817 | 0.15 | 299.814 | 0.5 | 1 | 101352.97 | 8633.0012 | 8626.6387 | 4629.972 | NORMAL
324.817 | 0.15 | 299.814 | 0.5 | 1 | 106868.78 | 8663.2181 | 8656.8506 | 4599.2346 | NORMAL
324.817 | 0.15 | 299.814 | 0.5 | 2 | 57226.51 | 9683.8804 | 9677.5181 | 7098.232 | NORMAL
324.817 | 0.15 | 299.814 | 0.5 | 2 | 79289.74 | 10626.2603 | 10620.0226 | 6214.38 | NORMAL
324.817 | 0.15 | 299.814 | 0.5 | 2 | 101352.97 | 10858.558 | 10852.3687 | 5902.582 | NORMAL
324.817 | 0.15 | 299.814 | 0.5 | 2 | 106868.78 | 10894.5487 | 10888.3605 | 5856.1251 | NORMAL
324.817 | 0.15 | 299.814 | 0.8 | 1 | 57226.51 | 9176.3775 | 9154.7121 | 5750.063 | NORMAL
324.817 | 0.15 | 299.814 | 0.8 | 1 | 79289.74 | 9705.6565 | 9696.3585 | 4837.441 | NORMAL
324.817 | 0.15 | 299.814 | 0.8 | 1 | 101352.97 | 9962.7784 | 9953.3636 | 4623.875 | NORMAL
324.817 | 0.15 | 299.814 | 0.8 | 1 | 106868.78 | 10007.7374 | 9998.3101 | 4586.962 | NORMAL
324.817 | 0.15 | 299.814 | 0.8 | 2 | 57226.51 | 10048.3587 | 10038.9233 | 7056.667 | NORMAL
324.817 | 0.15 | 299.814 | 0.8 | 2 | 79289.74 | 12345.5744 | 12335.4634 | 6403.027 | NORMAL
324.817 | 0.15 | 299.814 | 0.8 | 2 | 101352.97 | 12679.4842 | 12669.3152 | 6044.052 | NORMAL
324.817 | 0.15 | 299.814 | 0.8 | 2 | 106868.78 | 12740.5627 | 12730.383 | 5981.745 | NORMAL
324.817 | 0.15 | 299.814 | 1.11 | 1 | 57226.51 | 9638.6284 | 9627.9199 | 5678.85 | NORMAL
324.817 | 0.15 | 299.814 | 1.11 | 1 | 79289.74 | 10404.0152 | 10392.7685 | 4849.958 | NORMAL
324.817 | 0.15 | 299.814 | 1.11 | 1 | 101352.97 | 10703.7515 | 10692.3092 | 4625.511 | NORMAL
324.817 | 0.15 | 299.814 | 1.11 | 1 | 106868.78 | 10758.558 | 10747.0786 | 4585.08 | NORMAL
324.817 | 0.15 | 299.814 | 1.11 | 2 | 57226.51 | 10188.8921 | 10177.8066 | 7036.05 | NORMAL
324.817 | 0.15 | 299.814 | 1.11 | 2 | 79289.74 | 13335.8148 | 13322.9857 | 6510.088 | NORMAL
324.817 | 0.15 | 299.814 | 1.11 | 2 | 101352.97 | 13733.6753 | 13720.6832 | 6125.867 | NORMAL
324.817 | 0.15 | 299.814 | 1.11 | 2 | 106868.78 | 13808.6753 | 13795.6399 | 6058.424 | NORMAL
324.817 | 0.15 | 299.814 | 1.42 | 1 | 57226.51 | 9863.9801 | 9852.2123 | 5632.75 | NORMAL
324.817 | 0.15 | 299.814 | 1.42 | 1 | 79289.74 | 10857.034 | 10844.429 | 4860.84 | NORMAL
324.817 | 0.15 | 299.814 | 1.42 | 1 | 101352.97 | 11197.8605 | 11184.9718 | 4622.45 | NORMAL
324.817 | 0.15 | 299.814 | 1.42 | 1 | 106868.78 | 11252.6084 | 11239.6792 | 4584.734 | NORMAL
324.817 | 0.15 | 299.814 | 1.42 | 2 | 57226.51 | 10271.2778 | 10259.1783 | 7021.77 | NORMAL
324.817 | 0.15 | 299.814 | 1.42 | 2 | 79289.74 | 13998.3587 | 13983.5625 | 6582.69 | NORMAL
324.817 | 0.15 | 299.814 | 1.42 | 2 | 101352.97 | 14439.6835 | 14424.6084 | 6180.73 | NORMAL
324.817 | 0.15 | 299.814 | 1.42 | 2 | 106868.78 | 14524.3845 | 14507.1876 | 6109.941 | NORMAL
324.817 | 0.15 | 302.591 | 0.5 | 1 | 57226.51 | 8627.5791 | 8619.9006 | 5823.572 | NORMAL
324.817 | 0.15 | 302.591 | 0.5 | 1 | 79289.74 | 8994.4021 | 8986.6759 | 4821.244 | NORMAL
324.817 | 0.15 | 302.591 | 0.5 | 1 | 101352.97 | 9187.0457 | 9179.301 | 4627.597 | NORMAL
324.817 | 0.15 | 302.591 | 0.5 | 1 | 106868.78 | 9220.3986 | 9212.6535 | 4594.3124 | NORMAL
324.817 | 0.15 | 302.591 | 0.5 | 2 | 57226.51 | 9873.6225 | 9865.8717 | 7083.665 | NORMAL
324.817 | 0.15 | 302.591 | 0.5 | 2 | 79289.74 | 11197.626 | 11190.0116 | 6279.263 | NORMAL
324.817 | 0.15 | 302.591 | 0.5 | 2 | 101352.97 | 11446.7761 | 11439.2098 | 5948.179 | NORMAL
324.817 | 0.15 | 302.591 | 0.5 | 2 | 106868.78 | 11492.8781 | 11485.3273 | 5888.0495 | NORMAL
324.817 | 0.15 | 302.591 | 0.8 | 1 | 57226.51 | 9628.1946 | 9595.2854 | 5676.816 | NORMAL
324.817 | 0.15 | 302.591 | 0.8 | 1 | 79289.74 | 10347.3036 | 10336.0044 | 4851.724 | NORMAL
324.817 | 0.15 | 302.591 | 0.8 | 1 | 101352.97 | 10626.3189 | 10614.8743 | 4624.1 | NORMAL
324.817 | 0.15 | 302.591 | 0.8 | 1 | 106868.78 | 10674.2087 | 10662.7339 | 4585.504 | NORMAL
324.817 | 0.15 | 302.591 | 0.8 | 2 | 57226.51 | 10188.1887 | 10176.9817 | 7035.654 | NORMAL
324.817 | 0.15 | 302.591 | 0.8 | 2 | 79289.74 | 13048.1536 | 13034.8314 | 6479.195 | NORMAL
324.817 | 0.15 | 302.591 | 0.8 | 2 | 101352.97 | 13402.5205 | 13390.1768 | 6100.296 | NORMAL
324.817 | 0.15 | 302.591 | 0.8 | 2 | 106868.78 | 13468.8159 | 13456.4516 | 6034.077 | NORMAL
324.817 | 0.15 | 302.591 | 1.11 | 1 | 57226.51 | 9995.4279 | 9982.6537 | 5598.81 | NORMAL
324.817 | 0.15 | 302.591 | 1.11 | 1 | 79289.74 | 11106.3013 | 11092.6294 | 4866.925 | NORMAL
324.817 | 0.15 | 302.591 | 1.11 | 1 | 101352.97 | 11441.0903 | 11427.155 | 4622.826 | NORMAL
324.817 | 0.15 | 302.591 | 1.11 | 1 | 106868.78 | 11496.1899 | 11482.2221 | 4583.106 | NORMAL
324.817 | 0.15 | 302.591 | 1.11 | 2 | 57226.51 | 10329.8945 | 10303.1297 | 7012.99 | NORMAL
324.817 | 0.15 | 302.591 | 1.11 | 2 | 79289.74 | 14119.7831 | 14104.2514 | 6595.282 | NORMAL
324.817 | 0.15 | 302.591 | 1.11 | 2 | 101352.97 | 14539.5956 | 14523.8346 | 6188.545 | NORMAL
324.817 | 0.15 | 302.591 | 1.11 | 2 | 106868.78 | 14620.5158 | 14604.7257 | 6116.906 | NORMAL
324.817 | 0.15 | 302.591 | 1.42 | 1 | 57226.51 | 10181.3892 | 10119.2522 | 5552.35 | NORMAL
324.817 | 0.15 | 302.591 | 1.42 | 1 | 79289.74 | 11600.6448 | 11567.6526 | 4879.96 | NORMAL
324.817 | 0.15 | 302.591 | 1.42 | 1 | 101352.97 | 11972.4795 | 11956.7955 | 4626.538 | NORMAL
324.817 | 0.15 | 302.591 | 1.42 | 1 | 106868.78 | 12038.7456 | 12022.9869 | 4581.975 | NORMAL
324.817 | 0.15 | 302.591 | 1.42 | 2 | 57226.51 | 10435.9613 | 10421.7475 | 7000.58 | NORMAL
324.817 | 0.15 | 302.591 | 1.42 | 2 | 79289.74 | 14843.9625 | 14826.031 | 6668.64 | NORMAL
324.817 | 0.15 | 302.591 | 1.42 | 2 | 101352.97 | 15303.1067 | 15278.1473 | 6247.943 | NORMAL
324.817 | 0.15 | 302.591 | 1.42 | 2 | 106868.78 | 15394.4607 | 15376.1413 | 6172.893 | NORMAL
324.817 | 0.15 | 305.368 | 0.5 | 1 | 57226.51 | 9111.1079 | 9101.9056 | 5761.728 | NORMAL
324.817 | 0.15 | 305.368 | 0.5 | 1 | 79289.74 | 9538.7163 | 9529.4447 | 4833.875 | NORMAL
324.817 | 0.15 | 305.368 | 0.5 | 1 | 101352.97 | 9750.2931 | 9741.0011 | 4624.533 | NORMAL
324.817 | 0.15 | 305.368 | 0.5 | 1 | 106868.78 | 9786.8406 | 9777.5431 | 4588.566 | NORMAL
324.817 | 0.15 | 305.368 | 0.5 | 2 | 57226.51 | 10010.0528 | 10000.7434 | 7065.268 | NORMAL
324.817 | 0.15 | 305.368 | 0.5 | 2 | 79289.74 | 11783.7632 | 11774.5954 | 6337.83 | NORMAL
324.817 | 0.15 | 305.368 | 0.5 | 2 | 101352.97 | 12045.1934 | 12036.0873 | 5994.589 | NORMAL
324.817 | 0.15 | 305.368 | 0.5 | 2 | 106868.78 | 12092.0281 | 12082.9349 | 5935.2996 | NORMAL
324.817 | 0.15 | 305.368 | 0.8 | 1 | 57226.51 | 9989.83 | 9970.9592 | 5601.568 | NORMAL
324.817 | 0.15 | 305.368 | 0.8 | 1 | 79289.74 | 11002.9601 | 10983.3969 | 4864.562 | NORMAL
324.817 | 0.15 | 305.368 | 0.8 | 1 | 101352.97 | 11305.8617 | 11292.1137 | 4622.772 | NORMAL
324.817 | 0.15 | 305.368 | 0.8 | 1 | 106868.78 | 11355.2755 | 11341.5016 | 4583.996 | NORMAL
324.817 | 0.15 | 305.368 | 0.8 | 2 | 57226.51 | 10316.8816 | 10278.9258 | 7014.359 | NORMAL
324.817 | 0.15 | 305.368 | 0.8 | 2 | 79289.74 | 13766.442 | 13751.7394 | 6555.87 | NORMAL
324.817 | 0.15 | 305.368 | 0.8 | 2 | 101352.97 | 14139.8886 | 14125.0983 | 6157.459 | NORMAL
324.817 | 0.15 | 305.368 | 0.8 | 2 | 106868.78 | 14210.9027 | 14196.0949 | 6087.445 | NORMAL
324.817 | 0.15 | 305.368 | 1.11 | 1 | 57226.51 | 10265.7972 | 10250.8296 | 5517.5 | NORMAL
324.817 | 0.15 | 305.368 | 1.11 | 1 | 79289.74 | 11821.9226 | 11805.5138 | 4886.046 | NORMAL
324.817 | 0.15 | 305.368 | 1.11 | 1 | 101352.97 | 12182.3271 | 12165.6007 | 4628.284 | NORMAL
324.817 | 0.15 | 305.368 | 1.11 | 1 | 106868.78 | 12247.0985 | 12221.8695 | 4582.904 | NORMAL
324.817 | 0.15 | 305.368 | 1.11 | 2 | 57226.51 | 10473.2415 | 10458.0658 | 6992.7 | NORMAL
324.817 | 0.15 | 305.368 | 1.11 | 2 | 79289.74 | 14925.8499 | 14907.2523 | 6680.571 | NORMAL
324.817 | 0.15 | 305.368 | 1.11 | 2 | 101352.97 | 15361.6647 | 15342.8006 | 6252.609 | NORMAL
324.817 | 0.15 | 305.368 | 1.11 | 2 | 106868.78 | 15448.095 | 15429.1865 | 6176.83 | NORMAL
324.817 | 0.15 | 305.368 | 1.42 | 1 | 57226.51 | 10400.381 | 10344.8638 | 5472.29 | NORMAL
324.817 | 0.15 | 305.368 | 1.42 | 1 | 79289.74 | 12358.939 | 12340.5119 | 4901.34 | NORMAL
324.817 | 0.15 | 305.368 | 1.42 | 1 | 101352.97 | 12759.2614 | 12740.4032 | 4633.948 | NORMAL
324.817 | 0.15 | 305.368 | 1.42 | 1 | 106868.78 | 12832.6788 | 12813.7506 | 4586.373 | NORMAL
324.817 | 0.15 | 305.368 | 1.42 | 2 | 57226.51 | 11059.5838 | 11042.5963 | 6984.44 | NORMAL
324.817 | 0.15 | 305.368 | 1.42 | 2 | 79289.74 | 15716.1782 | 15694.7256 | 6756.52 | NORMAL
324.817 | 0.15 | 305.368 | 1.42 | 2 | 101352.97 | 16184.1735 | 16162.3249 | 6316.696 | NORMAL
324.817 | 0.15 | 305.368 | 1.42 | 2 | 106868.78 | 16282.1805 | 16260.2484 | 6237.446 | NORMAL
324.817 | 0.25 | 288.706 | 0.5 | 1 | 57226.51 | 5879.3962 | 5876.9563 | 5309.839 | NORMAL
324.817 | 0.25 | 288.706 | 0.5 | 1 | 79289.74 | 6362.3095 | 6359.8409 | 4781.737 | NORMAL
324.817 | 0.25 | 288.706 | 0.5 | 1 | 101352.97 | 6447.245 | 6444.7757 | 4687.637 | NORMAL
324.817 | 0.25 | 288.706 | 0.5 | 1 | 106868.78 | 6478.8687 | 6476.4002 | 4654.5417 | NORMAL
324.817 | 0.25 | 288.706 | 0.5 | 2 | 57226.51 | 7914.8007 | 7912.3946 | 6822.87 | NORMAL
324.817 | 0.25 | 288.706 | 0.5 | 2 | 79289.74 | 8459.3787 | 8457.0354 | 5959.649 | NORMAL
324.817 | 0.25 | 288.706 | 0.5 | 2 | 101352.97 | 8576.7585 | 8574.4685 | 5731.7978 | NORMAL
324.817 | 0.25 | 288.706 | 0.5 | 2 | 106868.78 | 8642.9367 | 8640.6204 | 5696.1211 | NORMAL
324.817 | 0.25 | 288.706 | 0.8 | 1 | 57226.51 | 6616.5299 | 6601.9801 | 5378.712 | NORMAL
324.817 | 0.25 | 288.706 | 0.8 | 1 | 79289.74 | 7248.7984 | 7245.1667 | 4788.002 | NORMAL
324.817 | 0.25 | 288.706 | 0.8 | 1 | 101352.97 | 7398.1829 | 7394.5134 | 4651.303 | NORMAL
324.817 | 0.25 | 288.706 | 0.8 | 1 | 106868.78 | 7420.3107 | 7416.6376 | 4630.996 | NORMAL
324.817 | 0.25 | 288.706 | 0.8 | 2 | 57226.51 | 9172.3916 | 9168.4658 | 7118.948 | NORMAL
324.817 | 0.25 | 288.706 | 0.8 | 2 | 79289.74 | 9694.9004 | 9690.9351 | 6108.456 | NORMAL
324.817 | 0.25 | 288.706 | 0.8 | 2 | 101352.97 | 9926.905 | 9922.9244 | 5838.731 | NORMAL
324.817 | 0.25 | 288.706 | 0.8 | 2 | 106868.78 | 9970.0469 | 9966.0589 | 5790.018 | NORMAL
324.817 | 0.25 | 288.706 | 1.11 | 1 | 57226.51 | 7003.4291 | 6995.186 | 5416.93 | NORMAL
324.817 | 0.25 | 288.706 | 1.11 | 1 | 79289.74 | 7725.6448 | 7721.2489 | 4794.739 | NORMAL
324.817 | 0.25 | 288.706 | 1.11 | 1 | 101352.97 | 7911.8992 | 7907.4369 | 4640.019 | NORMAL
324.817 | 0.25 | 288.706 | 1.11 | 1 | 106868.78 | 7942.2919 | 7937.8204 | 4614.85 | NORMAL
324.817 | 0.25 | 288.706 | 1.11 | 2 | 57226.51 | 9510.932 | 9506.0244 | 7108.6 | NORMAL
324.817 | 0.25 | 288.706 | 1.11 | 2 | 79289.74 | 10394.578 | 10386.7404 | 6186.809 | NORMAL
324.817 | 0.25 | 288.706 | 1.11 | 2 | 101352.97 | 10679.5721 | 10674.4139 | 5891.167 | NORMAL
324.817 | 0.25 | 288.706 | 1.11 | 2 | 106868.78 | 10727.6377 | 10722.467 | 5843.155 | NORMAL
324.817 | 0.25 | 288.706 | 1.42 | 1 | 57226.51 | 7248.5932 | 7244.0193 | 5440.02 | NORMAL
324.817 | 0.25 | 288.706 | 1.42 | 1 | 79289.74 | 8031.0375 | 8026.1145 | 4799.47 | NORMAL
324.817 | 0.25 | 288.706 | 1.42 | 1 | 101352.97 | 8239.3318 | 8234.314 | 4636.828 | NORMAL
324.817 | 0.25 | 288.706 | 1.42 | 1 | 106868.78 | 8277.8722 | 8266.3411 | 4606.788 | NORMAL
324.817 | 0.25 | 288.706 | 1.42 | 2 | 57226.51 | 9661.4889 | 9647.499 | 7100.3 | NORMAL
324.817 | 0.25 | 288.706 | 1.42 | 2 | 79289.74 | 10854.8652 | 10848.9384 | 6239.58 | NORMAL
324.817 | 0.25 | 288.706 | 1.42 | 2 | 101352.97 | 11178.136 | 11172.111 | 5926.825 | NORMAL
324.817 | 0.25 | 288.706 | 1.42 | 2 | 106868.78 | 11235.4044 | 11229.3598 | 5872.075 | NORMAL
324.817 | 0.25 | 291.483 | 0.5 | 1 | 57226.51 | 6360.6389 | 6357.4522 | 5352.998 | NORMAL
324.817 | 0.25 | 291.483 | 0.5 | 1 | 79289.74 | 6883.9097 | 6880.6881 | 4784.111 | NORMAL
324.817 | 0.25 | 291.483 | 0.5 | 1 | 101352.97 | 6995.0176 | 6991.7929 | 4663.538 | NORMAL
324.817 | 0.25 | 291.483 | 0.5 | 1 | 106868.78 | 7009.1735 | 7005.9423 | 4647.961 | NORMAL
324.817 | 0.25 | 291.483 | 0.5 | 2 | 57226.51 | 8714.449 | 8711.3118 | 7125.624 | NORMAL
324.817 | 0.25 | 291.483 | 0.5 | 2 | 79289.74 | 8931.1547 | 8928.1003 | 6021.918 | NORMAL
324.817 | 0.25 | 291.483 | 0.5 | 2 | 101352.97 | 9115.7386 | 9112.703 | 5775.632 | NORMAL
324.817 | 0.25 | 291.483 | 0.5 | 2 | 106868.78 | 9151.7878 | 9148.7586 | 5731.146 | NORMAL
324.817 | 0.25 | 291.483 | 0.8 | 1 | 57226.51 | 7170.0762 | 7164.5552 | 5431.272 | NORMAL
324.817 | 0.25 | 291.483 | 0.8 | 1 | 79289.74 | 7854.3083 | 7849.5722 | 4796.805 | NORMAL
324.817 | 0.25 | 291.483 | 0.8 | 1 | 101352.97 | 8032.1805 | 8027.3934 | 4637.869 | NORMAL
324.817 | 0.25 | 291.483 | 0.8 | 1 | 106868.78 | 8061.5768 | 8056.7801 | 4611.483 | NORMAL
324.817 | 0.25 | 291.483 | 0.8 | 2 | 57226.51 | 9506.4771 | 9501.4102 | 7107.988 | NORMAL
324.817 | 0.25 | 291.483 | 0.8 | 2 | 79289.74 | 10337.7198 | 10332.551 | 6180.405 | NORMAL
324.817 | 0.25 | 291.483 | 0.8 | 2 | 101352.97 | 10597.3623 | 10592.1695 | 5885.861 | NORMAL
324.817 | 0.25 | 291.483 | 0.8 | 2 | 106868.78 | 10640.9144 | 10635.7216 | 5837.646 | NORMAL
324.817 | 0.25 | 291.483 | 1.11 | 1 | 57226.51 | 7599.7069 | 7571.1472 | 5475.52 | NORMAL
324.817 | 0.25 | 291.483 | 1.11 | 1 | 79289.74 | 8381.272 | 8375.5476 | 4805.592 | NORMAL
324.817 | 0.25 | 291.483 | 1.11 | 1 | 101352.97 | 8593.6401 | 8587.8222 | 4633.54 | NORMAL
324.817 | 0.25 | 291.483 | 1.11 | 1 | 106868.78 | 8633.0305 | 8626.2449 | 4602.071 | NORMAL
324.817 | 0.25 | 291.483 | 1.11 | 2 | 57226.51 | 9757.3857 | 9751.18 | 7093.57 | NORMAL
324.817 | 0.25 | 291.483 | 1.11 | 2 | 79289.74 | 11103.4877 | 11096.87 | 6267.537 | NORMAL
324.817 | 0.25 | 291.483 | 1.11 | 2 | 101352.97 | 11420.8089 | 11414.1163 | 5945.951 | NORMAL
324.817 | 0.25 | 291.483 | 1.11 | 2 | 106868.78 | 11476.8757 | 11470.1732 | 5891.046 | NORMAL
324.817 | 0.25 | 291.483 | 1.42 | 1 | 57226.51 | 7877.6084 | 7871.653 | 5499.39 | NORMAL
324.817 | 0.25 | 291.483 | 1.42 | 1 | 79289.74 | 8720.2521 | 8713.8427 | 4811.9 | NORMAL
324.817 | 0.25 | 291.483 | 1.42 | 1 | 101352.97 | 8960.1114 | 8953.5794 | 4629.523 | NORMAL
324.817 | 0.25 | 291.483 | 1.42 | 1 | 106868.78 | 9002.6964 | 8990.5697 | 4597.415 | NORMAL
324.817 | 0.25 | 291.483 | 1.42 | 2 | 57226.51 | 9883.8511 | 9869.3713 | 7083.6 | NORMAL
324.817 | 0.25 | 291.483 | 1.42 | 2 | 79289.74 | 11615.6213 | 11604.4587 | 6318.48 | NORMAL
324.817 | 0.25 | 291.483 | 1.42 | 2 | 101352.97 | 11966.4713 | 11955.9886 | 5988.188 | NORMAL
324.817 | 0.25 | 291.483 | 1.42 | 2 | 106868.78 | 12030.1583 | 12022.3507 | 5930.637 | NORMAL
324.817 | 0.25 | 294.26 | 0.5 | 1 | 57226.51 | 6842.4385 | 6838.374 | 5401.547 | NORMAL
324.817 | 0.25 | 294.26 | 0.5 | 1 | 79289.74 | 7407.8546 | 7403.7433 | 4790.242 | NORMAL
324.817 | 0.25 | 294.26 | 0.5 | 1 | 101352.97 | 7541.0903 | 7536.9653 | 4647.653 | NORMAL
324.817 | 0.25 | 294.26 | 0.5 | 1 | 106868.78 | 7561.8113 | 7557.6901 | 4625.4916 | NORMAL
324.817 | 0.25 | 294.26 | 0.5 | 2 | 57226.51 | 9116.1489 | 9112.0922 | 7120.215 | NORMAL
324.817 | 0.25 | 294.26 | 0.5 | 2 | 79289.74 | 9458.5873 | 9454.6526 | 6081.69 | NORMAL
324.817 | 0.25 | 294.26 | 0.5 | 2 | 101352.97 | 9690.8851 | 9686.9215 | 5818.674 | NORMAL
324.817 | 0.25 | 294.26 | 0.5 | 2 | 106868.78 | 9704.0152 | 9700.0851 | 5771.7119 | NORMAL
324.817 | 0.25 | 294.26 | 0.8 | 1 | 57226.51 | 7732.7667 | 7726.9981 | 5486.886 | NORMAL
324.817 | 0.25 | 294.26 | 0.8 | 1 | 79289.74 | 8467.7608 | 8461.7233 | 4807.268 | NORMAL
324.817 | 0.25 | 294.26 | 0.8 | 1 | 101352.97 | 8667.7608 | 8661.6587 | 4632.407 | NORMAL
324.817 | 0.25 | 294.26 | 0.8 | 1 | 106868.78 | 8706.7409 | 8700.6288 | 4598.703 | NORMAL
324.817 | 0.25 | 294.26 | 0.8 | 2 | 57226.51 | 9760.7855 | 9754.4214 | 7093.869 | NORMAL
324.817 | 0.25 | 294.26 | 0.8 | 2 | 79289.74 | 10994.5193 | 10987.9446 | 6256.471 | NORMAL
324.817 | 0.25 | 294.26 | 0.8 | 2 | 101352.97 | 11282.7081 | 11276.0964 | 5935.211 | NORMAL
324.817 | 0.25 | 294.26 | 0.8 | 2 | 106868.78 | 11336.313 | 11329.6926 | 5876.728 | NORMAL
324.817 | 0.25 | 294.26 | 1.11 | 1 | 57226.51 | 8216.2954 | 8209.443 | 5531.82 | NORMAL
324.817 | 0.25 | 294.26 | 1.11 | 1 | 79289.74 | 9047.0106 | 9039.7277 | 4818.467 | NORMAL
324.817 | 0.25 | 294.26 | 1.11 | 1 | 101352.97 | 9289.449 | 9278.9612 | 4627.129 | NORMAL
324.817 | 0.25 | 294.26 | 1.11 | 1 | 106868.78 | 9332.6788 | 9325.25 | 4593.239 | NORMAL
324.817 | 0.25 | 294.26 | 1.11 | 2 | 57226.51 | 9920.9848 | 9913.3158 | 7075.5 | NORMAL
324.817 | 0.25 | 294.26 | 1.11 | 2 | 79289.74 | 11836.782 | 11828.4015 | 6343.432 | NORMAL
324.817 | 0.25 | 294.26 | 1.11 | 2 | 101352.97 | 12177.9601 | 12169.4599 | 6004.731 | NORMAL
324.817 | 0.25 | 294.26 | 1.11 | 2 | 106868.78 | 12240.0938 | 12231.5869 | 5945.709 | NORMAL
324.817 | 0.25 | 294.26 | 1.42 | 1 | 57226.51 | 8530.0117 | 8522.42 | 5559.94 | NORMAL
324.817 | 0.25 | 294.26 | 1.42 | 1 | 79289.74 | 9420.6331 | 9412.4748 | 4826.92 | NORMAL
324.817 | 0.25 | 294.26 | 1.42 | 1 | 101352.97 | 9693.8159 | 9685.4793 | 4624.859 | NORMAL
324.817 | 0.25 | 294.26 | 1.42 | 1 | 106868.78 | 9742.7608 | 9729.0918 | 4589.027 | NORMAL
324.817 | 0.25 | 294.26 | 1.42 | 2 | 57226.51 | 10014.9179 | 9992.7549 | 7063.62 | NORMAL
324.817 | 0.25 | 294.26 | 1.42 | 2 | 79289.74 | 12389.8593 | 12380.1704 | 6408.12 | NORMAL
324.817 | 0.25 | 294.26 | 1.42 | 2 | 101352.97 | 12774.5018 | 12764.6398 | 6051.274 | NORMAL
324.817 | 0.25 | 294.26 | 1.42 | 2 | 106868.78 | 12845.4279 | 12835.5369 | 5989.15 | NORMAL
324.817 | 0.25 | 297.037 | 0.5 | 1 | 57226.51 | 7333.558 | 7325.0951 | 5448.956 | NORMAL
324.817 | 0.25 | 297.037 | 0.5 | 1 | 79289.74 | 7937.0457 | 7931.8866 | 4798.199 | NORMAL
324.817 | 0.25 | 297.037 | 0.5 | 1 | 101352.97 | 8090.68 | 8085.5181 | 4636.652 | NORMAL
324.817 | 0.25 | 297.037 | 0.5 | 1 | 106868.78 | 8115.7679 | 8110.6062 | 4610.0984 | NORMAL
324.817 | 0.25 | 297.037 | 0.5 | 2 | 57226.51 | 9382.0926 | 9377.1107 | 7112.059 | NORMAL
324.817 | 0.25 | 297.037 | 0.5 | 2 | 79289.74 | 10078.3705 | 10066.1152 | 6150.052 | NORMAL
324.817 | 0.25 | 297.037 | 0.5 | 2 | 101352.97 | 10336.1665 | 10285.9637 | 5869.901 | NORMAL
324.817 | 0.25 | 297.037 | 0.5 | 2 | 106868.78 | 10330.5393 | 10325.5909 | 5814.3689 | NORMAL
324.817 | 0.25 | 297.037 | 0.8 | 1 | 57226.51 | 8314.068 | 8306.8514 | 5541.219 | NORMAL
324.817 | 0.25 | 297.037 | 0.8 | 1 | 79289.74 | 9090.592 | 9083.0468 | 4819.361 | NORMAL
324.817 | 0.25 | 297.037 | 0.8 | 1 | 101352.97 | 9315.1817 | 9307.5433 | 4626.917 | NORMAL
324.817 | 0.25 | 297.037 | 0.8 | 1 | 106868.78 | 9355.0703 | 9347.4179 | 4592.938 | NORMAL
324.817 | 0.25 | 297.037 | 0.8 | 2 | 57226.51 | 9940.5041 | 9932.6909 | 7076.722 | NORMAL
324.817 | 0.25 | 297.037 | 0.8 | 2 | 79289.74 | 11674.4138 | 11666.1951 | 6324.327 | NORMAL
324.817 | 0.25 | 297.037 | 0.8 | 2 | 101352.97 | 11980.3048 | 11972.0384 | 5989.331 | NORMAL
324.817 | 0.25 | 297.037 | 0.8 | 2 | 106868.78 | 12035.8734 | 12027.6047 | 5931.146 | NORMAL
324.817 | 0.25 | 297.037 | 1.11 | 1 | 57226.51 | 9163.7456 | 9154.9851 | 5754.49 | NORMAL
324.817 | 0.25 | 297.037 | 1.11 | 1 | 79289.74 | 9720.3693 | 9711.2613 | 4835.389 | NORMAL
324.817 | 0.25 | 297.037 | 1.11 | 1 | 101352.97 | 9996.102 | 9986.8256 | 4623.78 | NORMAL
324.817 | 0.25 | 297.037 | 1.11 | 1 | 106868.78 | 10044.7245 | 10035.4231 | 4586.818 | NORMAL
324.817 | 0.25 | 297.037 | 1.11 | 2 | 57226.51 | 10069.1383 | 10059.8647 | 7055.74 | NORMAL
324.817 | 0.25 | 297.037 | 1.11 | 2 | 79289.74 | 12581.9754 | 12571.5449 | 6428.871 | NORMAL
324.817 | 0.25 | 297.037 | 1.11 | 2 | 101352.97 | 12952.4326 | 12941.8504 | 6065.196 | NORMAL
324.817 | 0.25 | 297.037 | 1.11 | 2 | 106868.78 | 13021.0141 | 13010.4019 | 6001.796 | NORMAL
324.817 | 0.25 | 297.037 | 1.42 | 1 | 57226.51 | 9426.612 | 9416.9403 | 5710.66 | NORMAL
324.817 | 0.25 | 297.037 | 1.42 | 1 | 79289.74 | 10130.5686 | 10120.3671 | 4846.75 | NORMAL
324.817 | 0.25 | 297.037 | 1.42 | 1 | 101352.97 | 10438.5698 | 10428.1416 | 4624.562 | NORMAL
324.817 | 0.25 | 297.037 | 1.42 | 1 | 106868.78 | 10495.5744 | 10480.8701 | 4584.156 | NORMAL
324.817 | 0.25 | 297.037 | 1.42 | 2 | 57226.51 | 10147.245 | 10119.6242 | 7043.42 | NORMAL
324.817 | 0.25 | 297.037 | 1.42 | 2 | 79289.74 | 13189.0973 | 13177.0425 | 6494.39 | NORMAL
324.817 | 0.25 | 297.037 | 1.42 | 2 | 101352.97 | 13602.6671 | 13590.3839 | 6115.68 | NORMAL
324.817 | 0.25 | 297.037 | 1.42 | 2 | 106868.78 | 13680.5979 | 13668.2854 | 6049.184 | NORMAL
324.817 | 0.25 | 299.814 | 0.5 | 1 | 57226.51 | 8129.2204 | 8118.7662 | 5885.604 | NORMAL
324.817 | 0.25 | 299.814 | 0.5 | 1 | 79289.74 | 8467.4385 | 8461.0879 | 4812.737 | NORMAL
324.817 | 0.25 | 299.814 | 0.5 | 1 | 101352.97 | 8644.7831 | 8638.4206 | 4629.732 | NORMAL
324.817 | 0.25 | 299.814 | 0.5 | 1 | 106868.78 | 8674.3552 | 8667.9882 | 4599.0905 | NORMAL
324.817 | 0.25 | 299.814 | 0.5 | 2 | 57226.51 | 9626.6999 | 9620.5388 | 7096.505 | NORMAL
324.817 | 0.25 | 299.814 | 0.5 | 2 | 79289.74 | 10725.7327 | 10489.2732 | 6226.875 | NORMAL
324.817 | 0.25 | 299.814 | 0.5 | 2 | 101352.97 | 11009.1735 | 10655.1845 | 5913.434 | NORMAL
324.817 | 0.25 | 299.814 | 0.5 | 2 | 106868.78 | 10999.2087 | 10750.9235 | 5862.3934 | NORMAL
324.817 | 0.25 | 299.814 | 0.8 | 1 | 57226.51 | 9187.4853 | 9178.4632 | 5748.412 | NORMAL
324.817 | 0.25 | 299.814 | 0.8 | 1 | 79289.74 | 9718.8746 | 9709.5833 | 4835.726 | NORMAL
324.817 | 0.25 | 299.814 | 0.8 | 1 | 101352.97 | 9972.3036 | 9962.8998 | 4623.797 | NORMAL
324.817 | 0.25 | 299.814 | 0.8 | 1 | 106868.78 | 10016.7644 | 10007.3386 | 4586.929 | NORMAL
324.817 | 0.25 | 299.814 | 0.8 | 2 | 57226.51 | 10053.6928 | 10044.2826 | 7056.145 | NORMAL
324.817 | 0.25 | 299.814 | 0.8 | 2 | 79289.74 | 12361.3716 | 12351.2724 | 6404.908 | NORMAL
324.817 | 0.25 | 299.814 | 0.8 | 2 | 101352.97 | 12692.7315 | 12682.5647 | 6045.048 | NORMAL
324.817 | 0.25 | 299.814 | 0.8 | 2 | 106868.78 | 12753.2825 | 12743.1054 | 5982.665 | NORMAL
324.817 | 0.25 | 299.814 | 1.11 | 1 | 57226.51 | 9645.9261 | 9603.976 | 5677.49 | NORMAL
324.817 | 0.25 | 299.814 | 1.11 | 1 | 79289.74 | 10409.4373 | 10398.2263 | 4853.248 | NORMAL
324.817 | 0.25 | 299.814 | 1.11 | 1 | 101352.97 | 10711.8113 | 10700.3818 | 4625.416 | NORMAL
324.817 | 0.25 | 299.814 | 1.11 | 1 | 106868.78 | 10766.1782 | 10750.4165 | 4585.057 | NORMAL
324.817 | 0.25 | 299.814 | 1.11 | 2 | 57226.51 | 10192.4971 | 10155.9162 | 7035.6 | NORMAL
324.817 | 0.25 | 299.814 | 1.11 | 2 | 79289.74 | 13349.4431 | 13336.641 | 6511.545 | NORMAL
324.817 | 0.25 | 299.814 | 1.11 | 2 | 101352.97 | 13744.9883 | 13732.013 | 6126.756 | NORMAL
324.817 | 0.25 | 299.814 | 1.11 | 2 | 106868.78 | 13819.5487 | 13806.5306 | 6059.225 | NORMAL
324.817 | 0.25 | 299.814 | 1.42 | 1 | 57226.51 | 9869.0211 | 9857.3066 | 5631.65 | NORMAL
324.817 | 0.25 | 299.814 | 1.42 | 1 | 79289.74 | 10861.4009 | 10848.8343 | 4863.79 | NORMAL
324.817 | 0.25 | 299.814 | 1.42 | 1 | 101352.97 | 11204.7773 | 11191.9142 | 4622.392 | NORMAL
324.817 | 0.25 | 299.814 | 1.42 | 1 | 106868.78 | 11259.1735 | 11246.2592 | 4584.695 | NORMAL
324.817 | 0.25 | 299.814 | 1.42 | 2 | 57226.51 | 10274.0328 | 10246.9402 | 7021.49 | NORMAL
324.817 | 0.25 | 299.814 | 1.42 | 2 | 79289.74 | 14010.4044 | 13995.6375 | 6583.83 | NORMAL
324.817 | 0.25 | 299.814 | 1.42 | 2 | 101352.97 | 14449.5897 | 14434.5332 | 6181.527 | NORMAL
324.817 | 0.25 | 299.814 | 1.42 | 2 | 106868.78 | 14533.939 | 14518.8383 | 6110.645 | NORMAL
324.817 | 0.25 | 302.591 | 0.5 | 1 | 57226.51 | 8649.3552 | 8641.2508 | 5820.847 | NORMAL
324.817 | 0.25 | 302.591 | 0.5 | 1 | 79289.74 | 9012.2802 | 9004.5567 | 4821.546 | NORMAL
324.817 | 0.25 | 302.591 | 0.5 | 1 | 101352.97 | 9201.7878 | 9194.0491 | 4627.561 | NORMAL
324.817 | 0.25 | 302.591 | 0.5 | 1 | 106868.78 | 9237.1043 | 9229.3636 | 4591.775 | NORMAL
324.817 | 0.25 | 302.591 | 0.5 | 2 | 57226.51 | 9879.8066 | 9872.0509 | 7082.635 | NORMAL
324.817 | 0.25 | 302.591 | 0.5 | 2 | 79289.74 | 11418.5815 | 10922.5126 | 6299.308 | NORMAL
324.817 | 0.25 | 302.591 | 0.5 | 2 | 101352.97 | 11713.4232 | 11118.5804 | 5968.124 | NORMAL
324.817 | 0.25 | 302.591 | 0.5 | 2 | 106868.78 | 11703.517 | 11221.1799 | 5907.578 | NORMAL
324.817 | 0.25 | 302.591 | 0.8 | 1 | 57226.51 | 9640.0059 | 9629.1416 | 5674.755 | NORMAL
324.817 | 0.25 | 302.591 | 0.8 | 1 | 79289.74 | 10361.4889 | 10350.2052 | 4852.089 | NORMAL
324.817 | 0.25 | 302.591 | 0.8 | 1 | 101352.97 | 10638.6577 | 10627.2318 | 4624.083 | NORMAL
324.817 | 0.25 | 302.591 | 0.8 | 1 | 106868.78 | 10685.8148 | 10674.3596 | 4585.476 | NORMAL
324.817 | 0.25 | 302.591 | 0.8 | 2 | 57226.51 | 10192.0281 | 10180.8577 | 7035.018 | NORMAL
324.817 | 0.25 | 302.591 | 0.8 | 2 | 79289.74 | 13067.966 | 13055.7213 | 6481.366 | NORMAL
324.817 | 0.25 | 302.591 | 0.8 | 2 | 101352.97 | 13419.7831 | 13407.4503 | 6101.534 | NORMAL
324.817 | 0.25 | 302.591 | 0.8 | 2 | 106868.78 | 13484.9648 | 13472.6126 | 6035.243 | NORMAL
324.817 | 0.25 | 302.591 | 1.11 | 1 | 57226.51 | 10013.1887 | 10000.462 | 5598.13 | NORMAL
324.817 | 0.25 | 302.591 | 1.11 | 1 | 79289.74 | 11116.0903 | 11102.4619 | 4869.061 | NORMAL
324.817 | 0.25 | 302.591 | 1.11 | 1 | 101352.97 | 11451.1137 | 11437.2121 | 4622.963 | NORMAL
324.817 | 0.25 | 302.591 | 1.11 | 1 | 106868.78 | 11506.0375 | 11492.0922 | 4583.042 | NORMAL
324.817 | 0.25 | 302.591 | 1.11 | 2 | 57226.51 | 10333.0305 | 10320.0625 | 7012.53 | NORMAL
324.817 | 0.25 | 302.591 | 1.11 | 2 | 79289.74 | 14137.2509 | 14121.7565 | 6597.068 | NORMAL
324.817 | 0.25 | 302.591 | 1.11 | 2 | 101352.97 | 14554.0446 | 14535.2262 | 6189.688 | NORMAL
324.817 | 0.25 | 302.591 | 1.11 | 2 | 106868.78 | 14634.3787 | 14618.6174 | 6117.928 | NORMAL
324.817 | 0.25 | 302.591 | 1.42 | 1 | 57226.51 | 10185.6682 | 10132.6926 | 5551 | NORMAL
324.817 | 0.25 | 302.591 | 1.42 | 1 | 79289.74 | 11604.8359 | 11589.5639 | 4884.71 | NORMAL
324.817 | 0.25 | 302.591 | 1.42 | 1 | 101352.97 | 11980.9789 | 11965.3317 | 4626.742 | NORMAL
324.817 | 0.25 | 302.591 | 1.42 | 1 | 106868.78 | 12046.8054 | 12029.9399 | 4582.053 | NORMAL
324.817 | 0.25 | 302.591 | 1.42 | 2 | 57226.51 | 10438.306 | 10350.4259 | 7000.22 | NORMAL
324.817 | 0.25 | 302.591 | 1.42 | 2 | 79289.74 | 14859.3787 | 14835.0241 | 6670.25 | NORMAL
324.817 | 0.25 | 302.591 | 1.42 | 2 | 101352.97 | 15315.7093 | 15297.4836 | 6248.934 | NORMAL
324.817 | 0.25 | 302.591 | 1.42 | 2 | 106868.78 | 15406.6237 | 15388.336 | 6173.794 | NORMAL
324.817 | 0.25 | 305.368 | 0.5 | 1 | 57226.51 | 9129.3669 | 9120.1737 | 5756.543 | NORMAL
324.817 | 0.25 | 305.368 | 0.5 | 1 | 79289.74 | 9561.5768 | 9552.3116 | 4834.354 | NORMAL
324.817 | 0.25 | 305.368 | 0.5 | 1 | 101352.97 | 9769.0504 | 9759.76 | 4624.388 | NORMAL
324.817 | 0.25 | 305.368 | 0.5 | 1 | 106868.78 | 9804.7479 | 9795.453 | 4588.367 | NORMAL
324.817 | 0.25 | 305.368 | 0.5 | 2 | 57226.51 | 10017.3212 | 10008.0251 | 7063.968 | NORMAL
324.817 | 0.25 | 305.368 | 0.5 | 2 | 79289.74 | 12146.6588 | 11356.8952 | 6372.677 | NORMAL
324.817 | 0.25 | 305.368 | 0.5 | 2 | 101352.97 | 12452.2861 | 11566.2685 | 6025.476 | NORMAL
324.817 | 0.25 | 305.368 | 0.5 | 2 | 106868.78 | 12433.0891 | 11682.603 | 5961.3662 | NORMAL
324.817 | 0.25 | 305.368 | 0.8 | 1 | 57226.51 | 10000.9086 | 9979.9067 | 5598.895 | NORMAL
324.817 | 0.25 | 305.368 | 0.8 | 1 | 79289.74 | 11018.3177 | 11004.7872 | 4867.691 | NORMAL
324.817 | 0.25 | 305.368 | 0.8 | 1 | 101352.97 | 11321.5123 | 11307.7906 | 4622.646 | NORMAL
324.817 | 0.25 | 305.368 | 0.8 | 1 | 106868.78 | 11369.8124 | 11356.0663 | 4583.865 | NORMAL
324.817 | 0.25 | 305.368 | 0.8 | 2 | 57226.51 | 10321.9812 | 10308.9033 | 7013.602 | NORMAL
324.817 | 0.25 | 305.368 | 0.8 | 2 | 79289.74 | 13790.6213 | 13775.9481 | 6561.049 | NORMAL
324.817 | 0.25 | 305.368 | 0.8 | 2 | 101352.97 | 14160.9906 | 14146.2066 | 6159.197 | NORMAL
324.817 | 0.25 | 305.368 | 0.8 | 2 | 106868.78 | 14231.1841 | 14216.3836 | 6088.93 | NORMAL
324.817 | 0.25 | 305.368 | 1.11 | 1 | 57226.51 | 10271.4244 | 10227.8325 | 5515.45 | NORMAL
324.817 | 0.25 | 305.368 | 1.11 | 1 | 79289.74 | 11832.3857 | 11814.7909 | 4890.214 | NORMAL
324.817 | 0.25 | 305.368 | 1.11 | 1 | 101352.97 | 12195.0762 | 12178.3811 | 4628.522 | NORMAL
324.817 | 0.25 | 305.368 | 1.11 | 1 | 106868.78 | 12259.5252 | 12242.7787 | 4582.987 | NORMAL
324.817 | 0.25 | 305.368 | 1.11 | 2 | 57226.51 | 10495.1348 | 10480.0428 | 6992.41 | NORMAL
324.817 | 0.25 | 305.368 | 1.11 | 2 | 79289.74 | 14949.4431 | 14930.8909 | 6679.487 | NORMAL
324.817 | 0.25 | 305.368 | 1.11 | 2 | 101352.97 | 15379.9824 | 15361.1573 | 6254.005 | NORMAL
324.817 | 0.25 | 305.368 | 1.11 | 2 | 106868.78 | 15465.6506 | 15446.7671 | 6178.119 | NORMAL
324.817 | 0.25 | 305.368 | 1.42 | 1 | 57226.51 | 10404.0446 | 10387.9183 | 5470.7 | NORMAL
324.817 | 0.25 | 305.368 | 1.42 | 1 | 79289.74 | 12372.2157 | 12353.8677 | 4901.73 | NORMAL
324.817 | 0.25 | 305.368 | 1.42 | 1 | 101352.97 | 12770.4865 | 12732.009 | 4634.039 | NORMAL
324.817 | 0.25 | 305.368 | 1.42 | 1 | 106868.78 | 12843.2005 | 12824.321 | 4586.443 | NORMAL
324.817 | 0.25 | 305.368 | 1.42 | 2 | 57226.51 | 11063.4525 | 11046.5808 | 6984.05 | NORMAL
324.817 | 0.25 | 305.368 | 1.42 | 2 | 79289.74 | 15735.9906 | 15714.5897 | 6759.01 | NORMAL
324.817 | 0.25 | 305.368 | 1.42 | 2 | 101352.97 | 16200.1758 | 16178.3866 | 6317.965 | NORMAL
324.817 | 0.25 | 305.368 | 1.42 | 2 | 106868.78 | 16297.7139 | 16275.8261 | 6238.583 | NORMAL
324.817 | 0.35 | 288.706 | 0.5 | 1 | 57226.51 | 5884.5545 | 5882.1124 | 5311.251 | NORMAL
324.817 | 0.35 | 288.706 | 0.5 | 1 | 79289.74 | 6367.4385 | 6364.9679 | 4781.71 | NORMAL
324.817 | 0.35 | 288.706 | 0.5 | 1 | 101352.97 | 6451.6999 | 6449.2289 | 4687.521 | NORMAL
324.817 | 0.35 | 288.706 | 0.5 | 1 | 106868.78 | 6459.9648 | 6457.4971 | 4677.6537 | NORMAL
324.817 | 0.35 | 288.706 | 0.5 | 2 | 57226.51 | 8499.0621 | 7897.5835 | 7118.59 | NORMAL
324.817 | 0.35 | 288.706 | 0.5 | 2 | 79289.74 | 8718.5815 | 8037.3987 | 5995.644 | NORMAL
324.817 | 0.35 | 288.706 | 0.5 | 2 | 101352.97 | 8877.9894 | 8219.145 | 5754.916 | NORMAL
324.817 | 0.35 | 288.706 | 0.5 | 2 | 106868.78 | 8869.9004 | 8291.5474 | 5711.4434 | NORMAL
324.817 | 0.35 | 288.706 | 0.8 | 1 | 57226.51 | 6621.0141 | 6617.538 | 5379.173 | NORMAL
324.817 | 0.35 | 288.706 | 0.8 | 1 | 79289.74 | 7252.7257 | 7249.0921 | 4788.06 | NORMAL
324.817 | 0.35 | 288.706 | 0.8 | 1 | 101352.97 | 7401.4654 | 7397.7943 | 4651.253 | NORMAL
324.817 | 0.35 | 288.706 | 0.8 | 1 | 106868.78 | 7423.5053 | 7419.8306 | 4630.911 | NORMAL
324.817 | 0.35 | 288.706 | 0.8 | 2 | 57226.51 | 9163.3353 | 9156.2978 | 7118.156 | NORMAL
324.817 | 0.35 | 288.706 | 0.8 | 2 | 79289.74 | 9700.5569 | 9696.5893 | 6109.136 | NORMAL
324.817 | 0.35 | 288.706 | 0.8 | 2 | 101352.97 | 9869.2263 | 9865.3674 | 5834.246 | NORMAL
324.817 | 0.35 | 288.706 | 0.8 | 2 | 106868.78 | 9974.4724 | 9970.4926 | 5790.514 | NORMAL
324.817 | 0.35 | 288.706 | 1.11 | 1 | 57226.51 | 7007.034 | 7002.9069 | 5417.25 | NORMAL
324.817 | 0.35 | 288.706 | 1.11 | 1 | 79289.74 | 7728.8394 | 7724.4494 | 4794.792 | NORMAL
324.817 | 0.35 | 288.706 | 1.11 | 1 | 101352.97 | 7914.5955 | 7910.1317 | 4639.969 | NORMAL
324.817 | 0.35 | 288.706 | 1.11 | 1 | 106868.78 | 7945.1934 | 7940.7282 | 4614.54 | NORMAL
324.817 | 0.35 | 288.706 | 1.11 | 2 | 57226.51 | 9513.5698 | 9501.3448 | 7108.53 | NORMAL
324.817 | 0.35 | 288.706 | 1.11 | 2 | 79289.74 | 10397.6846 | 10392.5794 | 6189.402 | NORMAL
324.817 | 0.35 | 288.706 | 1.11 | 2 | 101352.97 | 10683.646 | 10678.4857 | 5891.409 | NORMAL
324.817 | 0.35 | 288.706 | 1.11 | 2 | 106868.78 | 10731.5065 | 10726.3446 | 5843.415 | NORMAL
324.817 | 0.35 | 288.706 | 1.42 | 1 | 57226.51 | 7251.5533 | 7246.9849 | 5440.31 | NORMAL
324.817 | 0.35 | 288.706 | 1.42 | 1 | 79289.74 | 8033.6166 | 8022.5142 | 4799.5 | NORMAL
324.817 | 0.35 | 288.706 | 1.42 | 1 | 101352.97 | 8241.5592 | 8236.5483 | 4636.809 | NORMAL
324.817 | 0.35 | 288.706 | 1.42 | 1 | 106868.78 | 8280.2169 | 8275.1908 | 4606.611 | NORMAL
324.817 | 0.35 | 288.706 | 1.42 | 2 | 57226.51 | 9663.4232 | 9657.8957 | 7100.16 | NORMAL
324.817 | 0.35 | 288.706 | 1.42 | 2 | 79289.74 | 10856.6823 | 10850.114 | 6241.63 | NORMAL
324.817 | 0.35 | 288.706 | 1.42 | 2 | 101352.97 | 11181.4771 | 11175.4615 | 5927.257 | NORMAL
324.817 | 0.35 | 288.706 | 1.42 | 2 | 106868.78 | 11238.8628 | 11227.7364 | 5872.218 | NORMAL
324.817 | 0.35 | 291.483 | 0.5 | 1 | 57226.51 | 6368.2298 | 6365.0457 | 5353.891 | NORMAL
324.817 | 0.35 | 291.483 | 0.5 | 1 | 79289.74 | 6836.5768 | 6833.3773 | 4783.905 | NORMAL
324.817 | 0.35 | 291.483 | 0.5 | 1 | 101352.97 | 6961.7233 | 6958.5279 | 4665.248 | NORMAL
324.817 | 0.35 | 291.483 | 0.5 | 1 | 106868.78 | 7014.5369 | 7011.3102 | 4647.6719 | NORMAL
324.817 | 0.35 | 291.483 | 0.5 | 2 | 57226.51 | 8951.2603 | 8272.1371 | 7109.661 | NORMAL
324.817 | 0.35 | 291.483 | 0.5 | 2 | 79289.74 | 9334.8769 | 8420.0776 | 6067.706 | NORMAL
324.817 | 0.35 | 291.483 | 0.5 | 2 | 101352.97 | 9508.5873 | 8638.0952 | 5809.265 | NORMAL
324.817 | 0.35 | 291.483 | 0.5 | 2 | 106868.78 | 9500.6448 | 8739.3296 | 5757.6926 | NORMAL
324.817 | 0.35 | 291.483 | 0.8 | 1 | 57226.51 | 7172.6846 | 7168.1587 | 5435.162 | NORMAL
324.817 | 0.35 | 291.483 | 0.8 | 1 | 79289.74 | 7859.4959 | 7852.2573 | 4796.887 | NORMAL
324.817 | 0.35 | 291.483 | 0.8 | 1 | 101352.97 | 8036.6061 | 8031.8243 | 4637.669 | NORMAL
324.817 | 0.35 | 291.483 | 0.8 | 1 | 106868.78 | 8066.0023 | 8061.2111 | 4611.308 | NORMAL
324.817 | 0.35 | 291.483 | 0.8 | 2 | 57226.51 | 9509.9355 | 9504.8762 | 7107.764 | NORMAL
324.817 | 0.35 | 291.483 | 0.8 | 2 | 79289.74 | 10222.4502 | 10217.4616 | 6171.244 | NORMAL
324.817 | 0.35 | 291.483 | 0.8 | 2 | 101352.97 | 10539.4197 | 10534.3292 | 5884.988 | NORMAL
324.817 | 0.35 | 291.483 | 0.8 | 2 | 106868.78 | 10549.1501 | 10544.0759 | 5832.019 | NORMAL
324.817 | 0.35 | 291.483 | 1.11 | 1 | 57226.51 | 7604.5721 | 7599.2033 | 5475.91 | NORMAL
324.817 | 0.35 | 291.483 | 1.11 | 1 | 79289.74 | 8385.4924 | 8368.931 | 4805.677 | NORMAL
324.817 | 0.35 | 291.483 | 1.11 | 1 | 101352.97 | 8597.4209 | 8591.609 | 4633.334 | NORMAL
324.817 | 0.35 | 291.483 | 1.11 | 1 | 106868.78 | 8636.4302 | 8630.6093 | 4602.045 | NORMAL
324.817 | 0.35 | 291.483 | 1.11 | 2 | 57226.51 | 9759.6717 | 9753.4646 | 7093.4 | NORMAL
324.817 | 0.35 | 291.483 | 1.11 | 2 | 79289.74 | 11109.7011 | 11103.0908 | 6268.325 | NORMAL
324.817 | 0.35 | 291.483 | 1.11 | 2 | 101352.97 | 11426.0551 | 11419.3594 | 5946.396 | NORMAL
324.817 | 0.35 | 291.483 | 1.11 | 2 | 106868.78 | 11481.9461 | 11475.2406 | 5891.413 | NORMAL
324.817 | 0.35 | 291.483 | 1.42 | 1 | 57226.51 | 7881.4185 | 7875.4759 | 5499.97 | NORMAL
324.817 | 0.35 | 291.483 | 1.42 | 1 | 79289.74 | 8723.8863 | 8717.483 | 4811.96 | NORMAL
324.817 | 0.35 | 291.483 | 1.42 | 1 | 101352.97 | 8963.1301 | 8956.605 | 4629.511 | NORMAL
324.817 | 0.35 | 291.483 | 1.42 | 1 | 106868.78 | 9005.5686 | 8999.0215 | 4597.395 | NORMAL
324.817 | 0.35 | 291.483 | 1.42 | 2 | 57226.51 | 9884.9941 | 9854.064 | 7083.44 | NORMAL
324.817 | 0.35 | 291.483 | 1.42 | 2 | 79289.74 | 11621.102 | 11613.4553 | 6319.05 | NORMAL
324.817 | 0.35 | 291.483 | 1.42 | 2 | 101352.97 | 11971.0434 | 11963.2622 | 5988.548 | NORMAL
324.817 | 0.35 | 291.483 | 1.42 | 2 | 106868.78 | 12034.6717 | 12026.8733 | 5930.958 | NORMAL
324.817 | 0.35 | 294.26 | 0.5 | 1 | 57226.51 | 6851.612 | 6847.549 | 5403.279 | NORMAL
324.817 | 0.35 | 294.26 | 0.5 | 1 | 79289.74 | 7372.1864 | 7368.1022 | 4789.55 | NORMAL
324.817 | 0.35 | 294.26 | 0.5 | 1 | 101352.97 | 7534.7304 | 7526.3367 | 4648.151 | NORMAL
324.817 | 0.35 | 294.26 | 0.5 | 1 | 106868.78 | 7528.2825 | 7524.1947 | 4626.9703 | NORMAL
324.817 | 0.35 | 294.26 | 0.5 | 2 | 57226.51 | 9364.3904 | 8476.3091 | 7104.455 | NORMAL
324.817 | 0.35 | 294.26 | 0.5 | 2 | 79289.74 | 10024.1501 | 8925.9142 | 6145.538 | NORMAL
324.817 | 0.35 | 294.26 | 0.5 | 2 | 101352.97 | 10183.7339 | 9118.994 | 5856.393 | NORMAL
324.817 | 0.35 | 294.26 | 0.5 | 2 | 106868.78 | 10156.4185 | 9089.893 | 5802.3097 | NORMAL
324.817 | 0.35 | 294.26 | 0.8 | 1 | 57226.51 | 7740.2696 | 7734.5109 | 5488.008 | NORMAL
324.817 | 0.35 | 294.26 | 0.8 | 1 | 79289.74 | 8474.5604 | 8468.535 | 4807.401 | NORMAL
324.817 | 0.35 | 294.26 | 0.8 | 1 | 101352.97 | 8673.388 | 8667.2907 | 4632.366 | NORMAL
324.817 | 0.35 | 294.26 | 0.8 | 1 | 106868.78 | 8712.163 | 8706.0557 | 4598.643 | NORMAL
324.817 | 0.35 | 294.26 | 0.8 | 2 | 57226.51 | 9763.4818 | 9757.1258 | 7093.536 | NORMAL
324.817 | 0.35 | 294.26 | 0.8 | 2 | 79289.74 | 10937.3974 | 10930.9444 | 6249.732 | NORMAL
324.817 | 0.35 | 294.26 | 0.8 | 2 | 101352.97 | 11290.211 | 11283.6288 | 5935.803 | NORMAL
324.817 | 0.35 | 294.26 | 0.8 | 2 | 106868.78 | 11295.2227 | 11288.6941 | 5878.373 | NORMAL
324.817 | 0.35 | 294.26 | 1.11 | 1 | 57226.51 | 8222.5674 | 8200.054 | 5532.71 | NORMAL
324.817 | 0.35 | 294.26 | 1.11 | 1 | 79289.74 | 9052.5791 | 9045.3099 | 4818.576 | NORMAL
324.817 | 0.35 | 294.26 | 1.11 | 1 | 101352.97 | 9294.2849 | 9286.8866 | 4627.001 | NORMAL
324.817 | 0.35 | 294.26 | 1.11 | 1 | 106868.78 | 9337.075 | 9329.6521 | 4593.211 | NORMAL
324.817 | 0.35 | 294.26 | 1.11 | 2 | 57226.51 | 9923.1243 | 9910.2639 | 7075.21 | NORMAL
324.817 | 0.35 | 294.26 | 1.11 | 2 | 79289.74 | 11844.959 | 11836.5964 | 6344.376 | NORMAL
324.817 | 0.35 | 294.26 | 1.11 | 2 | 101352.97 | 12184.8769 | 12176.3962 | 6005.215 | NORMAL
324.817 | 0.35 | 294.26 | 1.11 | 2 | 106868.78 | 12246.6882 | 12238.1767 | 5946.183 | NORMAL
324.817 | 0.35 | 294.26 | 1.42 | 1 | 57226.51 | 8535.4924 | 8526.6838 | 5560.52 | NORMAL
324.817 | 0.35 | 294.26 | 1.42 | 1 | 79289.74 | 9425.3224 | 9417.1883 | 4827.04 | NORMAL
324.817 | 0.35 | 294.26 | 1.42 | 1 | 101352.97 | 9697.8019 | 9689.4909 | 4624.853 | NORMAL
324.817 | 0.35 | 294.26 | 1.42 | 1 | 106868.78 | 9746.5709 | 9738.2181 | 4589.003 | NORMAL
324.817 | 0.35 | 294.26 | 1.42 | 2 | 57226.51 | 10015.8558 | 10007.4024 | 7063.41 | NORMAL
324.817 | 0.35 | 294.26 | 1.42 | 2 | 79289.74 | 12396.9519 | 12387.2823 | 6408.92 | NORMAL
324.817 | 0.35 | 294.26 | 1.42 | 2 | 101352.97 | 12780.4807 | 12770.6269 | 6051.752 | NORMAL
324.817 | 0.35 | 294.26 | 1.42 | 2 | 106868.78 | 12851.1723 | 12841.2898 | 5989.57 | NORMAL
324.817 | 0.35 | 297.037 | 0.5 | 1 | 57226.51 | 7236.2837 | 7231.3341 | 5439.691 | NORMAL
324.817 | 0.35 | 297.037 | 0.5 | 1 | 79289.74 | 7981.2134 | 7835.5163 | 4798.977 | NORMAL
324.817 | 0.35 | 297.037 | 0.5 | 1 | 101352.97 | 8170.4572 | 7952.927 | 4636.615 | NORMAL
324.817 | 0.35 | 297.037 | 0.5 | 1 | 106868.78 | 8150.3517 | 8045.3752 | 4609.2053 | NORMAL
324.817 | 0.35 | 297.037 | 0.5 | 2 | 57226.51 | 9689.6835 | 8664.7669 | 7088.988 | NORMAL
324.817 | 0.35 | 297.037 | 0.5 | 2 | 79289.74 | 10745.1934 | 9177.8136 | 6225.359 | NORMAL
324.817 | 0.35 | 297.037 | 0.5 | 2 | 101352.97 | 10941.0317 | 9443.3576 | 5910.678 | NORMAL
324.817 | 0.35 | 297.037 | 0.5 | 2 | 106868.78 | 10911.6647 | 9562.7975 | 5857.3762 | NORMAL
324.817 | 0.35 | 297.037 | 0.8 | 1 | 57226.51 | 8324.5604 | 8299.4701 | 5542.228 | NORMAL
324.817 | 0.35 | 297.037 | 0.8 | 1 | 79289.74 | 9099.3845 | 9091.8502 | 4819.545 | NORMAL
324.817 | 0.35 | 297.037 | 0.8 | 1 | 101352.97 | 9322.7726 | 9315.1465 | 4626.687 | NORMAL
324.817 | 0.35 | 297.037 | 0.8 | 1 | 106868.78 | 9362.1043 | 9354.4649 | 4592.894 | NORMAL
324.817 | 0.35 | 297.037 | 0.8 | 2 | 57226.51 | 9941.2661 | 9933.4722 | 7076.267 | NORMAL
324.817 | 0.35 | 297.037 | 0.8 | 2 | 79289.74 | 11694.2263 | 11686.0169 | 6329.467 | NORMAL
324.817 | 0.35 | 297.037 | 0.8 | 2 | 101352.97 | 12070.34 | 11900.4017 | 5996.446 | NORMAL
324.817 | 0.35 | 297.037 | 0.8 | 2 | 106868.78 | 12073.5053 | 12050.7467 | 5933.886 | NORMAL
324.817 | 0.35 | 297.037 | 1.11 | 1 | 57226.51 | 9171.1899 | 9162.4498 | 5753.45 | NORMAL
324.817 | 0.35 | 297.037 | 1.11 | 1 | 79289.74 | 9725.4396 | 9716.3561 | 4837.826 | NORMAL
324.817 | 0.35 | 297.037 | 1.11 | 1 | 101352.97 | 10002.1981 | 9992.9461 | 4623.78 | NORMAL
324.817 | 0.35 | 297.037 | 1.11 | 1 | 106868.78 | 10050.5862 | 10041.2894 | 4586.802 | NORMAL
324.817 | 0.35 | 297.037 | 1.11 | 2 | 57226.51 | 10071.1313 | 10035.0263 | 7055.4 | NORMAL
324.817 | 0.35 | 297.037 | 1.11 | 2 | 79289.74 | 12592.6143 | 12582.1876 | 6430.023 | NORMAL
324.817 | 0.35 | 297.037 | 1.11 | 2 | 101352.97 | 12961.313 | 12949.6867 | 6065.899 | NORMAL
324.817 | 0.35 | 297.037 | 1.11 | 2 | 106868.78 | 13029.5135 | 13018.9205 | 6002.413 | NORMAL
324.817 | 0.35 | 297.037 | 1.42 | 1 | 57226.51 | 9443.9332 | 9434.2909 | 5711.03 | NORMAL
324.817 | 0.35 | 297.037 | 1.42 | 1 | 79289.74 | 10137.8371 | 10123.715 | 4845.2 | NORMAL
324.817 | 0.35 | 297.037 | 1.42 | 1 | 101352.97 | 10443.8159 | 10433.4139 | 4624.555 | NORMAL
324.817 | 0.35 | 297.037 | 1.42 | 1 | 106868.78 | 10500.5862 | 10475.7838 | 4584.14 | NORMAL
324.817 | 0.35 | 297.037 | 1.42 | 2 | 57226.51 | 10148.9156 | 10096.0296 | 7043.15 | NORMAL
324.817 | 0.35 | 297.037 | 1.42 | 2 | 79289.74 | 13198.3587 | 13186.335 | 6495.38 | NORMAL
324.817 | 0.35 | 297.037 | 1.42 | 2 | 101352.97 | 13610.4338 | 13598.1844 | 6116.287 | NORMAL
324.817 | 0.35 | 297.037 | 1.42 | 2 | 106868.78 | 13689.6249 | 13677.3179 | 6049.722 | NORMAL
324.817 | 0.35 | 299.814 | 0.5 | 1 | 57226.51 | 8191.823 | 8122.4792 | 5872.297 | NORMAL
324.817 | 0.35 | 299.814 | 0.5 | 1 | 79289.74 | 8617.9367 | 8227.1822 | 4813.478 | NORMAL
324.817 | 0.35 | 299.814 | 0.5 | 1 | 101352.97 | 8831.3599 | 8367.4132 | 4628.908 | NORMAL
324.817 | 0.35 | 299.814 | 0.5 | 1 | 106868.78 | 8805.4513 | 8469.4265 | 4597.6998 | NORMAL
324.817 | 0.35 | 299.814 | 0.5 | 2 | 57226.51 | 9882.1805 | 8831.8629 | 7074.534 | NORMAL
324.817 | 0.35 | 299.814 | 0.5 | 2 | 79289.74 | 11504.5135 | 9530.3735 | 6309.906 | NORMAL
324.817 | 0.35 | 299.814 | 0.5 | 2 | 101352.97 | 11714.8886 | 9823.2153 | 5968.862 | NORMAL
324.817 | 0.35 | 299.814 | 0.5 | 2 | 106868.78 | 11683.7632 | 9953.9236 | 5906.0838 | NORMAL
324.817 | 0.35 | 299.814 | 0.8 | 1 | 57226.51 | 9199.2087 | 9176.4314 | 5746.76 | NORMAL
324.817 | 0.35 | 299.814 | 0.8 | 1 | 79289.74 | 9728.3998 | 9715.1983 | 4837.875 | NORMAL
324.817 | 0.35 | 299.814 | 0.8 | 1 | 101352.97 | 9981.7409 | 9972.3481 | 4623.802 | NORMAL
324.817 | 0.35 | 299.814 | 0.8 | 1 | 106868.78 | 10025.8792 | 10016.4649 | 4586.861 | NORMAL
324.817 | 0.35 | 299.814 | 0.8 | 2 | 57226.51 | 10056.5358 | 10036.483 | 7055.588 | NORMAL
324.817 | 0.35 | 299.814 | 0.8 | 2 | 79289.74 | 12476.143 | 12227.3937 | 6420.047 | NORMAL
324.817 | 0.35 | 299.814 | 0.8 | 2 | 101352.97 | 12885.0528 | 12462.7967 | 6060.114 | NORMAL
324.817 | 0.35 | 299.814 | 0.8 | 2 | 106868.78 | 12879.66 | 12604.2929 | 5993.513 | NORMAL
324.817 | 0.35 | 299.814 | 1.11 | 1 | 57226.51 | 9653.4877 | 9642.8592 | 5676.14 | NORMAL
324.817 | 0.35 | 299.814 | 1.11 | 1 | 79289.74 | 10418.8746 | 10407.6847 | 4853.436 | NORMAL
324.817 | 0.35 | 299.814 | 1.11 | 1 | 101352.97 | 10719.8124 | 10708.4065 | 4625.368 | NORMAL
324.817 | 0.35 | 299.814 | 1.11 | 1 | 106868.78 | 10773.9742 | 10762.5323 | 4584.923 | NORMAL
324.817 | 0.35 | 299.814 | 1.11 | 2 | 57226.51 | 10194.4607 | 10183.4609 | 7035.27 | NORMAL
324.817 | 0.35 | 299.814 | 1.11 | 2 | 79289.74 | 13363.0715 | 13339.4322 | 6513.022 | NORMAL
324.817 | 0.35 | 299.814 | 1.11 | 2 | 101352.97 | 13510.4044 | 13498.0695 | 6110.087 | NORMAL
324.817 | 0.35 | 299.814 | 1.11 | 2 | 106868.78 | 13652.5205 | 13639.9465 | 6045.68 | NORMAL
324.817 | 0.35 | 299.814 | 1.42 | 1 | 57226.51 | 9874.0914 | 9862.4301 | 5630.56 | NORMAL
324.817 | 0.35 | 299.814 | 1.42 | 1 | 79289.74 | 10872.9777 | 10834.8245 | 4861.25 | NORMAL
324.817 | 0.35 | 299.814 | 1.42 | 1 | 101352.97 | 11211.8113 | 11182.0215 | 4622.274 | NORMAL
324.817 | 0.35 | 299.814 | 1.42 | 1 | 106868.78 | 11265.7386 | 11252.8618 | 4584.658 | NORMAL
324.817 | 0.35 | 299.814 | 1.42 | 2 | 57226.51 | 10275.6448 | 10263.6531 | 7021.23 | NORMAL
324.817 | 0.35 | 299.814 | 1.42 | 2 | 79289.74 | 14022.4795 | 14007.3212 | 6585.08 | NORMAL
324.817 | 0.35 | 299.814 | 1.42 | 2 | 101352.97 | 14459.5252 | 14444.5018 | 6182.313 | NORMAL
324.817 | 0.35 | 299.814 | 1.42 | 2 | 106868.78 | 14543.4642 | 14528.3827 | 6111.343 | NORMAL
324.817 | 0.35 | 302.591 | 0.5 | 1 | 57226.51 | 8816.5592 | 8533.7064 | 5784.473 | NORMAL
324.817 | 0.35 | 302.591 | 0.5 | 1 | 79289.74 | 9288.9801 | 8586.4452 | 4826.37 | NORMAL
324.817 | 0.35 | 302.591 | 0.5 | 1 | 101352.97 | 9514.6835 | 8755.4974 | 4628.589 | NORMAL
324.817 | 0.35 | 302.591 | 0.5 | 1 | 106868.78 | 9489.83 | 8885.3563 | 4589.684 | NORMAL
324.817 | 0.35 | 302.591 | 0.5 | 2 | 57226.51 | 10020.3986 | 8949.1178 | 7057.421 | NORMAL
324.817 | 0.35 | 302.591 | 0.5 | 2 | 79289.74 | 12310.1993 | 9860.8389 | 6396.528 | NORMAL
324.817 | 0.35 | 302.591 | 0.5 | 2 | 101352.97 | 12525.1758 | 10181.0015 | 6034.376 | NORMAL
324.817 | 0.35 | 302.591 | 0.5 | 2 | 106868.78 | 12489.068 | 10284.4852 | 5965.4653 | NORMAL
324.817 | 0.35 | 302.591 | 0.8 | 1 | 57226.51 | 9661.8406 | 9651 | 5673.829 | NORMAL
324.817 | 0.35 | 302.591 | 0.8 | 1 | 79289.74 | 10375.9965 | 10364.7385 | 4852.419 | NORMAL
324.817 | 0.35 | 302.591 | 0.8 | 1 | 101352.97 | 10650.8206 | 10639.4136 | 4624.077 | NORMAL
324.817 | 0.35 | 302.591 | 0.8 | 1 | 106868.78 | 10697.7139 | 10686.2781 | 4585.23 | NORMAL
324.817 | 0.35 | 302.591 | 0.8 | 2 | 57226.51 | 10196.5416 | 10185.4172 | 7034.321 | NORMAL
324.817 | 0.35 | 302.591 | 0.8 | 2 | 79289.74 | 13314.5076 | 12776.961 | 6505.536 | NORMAL
324.817 | 0.35 | 302.591 | 0.8 | 2 | 101352.97 | 13738.4818 | 12994.282 | 6126.417 | NORMAL
324.817 | 0.35 | 302.591 | 0.8 | 2 | 106868.78 | 13728.517 | 13180.6256 | 6054.662 | NORMAL
324.817 | 0.35 | 302.591 | 1.11 | 1 | 57226.51 | 10008.4115 | 9958.0392 | 5595.48 | NORMAL
324.817 | 0.35 | 302.591 | 1.11 | 1 | 79289.74 | 11128.6342 | 11115.0462 | 4869.055 | NORMAL
324.817 | 0.35 | 302.591 | 1.11 | 1 | 101352.97 | 11461.2544 | 11444.8419 | 4623.023 | NORMAL
324.817 | 0.35 | 302.591 | 1.11 | 1 | 106868.78 | 11510.1407 | 11488.0182 | 4586.977 | NORMAL
324.817 | 0.35 | 302.591 | 1.11 | 2 | 57226.51 | 10336.3716 | 10323.4615 | 7012.06 | NORMAL
324.817 | 0.35 | 302.591 | 1.11 | 2 | 79289.74 | 13844.7245 | 13830.1045 | 6561.731 | NORMAL
324.817 | 0.35 | 302.591 | 1.11 | 2 | 101352.97 | 14374.5018 | 14359.3798 | 6178.335 | NORMAL
324.817 | 0.35 | 302.591 | 1.11 | 2 | 106868.78 | 14385.1407 | 14370.1226 | 6102.039 | NORMAL
324.817 | 0.35 | 302.591 | 1.42 | 1 | 57226.51 | 10190.0645 | 10176.2671 | 5549.62 | NORMAL
324.817 | 0.35 | 302.591 | 1.42 | 1 | 79289.74 | 11621.1606 | 11605.9253 | 4880.64 | NORMAL
324.817 | 0.35 | 302.591 | 1.42 | 1 | 101352.97 | 11989.9179 | 11974.3191 | 4626.688 | NORMAL
324.817 | 0.35 | 302.591 | 1.42 | 1 | 106868.78 | 12056.0375 | 12040.3767 | 4582.044 | NORMAL
324.817 | 0.35 | 302.591 | 1.42 | 2 | 57226.51 | 10440.592 | 10426.5494 | 6999.89 | NORMAL
324.817 | 0.35 | 302.591 | 1.42 | 2 | 79289.74 | 14874.7655 | 14856.9307 | 6671.86 | NORMAL
324.817 | 0.35 | 302.591 | 1.42 | 2 | 101352.97 | 15328.4584 | 15310.2635 | 6249.955 | NORMAL
324.817 | 0.35 | 302.591 | 1.42 | 2 | 106868.78 | 15418.7573 | 15400.5015 | 6174.681 | NORMAL
324.817 | 0.35 | 305.368 | 0.5 | 1 | 57226.51 | 9350.4982 | 8783.8113 | 5720.24 | NORMAL
324.817 | 0.35 | 305.368 | 0.5 | 1 | 79289.74 | 10001.524 | 8937.3819 | 4839.898 | NORMAL
324.817 | 0.35 | 305.368 | 0.5 | 1 | 101352.97 | 10242.3505 | 9135.0398 | 4624.254 | NORMAL
324.817 | 0.35 | 305.368 | 0.5 | 1 | 106868.78 | 10198.857 | 9268.5784 | 4587.913 | NORMAL
324.817 | 0.35 | 305.368 | 0.5 | 2 | 57226.51 | 10131.9754 | 9100.0033 | 7038.573 | NORMAL
324.817 | 0.35 | 305.368 | 0.5 | 2 | 79289.74 | 13157.8253 | 10191.5778 | 6489.903 | NORMAL
324.817 | 0.35 | 305.368 | 0.5 | 2 | 101352.97 | 13386.6061 | 10548.9 | 6100.598 | NORMAL
324.817 | 0.35 | 305.368 | 0.5 | 2 | 106868.78 | 13341.1782 | 10590.0138 | 6026.654 | NORMAL
324.817 | 0.35 | 305.368 | 0.8 | 1 | 57226.51 | 10022.8312 | 10010.012 | 5597.185 | NORMAL
324.817 | 0.35 | 305.368 | 0.8 | 1 | 79289.74 | 11036.8406 | 11023.3425 | 4868.136 | NORMAL
324.817 | 0.35 | 305.368 | 0.8 | 1 | 101352.97 | 11141.3247 | 11128.0331 | 4623.729 | NORMAL
324.817 | 0.35 | 305.368 | 0.8 | 1 | 106868.78 | 11383.6753 | 11369.9466 | 4584.529 | NORMAL
324.817 | 0.35 | 305.368 | 0.8 | 2 | 57226.51 | 10327.374 | 10314.3615 | 7012.89 | NORMAL
324.817 | 0.35 | 305.368 | 0.8 | 2 | 79289.74 | 14179.8945 | 13272.2111 | 6598.669 | NORMAL
324.817 | 0.35 | 305.368 | 0.8 | 2 | 101352.97 | 14633.6166 | 13510.311 | 6195.791 | NORMAL
324.817 | 0.35 | 305.368 | 0.8 | 2 | 106868.78 | 14614.9179 | 13722.1218 | 6118.853 | NORMAL
324.817 | 0.35 | 305.368 | 1.11 | 1 | 57226.51 | 10276.993 | 10262.2044 | 5513.36 | NORMAL
324.817 | 0.35 | 305.368 | 1.11 | 1 | 79289.74 | 11850.7034 | 11816.4904 | 4887.531 | NORMAL
324.817 | 0.35 | 305.368 | 1.11 | 1 | 101352.97 | 12208.0891 | 12184.9548 | 4628.567 | NORMAL
324.817 | 0.35 | 305.368 | 1.11 | 1 | 106868.78 | 12271.9812 | 12255.2791 | 4583.04 | NORMAL
324.817 | 0.35 | 305.368 | 1.11 | 2 | 57226.51 | 10498.6518 | 10461.833 | 6991.9 | NORMAL
324.817 | 0.35 | 305.368 | 1.11 | 2 | 79289.74 | 14720.5744 | 14702.8509 | 6654.599 | NORMAL
324.817 | 0.35 | 305.368 | 1.11 | 2 | 101352.97 | 15278.4291 | 15260.095 | 6248.921 | NORMAL
324.817 | 0.35 | 305.368 | 1.11 | 2 | 106868.78 | 15293.7866 | 15275.6023 | 6166.421 | NORMAL
324.817 | 0.35 | 305.368 | 1.42 | 1 | 57226.51 | 10407.4443 | 10381.8524 | 5469.1 | NORMAL
324.817 | 0.35 | 305.368 | 1.42 | 1 | 79289.74 | 12385.4044 | 12367.1236 | 4902.15 | NORMAL
324.817 | 0.35 | 305.368 | 1.42 | 1 | 101352.97 | 12781.6823 | 12762.9443 | 4634.169 | NORMAL
324.817 | 0.35 | 305.368 | 1.42 | 1 | 106868.78 | 12853.9859 | 12835.1677 | 4586.518 | NORMAL
324.817 | 0.35 | 305.368 | 1.42 | 2 | 57226.51 | 11067.2626 | 11050.5068 | 6983.68 | NORMAL
324.817 | 0.35 | 305.368 | 1.42 | 2 | 79289.74 | 15756.0961 | 15734.7781 | 6760.6 | NORMAL
324.817 | 0.35 | 305.368 | 1.42 | 2 | 101352.97 | 16216.2368 | 16194.4908 | 6319.203 | NORMAL
324.817 | 0.35 | 305.368 | 1.42 | 2 | 106868.78 | 16313.8042 | 16291.96 | 6239.735 | NORMAL
324.817 | 0.45 | 288.706 | 0.5 | 1 | 57226.51 | 5953.1067 | 5764.6313 | 5314.392 | NORMAL
324.817 | 0.45 | 288.706 | 0.5 | 1 | 79289.74 | 6547.3329 | 6198.6089 | 4779.273 | NORMAL
324.817 | 0.45 | 288.706 | 0.5 | 1 | 101352.97 | 6635.9906 | 6263.8111 | 4674.487 | NORMAL
324.817 | 0.45 | 288.706 | 0.5 | 1 | 106868.78 | 6596.2192 | 6200.6176 | 4670.537 | NORMAL
324.817 | 0.45 | 288.706 | 0.5 | 2 | 57226.51 | 8848.388 | 7131.3318 | 7115.131 | NORMAL
324.817 | 0.45 | 288.706 | 0.5 | 2 | 79289.74 | 9120.3986 | 7463.2678 | 6041.761 | NORMAL
324.817 | 0.45 | 288.706 | 0.5 | 2 | 101352.97 | 9234.8183 | 7773.2236 | 5784.334 | NORMAL
324.817 | 0.45 | 288.706 | 0.5 | 2 | 106868.78 | 9215.0059 | 7806.9253 | 5735.3845 | NORMAL
324.817 | 0.45 | 288.706 | 0.8 | 1 | 57226.51 | 6625.5275 | 6608.6258 | 5379.593 | NORMAL
324.817 | 0.45 | 288.706 | 0.8 | 1 | 79289.74 | 7256.6237 | 7248.1334 | 4788.164 | NORMAL
324.817 | 0.45 | 288.706 | 0.8 | 1 | 101352.97 | 7403.9273 | 7400.2624 | 4651.142 | NORMAL
324.817 | 0.45 | 288.706 | 0.8 | 1 | 106868.78 | 7426.6413 | 7422.9725 | 4630.845 | NORMAL
324.817 | 0.45 | 288.706 | 0.8 | 2 | 57226.51 | 9271.8054 | 8899.3292 | 7114.46 | NORMAL
324.817 | 0.45 | 288.706 | 0.8 | 2 | 79289.74 | 9954.6014 | 9235.1425 | 6138.875 | NORMAL
324.817 | 0.45 | 288.706 | 0.8 | 2 | 101352.97 | 10179.1032 | 9573.0088 | 5856.293 | NORMAL
324.817 | 0.45 | 288.706 | 0.8 | 2 | 106868.78 | 10160.8734 | 9792.9786 | 5802.689 | NORMAL
324.817 | 0.45 | 288.706 | 1.11 | 1 | 57226.51 | 7012.2216 | 7008.1054 | 5416.14 | NORMAL
324.817 | 0.45 | 288.706 | 1.11 | 1 | 79289.74 | 7732.034 | 7727.6499 | 4794.838 | NORMAL
324.817 | 0.45 | 288.706 | 1.11 | 1 | 101352.97 | 7917.2919 | 7912.8345 | 4639.936 | NORMAL
324.817 | 0.45 | 288.706 | 1.11 | 1 | 106868.78 | 7947.8605 | 7943.4017 | 4614.416 | NORMAL
324.817 | 0.45 | 288.706 | 1.11 | 2 | 57226.51 | 9452.5791 | 9447.9285 | 7111.01 | NORMAL
324.817 | 0.45 | 288.706 | 1.11 | 2 | 79289.74 | 10381.6823 | 10376.6679 | 6190.878 | NORMAL
324.817 | 0.45 | 288.706 | 1.11 | 2 | 101352.97 | 10722.5088 | 10717.362 | 5893.429 | NORMAL
324.817 | 0.45 | 288.706 | 1.11 | 2 | 106868.78 | 10722.3036 | 10717.2105 | 5842.809 | NORMAL
324.817 | 0.45 | 288.706 | 1.42 | 1 | 57226.51 | 7254.5428 | 7227.9767 | 5440.58 | NORMAL
324.817 | 0.45 | 288.706 | 1.42 | 1 | 79289.74 | 8036.3716 | 8011.9652 | 4799.48 | NORMAL
324.817 | 0.45 | 288.706 | 1.42 | 1 | 101352.97 | 8243.8159 | 8234.8796 | 4636.786 | NORMAL
324.817 | 0.45 | 288.706 | 1.42 | 1 | 106868.78 | 8282.3857 | 8277.3666 | 4606.579 | NORMAL
324.817 | 0.45 | 288.706 | 1.42 | 2 | 57226.51 | 9667.0574 | 9661.5376 | 7100.2 | NORMAL
324.817 | 0.45 | 288.706 | 1.42 | 2 | 79289.74 | 10863.1594 | 10843.4102 | 6240.35 | NORMAL
324.817 | 0.45 | 288.706 | 1.42 | 2 | 101352.97 | 11066.8816 | 11061.0493 | 5916.88 | NORMAL
324.817 | 0.45 | 288.706 | 1.42 | 2 | 106868.78 | 11241.9988 | 11220.2905 | 5876.379 | NORMAL
324.817 | 0.45 | 291.483 | 0.5 | 1 | 57226.51 | 6544.578 | 6094.2521 | 5364.548 | NORMAL
324.817 | 0.45 | 291.483 | 0.5 | 1 | 79289.74 | 7185.0821 | 6417.5069 | 4784.484 | NORMAL
324.817 | 0.45 | 291.483 | 0.5 | 1 | 101352.97 | 7288.8335 | 6547.4425 | 4655.394 | NORMAL
324.817 | 0.45 | 291.483 | 0.5 | 1 | 106868.78 | 7254.4256 | 6646.2508 | 4637.6263 | NORMAL
324.817 | 0.45 | 291.483 | 0.5 | 2 | 57226.51 | 9311.313 | 7243.168 | 7122.766 | NORMAL
324.817 | 0.45 | 291.483 | 0.5 | 2 | 79289.74 | 9816.5006 | 7745.1404 | 6122.052 | NORMAL
324.817 | 0.45 | 291.483 | 0.5 | 2 | 101352.97 | 9932.1805 | 8082.3516 | 5839.689 | NORMAL
324.817 | 0.45 | 291.483 | 0.5 | 2 | 106868.78 | 9910.0528 | 8105.9177 | 5785.542 | NORMAL
324.817 | 0.45 | 291.483 | 0.8 | 1 | 57226.51 | 7181.7702 | 7177.2601 | 5432.537 | NORMAL
324.817 | 0.45 | 291.483 | 0.8 | 1 | 79289.74 | 7756.0961 | 7751.5123 | 4795.231 | NORMAL
324.817 | 0.45 | 291.483 | 0.8 | 1 | 101352.97 | 7972.5381 | 7967.8582 | 4639.099 | NORMAL
324.817 | 0.45 | 291.483 | 0.8 | 1 | 106868.78 | 8003.5463 | 7998.8482 | 4612.965 | NORMAL
324.817 | 0.45 | 291.483 | 0.8 | 2 | 57226.51 | 9604.9531 | 9162.4145 | 7102.494 | NORMAL
324.817 | 0.45 | 291.483 | 0.8 | 2 | 79289.74 | 10714.5369 | 9683.4663 | 6220.997 | NORMAL
324.817 | 0.45 | 291.483 | 0.8 | 2 | 101352.97 | 10993.7573 | 9970.3375 | 5911.56 | NORMAL
324.817 | 0.45 | 291.483 | 0.8 | 2 | 106868.78 | 10974.7948 | 10131.2172 | 5860.792 | NORMAL
324.817 | 0.45 | 291.483 | 1.11 | 1 | 57226.51 | 7610.1407 | 7596.0924 | 5475.43 | NORMAL
324.817 | 0.45 | 291.483 | 1.11 | 1 | 79289.74 | 8389.7421 | 8384.0371 | 4805.751 | NORMAL
324.817 | 0.45 | 291.483 | 1.11 | 1 | 101352.97 | 8601.0844 | 8595.2873 | 4633.223 | NORMAL
324.817 | 0.45 | 291.483 | 1.11 | 1 | 106868.78 | 8639.9766 | 8634.1618 | 4601.887 | NORMAL
324.817 | 0.45 | 291.483 | 1.11 | 2 | 57226.51 | 9713.3939 | 9707.4979 | 7097.53 | NORMAL
324.817 | 0.45 | 291.483 | 1.11 | 2 | 79289.74 | 11166.2661 | 11159.6557 | 6272.348 | NORMAL
324.817 | 0.45 | 291.483 | 1.11 | 2 | 101352.97 | 11533.0012 | 11398.5148 | 5954.083 | NORMAL
324.817 | 0.45 | 291.483 | 1.11 | 2 | 106868.78 | 11533.939 | 11527.2494 | 5895.635 | NORMAL
324.817 | 0.45 | 291.483 | 1.42 | 1 | 57226.51 | 7886.6061 | 7859.4367 | 5499.51 | NORMAL
324.817 | 0.45 | 291.483 | 1.42 | 1 | 79289.74 | 8727.4326 | 8721.0441 | 4812.03 | NORMAL
324.817 | 0.45 | 291.483 | 1.42 | 1 | 101352.97 | 8966.1196 | 8959.6012 | 4629.501 | NORMAL
324.817 | 0.45 | 291.483 | 1.42 | 1 | 106868.78 | 9008.4701 | 9001.93 | 4597.368 | NORMAL
324.817 | 0.45 | 291.483 | 1.42 | 2 | 57226.51 | 9872.4502 | 9865.5592 | 7083.23 | NORMAL
324.817 | 0.45 | 291.483 | 1.42 | 2 | 79289.74 | 11464.5956 | 11457.3041 | 6301.6 | NORMAL
324.817 | 0.45 | 291.483 | 1.42 | 2 | 101352.97 | 11883.4701 | 11875.9241 | 5981.679 | NORMAL
324.817 | 0.45 | 291.483 | 1.42 | 2 | 106868.78 | 11896.0727 | 11888.5782 | 5921.833 | NORMAL
324.817 | 0.45 | 294.26 | 0.5 | 1 | 57226.51 | 7136.2837 | 6395.2235 | 5425.304 | NORMAL
324.817 | 0.45 | 294.26 | 0.5 | 1 | 79289.74 | 7847.4209 | 6750.7124 | 4793.528 | NORMAL
324.817 | 0.45 | 294.26 | 0.5 | 1 | 101352.97 | 7969.6073 | 6914.232 | 4639.749 | NORMAL
324.817 | 0.45 | 294.26 | 0.5 | 1 | 106868.78 | 7934.6131 | 7029.2976 | 4614.6843 | NORMAL
324.817 | 0.45 | 294.26 | 0.5 | 2 | 57226.51 | 9661.5182 | 7321.17 | 7135.118 | NORMAL
324.817 | 0.45 | 294.26 | 0.5 | 2 | 79289.74 | 10601.0844 | 8062.6866 | 6208.736 | NORMAL
324.817 | 0.45 | 294.26 | 0.5 | 2 | 101352.97 | 10726.5533 | 8422.4468 | 5893.882 | NORMAL
324.817 | 0.45 | 294.26 | 0.5 | 2 | 106868.78 | 10683.7925 | 8416.9802 | 5840.081 | NORMAL
324.817 | 0.45 | 294.26 | 0.8 | 1 | 57226.51 | 7690.7093 | 7684.9874 | 5482.96 | NORMAL
324.817 | 0.45 | 294.26 | 0.8 | 1 | 79289.74 | 8429.5721 | 8423.6377 | 4805.155 | NORMAL
324.817 | 0.45 | 294.26 | 0.8 | 1 | 101352.97 | 8675.4689 | 8669.3961 | 4631.255 | NORMAL
324.817 | 0.45 | 294.26 | 0.8 | 1 | 106868.78 | 8656.7995 | 8650.8004 | 4601.593 | NORMAL
324.817 | 0.45 | 294.26 | 0.8 | 2 | 57226.51 | 9848.9156 | 9407.763 | 7090.817 | NORMAL
324.817 | 0.45 | 294.26 | 0.8 | 2 | 79289.74 | 11515.3869 | 10102.495 | 6309.38 | NORMAL
324.817 | 0.45 | 294.26 | 0.8 | 2 | 101352.97 | 11818.4935 | 10424.254 | 5975.733 | NORMAL
324.817 | 0.45 | 294.26 | 0.8 | 2 | 106868.78 | 11800.7913 | 10624.9133 | 5914.451 | NORMAL
324.817 | 0.45 | 294.26 | 1.11 | 1 | 57226.51 | 8228.8394 | 8189.2669 | 5533.62 | NORMAL
324.817 | 0.45 | 294.26 | 1.11 | 1 | 79289.74 | 9058.177 | 9050.9214 | 4818.691 | NORMAL
324.817 | 0.45 | 294.26 | 1.11 | 1 | 101352.97 | 9299.0914 | 9291.6987 | 4626.986 | NORMAL
324.817 | 0.45 | 294.26 | 1.11 | 1 | 106868.78 | 9341.7057 | 9332.6163 | 4593.078 | NORMAL
324.817 | 0.45 | 294.26 | 1.11 | 2 | 57226.51 | 9896.1313 | 9888.8873 | 7079.7 | NORMAL
324.817 | 0.45 | 294.26 | 1.11 | 2 | 79289.74 | 11980.041 | 11700.5587 | 6359.414 | NORMAL
324.817 | 0.45 | 294.26 | 1.11 | 2 | 101352.97 | 12379.3669 | 11951.3379 | 6019.955 | NORMAL
324.817 | 0.45 | 294.26 | 1.11 | 2 | 106868.78 | 12379.0446 | 12189.7442 | 5955.828 | NORMAL
324.817 | 0.45 | 294.26 | 1.42 | 1 | 57226.51 | 8541.2075 | 8507.8028 | 5560.85 | NORMAL
324.817 | 0.45 | 294.26 | 1.42 | 1 | 79289.74 | 9432.7667 | 9424.6451 | 4825.25 | NORMAL
324.817 | 0.45 | 294.26 | 1.42 | 1 | 101352.97 | 9701.7878 | 9693.4831 | 4624.847 | NORMAL
324.817 | 0.45 | 294.26 | 1.42 | 1 | 106868.78 | 9750.4103 | 9742.0737 | 4588.991 | NORMAL
324.817 | 0.45 | 294.26 | 1.42 | 2 | 57226.51 | 10022.626 | 9992.2875 | 7063.57 | NORMAL
324.817 | 0.45 | 294.26 | 1.42 | 2 | 79289.74 | 12277.4033 | 12268.0602 | 6399.49 | NORMAL
324.817 | 0.45 | 294.26 | 1.42 | 2 | 101352.97 | 12741.442 | 12731.7967 | 6050.717 | NORMAL
324.817 | 0.45 | 294.26 | 1.42 | 2 | 106868.78 | 12755.5979 | 12746.0312 | 5982.991 | NORMAL
324.817 | 0.45 | 297.037 | 0.5 | 1 | 57226.51 | 7765.4748 | 6675.7845 | 5486.096 | NORMAL
324.817 | 0.45 | 297.037 | 0.5 | 1 | 79289.74 | 8533.0305 | 7065.9721 | 4807.032 | NORMAL
324.817 | 0.45 | 297.037 | 0.5 | 1 | 101352.97 | 8677.7843 | 7262.0906 | 4630.349 | NORMAL
324.817 | 0.45 | 297.037 | 0.5 | 1 | 106868.78 | 8640.3283 | 7350.5778 | 4599.635 | NORMAL
324.817 | 0.45 | 297.037 | 0.5 | 2 | 57226.51 | 9938.7456 | 7390.2326 | 7106.077 | NORMAL
324.817 | 0.45 | 297.037 | 0.5 | 2 | 79289.74 | 11416.354 | 8324.851 | 6298.199 | NORMAL
324.817 | 0.45 | 297.037 | 0.5 | 2 | 101352.97 | 11546.6295 | 8699.5078 | 5957.566 | NORMAL
324.817 | 0.45 | 297.037 | 0.5 | 2 | 106868.78 | 11502.4326 | 8697.7714 | 5893.3649 | NORMAL
324.817 | 0.45 | 297.037 | 0.8 | 1 | 57226.51 | 8179.1618 | 8172.324 | 5525.272 | NORMAL
324.817 | 0.45 | 297.037 | 0.8 | 1 | 79289.74 | 9133.6166 | 9055.9078 | 4820.043 | NORMAL
324.817 | 0.45 | 297.037 | 0.8 | 1 | 101352.97 | 9396.483 | 9178.6255 | 4631.621 | NORMAL
324.817 | 0.45 | 297.037 | 0.8 | 1 | 106868.78 | 9386.1372 | 9361.5643 | 4590.66 | NORMAL
324.817 | 0.45 | 297.037 | 0.8 | 2 | 57226.51 | 9991.6178 | 9556.0732 | 7073.014 | NORMAL
324.817 | 0.45 | 297.037 | 0.8 | 2 | 79289.74 | 12361.782 | 10527.8127 | 6398.098 | NORMAL
324.817 | 0.45 | 297.037 | 0.8 | 2 | 101352.97 | 12687.8957 | 10865.7743 | 6043.151 | NORMAL
324.817 | 0.45 | 297.037 | 0.8 | 2 | 106868.78 | 12660.7855 | 11056.2968 | 5977.687 | NORMAL
324.817 | 0.45 | 297.037 | 1.11 | 1 | 57226.51 | 9179.6307 | 9170.9192 | 5752.53 | NORMAL
324.817 | 0.45 | 297.037 | 1.11 | 1 | 79289.74 | 9732.8253 | 9723.7641 | 4837.98 | NORMAL
324.817 | 0.45 | 297.037 | 1.11 | 1 | 101352.97 | 10005.2755 | 9996.0306 | 4623.75 | NORMAL
324.817 | 0.45 | 297.037 | 1.11 | 1 | 106868.78 | 10056.7116 | 10047.4393 | 4586.559 | NORMAL
324.817 | 0.45 | 297.037 | 1.11 | 2 | 57226.51 | 10019.1676 | 10010.451 | 7059.79 | NORMAL
324.817 | 0.45 | 297.037 | 1.11 | 2 | 79289.74 | 12835.4044 | 12264.0621 | 6456.773 | NORMAL
324.817 | 0.45 | 297.037 | 1.11 | 2 | 101352.97 | 13267.1747 | 12537.5729 | 6089.282 | NORMAL
324.817 | 0.45 | 297.037 | 1.11 | 2 | 106868.78 | 13259.027 | 12764.7702 | 6020.644 | NORMAL
324.817 | 0.45 | 297.037 | 1.42 | 1 | 57226.51 | 9450.0293 | 9440.4186 | 5710.22 | NORMAL
324.817 | 0.45 | 297.037 | 1.42 | 1 | 79289.74 | 10142.8488 | 10132.7059 | 4845.91 | NORMAL
324.817 | 0.45 | 297.037 | 1.42 | 1 | 101352.97 | 10449.0328 | 10436.3163 | 4624.544 | NORMAL
324.817 | 0.45 | 297.037 | 1.42 | 1 | 106868.78 | 10505.6272 | 10486.5595 | 4584.132 | NORMAL
324.817 | 0.45 | 297.037 | 1.42 | 2 | 57226.51 | 10150.3224 | 10134.8026 | 7042.89 | NORMAL
324.817 | 0.45 | 297.037 | 1.42 | 2 | 79289.74 | 13143.0246 | 13131.2748 | 6489.52 | NORMAL
324.817 | 0.45 | 297.037 | 1.42 | 2 | 101352.97 | 13640.3283 | 13628.1884 | 6120.459 | NORMAL
324.817 | 0.45 | 297.037 | 1.42 | 2 | 106868.78 | 13647.4795 | 13635.4288 | 6048.513 | NORMAL
324.817 | 0.45 | 299.814 | 0.5 | 1 | 57226.51 | 8809.7597 | 7148.9702 | 5795.329 | NORMAL
324.817 | 0.45 | 299.814 | 0.5 | 1 | 79289.74 | 9245.7503 | 7351.6012 | 4825.427 | NORMAL
324.817 | 0.45 | 299.814 | 0.5 | 1 | 101352.97 | 9407.8253 | 7592.9806 | 4629.021 | NORMAL
324.817 | 0.45 | 299.814 | 0.5 | 1 | 106868.78 | 9369.197 | 7627.5476 | 4590.723 | NORMAL
324.817 | 0.45 | 299.814 | 0.5 | 2 | 57226.51 | 10018.8159 | 7385.8411 | 7064.312 | NORMAL
324.817 | 0.45 | 299.814 | 0.5 | 2 | 79289.74 | 12271.864 | 8527.0065 | 6392.04 | NORMAL
324.817 | 0.45 | 299.814 | 0.5 | 2 | 101352.97 | 12412.6026 | 8954.0791 | 6024.962 | NORMAL
324.817 | 0.45 | 299.814 | 0.5 | 2 | 106868.78 | 12361.3423 | 8946.7564 | 5954.7399 | NORMAL
324.817 | 0.45 | 299.814 | 0.8 | 1 | 57226.51 | 8861.4009 | 8852.8231 | 5586.712 | NORMAL
324.817 | 0.45 | 299.814 | 0.8 | 1 | 79289.74 | 9864.3611 | 9487.3353 | 4837.53 | NORMAL
324.817 | 0.45 | 299.814 | 0.8 | 1 | 101352.97 | 10159.2614 | 9669.5241 | 4626.548 | NORMAL
324.817 | 0.45 | 299.814 | 0.8 | 1 | 106868.78 | 10134.6131 | 9863.3703 | 4588.494 | NORMAL
324.817 | 0.45 | 299.814 | 0.8 | 2 | 57226.51 | 10083.4994 | 9774.5007 | 7047.269 | NORMAL
324.817 | 0.45 | 299.814 | 0.8 | 2 | 79289.74 | 13236.8992 | 10912.9233 | 6501.469 | NORMAL
324.817 | 0.45 | 299.814 | 0.8 | 2 | 101352.97 | 13597.1571 | 11293.5403 | 6113.942 | NORMAL
324.817 | 0.45 | 299.814 | 0.8 | 2 | 106868.78 | 13563.8335 | 11501.8731 | 6042.635 | NORMAL
324.817 | 0.45 | 299.814 | 1.11 | 1 | 57226.51 | 9660.6975 | 9650.1191 | 5674.77 | NORMAL
324.817 | 0.45 | 299.814 | 1.11 | 1 | 79289.74 | 10185.7855 | 10175.2024 | 4845.128 | NORMAL
324.817 | 0.45 | 299.814 | 1.11 | 1 | 101352.97 | 10549.6483 | 10538.6872 | 4628.19 | NORMAL
324.817 | 0.45 | 299.814 | 1.11 | 1 | 106868.78 | 10548.1536 | 10537.2046 | 4583.909 | NORMAL
324.817 | 0.45 | 299.814 | 1.11 | 2 | 57226.51 | 10196.6882 | 10185.7471 | 7034.89 | NORMAL
324.817 | 0.45 | 299.814 | 1.11 | 2 | 79289.74 | 13729.66 | 12771.7554 | 6550.993 | NORMAL
324.817 | 0.45 | 299.814 | 1.11 | 2 | 101352.97 | 14192.7022 | 13062.878 | 6161.025 | NORMAL
324.817 | 0.45 | 299.814 | 1.11 | 2 | 106868.78 | 14179.7186 | 13304.1919 | 6086.913 | NORMAL
324.817 | 0.45 | 299.814 | 1.42 | 1 | 57226.51 | 9879.0152 | 9867.4272 | 5629.5 | NORMAL
324.817 | 0.45 | 299.814 | 1.42 | 1 | 79289.74 | 10876.7292 | 10840.2378 | 4863.61 | NORMAL
324.817 | 0.45 | 299.814 | 1.42 | 1 | 101352.97 | 11218.8453 | 11206.0333 | 4622.143 | NORMAL
324.817 | 0.45 | 299.814 | 1.42 | 1 | 106868.78 | 11272.3329 | 11259.4825 | 4584.623 | NORMAL
324.817 | 0.45 | 299.814 | 1.42 | 2 | 57226.51 | 10277.5498 | 10265.6176 | 7020.9 | NORMAL
324.817 | 0.45 | 299.814 | 1.42 | 2 | 79289.74 | 14044.5193 | 14029.9411 | 6590.58 | NORMAL
324.817 | 0.45 | 299.814 | 1.42 | 2 | 101352.97 | 14586.0199 | 14570.938 | 6185.934 | NORMAL
324.817 | 0.45 | 299.814 | 1.42 | 2 | 106868.78 | 14577.0809 | 14562.1394 | 6115.36 | NORMAL
324.817 | 0.45 | 302.591 | 0.5 | 1 | 57226.51 | 9407.6495 | 7360.2345 | 5713.044 | NORMAL
324.817 | 0.45 | 302.591 | 0.5 | 1 | 79289.74 | 10003.0188 | 7625.5313 | 4840.877 | NORMAL
324.817 | 0.45 | 302.591 | 0.5 | 1 | 101352.97 | 10180.2755 | 7907.6104 | 4625.085 | NORMAL
324.817 | 0.45 | 302.591 | 0.5 | 1 | 106868.78 | 10128.3705 | 7874.1699 | 4588.282 | NORMAL
324.817 | 0.45 | 302.591 | 0.5 | 2 | 57226.51 | 10156.3306 | 7461.7342 | 7052.869 | NORMAL
324.817 | 0.45 | 302.591 | 0.5 | 2 | 79289.74 | 13179.748 | 8724.4001 | 6491.962 | NORMAL
324.817 | 0.45 | 302.591 | 0.5 | 2 | 101352.97 | 13331.1547 | 9195.2573 | 6096.467 | NORMAL
324.817 | 0.45 | 302.591 | 0.5 | 2 | 106868.78 | 13268.1125 | 9175.0458 | 6021.4 | NORMAL
324.817 | 0.45 | 302.591 | 0.8 | 1 | 57226.51 | 9697.2743 | 9686.5297 | 5664.621 | NORMAL
324.817 | 0.45 | 302.591 | 0.8 | 1 | 79289.74 | 10621.7468 | 9940.6379 | 4856.707 | NORMAL
324.817 | 0.45 | 302.591 | 0.8 | 1 | 101352.97 | 10960.4044 | 10119.6209 | 4625.257 | NORMAL
324.817 | 0.45 | 302.591 | 0.8 | 1 | 106868.78 | 10930.041 | 10333.0313 | 4583.186 | NORMAL
324.817 | 0.45 | 302.591 | 0.8 | 2 | 57226.51 | 10214.7128 | 10038.8358 | 7033.266 | NORMAL
324.817 | 0.45 | 302.591 | 0.8 | 2 | 79289.74 | 14174.0328 | 11346.0723 | 6597.942 | NORMAL
324.817 | 0.45 | 302.591 | 0.8 | 2 | 101352.97 | 14545.3986 | 11712.5659 | 6190.266 | NORMAL
324.817 | 0.45 | 302.591 | 0.8 | 2 | 106868.78 | 14512.1923 | 11938.9919 | 6110.846 | NORMAL
324.817 | 0.45 | 302.591 | 1.11 | 1 | 57226.51 | 10016.9695 | 10001.5233 | 5594.24 | NORMAL
324.817 | 0.45 | 302.591 | 1.11 | 1 | 79289.74 | 10941.9988 | 10928.9778 | 4864.974 | NORMAL
324.817 | 0.45 | 302.591 | 1.11 | 1 | 101352.97 | 11362.4267 | 11348.9168 | 4622.291 | NORMAL
324.817 | 0.45 | 302.591 | 1.11 | 1 | 106868.78 | 11346.483 | 11333.1055 | 4581.495 | NORMAL
324.817 | 0.45 | 302.591 | 1.11 | 2 | 57226.51 | 10365.0059 | 10352.1325 | 7018.83 | NORMAL
324.817 | 0.45 | 302.591 | 1.11 | 2 | 79289.74 | 14673.8277 | 13307.2541 | 6650.695 | NORMAL
324.817 | 0.45 | 302.591 | 1.11 | 2 | 101352.97 | 15159.8769 | 13608.976 | 6236.552 | NORMAL
324.817 | 0.45 | 302.591 | 1.11 | 2 | 106868.78 | 15142.4384 | 13883.481 | 6156.43 | NORMAL
324.817 | 0.45 | 302.591 | 1.42 | 1 | 57226.51 | 10194.49 | 10180.7784 | 5548.28 | NORMAL
324.817 | 0.45 | 302.591 | 1.42 | 1 | 79289.74 | 11627.1395 | 11611.9545 | 4884.2 | NORMAL
324.817 | 0.45 | 302.591 | 1.42 | 1 | 101352.97 | 11998.5053 | 11969.5049 | 4626.862 | NORMAL
324.817 | 0.45 | 302.591 | 1.42 | 1 | 106868.78 | 12064.2145 | 12048.5914 | 4582.091 | NORMAL
324.817 | 0.45 | 302.591 | 1.42 | 2 | 57226.51 | 10442.8781 | 10389.3061 | 6999.53 | NORMAL
324.817 | 0.45 | 302.591 | 1.42 | 2 | 79289.74 | 14997.0985 | 14914.3145 | 6686.53 | NORMAL
324.817 | 0.45 | 302.591 | 1.42 | 2 | 101352.97 | 15552.2861 | 15195.3144 | 6264.787 | NORMAL
324.817 | 0.45 | 302.591 | 1.42 | 2 | 106868.78 | 15546.102 | 15527.8042 | 6185.727 | NORMAL
324.817 | 0.45 | 305.368 | 0.5 | 1 | 57226.51 | 9870.9261 | 7397.1931 | 5631.201 | NORMAL
324.817 | 0.45 | 305.368 | 0.5 | 1 | 79289.74 | 10791.6471 | 7904.6225 | 4859.896 | NORMAL
324.817 | 0.45 | 305.368 | 0.5 | 1 | 101352.97 | 10997.4795 | 8211.554 | 4623.019 | NORMAL
324.817 | 0.45 | 305.368 | 0.5 | 1 | 106868.78 | 10932.0047 | 8093.4113 | 4583.729 | NORMAL
324.817 | 0.45 | 305.368 | 0.5 | 2 | 57226.51 | 10327.0516 | 7426.6269 | 7042.545 | NORMAL
324.817 | 0.45 | 305.368 | 0.5 | 2 | 79289.74 | 14148.3587 | 8956.4912 | 6594.033 | NORMAL
324.817 | 0.45 | 305.368 | 0.5 | 2 | 101352.97 | 14301.2016 | 9436.462 | 6171.959 | NORMAL
324.817 | 0.45 | 305.368 | 0.5 | 2 | 106868.78 | 14230.2755 | 9392.9779 | 6090.537 | NORMAL
324.817 | 0.45 | 305.368 | 0.8 | 1 | 57226.51 | 10051.7878 | 10039.0723 | 5585.873 | NORMAL
324.817 | 0.45 | 305.368 | 0.8 | 1 | 79289.74 | 11415.3283 | 10350.4037 | 4877.554 | NORMAL
324.817 | 0.45 | 305.368 | 0.8 | 1 | 101352.97 | 11794.3435 | 10562.6012 | 4625.231 | NORMAL
324.817 | 0.45 | 305.368 | 0.8 | 1 | 106868.78 | 11755.422 | 10779.2165 | 4581.749 | NORMAL
324.817 | 0.45 | 305.368 | 0.8 | 2 | 57226.51 | 10355.6858 | 10231.6351 | 7010.257 | NORMAL
324.817 | 0.45 | 305.368 | 0.8 | 2 | 79289.74 | 15166.4713 | 11722.742 | 6701.638 | NORMAL
324.817 | 0.45 | 305.368 | 0.8 | 2 | 101352.97 | 15545.721 | 12131.5387 | 6267.986 | NORMAL
324.817 | 0.45 | 305.368 | 0.8 | 2 | 106868.78 | 15504.1325 | 12354.3594 | 6182.907 | NORMAL
324.817 | 0.45 | 305.368 | 1.11 | 1 | 57226.51 | 10284.7304 | 10270.0335 | 5513.71 | NORMAL
324.817 | 0.45 | 305.368 | 1.11 | 1 | 79289.74 | 11754.1325 | 11738.2879 | 4885.185 | NORMAL
324.817 | 0.45 | 305.368 | 1.11 | 1 | 101352.97 | 12195.6038 | 12179.1519 | 4626.276 | NORMAL
324.817 | 0.45 | 305.368 | 1.11 | 1 | 106868.78 | 12167.7902 | 12151.5096 | 4584.109 | NORMAL
324.817 | 0.45 | 305.368 | 1.11 | 2 | 57226.51 | 10491.4127 | 10438.431 | 6991.42 | NORMAL
324.817 | 0.45 | 305.368 | 1.11 | 2 | 79289.74 | 15677.6377 | 13821.7974 | 6751.201 | NORMAL
324.817 | 0.45 | 305.368 | 1.11 | 2 | 101352.97 | 16168.7573 | 14134.5498 | 6315.638 | NORMAL
324.817 | 0.45 | 305.368 | 1.11 | 2 | 106868.78 | 16146.6882 | 14443.0834 | 6229.543 | NORMAL
324.817 | 0.45 | 305.368 | 1.42 | 1 | 57226.51 | 10410.7268 | 10394.8401 | 5467.51 | NORMAL
324.817 | 0.45 | 305.368 | 1.42 | 1 | 79289.74 | 12391.5006 | 12319.1466 | 4907.63 | NORMAL
324.817 | 0.45 | 305.368 | 1.42 | 1 | 101352.97 | 12457.796 | 12440.1558 | 4632.994 | NORMAL
324.817 | 0.45 | 305.368 | 1.42 | 1 | 106868.78 | 12430.6858 | 12413.0094 | 4585.206 | NORMAL
324.817 | 0.45 | 305.368 | 1.42 | 2 | 57226.51 | 11071.1899 | 10985.4989 | 6983.3 | NORMAL
324.817 | 0.45 | 305.368 | 1.42 | 2 | 79289.74 | 16018.6108 | 15647.2834 | 6782.8 | NORMAL
324.817 | 0.45 | 305.368 | 1.42 | 2 | 101352.97 | 16569.871 | 15840.1671 | 6346.346 | NORMAL
324.817 | 0.45 | 305.368 | 1.42 | 2 | 106868.78 | 16563.0715 | 16204.4976 | 6258.784 | NORMAL
324.817 | 0.55 | 288.706 | 0.5 | 1 | 57226.51 | 6334.9062 | 5117.1155 | 5347.689 | NORMAL
324.817 | 0.55 | 288.706 | 0.5 | 1 | 79289.74 | 6915.0059 | 5514.973 | 4778.247 | NORMAL
324.817 | 0.55 | 288.706 | 0.5 | 1 | 101352.97 | 6961.2251 | 5716.2309 | 4666.037 | NORMAL
324.817 | 0.55 | 288.706 | 0.5 | 1 | 106868.78 | 6915.4748 | 5709.1601 | 4652.8541 | NORMAL
324.817 | 0.55 | 288.706 | 0.5 | 2 | 57226.51 | 9027.9308 | 6193.5939 | 7061.552 | NORMAL
324.817 | 0.55 | 288.706 | 0.5 | 2 | 79289.74 | 9521.9812 | 6796.5617 | 6083.613 | NORMAL
324.817 | 0.55 | 288.706 | 0.5 | 2 | 101352.97 | 9578.4584 | 7177.3592 | 5826.692 | NORMAL
324.817 | 0.55 | 288.706 | 0.5 | 2 | 106868.78 | 9558.4701 | 7233.5443 | 5761.7237 | NORMAL
324.817 | 0.55 | 288.706 | 0.8 | 1 | 57226.51 | 6699.7362 | 6581.4189 | 5382.53 | NORMAL
324.817 | 0.55 | 288.706 | 0.8 | 1 | 79289.74 | 7439.2732 | 6846.9582 | 4790.345 | NORMAL
324.817 | 0.55 | 288.706 | 0.8 | 1 | 101352.97 | 7602.8136 | 7008.1823 | 4646.391 | NORMAL
324.817 | 0.55 | 288.706 | 0.8 | 1 | 106868.78 | 7571.1899 | 7155.2742 | 4625.879 | NORMAL
324.817 | 0.55 | 288.706 | 0.8 | 2 | 57226.51 | 9478.4584 | 7802.5437 | 7111.014 | NORMAL
324.817 | 0.55 | 288.706 | 0.8 | 2 | 79289.74 | 10375.381 | 8382.7683 | 6185.548 | NORMAL
324.817 | 0.55 | 288.706 | 0.8 | 2 | 101352.97 | 10592.4678 | 8735.4281 | 5883.933 | NORMAL
324.817 | 0.55 | 288.706 | 0.8 | 2 | 106868.78 | 10566.1196 | 8916.1143 | 5832.627 | NORMAL
324.817 | 0.55 | 288.706 | 1.11 | 1 | 57226.51 | 6880.6858 | 6876.7845 | 5409.09 | NORMAL
324.817 | 0.55 | 288.706 | 1.11 | 1 | 79289.74 | 7713.687 | 7709.3596 | 4794.149 | NORMAL
324.817 | 0.55 | 288.706 | 1.11 | 1 | 101352.97 | 7929.5721 | 7925.1474 | 4640.106 | NORMAL
324.817 | 0.55 | 288.706 | 1.11 | 1 | 106868.78 | 7911.4889 | 7907.1059 | 4615.473 | NORMAL
324.817 | 0.55 | 288.706 | 1.11 | 2 | 57226.51 | 9606.6823 | 8981.979 | 7105.02 | NORMAL
324.817 | 0.55 | 288.706 | 1.11 | 2 | 79289.74 | 10801.8171 | 9530.4864 | 6232.442 | NORMAL
324.817 | 0.55 | 288.706 | 1.11 | 2 | 101352.97 | 11106.6237 | 9866.447 | 5920.667 | NORMAL
324.817 | 0.55 | 288.706 | 1.11 | 2 | 106868.78 | 11090.7679 | 10076.6502 | 5867.022 | NORMAL
324.817 | 0.55 | 288.706 | 1.42 | 1 | 57226.51 | 7257.2685 | 7221.0039 | 5441.06 | NORMAL
324.817 | 0.55 | 288.706 | 1.42 | 1 | 79289.74 | 7918.9039 | 7914.1525 | 4796 | NORMAL
324.817 | 0.55 | 288.706 | 1.42 | 1 | 101352.97 | 8148.5932 | 8143.7366 | 4636.181 | NORMAL
324.817 | 0.55 | 288.706 | 1.42 | 1 | 106868.78 | 8284.1735 | 8279.1616 | 4606.82 | NORMAL
324.817 | 0.55 | 288.706 | 1.42 | 2 | 57226.51 | 9693.8453 | 9688.3973 | 7099.15 | NORMAL
324.817 | 0.55 | 288.706 | 1.42 | 2 | 79289.74 | 11066.7644 | 10537.6181 | 6266.62 | NORMAL
324.817 | 0.55 | 288.706 | 1.42 | 2 | 101352.97 | 11429.8652 | 10842.713 | 5946.173 | NORMAL
324.817 | 0.55 | 288.706 | 1.42 | 2 | 106868.78 | 11426.0258 | 11061.5927 | 5888.33 | NORMAL
324.817 | 0.55 | 291.483 | 0.5 | 1 | 57226.51 | 6959.3494 | 5381.7066 | 5409.637 | NORMAL
324.817 | 0.55 | 291.483 | 0.5 | 1 | 79289.74 | 7605.891 | 5790.3192 | 4787.064 | NORMAL
324.817 | 0.55 | 291.483 | 0.5 | 1 | 101352.97 | 7672.8019 | 6034.1139 | 4645.236 | NORMAL
324.817 | 0.55 | 291.483 | 0.5 | 1 | 106868.78 | 7626.0551 | 6010.2465 | 4623.6832 | NORMAL
324.817 | 0.55 | 291.483 | 0.5 | 2 | 57226.51 | 9562.6905 | 6288.4731 | 7106.329 | NORMAL
324.817 | 0.55 | 291.483 | 0.5 | 2 | 79289.74 | 10322.0106 | 7035.6888 | 6183.001 | NORMAL
324.817 | 0.55 | 291.483 | 0.5 | 2 | 101352.97 | 10397.0985 | 7458.1091 | 5871.283 | NORMAL
324.817 | 0.55 | 291.483 | 0.5 | 2 | 106868.78 | 10338.5111 | 7479.2305 | 5817.3892 | NORMAL
324.817 | 0.55 | 291.483 | 0.8 | 1 | 57226.51 | 7336.6647 | 6971.1374 | 5444.536 | NORMAL
324.817 | 0.55 | 291.483 | 0.8 | 1 | 79289.74 | 8150.381 | 7241.0593 | 4801.608 | NORMAL
324.817 | 0.55 | 291.483 | 0.8 | 1 | 101352.97 | 8340.7386 | 7445.2769 | 4635.328 | NORMAL
324.817 | 0.55 | 291.483 | 0.8 | 1 | 106868.78 | 8312.0164 | 7600.699 | 4606.086 | NORMAL
324.817 | 0.55 | 291.483 | 0.8 | 2 | 57226.51 | 9761.1958 | 7900.829 | 7093.718 | NORMAL
324.817 | 0.55 | 291.483 | 0.8 | 2 | 79289.74 | 11205.4513 | 8731.9152 | 6277.69 | NORMAL
324.817 | 0.55 | 291.483 | 0.8 | 2 | 101352.97 | 11448.0657 | 9127.1077 | 5947.965 | NORMAL
324.817 | 0.55 | 291.483 | 0.8 | 2 | 106868.78 | 11419.49 | 9316.2712 | 5887.554 | NORMAL
324.817 | 0.55 | 291.483 | 1.11 | 1 | 57226.51 | 7517.6729 | 7512.5233 | 5470.12 | NORMAL
324.817 | 0.55 | 291.483 | 1.11 | 1 | 79289.74 | 8432.8839 | 8403.9338 | 4806.264 | NORMAL
324.817 | 0.55 | 291.483 | 1.11 | 1 | 101352.97 | 8680.4513 | 8531.842 | 4631.539 | NORMAL
324.817 | 0.55 | 291.483 | 1.11 | 1 | 106868.78 | 8659.789 | 8653.9869 | 4601.739 | NORMAL
324.817 | 0.55 | 291.483 | 1.11 | 2 | 57226.51 | 9834.4959 | 9171.9459 | 7087.47 | NORMAL
324.817 | 0.55 | 291.483 | 1.11 | 2 | 79289.74 | 11649.5604 | 9995.2762 | 6325.551 | NORMAL
324.817 | 0.55 | 291.483 | 1.11 | 2 | 101352.97 | 11983.939 | 10342.2952 | 5988.99 | NORMAL
324.817 | 0.55 | 291.483 | 1.11 | 2 | 106868.78 | 11967.8195 | 10581.4792 | 5926.966 | NORMAL
324.817 | 0.55 | 291.483 | 1.42 | 1 | 57226.51 | 7888.8921 | 7882.9755 | 5501.35 | NORMAL
324.817 | 0.55 | 291.483 | 1.42 | 1 | 79289.74 | 8616.7937 | 8610.6499 | 4809.37 | NORMAL
324.817 | 0.55 | 291.483 | 1.42 | 1 | 101352.97 | 8899.5897 | 8893.2443 | 4629.401 | NORMAL
324.817 | 0.55 | 291.483 | 1.42 | 1 | 106868.78 | 8888.7749 | 8882.4728 | 4597.891 | NORMAL
324.817 | 0.55 | 291.483 | 1.42 | 2 | 57226.51 | 9887.8957 | 9881.0829 | 7083.39 | NORMAL
324.817 | 0.55 | 291.483 | 1.42 | 2 | 79289.74 | 11935.6682 | 11053.1569 | 6351.39 | NORMAL
324.817 | 0.55 | 291.483 | 1.42 | 2 | 101352.97 | 12322.2157 | 11354.7985 | 6015.336 | NORMAL
324.817 | 0.55 | 291.483 | 1.42 | 2 | 106868.78 | 12315.9437 | 11627.8889 | 5951.968 | NORMAL
324.817 | 0.55 | 294.26 | 0.5 | 1 | 57226.51 | 7621.2485 | 5541.4555 | 5471.266 | NORMAL
324.817 | 0.55 | 294.26 | 0.5 | 1 | 79289.74 | 8320.1641 | 6051.3968 | 4801.972 | NORMAL
324.817 | 0.55 | 294.26 | 0.5 | 1 | 101352.97 | 8409.7011 | 6307.8056 | 4633.008 | NORMAL
324.817 | 0.55 | 294.26 | 0.5 | 1 | 106868.78 | 8357.5615 | 6267.4608 | 4606.9531 | NORMAL
324.817 | 0.55 | 294.26 | 0.5 | 2 | 57226.51 | 9824.619 | 6272.7048 | 7088.975 | NORMAL
324.817 | 0.55 | 294.26 | 0.5 | 2 | 79289.74 | 11165.0645 | 7191.2729 | 6274.399 | NORMAL
324.817 | 0.55 | 294.26 | 0.5 | 2 | 101352.97 | 11246.1313 | 7663.7549 | 5931.398 | NORMAL
324.817 | 0.55 | 294.26 | 0.5 | 2 | 106868.78 | 11187.3095 | 7717.0397 | 5871.1973 | NORMAL
324.817 | 0.55 | 294.26 | 0.8 | 1 | 57226.51 | 8005.0117 | 7301.2591 | 5508.133 | NORMAL
324.817 | 0.55 | 294.26 | 0.8 | 1 | 79289.74 | 8889.5076 | 7643.7854 | 4815.349 | NORMAL
324.817 | 0.55 | 294.26 | 0.8 | 1 | 101352.97 | 9107.1219 | 7847.2609 | 4627.29 | NORMAL
324.817 | 0.55 | 294.26 | 0.8 | 1 | 106868.78 | 9072.5674 | 8036.8068 | 4595.248 | NORMAL
324.817 | 0.55 | 294.26 | 0.8 | 2 | 57226.51 | 9921.3658 | 8011.5922 | 7074.754 | NORMAL
324.817 | 0.55 | 294.26 | 0.8 | 2 | 79289.74 | 12080.422 | 9068.8091 | 6373.657 | NORMAL
324.817 | 0.55 | 294.26 | 0.8 | 2 | 101352.97 | 12345.7503 | 9499.9067 | 6017.917 | NORMAL
324.817 | 0.55 | 294.26 | 0.8 | 2 | 106868.78 | 12312.5146 | 9677.2918 | 5951.416 | NORMAL
324.817 | 0.55 | 294.26 | 1.11 | 1 | 57226.51 | 8206.6823 | 8200.0349 | 5525.96 | NORMAL
324.817 | 0.55 | 294.26 | 1.11 | 1 | 79289.74 | 9176.6706 | 8815.1098 | 4821.098 | NORMAL
324.817 | 0.55 | 294.26 | 1.11 | 1 | 101352.97 | 9448.9742 | 8986.5225 | 4630.948 | NORMAL
324.817 | 0.55 | 294.26 | 1.11 | 1 | 106868.78 | 9436.0492 | 9238.4489 | 4590.992 | NORMAL
324.817 | 0.55 | 294.26 | 1.11 | 2 | 57226.51 | 9974.4431 | 9314.0851 | 7067.78 | NORMAL
324.817 | 0.55 | 294.26 | 1.11 | 2 | 79289.74 | 12543.6108 | 10452.7288 | 6418.596 | NORMAL
324.817 | 0.55 | 294.26 | 1.11 | 2 | 101352.97 | 12904.1325 | 10816.8503 | 6060.461 | NORMAL
324.817 | 0.55 | 294.26 | 1.11 | 2 | 106868.78 | 12884.0856 | 11082.9548 | 5992.523 | NORMAL
324.817 | 0.55 | 294.26 | 1.42 | 1 | 57226.51 | 8329.1911 | 8322.1446 | 5542.97 | NORMAL
324.817 | 0.55 | 294.26 | 1.42 | 1 | 79289.74 | 9364.3904 | 9356.4681 | 4824.71 | NORMAL
324.817 | 0.55 | 294.26 | 1.42 | 1 | 101352.97 | 9677.1981 | 9669.0209 | 4628.943 | NORMAL
324.817 | 0.55 | 294.26 | 1.42 | 1 | 106868.78 | 9660.551 | 9652.4458 | 4594.607 | NORMAL
324.817 | 0.55 | 294.26 | 1.42 | 2 | 57226.51 | 10006.7409 | 9998.4954 | 7063.95 | NORMAL
324.817 | 0.55 | 294.26 | 1.42 | 2 | 79289.74 | 12823.1829 | 11539.9029 | 6458.35 | NORMAL
324.817 | 0.55 | 294.26 | 1.42 | 2 | 101352.97 | 13254.5428 | 11885.0437 | 6088.201 | NORMAL
324.817 | 0.55 | 294.26 | 1.42 | 2 | 106868.78 | 13245.8382 | 12190.4628 | 6018.592 | NORMAL
324.817 | 0.55 | 297.037 | 0.5 | 1 | 57226.51 | 8306.8875 | 5695.1605 | 5540.383 | NORMAL
324.817 | 0.55 | 297.037 | 0.5 | 1 | 79289.74 | 9075.5862 | 6234.4104 | 4816.715 | NORMAL
324.817 | 0.55 | 297.037 | 0.5 | 1 | 101352.97 | 9174.2966 | 6533.6221 | 4630.415 | NORMAL
324.817 | 0.55 | 297.037 | 0.5 | 1 | 106868.78 | 9124.3845 | 6495.7862 | 4594.4594 | NORMAL
324.817 | 0.55 | 297.037 | 0.5 | 2 | 57226.51 | 9981.4478 | 6235.8996 | 7067.74 | NORMAL
324.817 | 0.55 | 297.037 | 0.5 | 2 | 79289.74 | 12065.1231 | 7299.9786 | 6370.639 | NORMAL
324.817 | 0.55 | 297.037 | 0.5 | 2 | 101352.97 | 12145.3986 | 7832.1789 | 6004.579 | NORMAL
324.817 | 0.55 | 297.037 | 0.5 | 2 | 106868.78 | 12081.5944 | 7929.1383 | 5935.0753 | NORMAL
324.817 | 0.55 | 297.037 | 0.8 | 1 | 57226.51 | 8719.6952 | 7630.9715 | 5574.085 | NORMAL
324.817 | 0.55 | 297.037 | 0.8 | 1 | 79289.74 | 9662.8664 | 7976.2034 | 4830.098 | NORMAL
324.817 | 0.55 | 297.037 | 0.8 | 1 | 101352.97 | 9895.3107 | 8244.2385 | 4627.937 | NORMAL
324.817 | 0.55 | 297.037 | 0.8 | 1 | 106868.78 | 9856.1254 | 8436.2224 | 4592.662 | NORMAL
324.817 | 0.55 | 297.037 | 0.8 | 2 | 57226.51 | 10050.5276 | 8137.5001 | 7053.541 | NORMAL
324.817 | 0.55 | 297.037 | 0.8 | 2 | 79289.74 | 13003.4877 | 9378.2324 | 6478.052 | NORMAL
324.817 | 0.55 | 297.037 | 0.8 | 2 | 101352.97 | 13296.6002 | 9872.8985 | 6091.061 | NORMAL
324.817 | 0.55 | 297.037 | 0.8 | 2 | 106868.78 | 13255.5393 | 9952.5903 | 6019.093 | NORMAL
324.817 | 0.55 | 297.037 | 1.11 | 1 | 57226.51 | 9256.4771 | 9247.8131 | 5740.16 | NORMAL
324.817 | 0.55 | 297.037 | 1.11 | 1 | 79289.74 | 9949.3259 | 9308.659 | 4840.679 | NORMAL
324.817 | 0.55 | 297.037 | 1.11 | 1 | 101352.97 | 10262.2509 | 9501.8797 | 4626.013 | NORMAL
324.817 | 0.55 | 297.037 | 1.11 | 1 | 106868.78 | 10232.7081 | 9740.6581 | 4589.215 | NORMAL
324.817 | 0.55 | 297.037 | 1.11 | 2 | 57226.51 | 10128.2825 | 9542.4323 | 7046.53 | NORMAL
324.817 | 0.55 | 297.037 | 1.11 | 2 | 79289.74 | 13471.9226 | 10819.6109 | 6528.228 | NORMAL
324.817 | 0.55 | 297.037 | 1.11 | 2 | 101352.97 | 13871.3365 | 11293.0295 | 6135.889 | NORMAL
324.817 | 0.55 | 297.037 | 1.11 | 2 | 106868.78 | 13847.5674 | 11541.1443 | 6061.619 | NORMAL
324.817 | 0.55 | 297.037 | 1.42 | 1 | 57226.51 | 9356.5358 | 9347.3664 | 5722.82 | NORMAL
324.817 | 0.55 | 297.037 | 1.42 | 1 | 79289.74 | 10135.4044 | 10125.3704 | 4846.09 | NORMAL
324.817 | 0.55 | 297.037 | 1.42 | 1 | 101352.97 | 10496.102 | 10485.7318 | 4625.078 | NORMAL
324.817 | 0.55 | 297.037 | 1.42 | 1 | 106868.78 | 10474.5018 | 10464.2368 | 4587.368 | NORMAL
324.817 | 0.55 | 297.037 | 1.42 | 2 | 57226.51 | 10163.2474 | 10153.3687 | 7041.3 | NORMAL
324.817 | 0.55 | 297.037 | 1.42 | 2 | 79289.74 | 13768.8746 | 12043.7172 | 6559.49 | NORMAL
324.817 | 0.55 | 297.037 | 1.42 | 2 | 101352.97 | 14232.1512 | 12430.1616 | 6164.121 | NORMAL
324.817 | 0.55 | 297.037 | 1.42 | 2 | 106868.78 | 14220.2227 | 12716.4911 | 6088.539 | NORMAL
324.817 | 0.55 | 299.814 | 0.5 | 1 | 57226.51 | 9312.163 | 5760.8765 | 5742.941 | NORMAL
324.817 | 0.55 | 299.814 | 0.5 | 1 | 79289.74 | 9851.2309 | 6386.1097 | 4838.717 | NORMAL
324.817 | 0.55 | 299.814 | 0.5 | 1 | 101352.97 | 9980.4807 | 6741.1759 | 4625.458 | NORMAL
324.817 | 0.55 | 299.814 | 0.5 | 1 | 106868.78 | 9912.7491 | 6684.7813 | 4591.922 | NORMAL
324.817 | 0.55 | 299.814 | 0.5 | 2 | 57226.51 | 10117.5264 | 6187.0293 | 7044.734 | NORMAL
324.817 | 0.55 | 299.814 | 0.5 | 2 | 79289.74 | 13013.5991 | 7373.7265 | 6472.787 | NORMAL
324.817 | 0.55 | 299.814 | 0.5 | 2 | 101352.97 | 13101.2309 | 7959.8494 | 6078.859 | NORMAL
324.817 | 0.55 | 299.814 | 0.5 | 2 | 106868.78 | 13028.2239 | 8116.7268 | 6002.8489 | NORMAL
324.817 | 0.55 | 299.814 | 0.8 | 1 | 57226.51 | 9593.2591 | 8028.4067 | 5692.11 | NORMAL
324.817 | 0.55 | 299.814 | 0.8 | 1 | 79289.74 | 10453.5756 | 8312.1607 | 4852.768 | NORMAL
324.817 | 0.55 | 299.814 | 0.8 | 1 | 101352.97 | 10733.6166 | 8604.6467 | 4624.415 | NORMAL
324.817 | 0.55 | 299.814 | 0.8 | 1 | 106868.78 | 10691.6471 | 8846.1512 | 4583.919 | NORMAL
324.817 | 0.55 | 299.814 | 0.8 | 2 | 57226.51 | 10229.6893 | 8238.1325 | 7030.614 | NORMAL
324.817 | 0.55 | 299.814 | 0.8 | 2 | 79289.74 | 13976.2309 | 9649.3576 | 6581.753 | NORMAL
324.817 | 0.55 | 299.814 | 0.8 | 2 | 101352.97 | 14291.061 | 10198.7871 | 6168.201 | NORMAL
324.817 | 0.55 | 299.814 | 0.8 | 2 | 106868.78 | 14243.7573 | 10177.9195 | 6090.044 | NORMAL
324.817 | 0.55 | 299.814 | 1.11 | 1 | 57226.51 | 9739.4197 | 9658.9916 | 5652.45 | NORMAL
324.817 | 0.55 | 299.814 | 1.11 | 1 | 79289.74 | 10754.0739 | 9756.0635 | 4859.937 | NORMAL
324.817 | 0.55 | 299.814 | 1.11 | 1 | 101352.97 | 11105.3634 | 9997.348 | 4624.297 | NORMAL
324.817 | 0.55 | 299.814 | 1.11 | 1 | 106868.78 | 11070.7796 | 10244.512 | 4585.189 | NORMAL
324.817 | 0.55 | 299.814 | 1.11 | 2 | 57226.51 | 10255.1876 | 9743.2896 | 7025.87 | NORMAL
324.817 | 0.55 | 299.814 | 1.11 | 2 | 79289.74 | 14457.3271 | 11218.8135 | 6631.833 | NORMAL
324.817 | 0.55 | 299.814 | 1.11 | 2 | 101352.97 | 14879.8945 | 11702.0698 | 6214.433 | NORMAL
324.817 | 0.55 | 299.814 | 1.11 | 2 | 106868.78 | 14851.6413 | 12020.9333 | 6133.912 | NORMAL
324.817 | 0.55 | 299.814 | 1.42 | 1 | 57226.51 | 9832.4443 | 9821.314 | 5641.02 | NORMAL
324.817 | 0.55 | 299.814 | 1.42 | 1 | 79289.74 | 10943.2298 | 10930.7217 | 4865.11 | NORMAL
324.817 | 0.55 | 299.814 | 1.42 | 1 | 101352.97 | 11351.0844 | 11114.1078 | 4622.644 | NORMAL
324.817 | 0.55 | 299.814 | 1.42 | 1 | 106868.78 | 11325.9672 | 11313.1462 | 4581.921 | NORMAL
324.817 | 0.55 | 299.814 | 1.42 | 2 | 57226.51 | 10255.6565 | 10244.0574 | 7021.97 | NORMAL
324.817 | 0.55 | 299.814 | 1.42 | 2 | 79289.74 | 14763.5405 | 12570.4756 | 6662.54 | NORMAL
324.817 | 0.55 | 299.814 | 1.42 | 2 | 101352.97 | 15249.5604 | 12971.9928 | 6243.394 | NORMAL
324.817 | 0.55 | 299.814 | 1.42 | 2 | 106868.78 | 15234.1442 | 13326.22 | 6161.558 | NORMAL
324.817 | 0.55 | 302.591 | 0.5 | 1 | 57226.51 | 9812.8664 | 5759.0535 | 5663.496 | NORMAL
324.817 | 0.55 | 302.591 | 0.5 | 1 | 79289.74 | 10681.8875 | 6586.2382 | 4857.224 | NORMAL
324.817 | 0.55 | 302.591 | 0.5 | 1 | 101352.97 | 10829.8066 | 6954.5552 | 4623.295 | NORMAL
324.817 | 0.55 | 302.591 | 0.5 | 1 | 106868.78 | 10761.7233 | 6871.4895 | 4583.623 | NORMAL
324.817 | 0.55 | 302.591 | 0.5 | 2 | 57226.51 | 10266.1782 | 6155.1795 | 7021.341 | NORMAL
324.817 | 0.55 | 302.591 | 0.5 | 2 | 79289.74 | 14017.7902 | 7404.1407 | 6581.959 | NORMAL
324.817 | 0.55 | 302.591 | 0.5 | 2 | 101352.97 | 14116.1196 | 8052.3428 | 6157.603 | NORMAL
324.817 | 0.55 | 302.591 | 0.5 | 2 | 106868.78 | 14033.265 | 8293.0842 | 6075.007 | NORMAL
324.817 | 0.55 | 302.591 | 0.8 | 1 | 57226.51 | 10057.2685 | 8323.4155 | 5622.009 | NORMAL
324.817 | 0.55 | 302.591 | 0.8 | 1 | 79289.74 | 11294.0211 | 8616.0845 | 4873.193 | NORMAL
324.817 | 0.55 | 302.591 | 0.8 | 1 | 101352.97 | 11606.5358 | 8943.242 | 4623.963 | NORMAL
324.817 | 0.55 | 302.591 | 0.8 | 1 | 106868.78 | 11556.3892 | 9224.6566 | 4581.368 | NORMAL
324.817 | 0.55 | 302.591 | 0.8 | 2 | 57226.51 | 10331.7116 | 8373.222 | 7009.761 | NORMAL
324.817 | 0.55 | 302.591 | 0.8 | 2 | 79289.74 | 15008.6753 | 9963.8393 | 6687.937 | NORMAL
324.817 | 0.55 | 302.591 | 0.8 | 2 | 101352.97 | 15337.0164 | 10490.0284 | 6249.605 | NORMAL
324.817 | 0.55 | 302.591 | 0.8 | 2 | 106868.78 | 15283.3822 | 10401.3961 | 6165.008 | NORMAL
324.817 | 0.55 | 302.591 | 1.11 | 1 | 57226.51 | 10106.2134 | 9988.2536 | 5573.04 | NORMAL
324.817 | 0.55 | 302.591 | 1.11 | 1 | 79289.74 | 11590.1231 | 10095.1943 | 4882.458 | NORMAL
324.817 | 0.55 | 302.591 | 1.11 | 1 | 101352.97 | 11987.3095 | 10428.3 | 4626.843 | NORMAL
324.817 | 0.55 | 302.591 | 1.11 | 1 | 106868.78 | 11945.9554 | 10720.4079 | 4583.007 | NORMAL
324.817 | 0.55 | 302.591 | 1.11 | 2 | 57226.51 | 10388.5991 | 10040.1239 | 7004.42 | NORMAL
324.817 | 0.55 | 302.591 | 1.11 | 2 | 79289.74 | 15508.3822 | 11631.2556 | 6735.552 | NORMAL
324.817 | 0.55 | 302.591 | 1.11 | 2 | 101352.97 | 15936.313 | 12099.2791 | 6296.884 | NORMAL
324.817 | 0.55 | 302.591 | 1.11 | 2 | 106868.78 | 15898.8277 | 12413.9 | 6210.923 | NORMAL
324.817 | 0.55 | 302.591 | 1.42 | 1 | 57226.51 | 10659.9355 | 10646.2055 | 5703.3 | NORMAL
324.817 | 0.55 | 302.591 | 1.42 | 1 | 79289.74 | 11785.8441 | 11498.3638 | 4886.41 | NORMAL
324.817 | 0.55 | 302.591 | 1.42 | 1 | 101352.97 | 12230.5686 | 11694.7351 | 4628.154 | NORMAL
324.817 | 0.55 | 302.591 | 1.42 | 1 | 106868.78 | 12195.5158 | 11929.7024 | 4584.118 | NORMAL
324.817 | 0.55 | 302.591 | 1.42 | 2 | 57226.51 | 10404.5721 | 10391.1398 | 7000.89 | NORMAL
324.817 | 0.55 | 302.591 | 1.42 | 2 | 79289.74 | 15823.2708 | 13040.1473 | 6766.1 | NORMAL
324.817 | 0.55 | 302.591 | 1.42 | 2 | 101352.97 | 16311.1372 | 13499.1134 | 6326.53 | NORMAL
324.817 | 0.55 | 302.591 | 1.42 | 2 | 106868.78 | 16292.8781 | 13868.2697 | 6238.446 | NORMAL
324.817 | 0.55 | 305.368 | 0.5 | 1 | 57226.51 | 10206.1254 | 5761.4497 | 5573.493 | NORMAL
324.817 | 0.55 | 305.368 | 0.5 | 1 | 79289.74 | 11547.8019 | 6771.0536 | 4880.013 | NORMAL
324.817 | 0.55 | 305.368 | 0.5 | 1 | 101352.97 | 11716.9988 | 7125.2827 | 4627.265 | NORMAL
324.817 | 0.55 | 305.368 | 0.5 | 1 | 106868.78 | 11646.2778 | 7055.6994 | 4581.333 | NORMAL
324.817 | 0.55 | 305.368 | 0.5 | 2 | 57226.51 | 10406.3306 | 6121.7009 | 6999.612 | NORMAL
324.817 | 0.55 | 305.368 | 0.5 | 2 | 79289.74 | 15088.1887 | 7373.3564 | 6694.882 | NORMAL
324.817 | 0.55 | 305.368 | 0.5 | 2 | 101352.97 | 15189.5369 | 8090.0841 | 6241.014 | NORMAL
324.817 | 0.55 | 305.368 | 0.5 | 2 | 106868.78 | 15097.6553 | 8403.0379 | 6151.705 | NORMAL
324.817 | 0.55 | 305.368 | 0.8 | 1 | 57226.51 | 10325.8792 | 8492.7775 | 5529.071 | NORMAL
324.817 | 0.55 | 305.368 | 0.8 | 1 | 79289.74 | 12164.3318 | 8949.7368 | 4897.758 | NORMAL
324.817 | 0.55 | 305.368 | 0.8 | 1 | 101352.97 | 12506.3306 | 9272.3811 | 4632.816 | NORMAL
324.817 | 0.55 | 305.368 | 0.8 | 1 | 106868.78 | 12454.279 | 9531.7828 | 4584.623 | NORMAL
324.817 | 0.55 | 305.368 | 0.8 | 2 | 57226.51 | 10528.1653 | 8660.0371 | 6992.977 | NORMAL
324.817 | 0.55 | 305.368 | 0.8 | 2 | 79289.74 | 16116.9109 | 10311.4545 | 6795.877 | NORMAL
324.817 | 0.55 | 305.368 | 0.8 | 2 | 101352.97 | 16427.5498 | 10724.9395 | 6336.361 | NORMAL
324.817 | 0.55 | 305.368 | 0.8 | 2 | 106868.78 | 16367.2626 | 10582.4991 | 6245.062 | NORMAL
324.817 | 0.55 | 305.368 | 1.11 | 1 | 57226.51 | 10378.2532 | 10099.6179 | 5498.23 | NORMAL
324.817 | 0.55 | 305.368 | 1.11 | 1 | 79289.74 | 12469.871 | 10506.3527 | 4906.884 | NORMAL
324.817 | 0.55 | 305.368 | 1.11 | 1 | 101352.97 | 12894.7245 | 10812.3168 | 4635.506 | NORMAL
324.817 | 0.55 | 305.368 | 1.11 | 1 | 106868.78 | 12848.4467 | 11132.0998 | 4587.801 | NORMAL
324.817 | 0.55 | 305.368 | 1.11 | 2 | 57226.51 | 11039.6542 | 10521.7619 | 6988.89 | NORMAL
324.817 | 0.55 | 305.368 | 1.11 | 2 | 79289.74 | 16630.803 | 12076.9898 | 6841.296 | NORMAL
324.817 | 0.55 | 305.368 | 1.11 | 2 | 101352.97 | 17038.306 | 12489.4191 | 6383.285 | NORMAL
324.817 | 0.55 | 305.368 | 1.11 | 2 | 106868.78 | 16995.5451 | 12864.7099 | 6290.995 | NORMAL
324.817 | 0.55 | 305.368 | 1.42 | 1 | 57226.51 | 10387.0164 | 10371.7994 | 5480.46 | NORMAL
324.817 | 0.55 | 305.368 | 1.42 | 1 | 79289.74 | 12657.0633 | 11987.087 | 4913.6 | NORMAL
324.817 | 0.55 | 305.368 | 1.42 | 1 | 101352.97 | 13140.5041 | 12241.2206 | 4637.862 | NORMAL
324.817 | 0.55 | 305.368 | 1.42 | 1 | 106868.78 | 13101.9343 | 12548.43 | 4589.634 | NORMAL
324.817 | 0.55 | 305.368 | 1.42 | 2 | 57226.51 | 11069.5193 | 11053.3689 | 6987.14 | NORMAL
324.817 | 0.55 | 305.368 | 1.42 | 2 | 79289.74 | 16961.6647 | 13426.6503 | 6870.18 | NORMAL
324.817 | 0.55 | 305.368 | 1.42 | 2 | 101352.97 | 17422.6846 | 13945.0994 | 6411.704 | NORMAL
324.817 | 0.55 | 305.368 | 1.42 | 2 | 106868.78 | 17389.4783 | 14339.2769 | 6319.762 | NORMAL
324.817 | 0.65 | 288.706 | 0.5 | 1 | 57226.51 | 6693.2591 | 4382.6791 | 5385.399 | NORMAL
324.817 | 0.65 | 288.706 | 0.5 | 1 | 79289.74 | 7261.0492 | 4917.807 | 4788.164 | NORMAL
324.817 | 0.65 | 288.706 | 0.5 | 1 | 101352.97 | 7291.7644 | 5192.006 | 4654.033 | NORMAL
324.817 | 0.65 | 288.706 | 0.5 | 1 | 106868.78 | 7234.4666 | 5177.0928 | 4638.1746 | NORMAL
324.817 | 0.65 | 288.706 | 0.5 | 2 | 57226.51 | 9428.5463 | 5249.7014 | 7111.182 | NORMAL
324.817 | 0.65 | 288.706 | 0.5 | 2 | 79289.74 | 9952.0809 | 6090.2058 | 6137.249 | NORMAL
324.817 | 0.65 | 288.706 | 0.5 | 2 | 101352.97 | 9951.3482 | 6577.7416 | 5839.755 | NORMAL
324.817 | 0.65 | 288.706 | 0.5 | 2 | 106868.78 | 9905.4807 | 6693.6484 | 5785.2898 | NORMAL
324.817 | 0.65 | 288.706 | 0.8 | 1 | 57226.51 | 7042.1161 | 5625.4324 | 5420.698 | NORMAL
324.817 | 0.65 | 288.706 | 0.8 | 1 | 79289.74 | 7788.5991 | 6095.529 | 4795.552 | NORMAL
324.817 | 0.65 | 288.706 | 0.8 | 1 | 101352.97 | 7928.3411 | 6359.5286 | 4639.658 | NORMAL
324.817 | 0.65 | 288.706 | 0.8 | 1 | 106868.78 | 7888.3353 | 6504.1297 | 4616.094 | NORMAL
324.817 | 0.65 | 288.706 | 0.8 | 2 | 57226.51 | 9679.8945 | 6730.6823 | 7099.932 | NORMAL
324.817 | 0.65 | 288.706 | 0.8 | 2 | 79289.74 | 10795.8968 | 7546.9041 | 6231.875 | NORMAL
324.817 | 0.65 | 288.706 | 0.8 | 2 | 101352.97 | 10982.2098 | 7978.85 | 5911.352 | NORMAL
324.817 | 0.65 | 288.706 | 0.8 | 2 | 106868.78 | 10940.1231 | 7983.6424 | 5858.982 | NORMAL
324.817 | 0.65 | 288.706 | 1.11 | 1 | 57226.51 | 7214.068 | 6577.3616 | 5439.08 | NORMAL
324.817 | 0.65 | 288.706 | 1.11 | 1 | 79289.74 | 8049.3552 | 6912.0779 | 4799.608 | NORMAL
324.817 | 0.65 | 288.706 | 1.11 | 1 | 101352.97 | 8242.0574 | 7118.2035 | 4637.056 | NORMAL
324.817 | 0.65 | 288.706 | 1.11 | 1 | 106868.78 | 8215.5627 | 7336.8343 | 4607.851 | NORMAL
324.817 | 0.65 | 288.706 | 1.11 | 2 | 57226.51 | 9766.3834 | 7634.9776 | 7094.34 | NORMAL
324.817 | 0.65 | 288.706 | 1.11 | 2 | 79289.74 | 11218.8746 | 8540.7385 | 6278.39 | NORMAL
324.817 | 0.65 | 288.706 | 1.11 | 2 | 101352.97 | 11491.5592 | 8972.2532 | 5951.349 | NORMAL
324.817 | 0.65 | 288.706 | 1.11 | 2 | 106868.78 | 11466.9695 | 9205.3047 | 5891.451 | NORMAL
324.817 | 0.65 | 288.706 | 1.42 | 1 | 57226.51 | 7324.5311 | 7319.9679 | 5449.66 | NORMAL
324.817 | 0.65 | 288.706 | 1.42 | 1 | 79289.74 | 8212.837 | 7668.6873 | 4802.33 | NORMAL
324.817 | 0.65 | 288.706 | 1.42 | 1 | 101352.97 | 8440.211 | 7851.616 | 4634.381 | NORMAL
324.817 | 0.65 | 288.706 | 1.42 | 1 | 106868.78 | 8417.0281 | 8070.8105 | 4606.358 | NORMAL
324.817 | 0.65 | 288.706 | 1.42 | 2 | 57226.51 | 9812.5147 | 8540.9796 | 7090.64 | NORMAL
324.817 | 0.65 | 288.706 | 1.42 | 2 | 79289.74 | 11480.7737 | 9300.9077 | 6307.17 | NORMAL
324.817 | 0.65 | 288.706 | 1.42 | 2 | 101352.97 | 11810.6975 | 9715.0782 | 5976.079 | NORMAL
324.817 | 0.65 | 288.706 | 1.42 | 2 | 106868.78 | 11795.8089 | 10001.0412 | 5914.543 | NORMAL
324.817 | 0.65 | 291.483 | 0.5 | 1 | 57226.51 | 7368.9625 | 4550.946 | 5450.13 | NORMAL
324.817 | 0.65 | 291.483 | 0.5 | 1 | 79289.74 | 8002.4619 | 5096.872 | 4798.913 | NORMAL
324.817 | 0.65 | 291.483 | 0.5 | 1 | 101352.97 | 8048.1829 | 5422.2057 | 4639.297 | NORMAL
324.817 | 0.65 | 291.483 | 0.5 | 1 | 106868.78 | 7991.2661 | 5411.9971 | 4613.2706 | NORMAL
324.817 | 0.65 | 291.483 | 0.5 | 2 | 57226.51 | 9737.8957 | 5107.3218 | 7096.459 | NORMAL
324.817 | 0.65 | 291.483 | 0.5 | 2 | 79289.74 | 10807.796 | 6187.2038 | 6232.981 | NORMAL
324.817 | 0.65 | 291.483 | 0.5 | 2 | 101352.97 | 10836.5768 | 6764.3863 | 5902.939 | NORMAL
324.817 | 0.65 | 291.483 | 0.5 | 2 | 106868.78 | 10771.4537 | 6889.2818 | 5845.3051 | NORMAL
324.817 | 0.65 | 291.483 | 0.8 | 1 | 57226.51 | 7731.9461 | 5896.4285 | 5484.511 | NORMAL
324.817 | 0.65 | 291.483 | 0.8 | 1 | 79289.74 | 8550.8499 | 6388.0578 | 4808.679 | NORMAL
324.817 | 0.65 | 291.483 | 0.8 | 1 | 101352.97 | 8715.2403 | 6698.4291 | 4630.814 | NORMAL
324.817 | 0.65 | 291.483 | 0.8 | 1 | 106868.78 | 8673.0363 | 6774.5347 | 4601.393 | NORMAL
324.817 | 0.65 | 291.483 | 0.8 | 2 | 57226.51 | 9877.9894 | 6701.1688 | 7081.647 | NORMAL
324.817 | 0.65 | 291.483 | 0.8 | 2 | 79289.74 | 11692.1747 | 7742.1605 | 6330.165 | NORMAL
324.817 | 0.65 | 291.483 | 0.8 | 2 | 101352.97 | 11899.0914 | 8223.4145 | 5982.736 | NORMAL
324.817 | 0.65 | 291.483 | 0.8 | 2 | 106868.78 | 11855.9203 | 8210.8769 | 5919.206 | NORMAL
324.817 | 0.65 | 291.483 | 1.11 | 1 | 57226.51 | 7913.3646 | 6946.114 | 5501.06 | NORMAL
324.817 | 0.65 | 291.483 | 1.11 | 1 | 79289.74 | 8820.721 | 7335.4527 | 4813.711 | NORMAL
324.817 | 0.65 | 291.483 | 1.11 | 1 | 101352.97 | 9046.2778 | 7569.1654 | 4627.997 | NORMAL
324.817 | 0.65 | 291.483 | 1.11 | 1 | 106868.78 | 9014.3025 | 7789.4751 | 4596.101 | NORMAL
324.817 | 0.65 | 291.483 | 1.11 | 2 | 57226.51 | 9923.2122 | 7753.3034 | 7075.3 | NORMAL
324.817 | 0.65 | 291.483 | 1.11 | 2 | 79289.74 | 12128.4877 | 8839.3267 | 6380.019 | NORMAL
324.817 | 0.65 | 291.483 | 1.11 | 2 | 101352.97 | 12432.3564 | 9369.6827 | 6024.501 | NORMAL
324.817 | 0.65 | 291.483 | 1.11 | 2 | 106868.78 | 12403.2239 | 9615.8102 | 5958.483 | NORMAL
324.817 | 0.65 | 291.483 | 1.42 | 1 | 57226.51 | 8030.2462 | 7769.2471 | 5511.15 | NORMAL
324.817 | 0.65 | 291.483 | 1.42 | 1 | 79289.74 | 8990.1231 | 8048.2818 | 4817.02 | NORMAL
324.817 | 0.65 | 291.483 | 1.42 | 1 | 101352.97 | 9252.755 | 8315.5897 | 4627.245 | NORMAL
324.817 | 0.65 | 291.483 | 1.42 | 1 | 106868.78 | 9227.0223 | 8587.359 | 4594.522 | NORMAL
324.817 | 0.65 | 291.483 | 1.42 | 2 | 57226.51 | 9969.1383 | 8602.5888 | 7071.33 | NORMAL
324.817 | 0.65 | 291.483 | 1.42 | 2 | 79289.74 | 12409.3787 | 9692.4941 | 6400.79 | NORMAL
324.817 | 0.65 | 291.483 | 1.42 | 2 | 101352.97 | 12765.3283 | 10138.5173 | 6050.163 | NORMAL
324.817 | 0.65 | 291.483 | 1.42 | 2 | 106868.78 | 12746.864 | 10447.521 | 5982.736 | NORMAL
324.817 | 0.65 | 294.26 | 0.5 | 1 | 57226.51 | 8084.6424 | 4610.0976 | 5516.269 | NORMAL
324.817 | 0.65 | 294.26 | 0.5 | 1 | 79289.74 | 8776.6706 | 5217.757 | 4812.816 | NORMAL
324.817 | 0.65 | 294.26 | 0.5 | 1 | 101352.97 | 8838.687 | 5595.101 | 4629.148 | NORMAL
324.817 | 0.65 | 294.26 | 0.5 | 1 | 106868.78 | 8774.6776 | 5616.6536 | 4599.4009 | NORMAL
324.817 | 0.65 | 294.26 | 0.5 | 2 | 57226.51 | 9934.2907 | 4936.3093 | 7074.045 | NORMAL
324.817 | 0.65 | 294.26 | 0.5 | 2 | 79289.74 | 11722.2743 | 6263.4105 | 6333.86 | NORMAL
324.817 | 0.65 | 294.26 | 0.5 | 2 | 101352.97 | 11755.5979 | 6904.3565 | 5974.573 | NORMAL
324.817 | 0.65 | 294.26 | 0.5 | 2 | 106868.78 | 11683.2356 | 7050.2369 | 5907.0554 | NORMAL
324.817 | 0.65 | 294.26 | 0.8 | 1 | 57226.51 | 8463.0715 | 6252.3988 | 5551.096 | NORMAL
324.817 | 0.65 | 294.26 | 0.8 | 1 | 79289.74 | 9341.9402 | 6651.6576 | 4824.604 | NORMAL
324.817 | 0.65 | 294.26 | 0.8 | 1 | 101352.97 | 9526.3189 | 6983.7539 | 4629.815 | NORMAL
324.817 | 0.65 | 294.26 | 0.8 | 1 | 106868.78 | 9488.9508 | 7024.7746 | 4591.293 | NORMAL
324.817 | 0.65 | 294.26 | 0.8 | 2 | 57226.51 | 10020.8382 | 6734.7548 | 7060.445 | NORMAL
324.817 | 0.65 | 294.26 | 0.8 | 2 | 79289.74 | 12642.9074 | 7904.9526 | 6428.823 | NORMAL
324.817 | 0.65 | 294.26 | 0.8 | 2 | 101352.97 | 12866.7937 | 8456.1855 | 6058.177 | NORMAL
324.817 | 0.65 | 294.26 | 0.8 | 2 | 106868.78 | 12817.1454 | 8412.3796 | 5988.041 | NORMAL
324.817 | 0.65 | 294.26 | 1.11 | 1 | 57226.51 | 8650.1758 | 7272.1769 | 5569.15 | NORMAL
324.817 | 0.65 | 294.26 | 1.11 | 1 | 79289.74 | 9620.6038 | 7676.578 | 4829.668 | NORMAL
324.817 | 0.65 | 294.26 | 1.11 | 1 | 101352.97 | 9872.3329 | 7968.4733 | 4627.464 | NORMAL
324.817 | 0.65 | 294.26 | 1.11 | 1 | 106868.78 | 9835.551 | 8231.589 | 4592.344 | NORMAL
324.817 | 0.65 | 294.26 | 1.11 | 2 | 57226.51 | 10059.5838 | 7862.3896 | 7054.18 | NORMAL
324.817 | 0.65 | 294.26 | 1.11 | 2 | 79289.74 | 13084.7304 | 9141.516 | 6485.48 | NORMAL
324.817 | 0.65 | 294.26 | 1.11 | 2 | 101352.97 | 13419.9297 | 9677.7554 | 6101.334 | NORMAL
324.817 | 0.65 | 294.26 | 1.11 | 2 | 106868.78 | 13386.4302 | 9895.1689 | 6029.101 | NORMAL
324.817 | 0.65 | 294.26 | 1.42 | 1 | 57226.51 | 8773.0657 | 8251.8841 | 5579.62 | NORMAL
324.817 | 0.65 | 294.26 | 1.42 | 1 | 79289.74 | 9800.1758 | 8435.3348 | 4831.1 | NORMAL
324.817 | 0.65 | 294.26 | 1.42 | 1 | 101352.97 | 10088.7163 | 8723.1682 | 4626.31 | NORMAL
324.817 | 0.65 | 294.26 | 1.42 | 1 | 106868.78 | 10059.2028 | 9058.6843 | 4590.037 | NORMAL
324.817 | 0.65 | 294.26 | 1.42 | 2 | 57226.51 | 10101.2896 | 8688.402 | 7050.19 | NORMAL
324.817 | 0.65 | 294.26 | 1.42 | 2 | 79289.74 | 13364.5956 | 10124.2959 | 6515.52 | NORMAL
324.817 | 0.65 | 294.26 | 1.42 | 2 | 101352.97 | 13764.6249 | 10612.4019 | 6128.118 | NORMAL
324.817 | 0.65 | 294.26 | 1.42 | 2 | 106868.78 | 13741.7937 | 10936.2141 | 6054.634 | NORMAL
324.817 | 0.65 | 297.037 | 0.5 | 1 | 57226.51 | 8857.5029 | 4609.7457 | 5584.894 | NORMAL
324.817 | 0.65 | 297.037 | 0.5 | 1 | 79289.74 | 9588.6284 | 5289.7298 | 4831.196 | NORMAL
324.817 | 0.65 | 297.037 | 0.5 | 1 | 101352.97 | 9660.17 | 5713.4206 | 4628.884 | NORMAL
324.817 | 0.65 | 297.037 | 0.5 | 1 | 106868.78 | 9590.3283 | 5793.22 | 4594.844 | NORMAL
324.817 | 0.65 | 297.037 | 0.5 | 2 | 57226.51 | 10072.4209 | 4739.8194 | 7051.951 | NORMAL
324.817 | 0.65 | 297.037 | 0.5 | 2 | 79289.74 | 12699.8535 | 6299.8131 | 6439.747 | NORMAL
324.817 | 0.65 | 297.037 | 0.5 | 2 | 101352.97 | 12739.0973 | 7021.6376 | 6050.408 | NORMAL
324.817 | 0.65 | 297.037 | 0.5 | 2 | 106868.78 | 12654.7773 | 7182.8516 | 5976.6993 | NORMAL
324.817 | 0.65 | 297.037 | 0.8 | 1 | 57226.51 | 9473.388 | 6595.098 | 5707.003 | NORMAL
324.817 | 0.65 | 297.037 | 0.8 | 1 | 79289.74 | 10165.8558 | 6928.478 | 4845.615 | NORMAL
324.817 | 0.65 | 297.037 | 0.8 | 1 | 101352.97 | 10387.2216 | 7256.7 | 4625.115 | NORMAL
324.817 | 0.65 | 297.037 | 0.8 | 1 | 106868.78 | 10335.1407 | 7248.1789 | 4587.926 | NORMAL
324.817 | 0.65 | 297.037 | 0.8 | 2 | 57226.51 | 10164.9179 | 6617.941 | 7037.879 | NORMAL
324.817 | 0.65 | 297.037 | 0.8 | 2 | 79289.74 | 13639.2145 | 8109.386 | 6541.195 | NORMAL
324.817 | 0.65 | 297.037 | 0.8 | 2 | 101352.97 | 13890.3283 | 8636.1171 | 6137.716 | NORMAL
324.817 | 0.65 | 297.037 | 0.8 | 2 | 106868.78 | 13834.3201 | 8604.7949 | 6061.083 | NORMAL
324.817 | 0.65 | 297.037 | 1.11 | 1 | 57226.51 | 9607.0047 | 7728.6335 | 5683.6 | NORMAL
324.817 | 0.65 | 297.037 | 1.11 | 1 | 79289.74 | 10449.8535 | 7932.7659 | 4852.282 | NORMAL
324.817 | 0.65 | 297.037 | 1.11 | 1 | 101352.97 | 10745.4572 | 8300.7797 | 4624.24 | NORMAL
324.817 | 0.65 | 297.037 | 1.11 | 1 | 106868.78 | 10703.6342 | 8607.1883 | 4585.424 | NORMAL
324.817 | 0.65 | 297.037 | 1.11 | 2 | 57226.51 | 10205.9496 | 7886.9843 | 7032.56 | NORMAL
324.817 | 0.65 | 297.037 | 1.11 | 2 | 79289.74 | 14101.7292 | 9457.0709 | 6591.033 | NORMAL
324.817 | 0.65 | 297.037 | 1.11 | 2 | 101352.97 | 14460.2286 | 9984.918 | 6182.145 | NORMAL
324.817 | 0.65 | 297.037 | 1.11 | 2 | 106868.78 | 14422.5967 | 10159.6954 | 6103.446 | NORMAL
324.817 | 0.65 | 297.037 | 1.42 | 1 | 57226.51 | 9674.1208 | 8771.0513 | 5668.59 | NORMAL
324.817 | 0.65 | 297.037 | 1.42 | 1 | 79289.74 | 10623.2708 | 8855.8666 | 4859.14 | NORMAL
324.817 | 0.65 | 297.037 | 1.42 | 1 | 101352.97 | 10966.6178 | 9139.8535 | 4625.308 | NORMAL
324.817 | 0.65 | 297.037 | 1.42 | 1 | 106868.78 | 10934.8476 | 9508.7466 | 4584.184 | NORMAL
324.817 | 0.65 | 297.037 | 1.42 | 2 | 57226.51 | 10239.5369 | 8967.7557 | 7033.3 | NORMAL
324.817 | 0.65 | 297.037 | 1.42 | 2 | 79289.74 | 14389.3611 | 10434.6035 | 6620.87 | NORMAL
324.817 | 0.65 | 297.037 | 1.42 | 2 | 101352.97 | 14813.7749 | 11003.3757 | 6209.721 | NORMAL
324.817 | 0.65 | 297.037 | 1.42 | 2 | 106868.78 | 14785.551 | 11376.4761 | 6129.849 | NORMAL
324.817 | 0.65 | 299.814 | 0.5 | 1 | 57226.51 | 9718.6108 | 4583.7633 | 5659.559 | NORMAL
324.817 | 0.65 | 299.814 | 0.5 | 1 | 79289.74 | 10434.3494 | 5298.8548 | 4852.492 | NORMAL
324.817 | 0.65 | 299.814 | 0.5 | 1 | 101352.97 | 10538.1008 | 5794.2377 | 4622.827 | NORMAL
324.817 | 0.65 | 299.814 | 0.5 | 1 | 106868.78 | 10454.4549 | 5955.0979 | 4587.138 | NORMAL
324.817 | 0.65 | 299.814 | 0.5 | 2 | 57226.51 | 10252.4326 | 4570.4319 | 7027.25 | NORMAL
324.817 | 0.65 | 299.814 | 0.5 | 2 | 79289.74 | 13733.7046 | 6331.952 | 6547.997 | NORMAL
324.817 | 0.65 | 299.814 | 0.5 | 2 | 101352.97 | 13780.5979 | 7118.2163 | 6130.949 | NORMAL
324.817 | 0.65 | 299.814 | 0.5 | 2 | 106868.78 | 13685.0235 | 7283.1968 | 6050.574 | NORMAL
324.817 | 0.65 | 299.814 | 0.8 | 1 | 57226.51 | 9918.4056 | 6670.4154 | 5618.424 | NORMAL
324.817 | 0.65 | 299.814 | 0.8 | 1 | 79289.74 | 11024.6776 | 7219.1353 | 4866.889 | NORMAL
324.817 | 0.65 | 299.814 | 0.8 | 1 | 101352.97 | 11284.9062 | 7544.5692 | 4623.124 | NORMAL
324.817 | 0.65 | 299.814 | 0.8 | 1 | 106868.78 | 11218.9039 | 7412.7785 | 4586.744 | NORMAL
324.817 | 0.65 | 299.814 | 0.8 | 2 | 57226.51 | 10323.8277 | 6731.8377 | 7015.227 | NORMAL
324.817 | 0.65 | 299.814 | 0.8 | 2 | 79289.74 | 14693.0539 | 8169.7053 | 6651.698 | NORMAL
324.817 | 0.65 | 299.814 | 0.8 | 2 | 101352.97 | 14963.2474 | 8722.4061 | 6221.133 | NORMAL
324.817 | 0.65 | 299.814 | 0.8 | 2 | 106868.78 | 14900 | 8785.9489 | 6137.867 | NORMAL
324.817 | 0.65 | 299.814 | 1.11 | 1 | 57226.51 | 10009.2028 | 8016.3906 | 5597.07 | NORMAL
324.817 | 0.65 | 299.814 | 1.11 | 1 | 79289.74 | 11316.5006 | 8259.099 | 4873.978 | NORMAL
324.817 | 0.65 | 299.814 | 1.11 | 1 | 101352.97 | 11656.1547 | 8653.8906 | 4623.32 | NORMAL
324.817 | 0.65 | 299.814 | 1.11 | 1 | 106868.78 | 11604.3669 | 8983.7411 | 4582.013 | NORMAL
324.817 | 0.65 | 299.814 | 1.11 | 2 | 57226.51 | 10356.6237 | 8157.6846 | 7010.55 | NORMAL
324.817 | 0.65 | 299.814 | 1.11 | 2 | 79289.74 | 15168.7866 | 9806.6964 | 6702.219 | NORMAL
324.817 | 0.65 | 299.814 | 1.11 | 2 | 101352.97 | 15544.1676 | 10383.333 | 6266.648 | NORMAL
324.817 | 0.65 | 299.814 | 1.11 | 2 | 106868.78 | 15500.9086 | 10333.2312 | 6181.473 | NORMAL
324.817 | 0.65 | 299.814 | 1.42 | 1 | 57226.51 | 10057.0926 | 8957.7418 | 5584.55 | NORMAL
324.817 | 0.65 | 299.814 | 1.42 | 1 | 79289.74 | 11497.6553 | 9273.9283 | 4878.74 | NORMAL
324.817 | 0.65 | 299.814 | 1.42 | 1 | 101352.97 | 11882.2098 | 9664.1221 | 4625.184 | NORMAL
324.817 | 0.65 | 299.814 | 1.42 | 1 | 106868.78 | 11840.7679 | 9977.9783 | 4582.316 | NORMAL
324.817 | 0.65 | 299.814 | 1.42 | 2 | 57226.51 | 10378.9859 | 9050.0813 | 7007.25 | NORMAL
324.817 | 0.65 | 299.814 | 1.42 | 2 | 79289.74 | 15464.9765 | 10724.1725 | 6730.11 | NORMAL
324.817 | 0.65 | 299.814 | 1.42 | 2 | 101352.97 | 15904.8066 | 11336.2463 | 6294.897 | NORMAL
324.817 | 0.65 | 299.814 | 1.42 | 2 | 106868.78 | 15873.476 | 11747.5627 | 6208.601 | NORMAL
324.817 | 0.65 | 302.591 | 0.5 | 1 | 57226.51 | 10110.8734 | 4424.0935 | 5569.752 | NORMAL
324.817 | 0.65 | 302.591 | 0.5 | 1 | 79289.74 | 11319.0504 | 5265.1582 | 4875.602 | NORMAL
324.817 | 0.65 | 302.591 | 0.5 | 1 | 101352.97 | 11453.1653 | 5820.5444 | 4624.836 | NORMAL
324.817 | 0.65 | 302.591 | 0.5 | 1 | 106868.78 | 11364.3025 | 6112.1423 | 4582.845 | NORMAL
324.817 | 0.65 | 302.591 | 0.5 | 2 | 57226.51 | 10381.3892 | 4385.0573 | 7004.66 | NORMAL
324.817 | 0.65 | 302.591 | 0.5 | 2 | 79289.74 | 14831.7702 | 6358.6024 | 6667.876 | NORMAL
324.817 | 0.65 | 302.591 | 0.5 | 2 | 101352.97 | 14887.1923 | 7182.3855 | 6217.169 | NORMAL
324.817 | 0.65 | 302.591 | 0.5 | 2 | 106868.78 | 14781.9461 | 7359.8275 | 6129.6 | NORMAL
324.817 | 0.65 | 302.591 | 0.8 | 1 | 57226.51 | 10234.9941 | 6683.6559 | 5531.16 | NORMAL
324.817 | 0.65 | 302.591 | 0.8 | 1 | 79289.74 | 11923.6518 | 7405.8636 | 4892.029 | NORMAL
324.817 | 0.65 | 302.591 | 0.8 | 1 | 101352.97 | 12214.83 | 7660.9215 | 4629.668 | NORMAL
324.817 | 0.65 | 302.591 | 0.8 | 1 | 106868.78 | 12152.9015 | 7519.6807 | 4583.734 | NORMAL
324.817 | 0.65 | 302.591 | 0.8 | 2 | 57226.51 | 19931.9168 | 6856.2206 | 4873.088 | NORMAL
324.817 | 0.65 | 302.591 | 0.8 | 2 | 79289.74 | 15821.5416 | 8156.3844 | 6764.419 | NORMAL
324.817 | 0.65 | 302.591 | 0.8 | 2 | 101352.97 | 16089.4783 | 8736.5545 | 6309.103 | NORMAL
324.817 | 0.65 | 302.591 | 0.8 | 2 | 106868.78 | 16020.6038 | 8965.7386 | 6219.015 | NORMAL
324.817 | 0.65 | 302.591 | 1.11 | 1 | 57226.51 | 10310.6389 | 8177.708 | 5512.66 | NORMAL
324.817 | 0.65 | 302.591 | 1.11 | 1 | 79289.74 | 12209.5838 | 8608.5258 | 4901.902 | NORMAL
324.817 | 0.65 | 302.591 | 1.11 | 1 | 101352.97 | 12592.8488 | 9052.4575 | 4631.504 | NORMAL
324.817 | 0.65 | 302.591 | 1.11 | 1 | 106868.78 | 12537.9543 | 9327.2349 | 4585.609 | NORMAL
324.817 | 0.65 | 302.591 | 1.11 | 2 | 57226.51 | 10509.9062 | 8168.8666 | 6990.43 | NORMAL
324.817 | 0.65 | 302.591 | 1.11 | 2 | 79289.74 | 16308.5873 | 10032.6841 | 6812.304 | NORMAL
324.817 | 0.65 | 302.591 | 1.11 | 2 | 101352.97 | 16680.1876 | 10653.3689 | 6354.728 | NORMAL
324.817 | 0.65 | 302.591 | 1.11 | 2 | 106868.78 | 16630.9203 | 10437.7651 | 6263.78 | NORMAL
324.817 | 0.65 | 302.591 | 1.42 | 1 | 57226.51 | 10329.2497 | 9226.561 | 5500.36 | NORMAL
324.817 | 0.65 | 302.591 | 1.42 | 1 | 79289.74 | 12392.9074 | 9554.4607 | 4907.6 | NORMAL
324.817 | 0.65 | 302.591 | 1.42 | 1 | 101352.97 | 12823.388 | 9971.6974 | 4634.194 | NORMAL
324.817 | 0.65 | 302.591 | 1.42 | 1 | 106868.78 | 12778.7515 | 10412.4462 | 4587.004 | NORMAL
324.817 | 0.65 | 302.591 | 1.42 | 2 | 57226.51 | 10737.1336 | 9256.0964 | 6989.19 | NORMAL
324.817 | 0.65 | 302.591 | 1.42 | 2 | 79289.74 | 16619.6073 | 11238.0787 | 6842.38 | NORMAL
324.817 | 0.65 | 302.591 | 1.42 | 2 | 101352.97 | 17044.959 | 11706.1199 | 6384.167 | NORMAL
324.817 | 0.65 | 302.591 | 1.42 | 2 | 106868.78 | 17008.5287 | 12129.9384 | 6291.504 | NORMAL
324.817 | 0.65 | 305.368 | 0.5 | 1 | 57226.51 | 10393.9918 | 4279.9548 | 5481.287 | NORMAL
324.817 | 0.65 | 305.368 | 0.5 | 1 | 79289.74 | 12254.8359 | 5190.8053 | 4900.761 | NORMAL
324.817 | 0.65 | 305.368 | 0.5 | 1 | 101352.97 | 12410.8734 | 5796.3619 | 4632.16 | NORMAL
324.817 | 0.65 | 305.368 | 0.5 | 1 | 106868.78 | 12320.8089 | 6117.4541 | 4584.159 | NORMAL
324.817 | 0.65 | 305.368 | 0.5 | 2 | 57226.51 | 11034.1442 | 4179.9324 | 6984.001 | NORMAL
324.817 | 0.65 | 305.368 | 0.5 | 2 | 79289.74 | 16012.8077 | 6408.5338 | 6785.137 | NORMAL
324.817 | 0.65 | 305.368 | 0.5 | 2 | 101352.97 | 16056.272 | 7247.191 | 6309.364 | NORMAL
324.817 | 0.65 | 305.368 | 0.5 | 2 | 106868.78 | 15940.4455 | 7414.1084 | 6213.704 | NORMAL
324.817 | 0.65 | 305.368 | 0.8 | 1 | 57226.51 | 10462.1629 | 6652.3663 | 5447.474 | NORMAL
324.817 | 0.65 | 305.368 | 0.8 | 1 | 79289.74 | 12859.2321 | 7545.3345 | 4919.378 | NORMAL
324.817 | 0.65 | 305.368 | 0.8 | 1 | 101352.97 | 13183.646 | 7819.0754 | 4639.648 | NORMAL
324.817 | 0.65 | 305.368 | 0.8 | 1 | 106868.78 | 13117.5264 | 7611.261 | 4589.749 | NORMAL
324.817 | 0.65 | 305.368 | 0.8 | 2 | 57226.51 | 11143.0539 | 6527.0216 | 6976.39 | NORMAL
324.817 | 0.65 | 305.368 | 0.8 | 2 | 79289.74 | 17033.4408 | 8047.9601 | 6878.328 | NORMAL
324.817 | 0.65 | 305.368 | 0.8 | 2 | 101352.97 | 17269.0504 | 8678.8376 | 6401.437 | NORMAL
324.817 | 0.65 | 305.368 | 0.8 | 2 | 106868.78 | 17193.2591 | 9165.5201 | 6304.726 | NORMAL
324.817 | 0.65 | 305.368 | 1.11 | 1 | 57226.51 | 10477.4033 | 8308.1722 | 5430.78 | NORMAL
324.817 | 0.65 | 305.368 | 1.11 | 1 | 79289.74 | 13154.6014 | 8858.2165 | 4927.61 | NORMAL
324.817 | 0.65 | 305.368 | 1.11 | 1 | 101352.97 | 13561.6061 | 9328.8254 | 4643.987 | NORMAL
324.817 | 0.65 | 305.368 | 1.11 | 1 | 106868.78 | 13508.8804 | 9725.7995 | 4592.649 | NORMAL
324.817 | 0.65 | 305.368 | 1.11 | 2 | 57226.51 | 11188.218 | 8486.0732 | 6972.14 | NORMAL
324.817 | 0.65 | 305.368 | 1.11 | 2 | 79289.74 | 17550.4982 | 10317.9028 | 6923.312 | NORMAL
324.817 | 0.65 | 305.368 | 1.11 | 2 | 101352.97 | 17868.8746 | 10853.6616 | 6445.428 | NORMAL
324.817 | 0.65 | 305.368 | 1.11 | 2 | 106868.78 | 17808.2943 | 10566.9254 | 6350.132 | NORMAL
324.817 | 0.65 | 305.368 | 1.42 | 1 | 57226.51 | 10526.4068 | 9640.6728 | 5420.31 | NORMAL
324.817 | 0.65 | 305.368 | 1.42 | 1 | 79289.74 | 13340.0059 | 10007.3522 | 4933.35 | NORMAL
324.817 | 0.65 | 305.368 | 1.42 | 1 | 101352.97 | 13800.8206 | 10321.3577 | 4646.192 | NORMAL
324.817 | 0.65 | 305.368 | 1.42 | 1 | 106868.78 | 13752.6671 | 10733.9291 | 4594.844 | NORMAL
324.817 | 0.65 | 305.368 | 1.42 | 2 | 57226.51 | 11205.1876 | 9719.5366 | 6969.83 | NORMAL
324.817 | 0.65 | 305.368 | 1.42 | 2 | 79289.74 | 17888.1594 | 11541.3689 | 6951.88 | NORMAL
324.817 | 0.65 | 305.368 | 1.42 | 2 | 101352.97 | 18235.1993 | 12200.6248 | 6474.42 | NORMAL
324.817 | 0.65 | 305.368 | 1.42 | 2 | 106868.78 | 18189.9765 | 12560.8518 | 6378.453 | NORMAL
324.817 | 0.75 | 288.706 | 0.5 | 1 | 57226.51 | 7036.4596 | 3508.815 | 5421.116 | NORMAL
324.817 | 0.75 | 288.706 | 0.5 | 1 | 79289.74 | 7600.8206 | 4221.511 | 4797.763 | NORMAL
324.817 | 0.75 | 288.706 | 0.5 | 1 | 101352.97 | 7614.068 | 4619.3028 | 4645.509 | NORMAL
324.817 | 0.75 | 288.706 | 0.5 | 1 | 106868.78 | 7548.095 | 4692.2279 | 4626.3223 | NORMAL
324.817 | 0.75 | 288.706 | 0.5 | 2 | 57226.51 | 9623.1536 | 4487.5363 | 7103.456 | NORMAL
324.817 | 0.75 | 288.706 | 0.5 | 2 | 79289.74 | 10364.0094 | 5517.5809 | 6183.725 | NORMAL
324.817 | 0.75 | 288.706 | 0.5 | 2 | 101352.97 | 10356.0375 | 6089.2361 | 5867.323 | NORMAL
324.817 | 0.75 | 288.706 | 0.5 | 2 | 106868.78 | 10259.3201 | 6157.8593 | 5812.6061 | NORMAL
324.817 | 0.75 | 288.706 | 0.8 | 1 | 57226.51 | 7372.7726 | 4573.8985 | 5454.051 | NORMAL
324.817 | 0.75 | 288.706 | 0.8 | 1 | 79289.74 | 8126.9343 | 5231.5758 | 4801.008 | NORMAL
324.817 | 0.75 | 288.706 | 0.8 | 1 | 101352.97 | 8244.871 | 5569.9216 | 4636.734 | NORMAL
324.817 | 0.75 | 288.706 | 0.8 | 1 | 106868.78 | 8200.3517 | 5536.2542 | 4608.161 | NORMAL
324.817 | 0.75 | 288.706 | 0.8 | 2 | 57226.51 | 9799.3259 | 5240.7677 | 7092.37 | NORMAL
324.817 | 0.75 | 288.706 | 0.8 | 2 | 79289.74 | 11209.9355 | 6328.188 | 6275.646 | NORMAL
324.817 | 0.75 | 288.706 | 0.8 | 2 | 101352.97 | 11366.6178 | 6951.4711 | 5941.914 | NORMAL
324.817 | 0.75 | 288.706 | 0.8 | 2 | 106868.78 | 11318.0539 | 7134.1995 | 5880.452 | NORMAL
324.817 | 0.75 | 288.706 | 1.11 | 1 | 57226.51 | 7537.1923 | 5489.827 | 5467.45 | NORMAL
324.817 | 0.75 | 288.706 | 1.11 | 1 | 79289.74 | 8377.1981 | 5974.4837 | 4805.369 | NORMAL
324.817 | 0.75 | 288.706 | 1.11 | 1 | 101352.97 | 8554.0445 | 6330.9339 | 4632.569 | NORMAL
324.817 | 0.75 | 288.706 | 1.11 | 1 | 106868.78 | 8516.3247 | 6424.2981 | 4604.111 | NORMAL
324.817 | 0.75 | 288.706 | 1.11 | 2 | 57226.51 | 9859.6131 | 6264.1967 | 7086.28 | NORMAL
324.817 | 0.75 | 288.706 | 1.11 | 2 | 79289.74 | 11626.993 | 7386.8844 | 6318.461 | NORMAL
324.817 | 0.75 | 288.706 | 1.11 | 2 | 101352.97 | 11873.9156 | 7931.0988 | 5981.131 | NORMAL
324.817 | 0.75 | 288.706 | 1.11 | 2 | 106868.78 | 11838.3353 | 7894.7609 | 5917.656 | NORMAL
324.817 | 0.75 | 288.706 | 1.42 | 1 | 57226.51 | 7639.5955 | 6050.4374 | 5474.25 | NORMAL
324.817 | 0.75 | 288.706 | 1.42 | 1 | 79289.74 | 8532.1512 | 6481.0391 | 4807.25 | NORMAL
324.817 | 0.75 | 288.706 | 1.42 | 1 | 101352.97 | 8743.3177 | 6790.384 | 4630.598 | NORMAL
324.817 | 0.75 | 288.706 | 1.42 | 1 | 106868.78 | 8713.4525 | 7102.2306 | 4600.577 | NORMAL
324.817 | 0.75 | 288.706 | 1.42 | 2 | 57226.51 | 9877.4619 | 7005.3133 | 7081.78 | NORMAL
324.817 | 0.75 | 288.706 | 1.42 | 2 | 79289.74 | 11877.374 | 8155.9552 | 6351.48 | NORMAL
324.817 | 0.75 | 288.706 | 1.42 | 2 | 101352.97 | 12187.0457 | 8675.0804 | 6005.517 | NORMAL
324.817 | 0.75 | 288.706 | 1.42 | 2 | 106868.78 | 12162.0164 | 8799.1581 | 5940.85 | NORMAL
324.817 | 0.75 | 291.483 | 0.5 | 1 | 57226.51 | 7753.6049 | 3502.5282 | 5493.079 | NORMAL
324.817 | 0.75 | 291.483 | 0.5 | 1 | 79289.74 | 8393.9625 | 4293.7468 | 4805.906 | NORMAL
324.817 | 0.75 | 291.483 | 0.5 | 1 | 101352.97 | 8416.3834 | 4766.9554 | 4633.778 | NORMAL
324.817 | 0.75 | 291.483 | 0.5 | 1 | 106868.78 | 8347.0985 | 4863.1865 | 4607.1271 | NORMAL
324.817 | 0.75 | 291.483 | 0.5 | 2 | 57226.51 | 9875.7327 | 4284.7545 | 7085.159 | NORMAL
324.817 | 0.75 | 291.483 | 0.5 | 2 | 79289.74 | 11291.735 | 5592.706 | 6284.631 | NORMAL
324.817 | 0.75 | 291.483 | 0.5 | 2 | 101352.97 | 11281.9754 | 6205.8311 | 5936.102 | NORMAL
324.817 | 0.75 | 291.483 | 0.5 | 2 | 106868.78 | 11202.4912 | 6293.6716 | 5872.4202 | NORMAL
324.817 | 0.75 | 291.483 | 0.8 | 1 | 57226.51 | 8111.5475 | 4736.2596 | 5520.399 | NORMAL
324.817 | 0.75 | 291.483 | 0.8 | 1 | 79289.74 | 8934.789 | 5385.5155 | 4816.063 | NORMAL
324.817 | 0.75 | 291.483 | 0.8 | 1 | 101352.97 | 9079.4842 | 5784.5575 | 4628.203 | NORMAL
324.817 | 0.75 | 291.483 | 0.8 | 1 | 106868.78 | 9027.9308 | 5724.3582 | 4597.059 | NORMAL
324.817 | 0.75 | 291.483 | 0.8 | 2 | 57226.51 | 9970.0469 | 5097.8445 | 7071.882 | NORMAL
324.817 | 0.75 | 291.483 | 0.8 | 2 | 79289.74 | 12164.3904 | 6313.6349 | 6382.402 | NORMAL
324.817 | 0.75 | 291.483 | 0.8 | 2 | 101352.97 | 12344.8124 | 7023.0502 | 6018.176 | NORMAL
324.817 | 0.75 | 291.483 | 0.8 | 2 | 106868.78 | 12289.2145 | 7300.7274 | 5950.092 | NORMAL
324.817 | 0.75 | 291.483 | 1.11 | 1 | 57226.51 | 8283.1477 | 5708.5549 | 5534.46 | NORMAL
324.817 | 0.75 | 291.483 | 1.11 | 1 | 79289.74 | 9193.9625 | 6207.8922 | 4821.313 | NORMAL
324.817 | 0.75 | 291.483 | 1.11 | 1 | 101352.97 | 9402.8429 | 6627.3964 | 4626.278 | NORMAL
324.817 | 0.75 | 291.483 | 1.11 | 1 | 106868.78 | 9362.2216 | 6640.7829 | 4592.815 | NORMAL
324.817 | 0.75 | 291.483 | 1.11 | 2 | 57226.51 | 9992.6143 | 6271.055 | 7064.48 | NORMAL
324.817 | 0.75 | 291.483 | 1.11 | 2 | 79289.74 | 12592.1161 | 7537.2125 | 6429.656 | NORMAL
324.817 | 0.75 | 291.483 | 1.11 | 2 | 101352.97 | 12886.9285 | 8158.2892 | 6049.229 | NORMAL
324.817 | 0.75 | 291.483 | 1.11 | 2 | 106868.78 | 12834.4959 | 8078.7633 | 5988.277 | NORMAL
324.817 | 0.75 | 291.483 | 1.42 | 1 | 57226.51 | 8388.4232 | 6428.3423 | 5544.31 | NORMAL
324.817 | 0.75 | 291.483 | 1.42 | 1 | 79289.74 | 9353.1067 | 6811.2784 | 4824.62 | NORMAL
324.817 | 0.75 | 291.483 | 1.42 | 1 | 101352.97 | 9601.2603 | 7165.9966 | 4625.249 | NORMAL
324.817 | 0.75 | 291.483 | 1.42 | 1 | 106868.78 | 9568.2884 | 7472.0678 | 4590.664 | NORMAL
324.817 | 0.75 | 291.483 | 1.42 | 2 | 57226.51 | 10037.7198 | 7088.5374 | 7061.36 | NORMAL
324.817 | 0.75 | 291.483 | 1.42 | 2 | 79289.74 | 12855.3048 | 8396.3009 | 6458.26 | NORMAL
324.817 | 0.75 | 291.483 | 1.42 | 2 | 101352.97 | 13199.1208 | 9039.4838 | 6084.551 | NORMAL
324.817 | 0.75 | 291.483 | 1.42 | 2 | 106868.78 | 13171.102 | 8977.8709 | 6012.946 | NORMAL
324.817 | 0.75 | 294.26 | 0.5 | 1 | 57226.51 | 8525.8792 | 3469.8623 | 5557.86 | NORMAL
324.817 | 0.75 | 294.26 | 0.5 | 1 | 79289.74 | 9218.1419 | 4351.7742 | 4822.09 | NORMAL
324.817 | 0.75 | 294.26 | 0.5 | 1 | 101352.97 | 9256.5944 | 4886.982 | 4626.796 | NORMAL
324.817 | 0.75 | 294.26 | 0.5 | 1 | 106868.78 | 9181.4771 | 4998.9011 | 4594.7008 | NORMAL
324.817 | 0.75 | 294.26 | 0.5 | 2 | 57226.51 | 10014.6542 | 4039.1404 | 7061.49 | NORMAL
324.817 | 0.75 | 294.26 | 0.5 | 2 | 79289.74 | 12277.5205 | 5622.9448 | 6394.339 | NORMAL
324.817 | 0.75 | 294.26 | 0.5 | 2 | 101352.97 | 12272.0106 | 6282.6926 | 6013.316 | NORMAL
324.817 | 0.75 | 294.26 | 0.5 | 2 | 106868.78 | 12181.1254 | 6379.1214 | 5942.6223 | NORMAL
324.817 | 0.75 | 294.26 | 0.8 | 1 | 57226.51 | 9235.5803 | 4971.0973 | 5743.858 | NORMAL
324.817 | 0.75 | 294.26 | 0.8 | 1 | 79289.74 | 9769.4314 | 5538.3493 | 4837.224 | NORMAL
324.817 | 0.75 | 294.26 | 0.8 | 1 | 101352.97 | 9944.7538 | 5933.3584 | 4626.476 | NORMAL
324.817 | 0.75 | 294.26 | 0.8 | 1 | 106868.78 | 9893.9332 | 5885.3864 | 4587.537 | NORMAL
324.817 | 0.75 | 294.26 | 0.8 | 2 | 57226.51 | 10108.5287 | 4911.0164 | 7048.08 | NORMAL
324.817 | 0.75 | 294.26 | 0.8 | 2 | 79289.74 | 13173.476 | 6256.5185 | 6492.677 | NORMAL
324.817 | 0.75 | 294.26 | 0.8 | 2 | 101352.97 | 13378.3118 | 7055.4541 | 6098.781 | NORMAL
324.817 | 0.75 | 294.26 | 0.8 | 2 | 106868.78 | 13315.7093 | 7445.825 | 6023.999 | NORMAL
324.817 | 0.75 | 294.26 | 1.11 | 1 | 57226.51 | 9086.5182 | 6041.1989 | 5604.94 | NORMAL
324.817 | 0.75 | 294.26 | 1.11 | 1 | 79289.74 | 10043.4642 | 6478.1148 | 4838.779 | NORMAL
324.817 | 0.75 | 294.26 | 1.11 | 1 | 101352.97 | 10282.5909 | 6864.8633 | 4625.051 | NORMAL
324.817 | 0.75 | 294.26 | 1.11 | 1 | 106868.78 | 10236.3423 | 6842.5035 | 4588.426 | NORMAL
324.817 | 0.75 | 294.26 | 1.11 | 2 | 57226.51 | 16793.1418 | 6754.2856 | 4865.79 | NORMAL
324.817 | 0.75 | 294.26 | 1.11 | 2 | 79289.74 | 13614.2145 | 7682.0792 | 6536.233 | NORMAL
324.817 | 0.75 | 294.26 | 1.11 | 2 | 101352.97 | 13924.1501 | 8244.8095 | 6140.748 | NORMAL
324.817 | 0.75 | 294.26 | 1.11 | 2 | 106868.78 | 13878.9859 | 8227.3379 | 6064.322 | NORMAL
324.817 | 0.75 | 294.26 | 1.42 | 1 | 57226.51 | 9450.2931 | 6806.0916 | 5710.38 | NORMAL
324.817 | 0.75 | 294.26 | 1.42 | 1 | 79289.74 | 10197.9191 | 7118.2801 | 4848.41 | NORMAL
324.817 | 0.75 | 294.26 | 1.42 | 1 | 101352.97 | 10489.8886 | 7520.5159 | 4624.445 | NORMAL
324.817 | 0.75 | 294.26 | 1.42 | 1 | 106868.78 | 10452.1981 | 7873.0137 | 4586.553 | NORMAL
324.817 | 0.75 | 294.26 | 1.42 | 2 | 57226.51 | 10172.4502 | 7148.1502 | 7039.43 | NORMAL
324.817 | 0.75 | 294.26 | 1.42 | 2 | 79289.74 | 13881.8582 | 8618.4545 | 6569.54 | NORMAL
324.817 | 0.75 | 294.26 | 1.42 | 2 | 101352.97 | 14260.17 | 9282.2584 | 6166.89 | NORMAL
324.817 | 0.75 | 294.26 | 1.42 | 2 | 106868.78 | 14227.374 | 9155.4717 | 6089.008 | NORMAL
324.817 | 0.75 | 297.037 | 0.5 | 1 | 57226.51 | 9549.7948 | 3405.6574 | 5693.116 | NORMAL
324.817 | 0.75 | 297.037 | 0.5 | 1 | 79289.74 | 10075.8792 | 4378.1912 | 4846.773 | NORMAL
324.817 | 0.75 | 297.037 | 0.5 | 1 | 101352.97 | 10141.6471 | 4988.3821 | 4624.526 | NORMAL
324.817 | 0.75 | 297.037 | 0.5 | 1 | 106868.78 | 10061.313 | 5105.3718 | 4586.333 | NORMAL
324.817 | 0.75 | 297.037 | 0.5 | 2 | 57226.51 | 10178.0481 | 3752.1985 | 7035.931 | NORMAL
324.817 | 0.75 | 297.037 | 0.5 | 2 | 79289.74 | 13328.6635 | 5627.2951 | 6512.013 | NORMAL
324.817 | 0.75 | 297.037 | 0.5 | 2 | 101352.97 | 13332.5322 | 6329.0464 | 6095.993 | NORMAL
324.817 | 0.75 | 297.037 | 0.5 | 2 | 106868.78 | 13230.129 | 6434.1292 | 6018.0775 | NORMAL
324.817 | 0.75 | 297.037 | 0.8 | 1 | 57226.51 | 9802.6084 | 4940.3774 | 5659.829 | NORMAL
324.817 | 0.75 | 297.037 | 0.8 | 1 | 79289.74 | 10652.5791 | 5532.172 | 4854.992 | NORMAL
324.817 | 0.75 | 297.037 | 0.8 | 1 | 101352.97 | 10858.0305 | 5988.6598 | 4624.749 | NORMAL
324.817 | 0.75 | 297.037 | 0.8 | 1 | 106868.78 | 10797.0985 | 6052.2596 | 4584.659 | NORMAL
324.817 | 0.75 | 297.037 | 0.8 | 2 | 57226.51 | 10267.6436 | 4877.0178 | 7024.982 | NORMAL
324.817 | 0.75 | 297.037 | 0.8 | 2 | 79289.74 | 14244.7245 | 6102.9385 | 6608.083 | NORMAL
324.817 | 0.75 | 297.037 | 0.8 | 2 | 101352.97 | 14472.0692 | 7039.8512 | 6183.81 | NORMAL
324.817 | 0.75 | 297.037 | 0.8 | 2 | 106868.78 | 14402.3447 | 7450.5057 | 6102.135 | NORMAL
324.817 | 0.75 | 297.037 | 1.11 | 1 | 57226.51 | 9858.9977 | 6146.8977 | 5631.54 | NORMAL
324.817 | 0.75 | 297.037 | 1.11 | 1 | 79289.74 | 10913.5111 | 6772.8704 | 4869.168 | NORMAL
324.817 | 0.75 | 297.037 | 1.11 | 1 | 101352.97 | 11211.6354 | 7138.9416 | 4622.169 | NORMAL
324.817 | 0.75 | 297.037 | 1.11 | 1 | 106868.78 | 11157.9719 | 6996.2827 | 4583.071 | NORMAL
324.817 | 0.75 | 297.037 | 1.11 | 2 | 57226.51 | 10295.3693 | 6116.9628 | 7020.89 | NORMAL
324.817 | 0.75 | 297.037 | 1.11 | 2 | 79289.74 | 14693.5815 | 7701.2587 | 6653.545 | NORMAL
324.817 | 0.75 | 297.037 | 1.11 | 2 | 101352.97 | 15029.9238 | 8238.5926 | 6226.909 | NORMAL
324.817 | 0.75 | 297.037 | 1.11 | 2 | 106868.78 | 14979.7773 | 8392.9745 | 6143.705 | NORMAL
324.817 | 0.75 | 297.037 | 1.42 | 1 | 57226.51 | 9915.5041 | 7047.3652 | 5620.9 | NORMAL
324.817 | 0.75 | 297.037 | 1.42 | 1 | 79289.74 | 11085.1114 | 7324.831 | 4871.3 | NORMAL
324.817 | 0.75 | 297.037 | 1.42 | 1 | 101352.97 | 11425.7913 | 7847.0621 | 4622.674 | NORMAL
324.817 | 0.75 | 297.037 | 1.42 | 1 | 106868.78 | 11380.129 | 8193.3173 | 4582.89 | NORMAL
324.817 | 0.75 | 297.037 | 1.42 | 2 | 57226.51 | 10318.5229 | 7082.3039 | 7018.43 | NORMAL
324.817 | 0.75 | 297.037 | 1.42 | 2 | 79289.74 | 14972.5674 | 8918.6943 | 6682.05 | NORMAL
324.817 | 0.75 | 297.037 | 1.42 | 2 | 101352.97 | 15373.6518 | 9437.685 | 6253.603 | NORMAL
324.817 | 0.75 | 297.037 | 1.42 | 2 | 106868.78 | 15336.313 | 9311.7645 | 6169.254 | NORMAL
324.817 | 0.75 | 299.814 | 0.5 | 1 | 57226.51 | 9995.721 | 3187.5155 | 5600.949 | NORMAL
324.817 | 0.75 | 299.814 | 0.5 | 1 | 79289.74 | 10987.0457 | 4430.4053 | 4864.963 | NORMAL
324.817 | 0.75 | 299.814 | 0.5 | 1 | 101352.97 | 11076.2603 | 5079.6062 | 4622.012 | NORMAL
324.817 | 0.75 | 299.814 | 0.5 | 1 | 106868.78 | 10981.0961 | 5176.0824 | 4583.631 | NORMAL
324.817 | 0.75 | 299.814 | 0.5 | 2 | 57226.51 | 10328.8687 | 3366.4675 | 7012.661 | NORMAL
324.817 | 0.75 | 299.814 | 0.5 | 2 | 79289.74 | 14448.4467 | 5611.6755 | 6629.469 | NORMAL
324.817 | 0.75 | 299.814 | 0.5 | 2 | 101352.97 | 14455.2462 | 6342.2971 | 6183.117 | NORMAL
324.817 | 0.75 | 299.814 | 0.5 | 2 | 106868.78 | 14341.2075 | 6453.1992 | 6097.474 | NORMAL
324.817 | 0.75 | 299.814 | 0.8 | 1 | 57226.51 | 10153.8394 | 4767.4307 | 5562.228 | NORMAL
324.817 | 0.75 | 299.814 | 0.8 | 1 | 79289.74 | 11561.1958 | 5532.0669 | 4880.63 | NORMAL
324.817 | 0.75 | 299.814 | 0.8 | 1 | 101352.97 | 11812.6612 | 5996.2013 | 4624.855 | NORMAL
324.817 | 0.75 | 299.814 | 0.8 | 1 | 106868.78 | 11745.252 | 6208.3053 | 4581.213 | NORMAL
324.817 | 0.75 | 299.814 | 0.8 | 2 | 57226.51 | 19418.7866 | 5332.9814 | 4866.864 | NORMAL
324.817 | 0.75 | 299.814 | 0.8 | 2 | 79289.74 | 15380.6272 | 5906.0532 | 6716.984 | NORMAL
324.817 | 0.75 | 299.814 | 0.8 | 2 | 101352.97 | 15618.1125 | 6979.5002 | 6273.046 | NORMAL
324.817 | 0.75 | 299.814 | 0.8 | 2 | 106868.78 | 15539.449 | 7375.815 | 6184.138 | NORMAL
324.817 | 0.75 | 299.814 | 1.11 | 1 | 57226.51 | 10198.007 | 6175.0768 | 5544.72 | NORMAL
324.817 | 0.75 | 299.814 | 1.11 | 1 | 79289.74 | 11834.3494 | 6937.6033 | 4890.597 | NORMAL
324.817 | 0.75 | 299.814 | 1.11 | 1 | 101352.97 | 12166.5592 | 7218.2492 | 4628.03 | NORMAL
324.817 | 0.75 | 299.814 | 1.11 | 1 | 106868.78 | 12114.068 | 7044.1125 | 4582.431 | NORMAL
324.817 | 0.75 | 299.814 | 1.11 | 2 | 57226.51 | 10434.027 | 6158.7679 | 6997.83 | NORMAL
324.817 | 0.75 | 299.814 | 1.11 | 2 | 79289.74 | 15838.4525 | 7604.6588 | 6768.426 | NORMAL
324.817 | 0.75 | 299.814 | 1.11 | 2 | 101352.97 | 16182.5322 | 8216.9073 | 6316.895 | NORMAL
324.817 | 0.75 | 299.814 | 1.11 | 2 | 106868.78 | 16127.2567 | 8538.1729 | 6227.031 | NORMAL
324.817 | 0.75 | 299.814 | 1.42 | 1 | 57226.51 | 10234.8183 | 7274.8372 | 5534.12 | NORMAL
324.817 | 0.75 | 299.814 | 1.42 | 1 | 79289.74 | 12008.939 | 7580.955 | 4893.62 | NORMAL
324.817 | 0.75 | 299.814 | 1.42 | 1 | 101352.97 | 12384.408 | 8101.5205 | 4630.018 | NORMAL
324.817 | 0.75 | 299.814 | 1.42 | 1 | 106868.78 | 12340.3576 | 8413.5077 | 4583.624 | NORMAL
324.817 | 0.75 | 299.814 | 1.42 | 2 | 57226.51 | 10455.4513 | 7393.2065 | 6995.07 | NORMAL
324.817 | 0.75 | 299.814 | 1.42 | 2 | 79289.74 | 16127.3447 | 9022.9429 | 6796.06 | NORMAL
324.817 | 0.75 | 299.814 | 1.42 | 2 | 101352.97 | 16532.1805 | 9467.1367 | 6342.879 | NORMAL
324.817 | 0.75 | 299.814 | 1.42 | 2 | 106868.78 | 16488.9215 | 9341.5511 | 6253.006 | NORMAL
324.817 | 0.75 | 302.591 | 0.5 | 1 | 57226.51 | 10321.5416 | 2884.7057 | 5508.952 | NORMAL
324.817 | 0.75 | 302.591 | 0.5 | 1 | 79289.74 | 11934.027 | 4497.3858 | 4890.883 | NORMAL
324.817 | 0.75 | 302.591 | 0.5 | 1 | 101352.97 | 12052.1981 | 5161.9444 | 4628.13 | NORMAL
324.817 | 0.75 | 302.591 | 0.5 | 1 | 106868.78 | 11955.7151 | 5222.089 | 4582.059 | NORMAL
324.817 | 0.75 | 302.591 | 0.5 | 2 | 57226.51 | 10491.8816 | 2840.6769 | 6989.575 | NORMAL
324.817 | 0.75 | 302.591 | 0.5 | 2 | 79289.74 | 15647.5674 | 5603.2531 | 6749.413 | NORMAL
324.817 | 0.75 | 302.591 | 0.5 | 2 | 101352.97 | 15647.4502 | 6339.5175 | 6276.037 | NORMAL
324.817 | 0.75 | 302.591 | 0.5 | 2 | 106868.78 | 15521.5123 | 6443.3523 | 6182.802 | NORMAL
324.817 | 0.75 | 302.591 | 0.8 | 1 | 57226.51 | 10406.4185 | 4869.8813 | 5475.535 | NORMAL
324.817 | 0.75 | 302.591 | 0.8 | 1 | 79289.74 | 12510.9906 | 5347.0848 | 4907.802 | NORMAL
324.817 | 0.75 | 302.591 | 0.8 | 1 | 101352.97 | 12799.4724 | 5926.0149 | 4633.965 | NORMAL
324.817 | 0.75 | 302.591 | 0.8 | 1 | 106868.78 | 12728.8394 | 6361.7848 | 4585.963 | NORMAL
324.817 | 0.75 | 302.591 | 0.8 | 2 | 57226.51 | 11076.6706 | 4574.7314 | 6983.598 | NORMAL
324.817 | 0.75 | 302.591 | 0.8 | 2 | 79289.74 | 16597.2743 | 5593.9785 | 6840.322 | NORMAL
324.817 | 0.75 | 302.591 | 0.8 | 2 | 101352.97 | 16829.5428 | 6909.0827 | 6365.228 | NORMAL
324.817 | 0.75 | 302.591 | 0.8 | 2 | 106868.78 | 16736.694 | 7244.0261 | 6271.12 | NORMAL
324.817 | 0.75 | 302.591 | 1.11 | 1 | 57226.51 | 10423.095 | 5896.1364 | 5460.17 | NORMAL
324.817 | 0.75 | 302.591 | 1.11 | 1 | 79289.74 | 12791.2661 | 7070.7945 | 4915.56 | NORMAL
324.817 | 0.75 | 302.591 | 1.11 | 1 | 101352.97 | 13158.1184 | 7357.9277 | 4638.292 | NORMAL
324.817 | 0.75 | 302.591 | 1.11 | 1 | 106868.78 | 13102.9894 | 7128.1442 | 4588.856 | NORMAL
324.817 | 0.75 | 302.591 | 1.11 | 2 | 57226.51 | 22466.4127 | 5164.6463 | 4872.93 | NORMAL
324.817 | 0.75 | 302.591 | 1.11 | 2 | 79289.74 | 17075.9086 | 7387.26 | 6881.955 | NORMAL
324.817 | 0.75 | 302.591 | 1.11 | 2 | 101352.97 | 17392.5557 | 8048.3008 | 6408.648 | NORMAL
324.817 | 0.75 | 302.591 | 1.11 | 2 | 106868.78 | 17326.3775 | 8702.7449 | 6314.746 | NORMAL
324.817 | 0.75 | 302.591 | 1.42 | 1 | 57226.51 | 10456.2427 | 7322.7472 | 5450.02 | NORMAL
324.817 | 0.75 | 302.591 | 1.42 | 1 | 79289.74 | 12963.5698 | 7911.2648 | 4922.11 | NORMAL
324.817 | 0.75 | 302.591 | 1.42 | 1 | 101352.97 | 13380.3048 | 8451.2949 | 4641.06 | NORMAL
324.817 | 0.75 | 302.591 | 1.42 | 1 | 106868.78 | 13334.9355 | 8551.9742 | 4590.418 | NORMAL
324.817 | 0.75 | 302.591 | 1.42 | 2 | 57226.51 | 11142.2626 | 7585.1733 | 6977.19 | NORMAL
324.817 | 0.75 | 302.591 | 1.42 | 2 | 79289.74 | 17377.6671 | 9187.0686 | 6909.27 | NORMAL
324.817 | 0.75 | 302.591 | 1.42 | 2 | 101352.97 | 17742.9953 | 9669.3114 | 6436.025 | NORMAL
324.817 | 0.75 | 302.591 | 1.42 | 2 | 106868.78 | 17692.4971 | 9350.467 | 6340.933 | NORMAL
324.817 | 0.75 | 305.368 | 0.5 | 1 | 57226.51 | 10523.7104 | 2357.5532 | 5422.526 | NORMAL
324.817 | 0.75 | 305.368 | 0.5 | 1 | 79289.74 | 12917.2919 | 4525.8057 | 4922.639 | NORMAL
324.817 | 0.75 | 305.368 | 0.5 | 1 | 101352.97 | 13077.5791 | 5166.9515 | 4637.696 | NORMAL
324.817 | 0.75 | 305.368 | 0.5 | 1 | 106868.78 | 12971.5416 | 5239.8672 | 4587.823 | NORMAL
324.817 | 0.75 | 305.368 | 0.5 | 2 | 57226.51 | 11193.9918 | 2345.992 | 6972.007 | NORMAL
324.817 | 0.75 | 305.368 | 0.5 | 2 | 79289.74 | 16946.6882 | 5591.8648 | 6872.293 | NORMAL
324.817 | 0.75 | 305.368 | 0.5 | 2 | 101352.97 | 16906.9461 | 6312.5634 | 6374.233 | NORMAL
324.817 | 0.75 | 305.368 | 0.5 | 2 | 106868.78 | 16769.0211 | 6414.7207 | 6273.811 | NORMAL
324.817 | 0.75 | 305.368 | 0.8 | 1 | 57226.51 | 10567.8195 | 4714.0401 | 5392.495 | NORMAL
324.817 | 0.75 | 305.368 | 0.8 | 1 | 79289.74 | 13499.3552 | 5199.9111 | 4938.201 | NORMAL
324.817 | 0.75 | 305.368 | 0.8 | 1 | 101352.97 | 13827.1395 | 5730.8792 | 4646.711 | NORMAL
324.817 | 0.75 | 305.368 | 0.8 | 1 | 106868.78 | 13753.6928 | 6402.6879 | 4594.188 | NORMAL
324.817 | 0.75 | 305.368 | 0.8 | 2 | 57226.51 | 11267.0281 | 4377.8038 | 6965.288 | NORMAL
324.817 | 0.75 | 305.368 | 0.8 | 2 | 79289.74 | 17936.5182 | 5224.4055 | 6956.176 | NORMAL
324.817 | 0.75 | 305.368 | 0.8 | 2 | 101352.97 | 18089.3025 | 6798.7196 | 6467.253 | NORMAL
324.817 | 0.75 | 305.368 | 0.8 | 2 | 106868.78 | 17989.9473 | 7037.8113 | 6363.518 | NORMAL
324.817 | 0.75 | 305.368 | 1.11 | 1 | 57226.51 | 10592.9953 | 6167.369 | 5378.51 | NORMAL
324.817 | 0.75 | 305.368 | 1.11 | 1 | 79289.74 | 13779.2204 | 6929.0325 | 4947.492 | NORMAL
324.817 | 0.75 | 305.368 | 1.11 | 1 | 101352.97 | 14188.306 | 7458.4945 | 4652.047 | NORMAL
324.817 | 0.75 | 305.368 | 1.11 | 1 | 106868.78 | 14131.2134 | 7184.8176 | 4598.28 | NORMAL
324.817 | 0.75 | 305.368 | 1.11 | 2 | 57226.51 | 24292.3798 | 4806.7332 | 4904.09 | NORMAL
324.817 | 0.75 | 305.368 | 1.11 | 2 | 79289.74 | 18444.9883 | 7216.1774 | 6996.581 | NORMAL
324.817 | 0.75 | 305.368 | 1.11 | 2 | 101352.97 | 18645.8675 | 7811.854 | 6510.326 | NORMAL
324.817 | 0.75 | 305.368 | 1.11 | 2 | 106868.78 | 18574.9414 | 8767.6324 | 6407.088 | NORMAL
324.817 | 0.75 | 305.368 | 1.42 | 1 | 57226.51 | 10619.3435 | 7545.4152 | 5370.75 | NORMAL
324.817 | 0.75 | 305.368 | 1.42 | 1 | 79289.74 | 13955.2462 | 8066.7184 | 4953.48 | NORMAL
324.817 | 0.75 | 305.368 | 1.42 | 1 | 101352.97 | 14412.8664 | 8696.9542 | 4655.471 | NORMAL
324.817 | 0.75 | 305.368 | 1.42 | 1 | 106868.78 | 14366.1782 | 8512.4059 | 4600.96 | NORMAL
324.817 | 0.75 | 305.368 | 1.42 | 2 | 57226.51 | 11329.9531 | 7771.7247 | 6960.86 | NORMAL
324.817 | 0.75 | 305.368 | 1.42 | 2 | 79289.74 | 18785.6975 | 9067.1799 | 7024.28 | NORMAL
324.817 | 0.75 | 305.368 | 1.42 | 2 | 101352.97 | 18996.3658 | 9870.4547 | 6538.929 | NORMAL
324.817 | 0.75 | 305.368 | 1.42 | 2 | 106868.78 | 18942.4971 | 9404.5331 | 6434.113 | NORMAL
324.817 | 0.85 | 288.706 | 0.5 | 1 | 57226.51 | 7363.2767 | 2979.7855 | 5450.525 | NORMAL
324.817 | 0.85 | 288.706 | 0.5 | 1 | 79289.74 | 7944.2263 | 3702.2239 | 4798.344 | NORMAL
324.817 | 0.85 | 288.706 | 0.5 | 1 | 101352.97 | 7932.5909 | 4140.2254 | 4640.942 | NORMAL
324.817 | 0.85 | 288.706 | 0.5 | 1 | 106868.78 | 7858.939 | 4194.8816 | 4616.5061 | NORMAL
324.817 | 0.85 | 288.706 | 0.5 | 2 | 57226.51 | 9768.0539 | 3759.8412 | 7095.139 | NORMAL
324.817 | 0.85 | 288.706 | 0.5 | 2 | 79289.74 | 10778.6049 | 4915.572 | 6231.684 | NORMAL
324.817 | 0.85 | 288.706 | 0.5 | 2 | 101352.97 | 10734.2614 | 5559.2633 | 5892.693 | NORMAL
324.817 | 0.85 | 288.706 | 0.5 | 2 | 106868.78 | 10646.8054 | 5660.9916 | 5837.3682 | NORMAL
324.817 | 0.85 | 288.706 | 0.8 | 1 | 57226.51 | 7675.8206 | 3095.4742 | 5480.233 | NORMAL
324.817 | 0.85 | 288.706 | 0.8 | 1 | 79289.74 | 8447.8312 | 4027.0642 | 4806.796 | NORMAL
324.817 | 0.85 | 288.706 | 0.8 | 1 | 101352.97 | 8555.4513 | 4580.7769 | 4632.43 | NORMAL
324.817 | 0.85 | 288.706 | 0.8 | 1 | 106868.78 | 8497.8605 | 4756.2185 | 4605.858 | NORMAL
324.817 | 0.85 | 288.706 | 0.8 | 2 | 57226.51 | 9868.5229 | 3870.6222 | 7082.649 | NORMAL
324.817 | 0.85 | 288.706 | 0.8 | 2 | 79289.74 | 11619.0211 | 5463.3451 | 6323.448 | NORMAL
324.817 | 0.85 | 288.706 | 0.8 | 2 | 101352.97 | 11758.558 | 6181.2505 | 5972.492 | NORMAL
324.817 | 0.85 | 288.706 | 0.8 | 2 | 106868.78 | 11695.6624 | 6283.2958 | 5906.185 | NORMAL
324.817 | 0.85 | 288.706 | 1.11 | 1 | 57226.51 | 7820.6624 | 4060.8164 | 5490.17 | NORMAL
324.817 | 0.85 | 288.706 | 1.11 | 1 | 79289.74 | 8686.7233 | 4687.9205 | 4808.615 | NORMAL
324.817 | 0.85 | 288.706 | 1.11 | 1 | 101352.97 | 8850.1758 | 5116.7469 | 4630.513 | NORMAL
324.817 | 0.85 | 288.706 | 1.11 | 1 | 106868.78 | 8809.9941 | 5171.678 | 4599.056 | NORMAL
324.817 | 0.85 | 288.706 | 1.11 | 2 | 57226.51 | 9913.687 | 4073.9206 | 7077.64 | NORMAL
324.817 | 0.85 | 288.706 | 1.11 | 2 | 79289.74 | 12014.3611 | 5591.4596 | 6366.877 | NORMAL
324.817 | 0.85 | 288.706 | 1.11 | 2 | 101352.97 | 12253.1653 | 6490.0973 | 6011.066 | NORMAL
324.817 | 0.85 | 288.706 | 1.11 | 2 | 106868.78 | 12207.8253 | 6805.8992 | 5942.924 | NORMAL
324.817 | 0.85 | 288.706 | 1.42 | 1 | 57226.51 | 8357.6788 | 4557.2584 | 5856.26 | NORMAL
324.817 | 0.85 | 288.706 | 1.42 | 1 | 79289.74 | 8817.4971 | 5231.5004 | 4818.01 | NORMAL
324.817 | 0.85 | 288.706 | 1.42 | 1 | 101352.97 | 9026.8757 | 5648.3057 | 4629.324 | NORMAL
324.817 | 0.85 | 288.706 | 1.42 | 1 | 106868.78 | 8996.2485 | 5602.0539 | 4596.602 | NORMAL
324.817 | 0.85 | 288.706 | 1.42 | 2 | 57226.51 | 9955.9496 | 5120.1358 | 7078.68 | NORMAL
324.817 | 0.85 | 288.706 | 1.42 | 2 | 79289.74 | 12255.2755 | 6191.1446 | 6400.31 | NORMAL
324.817 | 0.85 | 288.706 | 1.42 | 2 | 101352.97 | 12556.9461 | 6912.7872 | 6034.521 | NORMAL
324.817 | 0.85 | 288.706 | 1.42 | 2 | 106868.78 | 12524.1501 | 7225.2824 | 5965.629 | NORMAL
324.817 | 0.85 | 291.483 | 0.5 | 1 | 57226.51 | 8122.9777 | 2991.8308 | 5525.397 | NORMAL
324.817 | 0.85 | 291.483 | 0.5 | 1 | 79289.74 | 8772.0692 | 3746.735 | 4817.431 | NORMAL
324.817 | 0.85 | 291.483 | 0.5 | 1 | 101352.97 | 8782.8839 | 4235.0276 | 4630.528 | NORMAL
324.817 | 0.85 | 291.483 | 0.5 | 1 | 106868.78 | 8701.6413 | 4299.1503 | 4600.5451 | NORMAL
324.817 | 0.85 | 291.483 | 0.5 | 2 | 57226.51 | 9962.2509 | 3528.7787 | 7072.846 | NORMAL
324.817 | 0.85 | 291.483 | 0.5 | 2 | 79289.74 | 11768.728 | 4911.408 | 6341.885 | NORMAL
324.817 | 0.85 | 291.483 | 0.5 | 2 | 101352.97 | 11723.5053 | 5606.9891 | 5970.002 | NORMAL
324.817 | 0.85 | 291.483 | 0.5 | 2 | 106868.78 | 11630.3634 | 5723.453 | 5901.9537 | NORMAL
324.817 | 0.85 | 291.483 | 0.8 | 1 | 57226.51 | 8879.4842 | 3015.8902 | 5793.466 | NORMAL
324.817 | 0.85 | 291.483 | 0.8 | 1 | 79289.74 | 9288.1008 | 3977.4713 | 4828.896 | NORMAL
324.817 | 0.85 | 291.483 | 0.8 | 1 | 101352.97 | 9433.0598 | 4659.9032 | 4625.913 | NORMAL
324.817 | 0.85 | 291.483 | 0.8 | 1 | 106868.78 | 9374.1794 | 4888.5502 | 4592.548 | NORMAL
324.817 | 0.85 | 291.483 | 0.8 | 2 | 57226.51 | 10036.2837 | 3422.7039 | 7061.627 | NORMAL
324.817 | 0.85 | 291.483 | 0.8 | 2 | 79289.74 | 12637.1043 | 5506.8078 | 6434.714 | NORMAL
324.817 | 0.85 | 291.483 | 0.8 | 2 | 101352.97 | 12799.4724 | 6237.7333 | 6053.657 | NORMAL
324.817 | 0.85 | 291.483 | 0.8 | 2 | 106868.78 | 12728.0774 | 6341.3573 | 5980.489 | NORMAL
324.817 | 0.85 | 291.483 | 1.11 | 1 | 57226.51 | 8607.8253 | 3841.6897 | 5562.73 | NORMAL
324.817 | 0.85 | 291.483 | 1.11 | 1 | 79289.74 | 9538.5404 | 4705.3811 | 4828.652 | NORMAL
324.817 | 0.85 | 291.483 | 1.11 | 1 | 101352.97 | 9742.8488 | 5191.7595 | 4624.525 | NORMAL
324.817 | 0.85 | 291.483 | 1.11 | 1 | 106868.78 | 9697.626 | 5321.6111 | 4589.331 | NORMAL
324.817 | 0.85 | 291.483 | 1.11 | 2 | 57226.51 | 10056.653 | 3828.5879 | 7055.83 | NORMAL
324.817 | 0.85 | 291.483 | 1.11 | 2 | 79289.74 | 13035.932 | 5592.467 | 6484.715 | NORMAL
324.817 | 0.85 | 291.483 | 1.11 | 2 | 101352.97 | 13311.7526 | 6525.0351 | 6093.477 | NORMAL
324.817 | 0.85 | 291.483 | 1.11 | 2 | 106868.78 | 13259.4666 | 6896.4077 | 6018.594 | NORMAL
324.817 | 0.85 | 291.483 | 1.42 | 1 | 57226.51 | 9095.1348 | 4758.2289 | 5763.82 | NORMAL
324.817 | 0.85 | 291.483 | 1.42 | 1 | 79289.74 | 9672.4795 | 5346.2212 | 4838.23 | NORMAL
324.817 | 0.85 | 291.483 | 1.42 | 1 | 101352.97 | 9923.6518 | 5826.7119 | 4626.938 | NORMAL
324.817 | 0.85 | 291.483 | 1.42 | 1 | 106868.78 | 9893.1712 | 5708.617 | 4587.922 | NORMAL
324.817 | 0.85 | 291.483 | 1.42 | 2 | 57226.51 | 10091.5006 | 4860.3392 | 7056.24 | NORMAL
324.817 | 0.85 | 291.483 | 1.42 | 2 | 79289.74 | 13284.6424 | 6112.5695 | 6507.07 | NORMAL
324.817 | 0.85 | 291.483 | 1.42 | 2 | 101352.97 | 13628.2825 | 6862.8079 | 6115.236 | NORMAL
324.817 | 0.85 | 291.483 | 1.42 | 2 | 106868.78 | 13587.1043 | 7359.3871 | 6041.835 | NORMAL
324.817 | 0.85 | 294.26 | 0.5 | 1 | 57226.51 | 9267.0868 | 3074.2819 | 5739.485 | NORMAL
324.817 | 0.85 | 294.26 | 0.5 | 1 | 79289.74 | 9643.2884 | 3765.2991 | 4836.564 | NORMAL
324.817 | 0.85 | 294.26 | 0.5 | 1 | 101352.97 | 9676.993 | 4294.7269 | 4624.384 | NORMAL
324.817 | 0.85 | 294.26 | 0.5 | 1 | 106868.78 | 9586.7819 | 4366.0602 | 4590.192 | NORMAL
324.817 | 0.85 | 294.26 | 0.5 | 2 | 57226.51 | 10111.2837 | 3310.5758 | 7048.319 | NORMAL
324.817 | 0.85 | 294.26 | 0.5 | 2 | 79289.74 | 12824.5018 | 4880.5565 | 6454.936 | NORMAL
324.817 | 0.85 | 294.26 | 0.5 | 2 | 101352.97 | 12781.3892 | 5620.4625 | 6052.415 | NORMAL
324.817 | 0.85 | 294.26 | 0.5 | 2 | 106868.78 | 12675.8792 | 5747.3831 | 5976.9243 | NORMAL
324.817 | 0.85 | 294.26 | 0.8 | 1 | 57226.51 | 9502.755 | 2675.7477 | 5698.828 | NORMAL
324.817 | 0.85 | 294.26 | 0.8 | 1 | 79289.74 | 10170.0176 | 3952.8723 | 4848.935 | NORMAL
324.817 | 0.85 | 294.26 | 0.8 | 1 | 101352.97 | 10347.3036 | 4723.3682 | 4624.362 | NORMAL
324.817 | 0.85 | 294.26 | 0.8 | 1 | 106868.78 | 10285.7561 | 4989.5689 | 4585.066 | NORMAL
324.817 | 0.85 | 294.26 | 0.8 | 2 | 57226.51 | 10182.4443 | 2882.1816 | 7038.484 | NORMAL
324.817 | 0.85 | 294.26 | 0.8 | 2 | 79289.74 | 13711.8113 | 5473.6454 | 6552.47 | NORMAL
324.817 | 0.85 | 294.26 | 0.8 | 2 | 101352.97 | 13899.7655 | 6248.4172 | 6139.358 | NORMAL
324.817 | 0.85 | 294.26 | 0.8 | 2 | 106868.78 | 13820.3693 | 6361.5713 | 6059.033 | NORMAL
324.817 | 0.85 | 294.26 | 1.11 | 1 | 57226.51 | 9605.7151 | 3594.6027 | 5681.41 | NORMAL
324.817 | 0.85 | 294.26 | 1.11 | 1 | 79289.74 | 10425.0586 | 4522.6719 | 4850.508 | NORMAL
324.817 | 0.85 | 294.26 | 1.11 | 1 | 101352.97 | 10667.1161 | 5151.1823 | 4624.923 | NORMAL
324.817 | 0.85 | 294.26 | 1.11 | 1 | 106868.78 | 10618.7866 | 5442.2025 | 4585.318 | NORMAL
324.817 | 0.85 | 294.26 | 1.11 | 2 | 57226.51 | 17522.0692 | 4985.0637 | 4868.19 | NORMAL
324.817 | 0.85 | 294.26 | 1.11 | 2 | 79289.74 | 14124.7069 | 5372.4029 | 6587.195 | NORMAL
324.817 | 0.85 | 294.26 | 1.11 | 2 | 101352.97 | 14426.143 | 6544.7516 | 6179.786 | NORMAL
324.817 | 0.85 | 294.26 | 1.11 | 2 | 106868.78 | 14364.7421 | 6840.5189 | 6098.039 | NORMAL
324.817 | 0.85 | 294.26 | 1.42 | 1 | 57226.51 | 9662.5733 | 4703.1223 | 5671.85 | NORMAL
324.817 | 0.85 | 294.26 | 1.42 | 1 | 79289.74 | 10565.5334 | 5495.0177 | 4858.74 | NORMAL
324.817 | 0.85 | 294.26 | 1.42 | 1 | 101352.97 | 10858.7046 | 5949.2128 | 4626.082 | NORMAL
324.817 | 0.85 | 294.26 | 1.42 | 1 | 106868.78 | 10823.095 | 5795.2046 | 4584.288 | NORMAL
324.817 | 0.85 | 294.26 | 1.42 | 2 | 57226.51 | 10227.9601 | 4935.3283 | 7031.03 | NORMAL
324.817 | 0.85 | 294.26 | 1.42 | 2 | 79289.74 | 14370.3107 | 5840.3242 | 6620.89 | NORMAL
324.817 | 0.85 | 294.26 | 1.42 | 2 | 101352.97 | 14742.0574 | 6753.4545 | 6204.387 | NORMAL
324.817 | 0.85 | 294.26 | 1.42 | 2 | 106868.78 | 14700.381 | 7457.077 | 6122.476 | NORMAL
324.817 | 0.85 | 297.037 | 0.5 | 1 | 57226.51 | 9821.0727 | 2977.3564 | 5643.657 | NORMAL
324.817 | 0.85 | 297.037 | 0.5 | 1 | 79289.74 | 10567.9953 | 3774.3912 | 4855.046 | NORMAL
324.817 | 0.85 | 297.037 | 0.5 | 1 | 101352.97 | 10620.5451 | 4327.0013 | 4623.164 | NORMAL
324.817 | 0.85 | 297.037 | 0.5 | 1 | 106868.78 | 10519.871 | 4400.9565 | 4585.875 | NORMAL
324.817 | 0.85 | 297.037 | 0.5 | 2 | 57226.51 | 10283.2356 | 3091.2229 | 7023.552 | NORMAL
324.817 | 0.85 | 297.037 | 0.5 | 2 | 79289.74 | 13951.2896 | 4829.9504 | 6578.052 | NORMAL
324.817 | 0.85 | 297.037 | 0.5 | 2 | 101352.97 | 13914.7714 | 5603.4367 | 6140.677 | NORMAL
324.817 | 0.85 | 297.037 | 0.5 | 2 | 106868.78 | 13796.8347 | 5739.4005 | 6057.46 | NORMAL
324.817 | 0.85 | 297.037 | 0.8 | 1 | 57226.51 | 9968.7866 | 2230.4562 | 5606.995 | NORMAL
324.817 | 0.85 | 297.037 | 0.8 | 1 | 79289.74 | 11091.7057 | 3880.9767 | 4872.042 | NORMAL
324.817 | 0.85 | 297.037 | 0.8 | 1 | 101352.97 | 11314.5076 | 4788.4241 | 4622.15 | NORMAL
324.817 | 0.85 | 297.037 | 0.8 | 1 | 106868.78 | 11238.8921 | 5009.9272 | 4583.729 | NORMAL
324.817 | 0.85 | 297.037 | 0.8 | 2 | 57226.51 | 10358.3236 | 2218.4111 | 7014.962 | NORMAL
324.817 | 0.85 | 297.037 | 0.8 | 2 | 79289.74 | 14860.8734 | 5438.7824 | 6671.01 | NORMAL
324.817 | 0.85 | 297.037 | 0.8 | 2 | 101352.97 | 15065.6799 | 6228.6643 | 6230.036 | NORMAL
324.817 | 0.85 | 297.037 | 0.8 | 2 | 106868.78 | 14976.8464 | 6344.4917 | 6142.568 | NORMAL
324.817 | 0.85 | 297.037 | 1.11 | 1 | 57226.51 | 10035.4631 | 3444.462 | 5591.14 | NORMAL
324.817 | 0.85 | 297.037 | 1.11 | 1 | 79289.74 | 11349.5604 | 4391.3265 | 4874.14 | NORMAL
324.817 | 0.85 | 297.037 | 1.11 | 1 | 101352.97 | 11642.8195 | 4967.7116 | 4624.079 | NORMAL
324.817 | 0.85 | 297.037 | 1.11 | 1 | 106868.78 | 11587.9543 | 5592.2309 | 4581.4 | NORMAL
324.817 | 0.85 | 297.037 | 1.11 | 2 | 57226.51 | 10364.449 | 3232.4125 | 7011.87 | NORMAL
324.817 | 0.85 | 297.037 | 1.11 | 2 | 79289.74 | 15268.3763 | 5158.0698 | 6715.091 | NORMAL
324.817 | 0.85 | 297.037 | 1.11 | 2 | 101352.97 | 15600.0586 | 6511.8857 | 6271.532 | NORMAL
324.817 | 0.85 | 297.037 | 1.11 | 2 | 106868.78 | 15529.3376 | 6740.6332 | 6182.702 | NORMAL
324.817 | 0.85 | 297.037 | 1.42 | 1 | 57226.51 | 10086.5475 | 4960.9373 | 5582.17 | NORMAL
324.817 | 0.85 | 297.037 | 1.42 | 1 | 79289.74 | 11495.5158 | 5628.5264 | 4882.23 | NORMAL
324.817 | 0.85 | 297.037 | 1.42 | 1 | 101352.97 | 11840.4162 | 5966.4449 | 4625.674 | NORMAL
324.817 | 0.85 | 297.037 | 1.42 | 1 | 106868.78 | 11800.3224 | 5876.7848 | 4580.653 | NORMAL
324.817 | 0.85 | 297.037 | 1.42 | 2 | 57226.51 | 10374.1208 | 4733.5868 | 7008.62 | NORMAL
324.817 | 0.85 | 297.037 | 1.42 | 2 | 79289.74 | 15522.9484 | 5507.9767 | 6738.67 | NORMAL
324.817 | 0.85 | 297.037 | 1.42 | 2 | 101352.97 | 15915.592 | 6435.3264 | 6296.036 | NORMAL
324.817 | 0.85 | 297.037 | 1.42 | 2 | 106868.78 | 15867.4384 | 7488.6693 | 6207.168 | NORMAL
324.817 | 0.85 | 299.814 | 0.5 | 1 | 57226.51 | 10197.3329 | 2854.3661 | 5549.869 | NORMAL
324.817 | 0.85 | 299.814 | 0.5 | 1 | 79289.74 | 11530.3927 | 3759.5422 | 4878.192 | NORMAL
324.817 | 0.85 | 299.814 | 0.5 | 1 | 101352.97 | 11612.4854 | 4330.6093 | 4624.951 | NORMAL
324.817 | 0.85 | 299.814 | 0.5 | 1 | 106868.78 | 11504.4256 | 4408.2543 | 4581.802 | NORMAL
324.817 | 0.85 | 299.814 | 0.5 | 2 | 57226.51 | 10439.8886 | 2928.1591 | 7000.03 | NORMAL
324.817 | 0.85 | 299.814 | 0.5 | 2 | 79289.74 | 15152.6377 | 4764.1863 | 6699.247 | NORMAL
324.817 | 0.85 | 299.814 | 0.5 | 2 | 101352.97 | 15113.4232 | 5554.8631 | 6234.019 | NORMAL
324.817 | 0.85 | 299.814 | 0.5 | 2 | 106868.78 | 14983.2356 | 5696.8809 | 6143.225 | NORMAL
324.817 | 0.85 | 299.814 | 0.8 | 1 | 57226.51 | 10291.9109 | 1721.6 | 5518.583 | NORMAL
324.817 | 0.85 | 299.814 | 0.8 | 1 | 79289.74 | 12048.9156 | 3767.467 | 4897.413 | NORMAL
324.817 | 0.85 | 299.814 | 0.8 | 1 | 101352.97 | 12310.0235 | 4815.7427 | 4629.62 | NORMAL
324.817 | 0.85 | 299.814 | 0.8 | 1 | 106868.78 | 12236.4009 | 4947.5073 | 4583.196 | NORMAL
324.817 | 0.85 | 299.814 | 0.8 | 2 | 57226.51 | 10493.6108 | 1642.1242 | 6993.089 | NORMAL
324.817 | 0.85 | 299.814 | 0.8 | 2 | 79289.74 | 16081.3599 | 5388.8959 | 6792.947 | NORMAL
324.817 | 0.85 | 299.814 | 0.8 | 2 | 101352.97 | 16282.7667 | 6194.86 | 6326.532 | NORMAL
324.817 | 0.85 | 299.814 | 0.8 | 2 | 106868.78 | 16188.2767 | 6290.8453 | 6230.74 | NORMAL
324.817 | 0.85 | 299.814 | 1.11 | 1 | 57226.51 | 10330.891 | 2950.2649 | 5504.39 | NORMAL
324.817 | 0.85 | 299.814 | 1.11 | 1 | 79289.74 | 12308.6166 | 4188.8684 | 4900.364 | NORMAL
324.817 | 0.85 | 299.814 | 1.11 | 1 | 101352.97 | 12641.9695 | 4849.1182 | 4632.8 | NORMAL
324.817 | 0.85 | 299.814 | 1.11 | 1 | 106868.78 | 12586.694 | 5659.3552 | 4585.117 | NORMAL
324.817 | 0.85 | 299.814 | 1.11 | 2 | 57226.51 | 10520.9554 | 2831.2733 | 6990.27 | NORMAL
324.817 | 0.85 | 299.814 | 1.11 | 2 | 79289.74 | 16501.7292 | 4885.3039 | 6827.384 | NORMAL
324.817 | 0.85 | 299.814 | 1.11 | 2 | 101352.97 | 16823.6225 | 6474.487 | 6367.219 | NORMAL
324.817 | 0.85 | 299.814 | 1.11 | 2 | 106868.78 | 16745.7503 | 6591.1273 | 6271.684 | NORMAL
324.817 | 0.85 | 299.814 | 1.42 | 1 | 57226.51 | 10353.6049 | 4782.0402 | 5496.04 | NORMAL
324.817 | 0.85 | 299.814 | 1.42 | 1 | 79289.74 | 12463.5405 | 5407.5688 | 4904.94 | NORMAL
324.817 | 0.85 | 299.814 | 1.42 | 1 | 101352.97 | 12843.6401 | 5842.3407 | 4634.876 | NORMAL
324.817 | 0.85 | 299.814 | 1.42 | 1 | 106868.78 | 12800.8206 | 5909.0124 | 4586.402 | NORMAL
324.817 | 0.85 | 299.814 | 1.42 | 2 | 57226.51 | 10836.1958 | 4739.1777 | 6987.01 | NORMAL
324.817 | 0.85 | 299.814 | 1.42 | 2 | 79289.74 | 16759.32 | 5181.9482 | 6853.7 | NORMAL
324.817 | 0.85 | 299.814 | 1.42 | 2 | 101352.97 | 17137.8664 | 6157.841 | 6391.565 | NORMAL
324.817 | 0.85 | 299.814 | 1.42 | 2 | 106868.78 | 17078.9273 | 7252.3957 | 6297.534 | NORMAL
324.817 | 0.85 | 302.591 | 0.5 | 1 | 57226.51 | 10421.2192 | 2674.533 | 5458.963 | NORMAL
324.817 | 0.85 | 302.591 | 0.5 | 1 | 79289.74 | 12535.17 | 3704.0299 | 4907.246 | NORMAL
324.817 | 0.85 | 302.591 | 0.5 | 1 | 101352.97 | 12651.7585 | 4318.3109 | 4633.161 | NORMAL
324.817 | 0.85 | 302.591 | 0.5 | 1 | 106868.78 | 12537.3974 | 4392.9787 | 4585.021 | NORMAL
324.817 | 0.85 | 302.591 | 0.5 | 2 | 57226.51 | 11112.4267 | 2837.7804 | 6981.361 | NORMAL
324.817 | 0.85 | 302.591 | 0.5 | 2 | 79289.74 | 16449.3845 | 4623.7739 | 6824.594 | NORMAL
324.817 | 0.85 | 302.591 | 0.5 | 2 | 101352.97 | 16386.0199 | 5482.7459 | 6332.507 | NORMAL
324.817 | 0.85 | 302.591 | 0.5 | 2 | 106868.78 | 16242.7022 | 5628.0638 | 6234.745 | NORMAL
324.817 | 0.85 | 302.591 | 0.8 | 1 | 57226.51 | 10485.17 | 1011.475 | 5433.027 | NORMAL
324.817 | 0.85 | 302.591 | 0.8 | 1 | 79289.74 | 13050.8792 | 3809.7083 | 4922.603 | NORMAL
324.817 | 0.85 | 302.591 | 0.8 | 1 | 101352.97 | 13350.5276 | 4926.5583 | 4640.842 | NORMAL
324.817 | 0.85 | 302.591 | 0.8 | 1 | 106868.78 | 13271.4537 | 4930.9157 | 4590.052 | NORMAL
324.817 | 0.85 | 302.591 | 0.8 | 2 | 57226.51 | 11176.8171 | 1063.4976 | 6976.22 | NORMAL
324.817 | 0.85 | 302.591 | 0.8 | 2 | 79289.74 | 17418.4642 | 5375.5819 | 6906.068 | NORMAL
324.817 | 0.85 | 302.591 | 0.8 | 2 | 101352.97 | 17564.3025 | 6138.4427 | 6426.604 | NORMAL
324.817 | 0.85 | 302.591 | 0.8 | 2 | 106868.78 | 17461.8699 | 6214.0159 | 6323.17 | NORMAL
324.817 | 0.85 | 302.591 | 1.11 | 1 | 57226.51 | 10512.3681 | 2945.8494 | 5420.75 | NORMAL
324.817 | 0.85 | 302.591 | 1.11 | 1 | 79289.74 | 13303.1946 | 3633.169 | 4930.301 | NORMAL
324.817 | 0.85 | 302.591 | 1.11 | 1 | 101352.97 | 13685.5217 | 4484.7044 | 4643.022 | NORMAL
324.817 | 0.85 | 302.591 | 1.11 | 1 | 106868.78 | 13625.1758 | 5501.5463 | 4592.886 | NORMAL
324.817 | 0.85 | 302.591 | 1.11 | 2 | 57226.51 | 11214.2732 | 2459.7499 | 6974.2 | NORMAL
324.817 | 0.85 | 302.591 | 1.11 | 2 | 79289.74 | 17858.5287 | 4896.63 | 6949.828 | NORMAL
324.817 | 0.85 | 302.591 | 1.11 | 2 | 101352.97 | 18103.8101 | 6550.6102 | 6469.196 | NORMAL
324.817 | 0.85 | 302.591 | 1.11 | 2 | 106868.78 | 18016.6178 | 6428.4914 | 6366.754 | NORMAL
324.817 | 0.85 | 302.591 | 1.42 | 1 | 57226.51 | 10529.4842 | 4421.2146 | 5413.41 | NORMAL
324.817 | 0.85 | 302.591 | 1.42 | 1 | 79289.74 | 13459.2321 | 5314.8489 | 4935.22 | NORMAL
324.817 | 0.85 | 302.591 | 1.42 | 1 | 101352.97 | 13885.3165 | 5575.0934 | 4647.737 | NORMAL
324.817 | 0.85 | 302.591 | 1.42 | 1 | 106868.78 | 13842.204 | 6095.3315 | 4594.835 | NORMAL
324.817 | 0.85 | 302.591 | 1.42 | 2 | 57226.51 | 11237.5733 | 4792.4317 | 6970.13 | NORMAL
324.817 | 0.85 | 302.591 | 1.42 | 2 | 79289.74 | 18125.4396 | 4336.1127 | 6971.58 | NORMAL
324.817 | 0.85 | 302.591 | 1.42 | 2 | 101352.97 | 18419.6366 | 5714.3975 | 6493.835 | NORMAL
324.817 | 0.85 | 302.591 | 1.42 | 2 | 106868.78 | 18345.4279 | 6970.5838 | 6391.203 | NORMAL
324.817 | 0.85 | 305.368 | 0.5 | 1 | 57226.51 | 10608.4994 | 2559.9794 | 5374.912 | NORMAL
324.817 | 0.85 | 305.368 | 0.5 | 1 | 79289.74 | 13586.5475 | 3564.7432 | 4939.186 | NORMAL
324.817 | 0.85 | 305.368 | 0.5 | 1 | 101352.97 | 13740.2403 | 4284.7978 | 4646.175 | NORMAL
324.817 | 0.85 | 305.368 | 0.5 | 1 | 106868.78 | 13619.0797 | 4359.3176 | 4593.196 | NORMAL
324.817 | 0.85 | 305.368 | 0.5 | 2 | 57226.51 | 11311.6647 | 2686.9615 | 6962.701 | NORMAL
324.817 | 0.85 | 305.368 | 0.5 | 2 | 79289.74 | 17875.2345 | 4481.643 | 6951.177 | NORMAL
324.817 | 0.85 | 305.368 | 0.5 | 2 | 101352.97 | 17726.8171 | 5389.7678 | 6438.758 | NORMAL
324.817 | 0.85 | 305.368 | 0.5 | 2 | 106868.78 | 17573.5053 | 5536.7261 | 6331.626 | NORMAL
324.817 | 0.85 | 305.368 | 0.8 | 1 | 57226.51 | 10654.1911 | 614.9535 | 5352.744 | NORMAL
324.817 | 0.85 | 305.368 | 0.8 | 1 | 79289.74 | 14086.1958 | 3643.4931 | 4955.322 | NORMAL
324.817 | 0.85 | 305.368 | 0.8 | 1 | 101352.97 | 14434.7011 | 4959.72 | 4655.968 | NORMAL
324.817 | 0.85 | 305.368 | 0.8 | 1 | 106868.78 | 14349.8242 | 4933.1825 | 4600.205 | NORMAL
324.817 | 0.85 | 305.368 | 0.8 | 2 | 57226.51 | 11360.0821 | 215.2236 | 6957.968 | NORMAL
324.817 | 0.85 | 305.368 | 0.8 | 2 | 79289.74 | 18920.6037 | 5299.0367 | 7032.908 | NORMAL
324.817 | 0.85 | 305.368 | 0.8 | 2 | 101352.97 | 18912.0457 | 6036.1009 | 6530.588 | NORMAL
324.817 | 0.85 | 305.368 | 0.8 | 2 | 106868.78 | 18791.5299 | 6124.2723 | 6422.966 | NORMAL
324.817 | 0.85 | 305.368 | 1.11 | 1 | 57226.51 | 10678.7222 | 2490.6518 | 5342.25 | NORMAL
324.817 | 0.85 | 305.368 | 1.11 | 1 | 79289.74 | 14327.5791 | 3424.1625 | 4968.17 | NORMAL
324.817 | 0.85 | 305.368 | 1.11 | 1 | 101352.97 | 14763.4818 | 4084.4354 | 4659.144 | NORMAL
324.817 | 0.85 | 305.368 | 1.11 | 1 | 106868.78 | 14702.5791 | 5083.4314 | 4604.544 | NORMAL
324.817 | 0.85 | 305.368 | 1.11 | 2 | 57226.51 | 11385.1407 | 1852.2713 | 6955.79 | NORMAL
324.817 | 0.85 | 305.368 | 1.11 | 2 | 79289.74 | 19352.0809 | 4553.8156 | 7056.321 | NORMAL
324.817 | 0.85 | 305.368 | 1.11 | 2 | 101352.97 | 19445.8089 | 6613.2279 | 6575.09 | NORMAL
324.817 | 0.85 | 305.368 | 1.11 | 2 | 106868.78 | 19344.7831 | 6179.6716 | 6465.233 | NORMAL
324.817 | 0.85 | 305.368 | 1.42 | 1 | 57226.51 | 10694.959 | 4610.6182 | 5335.77 | NORMAL
324.817 | 0.85 | 305.368 | 1.42 | 1 | 79289.74 | 14493.9918 | 5203.0677 | 4968.75 | NORMAL
324.817 | 0.85 | 305.368 | 1.42 | 1 | 101352.97 | 14968.0832 | 5472.5707 | 4662.195 | NORMAL
324.817 | 0.85 | 305.368 | 1.42 | 1 | 106868.78 | 14921.0434 | 6157.4968 | 4607.161 | NORMAL
324.817 | 0.85 | 305.368 | 1.42 | 2 | 57226.51 | 11403.3412 | 4374.4813 | 6954.48 | NORMAL
324.817 | 0.85 | 305.368 | 1.42 | 2 | 79289.74 | 19586.7233 | 3903.1051 | 7070.05 | NORMAL
324.817 | 0.85 | 305.368 | 1.42 | 2 | 101352.97 | 19761.8699 | 5102.8508 | 6599.491 | NORMAL
324.817 | 0.85 | 305.368 | 1.42 | 2 | 106868.78 | 19668.9918 | 6370.9635 | 6489.666 | NORMAL
324.817 | 0.95 | 288.706 | 0.5 | 1 | 57226.51 | 8095.0469 | 2443.7651 | 5887.342 | NORMAL
324.817 | 0.95 | 288.706 | 0.5 | 1 | 79289.74 | 8284.4959 | 3127.48 | 4808.668 | NORMAL
324.817 | 0.95 | 288.706 | 0.5 | 1 | 101352.97 | 8255.3341 | 3636.904 | 4636.998 | NORMAL
324.817 | 0.95 | 288.706 | 0.5 | 1 | 106868.78 | 8174.2087 | 3722.5837 | 4608.5867 | NORMAL
324.817 | 0.95 | 288.706 | 0.5 | 2 | 57226.51 | 9873.0657 | 2989.7025 | 7085.64 | NORMAL
324.817 | 0.95 | 288.706 | 0.5 | 2 | 79289.74 | 11191.442 | 4318.6991 | 6276.498 | NORMAL
324.817 | 0.95 | 288.706 | 0.5 | 2 | 101352.97 | 11109.1735 | 5034.5886 | 5921.316 | NORMAL
324.817 | 0.95 | 288.706 | 0.5 | 2 | 106868.78 | 11011.6647 | 5164.3937 | 5861.6577 | NORMAL
324.817 | 0.95 | 288.706 | 0.8 | 1 | 57226.51 | 7925.2638 | 2458.5119 | 5503.135 | NORMAL
324.817 | 0.95 | 288.706 | 0.8 | 1 | 79289.74 | 8766.442 | 3307.9029 | 4812.552 | NORMAL
324.817 | 0.95 | 288.706 | 0.8 | 1 | 101352.97 | 8871.8933 | 3864.7121 | 4630.271 | NORMAL
324.817 | 0.95 | 288.706 | 0.8 | 1 | 106868.78 | 8800.9086 | 3949.3109 | 4600.322 | NORMAL
324.817 | 0.95 | 288.706 | 0.8 | 2 | 57226.51 | 9943.1712 | 3009.2809 | 7075.018 | NORMAL
324.817 | 0.95 | 288.706 | 0.8 | 2 | 79289.74 | 12042.5264 | 4530.5791 | 6370.245 | NORMAL
324.817 | 0.95 | 288.706 | 0.8 | 2 | 101352.97 | 12152.8136 | 5324.8039 | 6004.502 | NORMAL
324.817 | 0.95 | 288.706 | 0.8 | 2 | 106868.78 | 12080.041 | 5469.8667 | 5933.242 | NORMAL
324.817 | 0.95 | 288.706 | 1.11 | 1 | 57226.51 | 8494.9883 | 2512.792 | 5841.89 | NORMAL
324.817 | 0.95 | 288.706 | 1.11 | 1 | 79289.74 | 8951.7878 | 3453.6087 | 4820.841 | NORMAL
324.817 | 0.95 | 288.706 | 1.11 | 1 | 101352.97 | 9142.4385 | 4022.3072 | 4627.629 | NORMAL
324.817 | 0.95 | 288.706 | 1.11 | 1 | 106868.78 | 9089.2438 | 4105.5206 | 4595.515 | NORMAL
324.817 | 0.95 | 288.706 | 1.11 | 2 | 57226.51 | 9993.4349 | 3145.3237 | 7071.11 | NORMAL
324.817 | 0.95 | 288.706 | 1.11 | 2 | 79289.74 | 12431.3892 | 4688.2125 | 6413.086 | NORMAL
324.817 | 0.95 | 288.706 | 1.11 | 2 | 101352.97 | 12654.6014 | 5511.5218 | 6042.778 | NORMAL
324.817 | 0.95 | 288.706 | 1.11 | 2 | 106868.78 | 12591.1782 | 5651.5755 | 5973.2 | NORMAL
324.817 | 0.95 | 288.706 | 1.42 | 1 | 57226.51 | 8552.8722 | 2017.1008 | 5834.92 | NORMAL
324.817 | 0.95 | 288.706 | 1.42 | 1 | 79289.74 | 9070.9555 | 3337.0957 | 4823.93 | NORMAL
324.817 | 0.95 | 288.706 | 1.42 | 1 | 101352.97 | 9290.6213 | 4056.9449 | 4627.027 | NORMAL
324.817 | 0.95 | 288.706 | 1.42 | 1 | 106868.78 | 9258.1477 | 4255.1188 | 4593.702 | NORMAL
324.817 | 0.95 | 288.706 | 1.42 | 2 | 57226.51 | 10005.8617 | 2665.8717 | 7069.25 | NORMAL
324.817 | 0.95 | 288.706 | 1.42 | 2 | 79289.74 | 12650.8206 | 4825.8832 | 6435.7 | NORMAL
324.817 | 0.95 | 288.706 | 1.42 | 2 | 101352.97 | 12949.5604 | 5666.896 | 6065.187 | NORMAL
324.817 | 0.95 | 288.706 | 1.42 | 2 | 106868.78 | 12901.612 | 5800.9905 | 5996.298 | NORMAL
324.817 | 0.95 | 291.483 | 0.5 | 1 | 57226.51 | 8500.9379 | 2276.4236 | 5553.679 | NORMAL
324.817 | 0.95 | 291.483 | 0.5 | 1 | 79289.74 | 9169.7245 | 3123.309 | 4821.088 | NORMAL
324.817 | 0.95 | 291.483 | 0.5 | 1 | 101352.97 | 9152.7843 | 3676.1151 | 4627.23 | NORMAL
324.817 | 0.95 | 291.483 | 0.5 | 1 | 106868.78 | 9059.8183 | 3771.9376 | 4596.2091 | NORMAL
324.817 | 0.95 | 291.483 | 0.5 | 2 | 57226.51 | 10038.0422 | 2696.8505 | 7061.365 | NORMAL
324.817 | 0.95 | 291.483 | 0.5 | 2 | 79289.74 | 12242.0574 | 4255.6942 | 6392.244 | NORMAL
324.817 | 0.95 | 291.483 | 0.5 | 2 | 101352.97 | 12159.1149 | 5021.8239 | 6003.377 | NORMAL
324.817 | 0.95 | 291.483 | 0.5 | 2 | 106868.78 | 12052.9601 | 5168.4901 | 5931.4186 | NORMAL
324.817 | 0.95 | 291.483 | 0.8 | 1 | 57226.51 | 8748.9742 | 2434.927 | 5574.868 | NORMAL
324.817 | 0.95 | 291.483 | 0.8 | 1 | 79289.74 | 9659.6131 | 3296.9805 | 4832.446 | NORMAL
324.817 | 0.95 | 291.483 | 0.8 | 1 | 101352.97 | 9797.9191 | 3891.0182 | 4624.324 | NORMAL
324.817 | 0.95 | 291.483 | 0.8 | 1 | 106868.78 | 9721.9812 | 3985.2151 | 4588.907 | NORMAL
324.817 | 0.95 | 291.483 | 0.8 | 2 | 57226.51 | 10092.6143 | 2639.259 | 7052.366 | NORMAL
324.817 | 0.95 | 291.483 | 0.8 | 2 | 79289.74 | 13119.2556 | 4451.9669 | 6487.143 | NORMAL
324.817 | 0.95 | 291.483 | 0.8 | 2 | 101352.97 | 13250.2931 | 5288.3775 | 6092.241 | NORMAL
324.817 | 0.95 | 291.483 | 0.8 | 2 | 106868.78 | 13168.347 | 5444.993 | 6014.585 | NORMAL
324.817 | 0.95 | 291.483 | 1.11 | 1 | 57226.51 | 9211.1665 | 2623.5244 | 5747.52 | NORMAL
324.817 | 0.95 | 291.483 | 1.11 | 1 | 79289.74 | 9841.7937 | 3439.0869 | 4838.983 | NORMAL
324.817 | 0.95 | 291.483 | 1.11 | 1 | 101352.97 | 10075.8206 | 4044.6863 | 4625.524 | NORMAL
324.817 | 0.95 | 291.483 | 1.11 | 1 | 106868.78 | 10013.2474 | 4134.2996 | 4589.29 | NORMAL
324.817 | 0.95 | 291.483 | 1.11 | 2 | 57226.51 | 10127.9015 | 2888.0724 | 7051.56 | NORMAL
324.817 | 0.95 | 291.483 | 1.11 | 2 | 79289.74 | 13521.1606 | 4580.5771 | 6525.447 | NORMAL
324.817 | 0.95 | 291.483 | 1.11 | 2 | 101352.97 | 13772.9484 | 5469.0037 | 6128.98 | NORMAL
324.817 | 0.95 | 291.483 | 1.11 | 2 | 106868.78 | 13701.9637 | 5617.1748 | 6053.141 | NORMAL
324.817 | 0.95 | 291.483 | 1.42 | 1 | 57226.51 | 9254.2497 | 1869.2844 | 5741.22 | NORMAL
324.817 | 0.95 | 291.483 | 1.42 | 1 | 79289.74 | 9968.4056 | 3463.7119 | 4842.74 | NORMAL
324.817 | 0.95 | 291.483 | 1.42 | 1 | 101352.97 | 10228.136 | 4159.4556 | 4625.592 | NORMAL
324.817 | 0.95 | 291.483 | 1.42 | 1 | 106868.78 | 10189.5662 | 4300.5268 | 4588.168 | NORMAL
324.817 | 0.95 | 291.483 | 1.42 | 2 | 57226.51 | 10128.517 | 2561.7754 | 7048.17 | NORMAL
324.817 | 0.95 | 291.483 | 1.42 | 2 | 79289.74 | 13741.6764 | 4752.2427 | 6551.93 | NORMAL
324.817 | 0.95 | 291.483 | 1.42 | 2 | 101352.97 | 14077.1688 | 5626.0109 | 6152.64 | NORMAL
324.817 | 0.95 | 291.483 | 1.42 | 2 | 106868.78 | 14018.4349 | 5760.9319 | 6076.062 | NORMAL
324.817 | 0.95 | 294.26 | 0.5 | 1 | 57226.51 | 9563.306 | 2219.1078 | 5691.006 | NORMAL
324.817 | 0.95 | 294.26 | 0.5 | 1 | 79289.74 | 10083.6753 | 3086.008 | 4845.398 | NORMAL
324.817 | 0.95 | 294.26 | 0.5 | 1 | 101352.97 | 10091.7644 | 3678.4077 | 4624.681 | NORMAL
324.817 | 0.95 | 294.26 | 0.5 | 1 | 106868.78 | 9994.1383 | 3786.6691 | 4586.82 | NORMAL
324.817 | 0.95 | 294.26 | 0.5 | 2 | 57226.51 | 10204.1911 | 2332.9128 | 7037.426 | NORMAL
324.817 | 0.95 | 294.26 | 0.5 | 2 | 79289.74 | 13360.0528 | 4164.2616 | 6512.564 | NORMAL
324.817 | 0.95 | 294.26 | 0.5 | 2 | 101352.97 | 13280.9203 | 4972.5359 | 6091.044 | NORMAL
324.817 | 0.95 | 294.26 | 0.5 | 2 | 106868.78 | 13162.5146 | 5133.5518 | 6011.4283 | NORMAL
324.817 | 0.95 | 294.26 | 0.8 | 1 | 57226.51 | 9708.177 | 2429.5295 | 5663.107 | NORMAL
324.817 | 0.95 | 294.26 | 0.8 | 1 | 79289.74 | 10577.5791 | 3231.9476 | 4857.69 | NORMAL
324.817 | 0.95 | 294.26 | 0.8 | 1 | 101352.97 | 10761.9285 | 3882.0321 | 4624.392 | NORMAL
324.817 | 0.95 | 294.26 | 0.8 | 1 | 106868.78 | 10681.9754 | 3983.8214 | 4583.238 | NORMAL
324.817 | 0.95 | 294.26 | 0.8 | 2 | 57226.51 | 10252.6377 | 2489.0739 | 7030.285 | NORMAL
324.817 | 0.95 | 294.26 | 0.8 | 2 | 79289.74 | 14258.4408 | 4351.3624 | 6608.944 | NORMAL
324.817 | 0.95 | 294.26 | 0.8 | 2 | 101352.97 | 14411.0492 | 5216.5548 | 6182.492 | NORMAL
324.817 | 0.95 | 294.26 | 0.8 | 2 | 106868.78 | 14321.3072 | 5383.4366 | 6097.588 | NORMAL
324.817 | 0.95 | 294.26 | 1.11 | 1 | 57226.51 | 9759.3787 | 2278.7564 | 5653.9 | NORMAL
324.817 | 0.95 | 294.26 | 1.11 | 1 | 79289.74 | 10782.034 | 3396.8367 | 4861.794 | NORMAL
324.817 | 0.95 | 294.26 | 1.11 | 1 | 101352.97 | 11049.8535 | 4037.3844 | 4623.682 | NORMAL
324.817 | 0.95 | 294.26 | 1.11 | 1 | 106868.78 | 10981.1547 | 4128.9142 | 4584.321 | NORMAL
324.817 | 0.95 | 294.26 | 1.11 | 2 | 57226.51 | 10268.4349 | 2513.8361 | 7028.23 | NORMAL
324.817 | 0.95 | 294.26 | 1.11 | 2 | 79289.74 | 14662.5146 | 4356.8343 | 6650.006 | NORMAL
324.817 | 0.95 | 294.26 | 1.11 | 2 | 101352.97 | 14946.8347 | 5392.0706 | 6220.534 | NORMAL
324.817 | 0.95 | 294.26 | 1.11 | 2 | 106868.78 | 14868.8453 | 5545.2615 | 6137.269 | NORMAL
324.817 | 0.95 | 294.26 | 1.42 | 1 | 57226.51 | 9800.5569 | 1103.6407 | 5650.69 | NORMAL
324.817 | 0.95 | 294.26 | 1.42 | 1 | 79289.74 | 10884.789 | 3199.1483 | 4863.13 | NORMAL
324.817 | 0.95 | 294.26 | 1.42 | 1 | 101352.97 | 11208.1477 | 4197.866 | 4624.063 | NORMAL
324.817 | 0.95 | 294.26 | 1.42 | 1 | 106868.78 | 11159.5545 | 4295.8817 | 4583.382 | NORMAL
324.817 | 0.95 | 294.26 | 1.42 | 2 | 57226.51 | 10276.6999 | 1156.8378 | 7026.97 | NORMAL
324.817 | 0.95 | 294.26 | 1.42 | 2 | 79289.74 | 14892.8488 | 4660.3596 | 6677.29 | NORMAL
324.817 | 0.95 | 294.26 | 1.42 | 2 | 101352.97 | 15257.1805 | 5555.826 | 6244.637 | NORMAL
324.817 | 0.95 | 294.26 | 1.42 | 2 | 106868.78 | 15192.0574 | 5684.2298 | 6160.864 | NORMAL
324.817 | 0.95 | 297.037 | 0.5 | 1 | 57226.51 | 10024.9414 | 1999.0535 | 5594.716 | NORMAL
324.817 | 0.95 | 297.037 | 0.5 | 1 | 79289.74 | 11059.4959 | 3032.7018 | 4865.771 | NORMAL
324.817 | 0.95 | 297.037 | 0.5 | 1 | 101352.97 | 11092.8488 | 3652.864 | 4622.999 | NORMAL
324.817 | 0.95 | 297.037 | 0.5 | 1 | 106868.78 | 10981.653 | 3769.7709 | 4583.395 | NORMAL
324.817 | 0.95 | 297.037 | 0.5 | 2 | 57226.51 | 10360.0821 | 2015.2432 | 7011.255 | NORMAL
324.817 | 0.95 | 297.037 | 0.5 | 2 | 79289.74 | 14560.8734 | 4055.7274 | 6639.15 | NORMAL
324.817 | 0.95 | 297.037 | 0.5 | 2 | 101352.97 | 14480.6272 | 4890.9622 | 6187.77 | NORMAL
324.817 | 0.95 | 297.037 | 0.5 | 2 | 106868.78 | 14349.4138 | 5064.7261 | 6099.584 | NORMAL
324.817 | 0.95 | 297.037 | 0.8 | 1 | 57226.51 | 10113.306 | 2285.951 | 5571.739 | NORMAL
324.817 | 0.95 | 297.037 | 0.8 | 1 | 79289.74 | 11557.7374 | 3138.0182 | 4879.481 | NORMAL
324.817 | 0.95 | 297.037 | 0.8 | 1 | 101352.97 | 11782.0926 | 3849.3393 | 4625.174 | NORMAL
324.817 | 0.95 | 297.037 | 0.8 | 1 | 106868.78 | 11692.2626 | 3953.3878 | 4581.166 | NORMAL
324.817 | 0.95 | 297.037 | 0.8 | 2 | 57226.51 | 10432.6788 | 2316.5137 | 7006.298 | NORMAL
324.817 | 0.95 | 297.037 | 0.8 | 2 | 79289.74 | 15480.041 | 4155.4158 | 6730.946 | NORMAL
324.817 | 0.95 | 297.037 | 0.8 | 2 | 101352.97 | 15641.823 | 5116.4716 | 6278.419 | NORMAL
324.817 | 0.95 | 297.037 | 0.8 | 2 | 106868.78 | 15542.2626 | 5286.8871 | 6185.998 | NORMAL
324.817 | 0.95 | 297.037 | 1.11 | 1 | 57226.51 | 10158.7632 | 1870.3299 | 5566.36 | NORMAL
324.817 | 0.95 | 297.037 | 1.11 | 1 | 79289.74 | 11751.9637 | 3360.8266 | 4886.076 | NORMAL
324.817 | 0.95 | 297.037 | 1.11 | 1 | 101352.97 | 12070.5744 | 4008.336 | 4628.63 | NORMAL
324.817 | 0.95 | 297.037 | 1.11 | 1 | 106868.78 | 11997.2743 | 4092.8341 | 4582.571 | NORMAL
324.817 | 0.95 | 297.037 | 1.11 | 2 | 57226.51 | 10444.4607 | 1135.6993 | 7004.62 | NORMAL
324.817 | 0.95 | 297.037 | 1.11 | 2 | 79289.74 | 15889.5369 | 4157.0207 | 6772.142 | NORMAL
324.817 | 0.95 | 297.037 | 1.11 | 2 | 101352.97 | 16183.4701 | 5278.2711 | 6317.278 | NORMAL
324.817 | 0.95 | 297.037 | 1.11 | 2 | 106868.78 | 16098.1829 | 5443.7615 | 6226.654 | NORMAL
324.817 | 0.95 | 297.037 | 1.42 | 1 | 57226.51 | 10173.2708 | 574.8793 | 5562.39 | NORMAL
324.817 | 0.95 | 297.037 | 1.42 | 1 | 79289.74 | 11855.6565 | 3168.5783 | 4889.09 | NORMAL
324.817 | 0.95 | 297.037 | 1.42 | 1 | 101352.97 | 12208.4994 | 3899.1139 | 4627.816 | NORMAL
324.817 | 0.95 | 297.037 | 1.42 | 1 | 106868.78 | 12169.49 | 4084.9084 | 4583.003 | NORMAL
324.817 | 0.95 | 297.037 | 1.42 | 2 | 57226.51 | 10450.1465 | 2248.0251 | 7003.65 | NORMAL
324.817 | 0.95 | 297.037 | 1.42 | 2 | 79289.74 | 16130.0117 | 4320.6172 | 6794.81 | NORMAL
324.817 | 0.95 | 297.037 | 1.42 | 2 | 101352.97 | 16503.6928 | 5412.7822 | 6338.476 | NORMAL
324.817 | 0.95 | 297.037 | 1.42 | 2 | 106868.78 | 16425.2052 | 5578.8866 | 6250.69 | NORMAL
324.817 | 0.95 | 299.814 | 0.5 | 1 | 57226.51 | 10334.2907 | 1694.338 | 5503.074 | NORMAL
324.817 | 0.95 | 299.814 | 0.5 | 1 | 79289.74 | 12070.8089 | 2957.6258 | 4892.855 | NORMAL
324.817 | 0.95 | 299.814 | 0.5 | 1 | 101352.97 | 12134.7011 | 3598.3029 | 4629.91 | NORMAL
324.817 | 0.95 | 299.814 | 0.5 | 1 | 106868.78 | 12018.2005 | 3722.4814 | 4582.924 | NORMAL
324.817 | 0.95 | 299.814 | 0.5 | 2 | 57226.51 | 10552.5498 | 1760.7246 | 6988.633 | NORMAL
324.817 | 0.95 | 299.814 | 0.5 | 2 | 79289.74 | 15843.7866 | 3903.7031 | 6771.511 | NORMAL
324.817 | 0.95 | 299.814 | 0.5 | 2 | 101352.97 | 15750.4689 | 4775.4792 | 6286.708 | NORMAL
324.817 | 0.95 | 299.814 | 0.5 | 2 | 106868.78 | 15606.6237 | 4964.5294 | 6190.628 | NORMAL
324.817 | 0.95 | 299.814 | 0.8 | 1 | 57226.51 | 10389.83 | 2116.6785 | 5486.024 | NORMAL
324.817 | 0.95 | 299.814 | 0.8 | 1 | 79289.74 | 12556.4185 | 2894.8321 | 4912.427 | NORMAL
324.817 | 0.95 | 299.814 | 0.8 | 1 | 101352.97 | 12835.2286 | 3789.0622 | 4633.084 | NORMAL
324.817 | 0.95 | 299.814 | 0.8 | 1 | 106868.78 | 12737.7784 | 3893.786 | 4586.106 | NORMAL
324.817 | 0.95 | 299.814 | 0.8 | 2 | 57226.51 | 11073.007 | 2122.5072 | 6986.701 | NORMAL
324.817 | 0.95 | 299.814 | 0.8 | 2 | 79289.74 | 16790.2403 | 3937.8822 | 6853.309 | NORMAL
324.817 | 0.95 | 299.814 | 0.8 | 2 | 101352.97 | 16926.7878 | 4987.8843 | 6378.846 | NORMAL
324.817 | 0.95 | 299.814 | 0.8 | 2 | 106868.78 | 16819.6073 | 5162.543 | 6279.167 | NORMAL
324.817 | 0.95 | 299.814 | 1.11 | 1 | 57226.51 | 10401.4654 | 1156.6846 | 5479.9 | NORMAL
324.817 | 0.95 | 299.814 | 1.11 | 1 | 79289.74 | 12760.2872 | 3258.1479 | 4916.135 | NORMAL
324.817 | 0.95 | 299.814 | 1.11 | 1 | 101352.97 | 13122.7433 | 3920.1702 | 4639.129 | NORMAL
324.817 | 0.95 | 299.814 | 1.11 | 1 | 106868.78 | 13045.6624 | 4022.6691 | 4588.766 | NORMAL
324.817 | 0.95 | 299.814 | 1.11 | 2 | 57226.51 | 11086.6061 | 2088.7498 | 6985.42 | NORMAL
324.817 | 0.95 | 299.814 | 1.11 | 2 | 79289.74 | 17214.8593 | 3796.9438 | 6890.488 | NORMAL
324.817 | 0.95 | 299.814 | 1.11 | 2 | 101352.97 | 17468.2298 | 5123.0999 | 6420.513 | NORMAL
324.817 | 0.95 | 299.814 | 1.11 | 2 | 106868.78 | 17378.2532 | 5314.8259 | 6320.233 | NORMAL
324.817 | 0.95 | 299.814 | 1.42 | 1 | 57226.51 | 10409.2907 | 1981.7624 | 5476.51 | NORMAL
324.817 | 0.95 | 299.814 | 1.42 | 1 | 79289.74 | 12859.3201 | 3270.6909 | 4917.41 | NORMAL
324.817 | 0.95 | 299.814 | 1.42 | 1 | 101352.97 | 13263.4525 | 4036.0288 | 4638.878 | NORMAL
324.817 | 0.95 | 299.814 | 1.42 | 1 | 106868.78 | 13216.3834 | 4057.8658 | 4589.597 | NORMAL
324.817 | 0.95 | 299.814 | 1.42 | 2 | 57226.51 | 11093.728 | 2123.4283 | 6984.52 | NORMAL
324.817 | 0.95 | 299.814 | 1.42 | 2 | 79289.74 | 17470.5158 | 4128.2654 | 6915.48 | NORMAL
324.817 | 0.95 | 299.814 | 1.42 | 2 | 101352.97 | 17785.6389 | 5050.001 | 6444.128 | NORMAL
324.817 | 0.95 | 299.814 | 1.42 | 2 | 106868.78 | 17705.4513 | 5450.3576 | 6345.027 | NORMAL
324.817 | 0.95 | 302.591 | 0.5 | 1 | 57226.51 | 10531.2134 | 1505.7318 | 5416.054 | NORMAL
324.817 | 0.95 | 302.591 | 0.5 | 1 | 79289.74 | 13127.374 | 2870.0378 | 4925.086 | NORMAL
324.817 | 0.95 | 302.591 | 0.5 | 1 | 101352.97 | 13229.3083 | 3521.1788 | 4641.121 | NORMAL
324.817 | 0.95 | 302.591 | 0.5 | 1 | 106868.78 | 13106.2134 | 3652.9114 | 4589.32 | NORMAL
324.817 | 0.95 | 302.591 | 0.5 | 2 | 57226.51 | 11226.0844 | 1474.6584 | 6969.218 | NORMAL
324.817 | 0.95 | 302.591 | 0.5 | 2 | 79289.74 | 17240.7679 | 3787.0554 | 6893.109 | NORMAL
324.817 | 0.95 | 302.591 | 0.5 | 2 | 101352.97 | 17100.6448 | 4643.7485 | 6390.66 | NORMAL
324.817 | 0.95 | 302.591 | 0.5 | 2 | 106868.78 | 16943.1125 | 4839.8679 | 6287.189 | NORMAL
324.817 | 0.95 | 302.591 | 0.8 | 1 | 57226.51 | 10560.1114 | 1800.5835 | 5402.401 | NORMAL
324.817 | 0.95 | 302.591 | 0.8 | 1 | 79289.74 | 13603.9273 | 2751.5712 | 4945.39 | NORMAL
324.817 | 0.95 | 302.591 | 0.8 | 1 | 101352.97 | 13931.9168 | 3640.9532 | 4646.678 | NORMAL
324.817 | 0.95 | 302.591 | 0.8 | 1 | 106868.78 | 13828.9273 | 3814.6958 | 4595.597 | NORMAL
324.817 | 0.95 | 302.591 | 0.8 | 2 | 57226.51 | 11260.1993 | 2066.8771 | 6966.502 | NORMAL
324.817 | 0.95 | 302.591 | 0.8 | 2 | 79289.74 | 18242.0574 | 3700.8574 | 6980.797 | NORMAL
324.817 | 0.95 | 302.591 | 0.8 | 2 | 101352.97 | 18279.9531 | 4841.866 | 6482.829 | NORMAL
324.817 | 0.95 | 302.591 | 0.8 | 2 | 106868.78 | 18159.4959 | 5012.3296 | 6377.875 | NORMAL
324.817 | 0.95 | 302.591 | 1.11 | 1 | 57226.51 | 10569.8417 | 1830.1998 | 5398.34 | NORMAL
324.817 | 0.95 | 302.591 | 1.11 | 1 | 79289.74 | 13796.8054 | 3213.8003 | 4947.209 | NORMAL
324.817 | 0.95 | 302.591 | 1.11 | 1 | 101352.97 | 14215.2403 | 3869.6301 | 4651.998 | NORMAL
324.817 | 0.95 | 302.591 | 1.11 | 1 | 106868.78 | 14138.9214 | 3941.0123 | 4598.308 | NORMAL
324.817 | 0.95 | 302.591 | 1.11 | 2 | 57226.51 | 11270.5451 | 1119.9034 | 6965.5 | NORMAL
324.817 | 0.95 | 302.591 | 1.11 | 2 | 79289.74 | 18712.2216 | 3507.5124 | 7017.712 | NORMAL
324.817 | 0.95 | 302.591 | 1.11 | 2 | 101352.97 | 18815.5334 | 4810.3793 | 6527.935 | NORMAL
324.817 | 0.95 | 302.591 | 1.11 | 2 | 106868.78 | 18715.7679 | 5171.6346 | 6419.507 | NORMAL
324.817 | 0.95 | 302.591 | 1.42 | 1 | 57226.51 | 10576.2309 | 1781.5344 | 5395.9 | NORMAL
324.817 | 0.95 | 302.591 | 1.42 | 1 | 79289.74 | 13892.8781 | 2836.7451 | 4956.42 | NORMAL
324.817 | 0.95 | 302.591 | 1.42 | 1 | 101352.97 | 14360.0528 | 3856.1911 | 4653.883 | NORMAL
324.817 | 0.95 | 302.591 | 1.42 | 1 | 106868.78 | 14305.4807 | 3833.8116 | 4600.05 | NORMAL
324.817 | 0.95 | 302.591 | 1.42 | 2 | 57226.51 | 11276.4068 | 1910.3925 | 6964.98 | NORMAL
324.817 | 0.95 | 302.591 | 1.42 | 2 | 79289.74 | 18992.5557 | 3740.8687 | 7035.23 | NORMAL
324.817 | 0.95 | 302.591 | 1.42 | 2 | 101352.97 | 19135.3165 | 4820.7986 | 6551.553 | NORMAL
324.817 | 0.95 | 302.591 | 1.42 | 2 | 106868.78 | 19042.3505 | 5305.732 | 6444.129 | NORMAL
324.817 | 0.95 | 305.368 | 0.5 | 1 | 57226.51 | 10709.1149 | 1383.5534 | 5334.297 | NORMAL
324.817 | 0.95 | 305.368 | 0.5 | 1 | 79289.74 | 14227.8722 | 2718.363 | 4965.013 | NORMAL
324.817 | 0.95 | 305.368 | 0.5 | 1 | 101352.97 | 14376.7878 | 3427.1387 | 4656.698 | NORMAL
324.817 | 0.95 | 305.368 | 0.5 | 1 | 106868.78 | 14247.2743 | 3560.9068 | 4599.958 | NORMAL
324.817 | 0.95 | 305.368 | 0.5 | 2 | 57226.51 | 11426.7585 | 1348.6889 | 6953.143 | NORMAL
324.817 | 0.95 | 305.368 | 0.5 | 2 | 79289.74 | 18818.5815 | 3522.9702 | 7015.049 | NORMAL
324.817 | 0.95 | 305.368 | 0.5 | 2 | 101352.97 | 18522.9484 | 4457.8439 | 6501.82 | NORMAL
324.817 | 0.95 | 305.368 | 0.5 | 2 | 106868.78 | 18349.4431 | 4687.9708 | 6390.742 | NORMAL
324.817 | 0.95 | 305.368 | 0.8 | 1 | 57226.51 | 10724.8828 | 1656.7906 | 5324.334 | NORMAL
324.817 | 0.95 | 305.368 | 0.8 | 1 | 79289.74 | 14699.5604 | 2453.8711 | 4979.698 | NORMAL
324.817 | 0.95 | 305.368 | 0.8 | 1 | 101352.97 | 15074.2966 | 3478.3487 | 4664.276 | NORMAL
324.817 | 0.95 | 305.368 | 0.8 | 1 | 106868.78 | 14966.6471 | 3721.1874 | 4608.593 | NORMAL
324.817 | 0.95 | 305.368 | 0.8 | 2 | 57226.51 | 11452.374 | 1935.7032 | 6951.485 | NORMAL
324.817 | 0.95 | 305.368 | 0.8 | 2 | 79289.74 | 19767.0574 | 3426.1055 | 7082.567 | NORMAL
324.817 | 0.95 | 305.368 | 0.8 | 2 | 101352.97 | 19706.3892 | 4683.9131 | 6591.486 | NORMAL
324.817 | 0.95 | 305.368 | 0.8 | 2 | 106868.78 | 19563.4818 | 4848.3394 | 6481.967 | NORMAL
324.817 | 0.95 | 305.368 | 1.11 | 1 | 57226.51 | 10732.8253 | 1644.0864 | 5321.29 | NORMAL
324.817 | 0.95 | 305.368 | 1.11 | 1 | 79289.74 | 14888.9214 | 3035.5533 | 4983.366 | NORMAL
324.817 | 0.95 | 305.368 | 1.11 | 1 | 101352.97 | 15353.898 | 3571.1171 | 4670.492 | NORMAL
324.817 | 0.95 | 305.368 | 1.11 | 1 | 106868.78 | 15274.0035 | 3844.0085 | 4612.118 | NORMAL
324.817 | 0.95 | 305.368 | 1.11 | 2 | 57226.51 | 11459.9355 | 1733.1433 | 6950.92 | NORMAL
324.817 | 0.95 | 305.368 | 1.11 | 2 | 79289.74 | 20160.5803 | 3098.4191 | 7107.606 | NORMAL
324.817 | 0.95 | 305.368 | 1.11 | 2 | 101352.97 | 20240.1524 | 4405.087 | 6635.294 | NORMAL
324.817 | 0.95 | 305.368 | 1.11 | 2 | 106868.78 | 20115.8558 | 5016.6933 | 6523.69 | NORMAL
324.817 | 0.95 | 305.368 | 1.42 | 1 | 57226.51 | 10737.6026 | 1598.2814 | 5319.34 | NORMAL
324.817 | 0.95 | 305.368 | 1.42 | 1 | 79289.74 | 14985.0528 | 2990.8667 | 4986.39 | NORMAL
324.817 | 0.95 | 305.368 | 1.42 | 1 | 101352.97 | 15500.0586 | 3957.9865 | 4672.818 | NORMAL
324.817 | 0.95 | 305.368 | 1.42 | 1 | 106868.78 | 15437.6612 | 3656.8886 | 4614.445 | NORMAL
324.817 | 0.95 | 305.368 | 1.42 | 2 | 57226.51 | 11464.6249 | 1716.9651 | 6950.57 | NORMAL
324.817 | 0.95 | 305.368 | 1.42 | 2 | 79289.74 | 20388.4525 | 3652.3874 | 7119.76 | NORMAL
324.817 | 0.95 | 305.368 | 1.42 | 2 | 101352.97 | 20555.7737 | 4377.167 | 6659.286 | NORMAL
324.817 | 0.95 | 305.368 | 1.42 | 2 | 106868.78 | 20434.7597 | 5164.8855 | 6552.767
Note on A2: Data group defining the grid variables for cooling performance
Note on G2: Data group defining the lookup variables for cooling performance
Note on A3: Dry bulb temperature of the air entering the outdoor coil
Note on B3: Relative humidity of the air entering the indoor coil
Note on C3: Dry bulb temperature of the air entering the indoor coil
Note on D3: Mass flow rate of air entering the indoor coil
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Ambient absolute air pressure
Note on G3: Total heat removed by the indoor coil
Note on H3: Sensible heat removed by the indoor coil
Note on I3: Gross power draw (of the outdoor unit)
Note on J3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
outdoor_coil_environment_dry_bulb_temperature | gross_power
K | W
283.15 | 50
323.15 | 50
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the outdoor coil
Note on B3: Gross power draw (of the outdoor unit)