## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'AB': 350.0 ton, 2.03 COP liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 660f0087-cab0-41d4-b86b-98701d85e974 |  | ✓
| data_timestamp | 2022-12-20T09:13Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'AB' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 608214.9022 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.052741 | 277.0389 | 0.08546 | 285.9278 | 1 | 195394.8379 | 321295.9475 | 516690.7854 | 278.4867 | 287.3712 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.08546 | 285.9278 | 2 | 266550.5934 | 642591.895 | 909142.4884 | 279.9346 | 288.4676 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.08546 | 285.9278 | 3 | 372034.2875 | 963887.8425 | 1335922.13 | 281.3824 | 289.6598 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.08546 | 285.9278 | 4 | 511845.9203 | 1285183.7901 | 1797029.7104 | 282.8302 | 290.948 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.08546 | 295.0019 | 1 | 223501.0826 | 303192.1191 | 526693.2017 | 278.4051 | 296.4785 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.08546 | 295.0019 | 2 | 304892.119 | 606384.2383 | 911276.3573 | 279.7714 | 297.5567 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.08546 | 295.0019 | 3 | 425548.9392 | 909576.3574 | 1335125.2966 | 281.1376 | 298.745 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.08546 | 295.0019 | 4 | 585471.5432 | 1212768.4765 | 1798240.0198 | 282.5039 | 300.0434 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.08546 | 304.0759 | 1 | 225612.519 | 277639.0111 | 503251.5301 | 278.29 | 305.4914 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.08546 | 304.0759 | 2 | 307772.4645 | 555278.0221 | 863050.4866 | 279.5411 | 306.5034 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.08546 | 304.0759 | 3 | 429569.1414 | 832917.0332 | 1262486.1746 | 280.7922 | 307.6268 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.08546 | 304.0759 | 4 | 591002.5497 | 1110556.0443 | 1701558.594 | 282.0433 | 308.8618 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.08546 | 313.15 | 1 | 204149.0723 | 244636.6233 | 448785.6956 | 278.1413 | 314.4163 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.08546 | 313.15 | 2 | 278492.8043 | 489273.2466 | 767766.0509 | 279.2437 | 315.3164 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.08546 | 313.15 | 3 | 388702.4625 | 733909.8699 | 1122612.3324 | 280.3461 | 316.3177 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.08546 | 313.15 | 4 | 534778.0469 | 978546.4932 | 1513324.5401 | 281.4484 | 317.4202 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 285.9278 | 1 | 186552.2728 | 344598.094 | 531150.3668 | 282.484 | 287.4116 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 285.9278 | 2 | 254487.8848 | 689196.1879 | 943684.0727 | 284.0402 | 288.5641 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 285.9278 | 3 | 355197.9296 | 1033794.2819 | 1388992.2115 | 285.5965 | 289.8081 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 285.9278 | 4 | 488682.4072 | 1378392.3759 | 1867074.7831 | 287.1527 | 291.1436 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 295.0019 | 1 | 222315.0218 | 331956.3468 | 554271.3686 | 282.4269 | 296.5558 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 295.0019 | 2 | 303274.1377 | 663912.6935 | 967186.8313 | 283.926 | 297.7135 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 295.0019 | 3 | 423290.6643 | 995869.0403 | 1419159.7046 | 285.4252 | 298.9806 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 295.0019 | 4 | 582364.6016 | 1327825.3871 | 1910189.9887 | 286.9243 | 300.3572 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 304.0759 | 1 | 232183.2558 | 311865.3199 | 544048.5757 | 282.3362 | 305.6061 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 304.0759 | 2 | 316736.0267 | 623730.6397 | 940466.6665 | 283.7446 | 306.7211 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 304.0759 | 3 | 442079.9089 | 935595.9596 | 1377675.8685 | 285.153 | 307.9508 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 304.0759 | 4 | 608214.9022 | 1247461.2795 | 1855676.1817 | 286.5614 | 309.2953 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 313.15 | 1 | 217714.0494 | 284325.0133 | 502039.0627 | 282.2118 | 314.5666 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 313.15 | 2 | 296997.657 | 568650.0266 | 865647.6836 | 283.4958 | 315.5926 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 313.15 | 3 | 414530.3536 | 852975.0398 | 1267505.3934 | 284.7799 | 316.7265 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.08546 | 313.15 | 4 | 570312.1391 | 1137300.0531 | 1707612.1923 | 286.0639 | 317.9684 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 285.9278 | 1 | 175921.0738 | 353473.2723 | 529394.3461 | 286.416 | 287.4067 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 285.9278 | 2 | 239985.1865 | 706946.5445 | 946931.731 | 288.0152 | 288.5731 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 285.9278 | 3 | 334955.9899 | 1060419.8168 | 1395375.8067 | 289.6145 | 289.8259 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 285.9278 | 4 | 460833.4841 | 1413893.089 | 1874726.5731 | 291.2138 | 291.165 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 295.0019 | 1 | 216564.483 | 346293.6062 | 562858.0892 | 286.3835 | 296.5799 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 295.0019 | 2 | 295429.4599 | 692587.2125 | 988016.6724 | 287.9503 | 297.7718 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 295.0019 | 3 | 412341.5643 | 1038880.8187 | 1451222.383 | 289.5171 | 299.0705 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 295.0019 | 4 | 567300.7961 | 1385174.4249 | 1952475.221 | 291.0839 | 300.4758 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 304.0759 | 1 | 231999.7184 | 331664.6605 | 563664.3789 | 286.3173 | 305.6613 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 304.0759 | 2 | 316485.6516 | 663329.321 | 979814.9726 | 287.8179 | 306.8318 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 304.0759 | 3 | 441730.4512 | 994993.9815 | 1436724.4327 | 289.3185 | 308.1169 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 304.0759 | 4 | 607734.1174 | 1326658.642 | 1934392.7594 | 290.8191 | 309.5167 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 313.15 | 1 | 222921.0043 | 309586.4351 | 532507.4394 | 286.2174 | 314.6526 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 313.15 | 2 | 304100.7972 | 619172.8702 | 923273.6674 | 287.6181 | 315.7552 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 313.15 | 3 | 424444.4628 | 928759.3053 | 1353203.7681 | 289.0188 | 316.9684 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.08546 | 313.15 | 4 | 583952.0011 | 1238345.7404 | 1822297.7415 | 290.4196 | 318.292 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 285.9278 | 1 | 166006.7293 | 347921.4824 | 513928.2117 | 290.2823 | 287.3635 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 285.9278 | 2 | 226460.3951 | 695842.9648 | 922303.3599 | 291.8591 | 288.5043 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 285.9278 | 3 | 316078.9503 | 1043764.4471 | 1359843.3974 | 293.4359 | 289.7266 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 285.9278 | 4 | 434862.3948 | 1391685.9295 | 1826548.3243 | 295.0127 | 291.0304 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 295.0019 | 1 | 209162.4694 | 346203.8975 | 555366.3669 | 290.2746 | 296.5589 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 295.0019 | 2 | 285331.8998 | 692407.7951 | 977739.6949 | 291.8435 | 297.743 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 295.0019 | 3 | 398248.0351 | 1038611.6926 | 1436859.7276 | 293.4125 | 299.0302 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 295.0019 | 4 | 547910.8751 | 1384815.5901 | 1932726.4652 | 294.9815 | 300.4204 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 304.0759 | 1 | 228382.4251 | 337037.033 | 565419.4581 | 290.233 | 305.6662 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 304.0759 | 2 | 311551.0705 | 674074.066 | 985625.1364 | 291.7605 | 306.8481 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 304.0759 | 3 | 434843.0782 | 1011111.0989 | 1445954.1771 | 293.2879 | 308.1429 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 304.0759 | 4 | 598258.4483 | 1348148.1319 | 1946406.5802 | 294.8154 | 309.5505 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 313.15 | 1 | 223497.9704 | 320420.8887 | 543918.8592 | 290.1577 | 314.6848 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 313.15 | 2 | 304887.8735 | 640841.7775 | 945729.651 | 291.6098 | 315.8186 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 313.15 | 3 | 425543.0137 | 961262.6662 | 1386805.6799 | 293.062 | 317.0632 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.08546 | 313.15 | 4 | 585463.3908 | 1281683.5549 | 1867146.9457 | 294.5141 | 318.4186 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation