## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'C': 37.5 ton, 2.64 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 04e19f33-6165-491c-a56a-f579bce281b5 |  | ✓
| data_timestamp | 2022-12-20T09:13Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'C' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 60325.5736 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.0056508 | 277.0389 | 0.0084573 | 285.9278 | 1 | 12480.8909 | 33321.1319 | 45802.0228 | 278.4403 | 287.2207 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0084573 | 285.9278 | 2 | 18351.3727 | 66642.2638 | 84993.6365 | 279.8417 | 288.3271 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0084573 | 285.9278 | 3 | 27062.8296 | 99963.3957 | 127026.2253 | 281.2432 | 289.5136 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0084573 | 285.9278 | 4 | 38615.2615 | 133284.5276 | 171899.7891 | 282.6446 | 290.7804 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0084573 | 295.0019 | 1 | 13932.4859 | 31768.5818 | 45701.0677 | 278.375 | 296.2966 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0084573 | 295.0019 | 2 | 20485.7365 | 63537.1636 | 84022.9001 | 279.7111 | 297.3822 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0084573 | 295.0019 | 3 | 30210.3829 | 95305.7454 | 125516.1283 | 281.0473 | 298.5577 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0084573 | 295.0019 | 4 | 43106.425 | 127074.3273 | 170180.7523 | 282.3834 | 299.8231 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0084573 | 304.0759 | 1 | 15987.5191 | 29265.8685 | 45253.3876 | 278.2698 | 305.3621 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0084573 | 304.0759 | 2 | 23507.3701 | 58531.737 | 82039.1071 | 279.5006 | 306.4076 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0084573 | 304.0759 | 3 | 34666.3959 | 87797.6055 | 122464.0014 | 280.7315 | 307.5565 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0084573 | 304.0759 | 4 | 49464.5963 | 117063.474 | 166528.0703 | 281.9624 | 308.8089 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0084573 | 313.15 | 1 | 18010.626 | 25812.992 | 43823.618 | 278.1245 | 314.3996 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0084573 | 313.15 | 2 | 26482.0608 | 51625.9839 | 78108.0447 | 279.2102 | 315.3771 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0084573 | 313.15 | 3 | 39053.182 | 77438.9759 | 116492.1579 | 280.2958 | 316.4716 | 15000 | 15000 | 0 | 0
0.0056508 | 277.0389 | 0.0084573 | 313.15 | 4 | 55723.9896 | 103251.9678 | 158975.9574 | 281.3815 | 317.6829 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 285.9278 | 1 | 12672.6018 | 37498.651 | 50171.2528 | 282.5083 | 287.3441 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 285.9278 | 2 | 18633.2564 | 74997.3019 | 93630.5583 | 284.0889 | 288.5709 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 285.9278 | 3 | 27478.5244 | 112495.9529 | 139974.4773 | 285.6695 | 289.8791 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 285.9278 | 4 | 39208.4058 | 149994.6039 | 189203.0097 | 287.25 | 291.2688 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 295.0019 | 1 | 14205.6003 | 35969.3702 | 50174.9704 | 282.4439 | 296.4233 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 295.0019 | 2 | 20887.3123 | 71938.7404 | 92826.0526 | 283.96 | 297.6316 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 295.0019 | 3 | 30802.588 | 107908.1105 | 138710.6985 | 285.4761 | 298.9315 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 295.0019 | 4 | 43951.4273 | 143877.4807 | 187828.9081 | 286.9922 | 300.3231 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 304.0759 | 1 | 16599.2685 | 33489.9262 | 50089.1946 | 282.3394 | 305.4995 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 304.0759 | 2 | 24406.8605 | 66979.8523 | 91386.7129 | 283.751 | 306.6733 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 304.0759 | 3 | 35992.8773 | 100469.7785 | 136462.6558 | 285.1626 | 307.9544 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 304.0759 | 4 | 51357.3189 | 133959.7047 | 185317.0236 | 286.5742 | 309.3429 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 313.15 | 1 | 19241.2769 | 30060.3189 | 49301.5959 | 282.1948 | 314.5558 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 313.15 | 2 | 28291.5577 | 60120.6379 | 88412.1956 | 283.4619 | 315.6709 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 313.15 | 3 | 41721.653 | 90180.9568 | 131902.6098 | 284.7289 | 316.911 | 15000 | 15000 | 0 | 0
0.0056508 | 280.9278 | 0.0084573 | 313.15 | 4 | 59531.5629 | 120241.2757 | 179772.8386 | 285.9959 | 318.2759 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 285.9278 | 1 | 12838.1041 | 39564.9794 | 52403.0834 | 286.4874 | 287.4071 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 285.9278 | 2 | 18876.6039 | 79129.9587 | 98006.5626 | 288.1582 | 288.6944 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 285.9278 | 3 | 27837.3897 | 118694.9381 | 146532.3278 | 289.829 | 290.0643 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 285.9278 | 4 | 39720.4615 | 158259.9175 | 197980.379 | 291.4998 | 291.5166 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 295.0019 | 1 | 14251.5307 | 38058.9679 | 52310.4986 | 286.4238 | 296.4838 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 295.0019 | 2 | 20954.8464 | 76117.9358 | 97072.7822 | 288.031 | 297.7519 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 295.0019 | 3 | 30902.1808 | 114176.9036 | 145079.0844 | 289.6382 | 299.112 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 295.0019 | 4 | 44093.5338 | 152235.8715 | 196329.4053 | 291.2454 | 300.5639 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 304.0759 | 1 | 16667.8977 | 35602.7932 | 52270.6909 | 286.3201 | 305.5615 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 304.0759 | 2 | 24507.77 | 71205.5863 | 95713.3564 | 287.8236 | 306.7962 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 304.0759 | 3 | 36141.6889 | 106808.3795 | 142950.0684 | 289.327 | 308.1388 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 304.0759 | 4 | 51569.6543 | 142411.1727 | 193980.827 | 290.8305 | 309.5891 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 313.15 | 1 | 19497.9102 | 32196.4552 | 51694.3655 | 286.1763 | 314.624 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 313.15 | 2 | 28668.9004 | 64392.9105 | 93061.8109 | 287.5359 | 315.8035 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 313.15 | 3 | 42278.1216 | 96589.3657 | 138867.4873 | 288.8955 | 317.1096 | 15000 | 15000 | 0 | 0
0.0056508 | 284.8167 | 0.0084573 | 313.15 | 4 | 60325.5736 | 128785.8209 | 189111.3946 | 290.2551 | 318.5422 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 285.9278 | 1 | 13206.1897 | 39520.1171 | 52726.3068 | 290.3772 | 287.4162 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 285.9278 | 2 | 19417.8213 | 79040.2342 | 98458.0555 | 292.0488 | 288.7072 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 285.9278 | 3 | 28635.5249 | 118560.3513 | 147195.8762 | 293.7205 | 290.083 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 285.9278 | 4 | 40859.3003 | 158080.4684 | 198939.7687 | 295.3921 | 291.5437 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 295.0019 | 1 | 14345.0845 | 38037.3749 | 52382.4594 | 290.3145 | 296.4859 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 295.0019 | 2 | 21092.4039 | 76074.7498 | 97167.1538 | 291.9234 | 297.7546 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 295.0019 | 3 | 31105.0373 | 114112.1248 | 145217.1621 | 293.5323 | 299.1159 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 295.0019 | 4 | 44382.9847 | 152149.4997 | 196532.4843 | 295.1413 | 300.5696 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 304.0759 | 1 | 16514.2291 | 35604.4695 | 52118.6986 | 290.2116 | 305.5572 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 304.0759 | 2 | 24281.8223 | 71208.939 | 95490.7613 | 291.7176 | 306.7899 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 304.0759 | 3 | 35808.483 | 106813.4085 | 142621.8915 | 293.2236 | 308.1294 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 304.0759 | 4 | 51094.2113 | 142417.878 | 193512.0894 | 294.7296 | 309.5758 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 313.15 | 1 | 19147.3634 | 32221.4009 | 51368.7643 | 290.0685 | 314.6147 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 313.15 | 2 | 28153.4713 | 64442.8018 | 92596.2731 | 291.4314 | 315.7902 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 313.15 | 3 | 41518.0166 | 96664.2026 | 138182.2192 | 292.7943 | 317.09 | 15000 | 15000 | 0 | 0
0.0056508 | 288.7056 | 0.0084573 | 313.15 | 4 | 59240.9992 | 128885.6035 | 188126.6027 | 294.1572 | 318.5141 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation