## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'E': 225.0 ton, 2.32 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 0b2012ae-a354-4a6f-bf9a-81de03d39030 |  | ✓
| data_timestamp | 2022-12-20T09:13Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'E' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 394802.7683 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.033905 | 277.0389 | 0.052646 | 285.9278 | 1 | 79389.5655 | 191894.2227 | 271283.7882 | 278.384 | 287.158 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.052646 | 285.9278 | 2 | 116244.4068 | 383788.4454 | 500032.8522 | 279.7291 | 288.1954 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.052646 | 285.9278 | 3 | 170227.6592 | 575682.6681 | 745910.3273 | 281.0742 | 289.3104 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.052646 | 285.9278 | 4 | 241339.3227 | 767576.8908 | 1008916.2135 | 282.4194 | 290.5031 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.052646 | 295.0019 | 1 | 96943.651 | 190688.4739 | 287632.1249 | 278.3756 | 296.3109 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.052646 | 295.0019 | 2 | 141947.5864 | 381376.9478 | 523324.5341 | 279.7122 | 297.3835 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.052646 | 295.0019 | 3 | 207867.2516 | 572065.4217 | 779932.6732 | 281.0489 | 298.5514 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.052646 | 295.0019 | 4 | 294702.6467 | 762753.8955 | 1057456.5422 | 282.3856 | 299.8144 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.052646 | 304.0759 | 1 | 113015.1027 | 182087.7404 | 295102.8431 | 278.3153 | 305.4233 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.052646 | 304.0759 | 2 | 165479.8522 | 364175.4808 | 529655.333 | 279.5916 | 306.4942 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.052646 | 304.0759 | 3 | 242327.77 | 546263.2212 | 788590.9912 | 280.868 | 307.6764 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.052646 | 304.0759 | 4 | 343558.8562 | 728350.9616 | 1071909.8179 | 282.1444 | 308.97 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.052646 | 313.15 | 1 | 124658.9021 | 166092.0223 | 290750.9244 | 278.2031 | 314.4818 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.052646 | 313.15 | 2 | 182529.0267 | 332184.0446 | 514713.0713 | 279.3674 | 315.5076 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.052646 | 313.15 | 3 | 267294.4859 | 498276.0669 | 765570.5528 | 280.5316 | 316.6567 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.052646 | 313.15 | 4 | 378955.2796 | 664368.0891 | 1043323.3688 | 281.6959 | 317.929 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 285.9278 | 1 | 79555.761 | 207646.9903 | 287202.7513 | 282.3865 | 287.2302 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 285.9278 | 2 | 116487.7548 | 415293.9806 | 531781.7354 | 283.8452 | 288.3393 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 285.9278 | 3 | 170584.0166 | 622940.9709 | 793524.9875 | 285.3039 | 289.5263 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 285.9278 | 4 | 241844.5464 | 830587.9613 | 1072432.5077 | 286.7626 | 290.7911 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 295.0019 | 1 | 97499.6621 | 207746.6494 | 305246.3115 | 282.3872 | 296.3911 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 295.0019 | 2 | 142761.7131 | 415493.2988 | 558255.0119 | 283.8466 | 297.5425 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 295.0019 | 3 | 209059.4543 | 623239.9482 | 832299.4025 | 285.306 | 298.7897 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 295.0019 | 4 | 296392.8855 | 830986.5977 | 1127379.4831 | 286.7654 | 300.1326 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 304.0759 | 1 | 114881.2938 | 200451.3239 | 315332.6177 | 282.3359 | 305.5157 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 304.0759 | 2 | 168212.3811 | 400902.6477 | 569115.0289 | 283.7441 | 306.6744 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 304.0759 | 3 | 246329.2702 | 601353.9716 | 847683.2418 | 285.1523 | 307.9462 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 304.0759 | 4 | 349231.9609 | 801805.2955 | 1151037.2564 | 286.5604 | 309.3313 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 313.15 | 1 | 129012.7517 | 185761.0137 | 314773.7653 | 282.2327 | 314.5918 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 313.15 | 2 | 188904.0542 | 371522.0273 | 560426.0815 | 283.5377 | 315.717 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 313.15 | 3 | 276630.0404 | 557283.041 | 833913.0814 | 284.8427 | 316.9697 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.052646 | 313.15 | 4 | 392190.7104 | 743044.0547 | 1135234.7651 | 286.1476 | 318.35 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 285.9278 | 1 | 80403.0932 | 214532.1588 | 294935.252 | 286.3266 | 287.2653 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 285.9278 | 2 | 117728.4422 | 429064.3175 | 546792.7597 | 287.8365 | 288.4074 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 285.9278 | 3 | 172400.8723 | 643596.4763 | 815997.3486 | 289.3464 | 289.6282 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 285.9278 | 4 | 244420.3835 | 858128.6351 | 1102549.0186 | 290.8563 | 290.9277 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 295.0019 | 1 | 97709.7404 | 215937.2258 | 313646.9662 | 286.3365 | 296.4293 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 295.0019 | 2 | 143069.3157 | 431874.4516 | 574943.7673 | 287.8562 | 297.6185 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 295.0019 | 3 | 209509.9057 | 647811.6774 | 857321.5831 | 289.376 | 298.9036 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 295.0019 | 4 | 297031.5105 | 863748.9032 | 1160780.4137 | 290.8958 | 300.2847 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 304.0759 | 1 | 115009.6393 | 209947.3082 | 324956.9475 | 286.2943 | 305.5596 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 304.0759 | 2 | 168400.3081 | 419894.6164 | 588294.9245 | 287.7719 | 306.7619 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 304.0759 | 3 | 246604.4694 | 629841.9245 | 876446.394 | 289.2496 | 308.0776 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 304.0759 | 4 | 349622.1231 | 839789.2327 | 1189411.3559 | 290.7272 | 309.5065 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 313.15 | 1 | 129871.9989 | 196562.4059 | 326434.4048 | 286.2001 | 314.6452 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 313.15 | 2 | 190162.1878 | 393124.8118 | 583286.9996 | 287.5835 | 315.8218 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 313.15 | 3 | 278472.4443 | 589687.2177 | 868159.662 | 288.967 | 317.1266 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.052646 | 313.15 | 4 | 394802.7683 | 786249.6236 | 1181052.3919 | 290.3504 | 318.5598 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 285.9278 | 1 | 82612.9578 | 212549.7281 | 295162.6858 | 290.204 | 287.2663 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 285.9278 | 2 | 120964.1872 | 425099.4562 | 546063.6434 | 291.7024 | 288.4041 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 285.9278 | 3 | 177139.2792 | 637649.1843 | 814788.4635 | 293.2008 | 289.6227 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 285.9278 | 4 | 251138.2338 | 850198.9123 | 1101337.1461 | 294.6993 | 290.9222 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 295.0019 | 1 | 98568.0235 | 215260.203 | 313828.2265 | 290.2231 | 296.4301 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 295.0019 | 2 | 144326.0376 | 430520.4061 | 574846.4437 | 291.7406 | 297.618 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 295.0019 | 3 | 211350.2423 | 645780.6091 | 857130.8514 | 293.2582 | 298.9027 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 295.0019 | 4 | 299640.6375 | 861040.8122 | 1160681.4497 | 294.7757 | 300.2842 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 304.0759 | 1 | 114707.0184 | 210575.6933 | 325282.7118 | 290.1901 | 305.5611 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 304.0759 | 2 | 167957.2022 | 421151.3867 | 589108.5889 | 291.6746 | 306.7657 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 304.0759 | 3 | 245955.5876 | 631727.08 | 877682.6676 | 293.1591 | 308.0832 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 304.0759 | 4 | 348702.1745 | 842302.7734 | 1191004.9479 | 294.6436 | 309.5138 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 313.15 | 1 | 128856.2651 | 198496.199 | 327352.4641 | 290.1049 | 314.6494 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 313.15 | 2 | 188674.9221 | 396992.398 | 585667.3201 | 291.5043 | 315.8327 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 313.15 | 3 | 276294.5007 | 595488.597 | 871783.0977 | 292.9036 | 317.1432 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.052646 | 313.15 | 4 | 391715.0009 | 793984.796 | 1185699.7969 | 294.303 | 318.5811 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation