## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'F': 450.0 ton, 2.15 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | eb8cb70c-ecc7-47ef-8d0c-141da84ce4a7 |  | ✓
| data_timestamp | 2022-12-20T09:13Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'F' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 805220.2121 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.067809 | 277.0389 | 0.10789 | 285.9278 | 1 | 185909.3057 | 389171.2044 | 575080.51 | 278.4029 | 287.2003 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10789 | 285.9278 | 2 | 272261.486 | 778342.4087 | 1050603.8947 | 279.7669 | 288.2526 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10789 | 285.9278 | 3 | 395812.0827 | 1167513.6131 | 1563325.6957 | 281.1308 | 289.3871 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10789 | 285.9278 | 4 | 556561.0957 | 1556684.8175 | 2113245.9131 | 282.4948 | 290.604 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10789 | 295.0019 | 1 | 223228.0117 | 386210.0193 | 609438.0309 | 278.3925 | 296.3553 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10789 | 295.0019 | 2 | 326914.1905 | 772420.0386 | 1099334.229 | 279.7461 | 297.4432 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10789 | 295.0019 | 3 | 475265.8501 | 1158630.0579 | 1633895.9079 | 281.0997 | 298.6303 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10789 | 295.0019 | 4 | 668282.9904 | 1544840.0771 | 2213123.0676 | 282.4533 | 299.9166 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10789 | 304.0759 | 1 | 251549.6626 | 370413.4864 | 621963.149 | 278.3371 | 305.4616 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10789 | 304.0759 | 2 | 368390.8382 | 740826.9728 | 1109217.811 | 279.6354 | 306.5471 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10789 | 304.0759 | 3 | 535564.3468 | 1111240.4592 | 1646804.8059 | 280.9336 | 307.7448 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10789 | 304.0759 | 4 | 753070.1883 | 1481653.9456 | 2234724.1339 | 282.2319 | 309.0546 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10789 | 313.15 | 1 | 266942.2071 | 341781.6057 | 608723.8128 | 278.2368 | 314.5106 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10789 | 313.15 | 2 | 390932.9967 | 683563.2114 | 1074496.2081 | 279.4347 | 315.5516 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10789 | 313.15 | 3 | 568335.9989 | 1025344.8171 | 1593680.816 | 280.6326 | 316.712 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10789 | 313.15 | 4 | 799151.2137 | 1367126.4228 | 2166277.6364 | 281.8304 | 317.9918 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 285.9278 | 1 | 179247.6619 | 410923.9191 | 590171.581 | 282.3711 | 287.2337 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 285.9278 | 2 | 262505.6051 | 821847.8383 | 1084353.4434 | 283.8145 | 288.3273 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 285.9278 | 3 | 381629.0427 | 1232771.7574 | 1614400.8001 | 285.2579 | 289.5001 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 285.9278 | 4 | 536617.9747 | 1643695.6765 | 2180313.6513 | 286.7012 | 290.7524 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 295.0019 | 1 | 217883.8038 | 411704.4381 | 629588.2418 | 282.3739 | 296.4 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 295.0019 | 2 | 319087.6754 | 823408.8761 | 1142496.5515 | 283.82 | 297.539 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 295.0019 | 3 | 463887.7103 | 1235113.3142 | 1699001.0245 | 285.2661 | 298.7749 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 295.0019 | 4 | 652283.9086 | 1646817.7522 | 2299101.6608 | 286.7122 | 300.1075 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 304.0759 | 1 | 249005.3336 | 399649.6092 | 648654.9428 | 282.3315 | 305.5211 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 304.0759 | 2 | 364664.7052 | 799299.2183 | 1163963.9236 | 283.7353 | 306.6691 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 304.0759 | 3 | 530147.3174 | 1198948.8275 | 1729096.145 | 285.1391 | 307.9282 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 304.0759 | 4 | 745453.1703 | 1598598.4367 | 2344051.607 | 286.5428 | 309.2982 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 313.15 | 1 | 268969.4478 | 374759.4325 | 643728.8802 | 282.2441 | 314.5888 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 313.15 | 2 | 393901.8613 | 749518.865 | 1143420.7262 | 283.5605 | 315.7056 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 313.15 | 3 | 572652.1161 | 1124278.2974 | 1696930.4135 | 284.8768 | 316.9428 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10789 | 313.15 | 4 | 805220.2121 | 1499037.7299 | 2304257.942 | 286.1931 | 318.3002 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 285.9278 | 1 | 176413.4212 | 419094.009 | 595507.4303 | 286.2915 | 287.2455 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 285.9278 | 2 | 258354.9007 | 838188.0181 | 1096542.9188 | 287.7663 | 288.3542 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 285.9278 | 3 | 375594.7741 | 1257282.0271 | 1632876.8012 | 289.2411 | 289.541 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 285.9278 | 4 | 528133.0413 | 1676376.0361 | 2204509.0774 | 290.7159 | 290.8059 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 295.0019 | 1 | 214639.5857 | 423616.232 | 638255.8177 | 286.3074 | 296.4192 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 295.0019 | 2 | 314336.5651 | 847232.4639 | 1161569.029 | 287.7981 | 297.5814 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 295.0019 | 3 | 456980.5752 | 1270848.6959 | 1727829.2711 | 289.2889 | 298.8389 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 295.0019 | 4 | 642571.6161 | 1694464.9278 | 2337036.5439 | 290.7796 | 300.1918 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 304.0759 | 1 | 246376.9066 | 415303.1071 | 661680.0137 | 286.2781 | 305.5501 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 304.0759 | 2 | 360815.4119 | 830606.2142 | 1191421.6261 | 287.7396 | 306.7303 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 304.0759 | 3 | 524551.2384 | 1245909.3212 | 1770460.5596 | 289.2011 | 308.0203 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 304.0759 | 4 | 737584.3861 | 1661212.4283 | 2398796.8144 | 290.6626 | 309.4202 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 313.15 | 1 | 268271.8281 | 394154.6344 | 662426.4624 | 286.2037 | 314.6306 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 313.15 | 2 | 392880.2073 | 788309.2688 | 1181189.4761 | 287.5908 | 315.7901 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 313.15 | 3 | 571166.8418 | 1182463.9031 | 1753630.7449 | 288.9778 | 317.0695 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10789 | 313.15 | 4 | 803131.7314 | 1576618.5375 | 2379750.269 | 290.3649 | 318.469 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 285.9278 | 1 | 178671.6328 | 413681.4741 | 592353.1068 | 290.1637 | 287.2385 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 285.9278 | 2 | 261662.0188 | 827362.9481 | 1089024.967 | 291.6219 | 288.3376 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 285.9278 | 3 | 380402.6422 | 1241044.4222 | 1621447.0643 | 293.0801 | 289.5157 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 285.9278 | 4 | 534893.5027 | 1654725.8963 | 2189619.399 | 294.5383 | 290.773 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 295.0019 | 1 | 215351.2451 | 421945.401 | 637296.6461 | 290.1929 | 296.4171 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 295.0019 | 2 | 315378.7799 | 843890.802 | 1159269.5819 | 291.6802 | 297.5763 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 295.0019 | 3 | 458495.7408 | 1265836.203 | 1724331.9438 | 293.1675 | 298.8311 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 295.0019 | 4 | 644702.1277 | 1687781.604 | 2332483.7317 | 294.6548 | 300.1817 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 304.0759 | 1 | 246111.1078 | 417373.9801 | 663485.0879 | 290.1768 | 305.5541 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 304.0759 | 2 | 360426.1534 | 834747.9602 | 1195174.1136 | 291.6479 | 306.7386 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 304.0759 | 3 | 523985.3367 | 1252121.9403 | 1776107.277 | 293.1191 | 308.0329 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 304.0759 | 4 | 736788.6578 | 1669495.9204 | 2406284.5782 | 294.5903 | 309.4369 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 313.15 | 1 | 267886.9127 | 399967.2114 | 667854.1241 | 290.1154 | 314.6427 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 313.15 | 2 | 392316.5043 | 799934.4228 | 1192250.9272 | 291.5252 | 315.8148 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 313.15 | 3 | 570347.3338 | 1199901.6343 | 1770248.9681 | 292.9351 | 317.1067 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10789 | 313.15 | 4 | 801979.4011 | 1599868.8457 | 2401848.2468 | 294.3449 | 318.5183 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation