## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'G': 650.0 ton, 1.97 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 2b97164d-8b25-4ca5-aaf1-3ad3e0c315c9 |  | ✓
| data_timestamp | 2022-12-20T09:13Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'G' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 1219036.8567 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.097947 | 277.0389 | 0.16027 | 285.9278 | 1 | 305679.4596 | 552588.9297 | 858268.3893 | 278.3797 | 287.2063 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.16027 | 285.9278 | 2 | 436786.9573 | 1105177.8594 | 1541964.8167 | 279.7205 | 288.2248 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.16027 | 285.9278 | 3 | 618003.9609 | 1657766.7891 | 2275770.75 | 281.0613 | 289.3179 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.16027 | 285.9278 | 4 | 849330.4705 | 2210355.7188 | 3059686.1893 | 282.4022 | 290.4857 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.16027 | 295.0019 | 1 | 383302.2575 | 558114.4216 | 941416.6791 | 278.3931 | 296.4093 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.16027 | 295.0019 | 2 | 547702.5738 | 1116228.8431 | 1663931.4169 | 279.7473 | 297.4894 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.16027 | 295.0019 | 3 | 774936.9672 | 1674343.2647 | 2449280.2319 | 281.1016 | 298.6635 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.16027 | 295.0019 | 4 | 1065005.4378 | 2232457.6863 | 3297463.1241 | 282.4558 | 299.9315 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.16027 | 304.0759 | 1 | 429973.0431 | 538888.6139 | 968861.657 | 278.3465 | 305.529 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.16027 | 304.0759 | 2 | 614390.7002 | 1077777.2277 | 1692167.9279 | 279.654 | 306.6139 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.16027 | 304.0759 | 3 | 869293.0957 | 1616665.8416 | 2485958.9373 | 280.9616 | 307.8044 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.16027 | 304.0759 | 4 | 1194680.2297 | 2155554.4554 | 3350234.6851 | 282.2692 | 309.1006 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.16027 | 313.15 | 1 | 438739.1487 | 494911.5066 | 933650.6553 | 278.2398 | 314.5548 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.16027 | 313.15 | 2 | 626916.6337 | 989823.0131 | 1616739.6468 | 279.4406 | 315.5826 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.16027 | 313.15 | 3 | 887015.8697 | 1484734.5197 | 2371750.3894 | 280.6415 | 316.7187 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.16027 | 313.15 | 4 | 1219036.8567 | 1979646.0263 | 3198682.883 | 281.8424 | 317.9629 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 285.9278 | 1 | 288269.0068 | 574936.9587 | 863205.9655 | 282.3259 | 287.2137 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 285.9278 | 2 | 411909.0714 | 1149873.9175 | 1561782.9889 | 283.724 | 288.2543 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 285.9278 | 3 | 582804.5765 | 1724810.8762 | 2307615.4527 | 285.122 | 289.3653 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 285.9278 | 4 | 800955.5221 | 2299747.8349 | 3100703.357 | 286.5201 | 290.5468 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 295.0019 | 1 | 368659.1637 | 588065.3077 | 956724.4714 | 282.3578 | 296.4321 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 295.0019 | 2 | 526778.9814 | 1176130.6154 | 1702909.5968 | 283.7878 | 297.5477 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 295.0019 | 3 | 745332.4592 | 1764195.9231 | 2509528.3823 | 285.2178 | 298.7536 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 295.0019 | 4 | 1024319.5971 | 2352261.2308 | 3376580.8279 | 286.6478 | 300.0498 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 304.0759 | 1 | 420753.9365 | 576442.3571 | 997196.2936 | 282.3295 | 305.5715 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 304.0759 | 2 | 601217.4712 | 1152884.7142 | 1754102.1854 | 283.7313 | 306.7067 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 304.0759 | 3 | 850654.4721 | 1729327.0712 | 2579981.5433 | 285.133 | 307.9454 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 304.0759 | 4 | 1169064.9392 | 2305769.4283 | 3474834.3676 | 286.5348 | 309.2875 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 313.15 | 1 | 437688.5999 | 540068.1069 | 977756.7068 | 282.2411 | 314.6212 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 313.15 | 2 | 625415.499 | 1080136.2138 | 1705551.7128 | 283.5544 | 315.7163 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 313.15 | 3 | 884891.9345 | 1620204.3207 | 2505096.2552 | 284.8677 | 316.9193 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.16027 | 313.15 | 4 | 1216117.9064 | 2160272.4275 | 3376390.3339 | 286.181 | 318.2303 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 285.9278 | 1 | 279073.4742 | 580880.7936 | 859954.2678 | 286.2318 | 287.2088 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 285.9278 | 2 | 398769.5274 | 1161761.5873 | 1560531.1147 | 287.647 | 288.2524 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 285.9278 | 3 | 564213.6133 | 1742642.3809 | 2306855.9942 | 289.0622 | 289.3642 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 285.9278 | 4 | 775405.732 | 2323523.1745 | 3098928.9065 | 290.4774 | 290.5441 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 295.0019 | 1 | 359671.613 | 601611.9997 | 961283.6127 | 286.2824 | 296.439 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 295.0019 | 2 | 513936.6239 | 1203223.9994 | 1717160.6233 | 287.748 | 297.569 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 295.0019 | 3 | 727161.9813 | 1804835.9991 | 2531997.9804 | 289.2137 | 298.7872 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 295.0019 | 4 | 999347.685 | 2406447.9988 | 3405795.6838 | 290.6794 | 300.0935 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 304.0759 | 1 | 413990.9336 | 597591.9062 | 1011582.8397 | 286.2726 | 305.5931 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 304.0759 | 2 | 591553.7813 | 1195183.8124 | 1786737.5937 | 287.7285 | 306.7557 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 304.0759 | 3 | 836981.448 | 1792775.7185 | 2629757.1665 | 289.1844 | 308.0201 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 304.0759 | 4 | 1150273.9334 | 2390367.6247 | 3540641.5582 | 290.6402 | 309.3862 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 313.15 | 1 | 435254.6522 | 568820.5131 | 1004075.1653 | 286.2025 | 314.6608 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 313.15 | 2 | 621937.6187 | 1137641.0262 | 1759578.6448 | 287.5883 | 315.7976 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 313.15 | 3 | 879971.1287 | 1706461.5392 | 2586432.6679 | 288.9741 | 317.0417 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.16027 | 313.15 | 4 | 1209355.1822 | 2275282.0523 | 3484637.2345 | 290.3599 | 318.3932 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 285.9278 | 1 | 279674.0312 | 570420.4344 | 850094.4656 | 290.0976 | 287.1941 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 285.9278 | 2 | 399627.6664 | 1140840.8688 | 1540468.5353 | 291.4896 | 288.2226 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 285.9278 | 3 | 565427.7827 | 1711261.3032 | 2276689.0859 | 292.8816 | 289.3193 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 285.9278 | 4 | 777074.3799 | 2281681.7376 | 3058756.1175 | 294.2736 | 290.4843 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 295.0019 | 1 | 359022.1709 | 598754.4976 | 957776.6685 | 290.1667 | 296.4337 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 295.0019 | 2 | 513008.6327 | 1197508.9951 | 1710517.6279 | 291.6278 | 297.5591 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 295.0019 | 3 | 725848.9791 | 1796263.4927 | 2522112.4718 | 293.089 | 298.7724 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 295.0019 | 4 | 997543.2099 | 2395017.9903 | 3392561.2002 | 294.5501 | 300.0737 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 304.0759 | 1 | 413467.9952 | 602337.2611 | 1015805.2564 | 290.1754 | 305.5994 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 304.0759 | 2 | 590806.552 | 1204674.5223 | 1795481.0743 | 291.6453 | 306.7688 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 304.0759 | 3 | 835924.2033 | 1807011.7834 | 2642935.9868 | 293.1152 | 308.0398 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 304.0759 | 4 | 1148820.9491 | 2409349.0446 | 3558169.9937 | 294.5851 | 309.4125 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 313.15 | 1 | 436322.6627 | 581168.7251 | 1017491.3878 | 290.1238 | 314.681 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 313.15 | 2 | 623463.7043 | 1162337.4503 | 1785801.1546 | 291.542 | 315.837 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 313.15 | 3 | 882130.3666 | 1743506.1754 | 2625636.542 | 292.9602 | 317.1007 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.16027 | 313.15 | 4 | 1212322.6494 | 2324674.9006 | 3536997.55 | 294.3785 | 318.472 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation