## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'H': 150.0 ton, 2.15 COP liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 1093c9f2-ab07-4a51-b82a-a0c85bc6402b |  | ✓
| data_timestamp | 2022-12-20T09:13Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'H' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 259281.0647 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.022603 | 277.0389 | 0.035963 | 285.9278 | 1 | 67462.3216 | 131279.4784 | 198741.8 | 278.4192 | 287.2471 | 15000 | 15000 | 0 | 0
0.022603 | 277.0389 | 0.035963 | 285.9278 | 2 | 92652.8502 | 262558.9567 | 355211.8069 | 279.7996 | 288.2858 | 15000 | 15000 | 0 | 0
0.022603 | 277.0389 | 0.035963 | 285.9278 | 3 | 132339.6993 | 393838.4351 | 526178.1344 | 281.1799 | 289.4208 | 15000 | 15000 | 0 | 0
0.022603 | 277.0389 | 0.035963 | 285.9278 | 4 | 186522.869 | 525117.9134 | 711640.7825 | 282.5603 | 290.652 | 15000 | 15000 | 0 | 0
0.022603 | 277.0389 | 0.035963 | 295.0019 | 1 | 81750.711 | 126694.5391 | 208445.2501 | 278.371 | 296.3906 | 15000 | 15000 | 0 | 0
0.022603 | 277.0389 | 0.035963 | 295.0019 | 2 | 112276.5448 | 253389.0782 | 365665.623 | 279.7032 | 297.438 | 15000 | 15000 | 0 | 0
0.022603 | 277.0389 | 0.035963 | 295.0019 | 3 | 160368.9919 | 380083.6174 | 540452.6092 | 281.0353 | 298.6025 | 15000 | 15000 | 0 | 0
0.022603 | 277.0389 | 0.035963 | 295.0019 | 4 | 226028.0522 | 506778.1565 | 732806.2087 | 282.3674 | 299.884 | 15000 | 15000 | 0 | 0
0.022603 | 277.0389 | 0.035963 | 304.0759 | 1 | 82030.1845 | 115116.3985 | 197146.583 | 278.2493 | 305.3936 | 15000 | 15000 | 0 | 0
0.022603 | 277.0389 | 0.035963 | 304.0759 | 2 | 112660.3741 | 230232.7971 | 342893.1712 | 279.4597 | 306.3677 | 15000 | 15000 | 0 | 0
0.022603 | 277.0389 | 0.035963 | 304.0759 | 3 | 160917.2304 | 345349.1956 | 506266.426 | 280.6701 | 307.4596 | 15000 | 15000 | 0 | 0
0.022603 | 277.0389 | 0.035963 | 304.0759 | 4 | 226800.7533 | 460465.5941 | 687266.3474 | 281.8805 | 308.6694 | 15000 | 15000 | 0 | 0
0.022603 | 277.0389 | 0.035963 | 313.15 | 1 | 69112.9604 | 96545.0566 | 165658.017 | 278.054 | 314.2608 | 15000 | 15000 | 0 | 0
0.022603 | 277.0389 | 0.035963 | 313.15 | 2 | 94919.8398 | 193090.1132 | 288009.953 | 279.0691 | 315.0812 | 15000 | 15000 | 0 | 0
0.022603 | 277.0389 | 0.035963 | 313.15 | 3 | 135577.7295 | 289635.1698 | 425212.8993 | 280.0843 | 316.0012 | 15000 | 15000 | 0 | 0
0.022603 | 277.0389 | 0.035963 | 313.15 | 4 | 191086.6294 | 386180.2264 | 577266.8559 | 281.0994 | 317.0207 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 285.9278 | 1 | 65610.5923 | 143355.2211 | 208965.8134 | 282.4384 | 287.315 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 285.9278 | 2 | 90109.6824 | 286710.4423 | 376820.1246 | 283.949 | 288.4293 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 285.9278 | 3 | 128707.193 | 430065.6634 | 558772.8564 | 285.4596 | 289.6372 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 285.9278 | 4 | 181403.1242 | 573420.8845 | 754824.0087 | 286.9702 | 290.9386 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 295.0019 | 1 | 84986.6466 | 142521.2936 | 227507.9402 | 282.4296 | 296.5176 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 295.0019 | 2 | 116720.7834 | 285042.5872 | 401763.3706 | 283.9314 | 297.6785 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 295.0019 | 3 | 166716.8722 | 427563.8808 | 594280.753 | 285.4332 | 298.9611 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 295.0019 | 4 | 234974.9129 | 570085.1744 | 805060.0873 | 286.935 | 300.3653 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 304.0759 | 1 | 90364.9142 | 134694.1648 | 225059.0789 | 282.3471 | 305.5801 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 304.0759 | 2 | 124107.304 | 269388.3295 | 393495.6335 | 283.7664 | 306.7059 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 304.0759 | 3 | 177267.3291 | 404082.4943 | 581349.8234 | 285.1858 | 307.9615 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 304.0759 | 4 | 249844.9898 | 538776.659 | 788621.6488 | 286.6051 | 309.3468 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 313.15 | 1 | 81684.6661 | 119873.8345 | 201558.5006 | 282.1909 | 314.5015 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 313.15 | 2 | 112185.8386 | 239747.6691 | 351933.5077 | 283.4541 | 315.5098 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 313.15 | 3 | 160239.4327 | 359621.5036 | 519860.9363 | 284.7173 | 316.6358 | 15000 | 15000 | 0 | 0
0.022603 | 280.9278 | 0.035963 | 313.15 | 4 | 225845.4483 | 479495.3382 | 705340.7864 | 285.9804 | 317.8795 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 285.9278 | 1 | 61097.7509 | 146786.7501 | 207884.5009 | 286.3663 | 287.3078 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 285.9278 | 2 | 83911.7395 | 293573.5001 | 377485.2396 | 287.916 | 288.4337 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 285.9278 | 3 | 119854.4281 | 440360.2502 | 560214.6783 | 289.4656 | 289.6467 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 285.9278 | 4 | 168925.8168 | 587147.0002 | 756072.817 | 291.0153 | 290.9469 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 295.0019 | 1 | 84151.4616 | 149703.8343 | 233855.2959 | 286.3971 | 296.5598 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 295.0019 | 2 | 115573.7392 | 299407.6685 | 414981.4077 | 287.9776 | 297.7665 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 295.0019 | 3 | 165078.5039 | 449111.5028 | 614190.0068 | 289.558 | 299.0937 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 295.0019 | 4 | 232665.7559 | 598815.3371 | 831481.093 | 291.1385 | 300.5413 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 304.0759 | 1 | 93777.7907 | 145627.7171 | 239405.5079 | 286.3541 | 305.676 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 304.0759 | 2 | 128794.5535 | 291255.4343 | 420049.9878 | 287.8915 | 306.8834 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 304.0759 | 3 | 183962.3115 | 436883.1514 | 620845.4629 | 289.4289 | 308.2255 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 304.0759 | 4 | 259281.0647 | 582510.8685 | 841791.9332 | 290.9663 | 309.7022 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 313.15 | 1 | 89043.0619 | 134558.3987 | 223601.4605 | 286.2372 | 314.6493 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 313.15 | 2 | 122291.8701 | 269116.7973 | 391408.6674 | 287.6578 | 315.7745 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 313.15 | 3 | 174674.2737 | 403675.196 | 578349.4697 | 289.0783 | 317.028 | 15000 | 15000 | 0 | 0
0.022603 | 284.8167 | 0.035963 | 313.15 | 4 | 246190.2729 | 538233.5946 | 784423.8675 | 290.4989 | 318.4098 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 285.9278 | 1 | 55150.5006 | 141574.0652 | 196724.5657 | 290.2027 | 287.2337 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 285.9278 | 2 | 75743.7773 | 283148.1303 | 358891.9077 | 291.6998 | 288.3103 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 285.9278 | 3 | 108187.8075 | 424722.1955 | 532910.003 | 293.1968 | 289.4655 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 285.9278 | 4 | 152482.591 | 566296.2607 | 718778.8517 | 294.6939 | 290.6994 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 295.0019 | 1 | 80449.8297 | 148242.1611 | 228691.9908 | 290.2732 | 296.5254 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 295.0019 | 2 | 110489.9125 | 296484.3222 | 406974.2347 | 291.8408 | 297.7132 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 295.0019 | 3 | 157817.0749 | 444726.4833 | 602543.5582 | 293.4084 | 299.0161 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 295.0019 | 4 | 222431.3169 | 592968.6444 | 815399.9613 | 294.976 | 300.4342 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 304.0759 | 1 | 93451.458 | 147917.0557 | 241368.5137 | 290.2697 | 305.6892 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 304.0759 | 2 | 128346.3677 | 295834.1114 | 424180.4791 | 291.8339 | 306.911 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 304.0759 | 3 | 183322.1502 | 443751.1671 | 627073.3172 | 293.3981 | 308.2671 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 304.0759 | 4 | 258378.8054 | 591668.2227 | 850047.0281 | 294.9622 | 309.7574 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 313.15 | 1 | 92348.7622 | 140598.7489 | 232947.5111 | 290.1923 | 314.712 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 313.15 | 2 | 126831.9236 | 281197.4979 | 408029.4215 | 291.6791 | 315.8859 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 313.15 | 3 | 181159.0103 | 421796.2468 | 602955.2571 | 293.1659 | 317.193 | 15000 | 15000 | 0 | 0
0.022603 | 288.7056 | 0.035963 | 313.15 | 4 | 255330.0221 | 562394.9957 | 817725.0178 | 294.6527 | 318.6331 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation