## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'J': 450.0 ton, 1.97 COP liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 9758c91b-2950-4500-9623-b630efa97f03 |  | ✓
| data_timestamp | 2022-12-20T09:13Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'J' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 875073.889 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.067809 | 277.0389 | 0.11095 | 285.9278 | 1 | 219230.762 | 401365.947 | 620596.7091 | 278.4456 | 287.2631 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.11095 | 285.9278 | 2 | 305707.283 | 802731.8941 | 1108439.177 | 279.8523 | 288.3128 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.11095 | 285.9278 | 3 | 443571.4372 | 1204097.8411 | 1647669.2782 | 281.2591 | 289.4731 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.11095 | 285.9278 | 4 | 632823.2246 | 1605463.7881 | 2238287.0127 | 282.6658 | 290.744 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.11095 | 295.0019 | 1 | 251956.3407 | 374998.9009 | 626955.2416 | 278.3532 | 296.3557 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.11095 | 295.0019 | 2 | 351341.6075 | 749997.8018 | 1101339.4093 | 279.6675 | 297.3801 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.11095 | 295.0019 | 3 | 509785.3747 | 1124996.7026 | 1634782.0773 | 280.9818 | 298.5321 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.11095 | 295.0019 | 4 | 727287.6421 | 1499995.6035 | 2227283.2456 | 282.2961 | 299.8115 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.11095 | 304.0759 | 1 | 253713.6721 | 341790.6795 | 595504.3516 | 278.2368 | 305.366 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.11095 | 304.0759 | 2 | 353792.1259 | 683581.359 | 1037373.4849 | 279.4347 | 306.3233 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.11095 | 304.0759 | 3 | 513340.998 | 1025372.0385 | 1538713.0365 | 280.6327 | 307.4094 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.11095 | 304.0759 | 4 | 732360.2884 | 1367162.718 | 2099523.0064 | 281.8306 | 308.6243 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.11095 | 313.15 | 1 | 228561.9434 | 301741.2829 | 530303.2263 | 278.0964 | 314.3026 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.11095 | 313.15 | 2 | 318719.1892 | 603482.5658 | 922201.755 | 279.154 | 315.1543 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.11095 | 313.15 | 3 | 462451.2946 | 905223.8487 | 1367675.1433 | 280.2116 | 316.1225 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.11095 | 313.15 | 4 | 659758.2598 | 1206965.1316 | 1866723.3914 | 281.2691 | 317.2071 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 285.9278 | 1 | 226888.3859 | 452239.8437 | 679128.2296 | 282.5163 | 287.3891 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 285.9278 | 2 | 316385.4897 | 904479.6874 | 1220865.1771 | 284.1048 | 288.5548 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 285.9278 | 3 | 459065.1717 | 1356719.5311 | 1815784.7028 | 285.6932 | 289.8349 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 285.9278 | 4 | 654927.432 | 1808959.3748 | 2463886.8068 | 287.2817 | 291.2294 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 295.0019 | 1 | 272328.3584 | 432434.7412 | 704763.0995 | 282.4467 | 296.5237 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 295.0019 | 2 | 379749.4556 | 864869.4823 | 1244618.9379 | 283.9656 | 297.6895 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 295.0019 | 3 | 551004.2487 | 1297304.2235 | 1848308.4721 | 285.4845 | 298.9931 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 295.0019 | 4 | 786092.7377 | 1729738.9646 | 2515831.7023 | 287.0035 | 300.4346 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 304.0759 | 1 | 285090.9209 | 405788.4634 | 690879.3842 | 282.3531 | 305.5726 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 304.0759 | 2 | 397546.2659 | 811576.9267 | 1209123.1927 | 283.7784 | 306.6954 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 304.0759 | 3 | 576826.8482 | 1217365.3901 | 1794192.2383 | 285.2038 | 307.9629 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 304.0759 | 4 | 822932.6678 | 1623153.8534 | 2446086.5212 | 286.6291 | 309.3751 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 313.15 | 1 | 268098.6696 | 372301.0103 | 640399.68 | 282.2355 | 314.5418 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 313.15 | 2 | 373851.3478 | 744602.0207 | 1118453.3685 | 283.5432 | 315.5808 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 313.15 | 3 | 542446.284 | 1116903.031 | 1659349.315 | 284.8509 | 316.7564 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.11095 | 313.15 | 4 | 773883.4781 | 1489204.0414 | 2263087.5195 | 286.1586 | 318.0686 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 285.9278 | 1 | 225882.9915 | 472669.5134 | 698552.5048 | 286.48 | 287.4309 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 285.9278 | 2 | 314983.513 | 945339.0267 | 1260322.5398 | 288.1434 | 288.6397 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 285.9278 | 3 | 457030.9487 | 1418008.5401 | 1875039.4888 | 289.8067 | 289.9624 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 285.9278 | 4 | 652025.2984 | 1890678.0535 | 2542703.3519 | 291.4701 | 291.399 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 295.0019 | 1 | 279481.6249 | 459426.3544 | 738907.9793 | 286.4334 | 296.5975 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 295.0019 | 2 | 389724.359 | 918852.7088 | 1308577.0678 | 288.0502 | 297.8276 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 295.0019 | 3 | 565477.5128 | 1378279.0632 | 1943756.576 | 289.6669 | 299.1993 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 295.0019 | 4 | 806741.0863 | 1837705.4176 | 2644446.5039 | 291.2837 | 300.7124 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 304.0759 | 1 | 300296.7233 | 439342.0202 | 739638.7435 | 286.3627 | 305.6783 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 304.0759 | 2 | 418750.0628 | 878684.0404 | 1297434.1032 | 287.9088 | 306.8867 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 304.0759 | 3 | 607592.8757 | 1318026.0606 | 1925618.9362 | 289.4549 | 308.2476 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 304.0759 | 4 | 866825.1618 | 1757368.0808 | 2624193.2426 | 291.0009 | 309.761 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 313.15 | 1 | 290114.2919 | 412416.5108 | 702530.8026 | 286.268 | 314.6769 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 313.15 | 2 | 404551.1273 | 824833.0215 | 1229384.1489 | 287.7193 | 315.8219 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 313.15 | 3 | 586990.6768 | 1237249.5323 | 1824240.2091 | 289.1706 | 317.1148 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.11095 | 313.15 | 4 | 837432.9405 | 1649666.0431 | 2487098.9835 | 290.6219 | 318.5554 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 285.9278 | 1 | 219658.0843 | 462654.956 | 682313.0403 | 290.3364 | 287.3959 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 285.9278 | 2 | 306303.1644 | 925309.912 | 1231613.0764 | 291.9672 | 288.5779 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 285.9278 | 3 | 444436.0419 | 1387964.868 | 1832400.91 | 293.598 | 289.8706 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 285.9278 | 4 | 634056.717 | 1850619.8241 | 2484676.541 | 295.2288 | 291.2741 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 295.0019 | 1 | 277049.5302 | 455973.7406 | 733023.2709 | 290.3128 | 296.5848 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 295.0019 | 2 | 386332.914 | 911947.4813 | 1298280.3953 | 291.9201 | 297.8054 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 295.0019 | 3 | 560556.6352 | 1367921.2219 | 1928477.8571 | 293.5273 | 299.1663 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 295.0019 | 4 | 799720.6938 | 1823894.9625 | 2623615.6563 | 295.1346 | 300.6674 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 304.0759 | 1 | 303154.3535 | 442451.35 | 745605.7035 | 290.2651 | 305.6912 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 304.0759 | 2 | 422734.8975 | 884902.7 | 1307637.5975 | 291.8247 | 306.9088 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 304.0759 | 3 | 613374.7427 | 1327354.05 | 1940728.7927 | 293.3843 | 308.2803 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 304.0759 | 4 | 875073.889 | 1769805.4 | 2644879.289 | 294.9439 | 309.8058 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 313.15 | 1 | 298621.9684 | 422087.7842 | 720709.7526 | 290.1934 | 314.7164 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 313.15 | 2 | 416414.6936 | 844175.5683 | 1260590.2619 | 291.6812 | 315.8898 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 313.15 | 3 | 604204.33 | 1266263.3525 | 1870467.6825 | 293.169 | 317.2153 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.11095 | 313.15 | 4 | 861990.8777 | 1688351.1367 | 2550342.0143 | 294.6568 | 318.6929 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation