## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'N': 112.5 ton, 2.64 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | dd55891b-2d56-4f94-ac63-7e6ec43561d8 |  | ✓
| data_timestamp | 2022-12-20T09:13Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'N' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 179575.5416 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.016952 | 277.0389 | 0.025372 | 285.9278 | 1 | 26119.9743 | 100049.4035 | 126169.3779 | 278.4415 | 287.115 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025372 | 285.9278 | 2 | 43364.8817 | 200098.8071 | 243463.6888 | 279.8441 | 288.2187 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025372 | 285.9278 | 3 | 72961.2757 | 300148.2106 | 373109.4863 | 281.2468 | 289.4386 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025372 | 285.9278 | 4 | 114909.1561 | 400197.6142 | 515106.7703 | 282.6494 | 290.7748 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025372 | 295.0019 | 1 | 29386.0559 | 95242.3311 | 124628.387 | 278.3741 | 296.1788 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025372 | 295.0019 | 2 | 48787.2929 | 190484.6622 | 239271.9551 | 279.7094 | 297.2614 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025372 | 295.0019 | 3 | 82084.4652 | 285726.9933 | 367811.4585 | 281.0446 | 298.4752 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025372 | 295.0019 | 4 | 129277.5729 | 380969.3244 | 510246.8973 | 282.3798 | 299.8203 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025372 | 304.0759 | 1 | 33658.2079 | 87943.1163 | 121601.3241 | 278.2718 | 305.228 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025372 | 304.0759 | 2 | 55880.0015 | 175886.2325 | 231766.234 | 279.5047 | 306.2716 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025372 | 304.0759 | 3 | 94017.9249 | 263829.3488 | 357847.2736 | 280.7376 | 307.4661 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025372 | 304.0759 | 4 | 148071.978 | 351772.465 | 499844.443 | 281.9705 | 308.8114 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025372 | 313.15 | 1 | 37796.7126 | 78151.759 | 115948.4716 | 278.1345 | 314.252 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025372 | 313.15 | 2 | 62750.8262 | 156303.518 | 219054.3442 | 279.2302 | 315.232 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025372 | 313.15 | 3 | 105578.0657 | 234455.277 | 340033.3427 | 280.3258 | 316.3818 | 15000 | 15000 | 0 | 0
0.016952 | 277.0389 | 0.025372 | 313.15 | 4 | 166278.4308 | 312607.036 | 478885.4668 | 281.4214 | 317.7015 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 285.9278 | 1 | 26527.2911 | 112396.5566 | 138923.8477 | 282.5069 | 287.235 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 285.9278 | 2 | 44041.1169 | 224793.1132 | 268834.2301 | 284.0861 | 288.4574 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 285.9278 | 3 | 74099.0391 | 337189.6698 | 411288.709 | 285.6653 | 289.7979 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 285.9278 | 4 | 116701.0579 | 449586.2265 | 566287.2843 | 287.2444 | 291.2564 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 295.0019 | 1 | 30003.9856 | 107669.7633 | 137673.7489 | 282.4405 | 296.302 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 295.0019 | 2 | 49813.1916 | 215339.5265 | 265152.7182 | 283.9533 | 297.5058 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 295.0019 | 3 | 83810.5366 | 323009.2898 | 406819.8264 | 285.466 | 298.8436 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 295.0019 | 4 | 131996.0204 | 430679.0531 | 562675.0735 | 286.9788 | 300.3154 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 304.0759 | 1 | 34960.5503 | 100450.8275 | 135411.3778 | 282.3391 | 305.3588 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 304.0759 | 2 | 58042.1753 | 200901.655 | 258943.8303 | 283.7504 | 306.5291 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 304.0759 | 3 | 97655.7754 | 301352.4826 | 399008.258 | 285.1618 | 307.8561 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 304.0759 | 4 | 153801.3507 | 401803.3101 | 555604.6608 | 286.5731 | 309.3396 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 313.15 | 1 | 40299.7197 | 90739.7494 | 131039.4691 | 282.2027 | 314.3955 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 313.15 | 2 | 66906.3667 | 181479.4987 | 248385.8654 | 283.4776 | 315.5108 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 313.15 | 3 | 112569.7493 | 272219.2481 | 384788.9974 | 284.7524 | 316.8072 | 15000 | 15000 | 0 | 0
0.016952 | 280.9278 | 0.025372 | 313.15 | 4 | 177289.8675 | 362958.9975 | 540248.865 | 286.0273 | 318.2848 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 285.9278 | 1 | 26866.8415 | 118529.8084 | 145396.6499 | 286.4851 | 287.2959 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 285.9278 | 2 | 44604.8449 | 237059.6168 | 281664.4617 | 288.1536 | 288.5782 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 285.9278 | 3 | 75047.5098 | 355589.4252 | 430636.935 | 289.822 | 289.9799 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 285.9278 | 4 | 118194.8361 | 474119.2336 | 592314.0696 | 291.4905 | 291.5013 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 295.0019 | 1 | 30122.3039 | 113883.2941 | 144005.598 | 286.4197 | 296.3618 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 295.0019 | 2 | 50009.6259 | 227766.5883 | 277776.2142 | 288.0228 | 297.625 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 295.0019 | 3 | 84141.0367 | 341649.8824 | 425790.9191 | 289.6258 | 299.0228 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 295.0019 | 4 | 132516.5361 | 455533.1766 | 588049.7127 | 291.2289 | 300.555 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 304.0759 | 1 | 35124.7197 | 106744.6375 | 141869.3572 | 286.3192 | 305.42 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 304.0759 | 2 | 58314.7326 | 213489.275 | 271804.0075 | 287.8218 | 306.6509 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 304.0759 | 3 | 98114.3521 | 320233.9125 | 418348.2646 | 289.3244 | 308.0393 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 304.0759 | 4 | 154523.5785 | 426978.55 | 581502.1285 | 290.8269 | 309.585 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 313.15 | 1 | 40819.2758 | 97113.8384 | 137933.1142 | 286.1837 | 314.461 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 313.15 | 2 | 67768.9436 | 194227.6769 | 261996.6205 | 287.5507 | 315.6401 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 313.15 | 3 | 114021.0323 | 291341.5153 | 405362.5476 | 288.9177 | 317.0027 | 15000 | 15000 | 0 | 0
0.016952 | 284.8167 | 0.025372 | 313.15 | 4 | 179575.5416 | 388455.3538 | 568030.8954 | 290.2847 | 318.5488 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 285.9278 | 1 | 27601.9042 | 118449.1589 | 146051.0631 | 290.3756 | 287.3021 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 285.9278 | 2 | 45825.2101 | 236898.3178 | 282723.5279 | 292.0457 | 288.5881 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 285.9278 | 3 | 77100.7703 | 355347.4767 | 432448.247 | 293.7158 | 289.997 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 285.9278 | 4 | 121428.5848 | 473796.6356 | 595225.2204 | 295.3859 | 291.5287 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 295.0019 | 1 | 30297.8786 | 113882.9237 | 144180.8024 | 290.3113 | 296.3634 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 295.0019 | 2 | 50301.1185 | 227765.8475 | 278066.966 | 291.917 | 297.6277 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 295.0019 | 3 | 84631.4719 | 341648.7712 | 426280.2432 | 293.5226 | 299.0274 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 295.0019 | 4 | 133288.939 | 455531.695 | 588820.634 | 295.1283 | 300.5623 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 304.0759 | 1 | 34801.1732 | 106824.5462 | 141625.7193 | 290.2117 | 305.4177 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 304.0759 | 2 | 57777.5743 | 213649.0924 | 271426.6667 | 291.7179 | 306.6474 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 304.0759 | 3 | 97210.5852 | 320473.6386 | 417684.2237 | 293.2241 | 308.033 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 304.0759 | 4 | 153100.2056 | 427298.1847 | 580398.3903 | 294.7303 | 309.5745 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 313.15 | 1 | 40099.4269 | 97274.0262 | 137373.4531 | 290.0771 | 314.4557 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 313.15 | 2 | 66573.8366 | 194548.0524 | 261121.8891 | 291.4486 | 315.6318 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 313.15 | 3 | 112010.2685 | 291822.0787 | 403832.3472 | 292.8201 | 316.9882 | 15000 | 15000 | 0 | 0
0.016952 | 288.7056 | 0.025372 | 313.15 | 4 | 176408.7224 | 389096.1049 | 565504.8273 | 294.1916 | 318.5248 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation