## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'P': 450.0 ton, 2.20 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | ffe769c3-76fe-455f-b093-1b472e704598 |  | ✓
| data_timestamp | 2022-12-20T09:13Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'P' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 791195.685 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.067809 | 277.0389 | 0.10707 | 285.9278 | 1 | 103446.4352 | 392817.2434 | 496263.6787 | 278.4157 | 287.0344 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10707 | 285.9278 | 2 | 201061.5006 | 785634.4869 | 986695.9875 | 279.7924 | 288.1279 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10707 | 285.9278 | 3 | 350122.2284 | 1178451.7303 | 1528573.9587 | 281.1692 | 289.3362 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10707 | 285.9278 | 4 | 550628.6186 | 1571268.9738 | 2121897.5924 | 282.5459 | 290.6592 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10707 | 295.0019 | 1 | 122184.4311 | 385973.2759 | 508157.707 | 278.3917 | 296.139 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10707 | 295.0019 | 2 | 237481.2144 | 771946.5518 | 1009427.7662 | 279.7444 | 297.2608 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10707 | 295.0019 | 3 | 413542.3825 | 1157919.8277 | 1571462.2102 | 281.0972 | 298.5185 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10707 | 295.0019 | 4 | 650367.9354 | 1543893.1036 | 2194261.039 | 282.45 | 299.9122 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10707 | 304.0759 | 1 | 137157.5155 | 367792.5037 | 504950.0191 | 278.3279 | 305.2095 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10707 | 304.0759 | 2 | 266583.3367 | 735585.0074 | 1002168.3441 | 279.617 | 306.3258 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10707 | 304.0759 | 3 | 464219.9109 | 1103377.5111 | 1567597.422 | 280.9061 | 307.5952 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10707 | 304.0759 | 4 | 730067.2381 | 1471170.0148 | 2201237.2529 | 282.1951 | 309.0178 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10707 | 313.15 | 1 | 146277.5191 | 338274.9268 | 484552.446 | 278.2245 | 314.2413 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10707 | 313.15 | 2 | 284309.2411 | 676549.8536 | 960859.0948 | 279.4101 | 315.3141 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10707 | 313.15 | 3 | 495087.2482 | 1014824.7805 | 1509912.0287 | 280.5957 | 316.5507 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10707 | 313.15 | 4 | 778611.5404 | 1353099.7073 | 2131711.2477 | 281.7813 | 317.9512 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 285.9278 | 1 | 100966.6016 | 418500.628 | 519467.2296 | 282.3978 | 287.0861 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 285.9278 | 2 | 196241.6239 | 837001.2559 | 1033242.8798 | 283.8677 | 288.2317 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 285.9278 | 3 | 341729.0453 | 1255501.8839 | 1597230.9292 | 285.3377 | 289.4893 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 285.9278 | 4 | 537428.8659 | 1674002.5118 | 2211431.3778 | 286.8077 | 290.8589 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 295.0019 | 1 | 120440.4241 | 414895.7475 | 535336.1715 | 282.3851 | 296.1998 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 295.0019 | 2 | 234091.5116 | 829791.4949 | 1063883.0066 | 283.8424 | 297.3826 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 295.0019 | 3 | 407639.6598 | 1244687.2424 | 1652326.9022 | 285.2997 | 298.6994 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 295.0019 | 4 | 641084.8686 | 1659582.9898 | 2300667.8584 | 286.757 | 300.1503 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 304.0759 | 1 | 136970.568 | 399954.0623 | 536924.6302 | 282.3326 | 305.2813 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 304.0759 | 2 | 266219.9801 | 799908.1246 | 1066128.1047 | 283.7374 | 306.4694 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 304.0759 | 3 | 463587.173 | 1199862.1869 | 1663449.3599 | 285.1423 | 307.8104 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 304.0759 | 4 | 729072.1468 | 1599816.2492 | 2328888.396 | 286.5471 | 309.3043 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 313.15 | 1 | 148641.6986 | 373675.5725 | 522317.2711 | 282.2403 | 314.3264 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 313.15 | 2 | 288904.3292 | 747351.1449 | 1036255.4741 | 283.5528 | 315.4839 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 313.15 | 3 | 503088.9913 | 1121026.7174 | 1624115.7087 | 284.8654 | 316.808 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10707 | 313.15 | 4 | 791195.685 | 1494702.2899 | 2285897.9749 | 286.1779 | 318.2985 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 285.9278 | 1 | 99994.8354 | 429141.405 | 529136.2404 | 286.3268 | 287.1077 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 285.9278 | 2 | 194352.8707 | 858282.81 | 1052635.6808 | 287.837 | 288.275 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 285.9278 | 3 | 338440.0295 | 1287424.215 | 1625864.2446 | 289.3472 | 289.5532 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 285.9278 | 4 | 532256.3117 | 1716565.6201 | 2248821.9318 | 290.8574 | 290.9423 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 295.0019 | 1 | 119139.6677 | 428775.6116 | 547915.2792 | 286.3256 | 296.228 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 295.0019 | 2 | 231563.3237 | 857551.2231 | 1089114.5468 | 287.8344 | 297.4391 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 295.0019 | 3 | 403237.1521 | 1286326.8347 | 1689563.9867 | 289.3433 | 298.7828 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 295.0019 | 4 | 634161.1529 | 1715102.4463 | 2349263.5991 | 290.8522 | 300.2591 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 304.0759 | 1 | 135903.6725 | 417073.0134 | 552976.686 | 286.2844 | 305.3174 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 304.0759 | 2 | 264146.3311 | 834146.0269 | 1098292.358 | 287.7521 | 306.5416 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 304.0759 | 3 | 459976.1854 | 1251219.0403 | 1711195.2257 | 289.2198 | 307.9176 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 304.0759 | 4 | 723393.2353 | 1668292.0538 | 2391685.2891 | 290.6875 | 309.4453 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 313.15 | 1 | 148544.35 | 394033.6107 | 542577.9607 | 286.2033 | 314.372 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 313.15 | 2 | 288715.1196 | 788067.2213 | 1076782.3409 | 287.5899 | 315.5752 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 313.15 | 3 | 502759.5076 | 1182100.832 | 1684860.3396 | 288.9765 | 316.9448 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10707 | 313.15 | 4 | 790677.5141 | 1576134.4427 | 2366811.9568 | 290.3632 | 318.4807 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 285.9278 | 1 | 101345.1049 | 424739.5746 | 526084.6795 | 290.2027 | 287.1009 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 285.9278 | 2 | 196977.2938 | 849479.1492 | 1046456.443 | 291.6999 | 288.2612 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 285.9278 | 3 | 343010.118 | 1274218.7238 | 1617228.8418 | 293.197 | 289.5339 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 285.9278 | 4 | 539443.5774 | 1698958.2985 | 2238401.8759 | 294.6942 | 290.919 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 295.0019 | 1 | 119419.4398 | 427612.8682 | 547032.3081 | 290.2128 | 296.226 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 295.0019 | 2 | 232107.097 | 855225.7364 | 1087332.8334 | 291.7201 | 297.4351 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 295.0019 | 3 | 404184.062 | 1282838.6046 | 1687022.6666 | 293.2274 | 298.7771 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 295.0019 | 4 | 635650.3348 | 1710451.4728 | 2346101.8077 | 294.7347 | 300.252 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 304.0759 | 1 | 135417.4169 | 419149.3571 | 554566.774 | 290.183 | 305.3209 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 304.0759 | 2 | 263201.2305 | 838298.7143 | 1101499.9447 | 291.6605 | 306.5488 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 304.0759 | 3 | 458330.4165 | 1257448.0714 | 1715778.488 | 293.1379 | 307.9279 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 304.0759 | 4 | 720804.9751 | 1676597.4286 | 2397402.4037 | 294.6154 | 309.4581 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 313.15 | 1 | 147769.3706 | 399349.0414 | 547118.412 | 290.1132 | 314.3823 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 313.15 | 2 | 287208.847 | 798698.0828 | 1085906.9298 | 291.5209 | 315.5958 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 313.15 | 3 | 500136.5315 | 1198047.1242 | 1698183.6557 | 292.9285 | 316.9748 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10707 | 313.15 | 4 | 786552.424 | 1597396.1656 | 2383948.5897 | 294.3362 | 318.5193 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation