## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'Q': 650.0 ton, 2.06 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 64e58cf4-ab9c-4592-9ef6-f8da9794b399 |  | ✓
| data_timestamp | 2022-12-20T09:13Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'Q' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 1176816.6469 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.097947 | 277.0389 | 0.15796 | 285.9278 | 1 | 137783.856 | 553665.0499 | 691448.9059 | 278.3823 | 286.9728 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.15796 | 285.9278 | 2 | 294205.7236 | 1107330.0998 | 1401535.8234 | 279.7257 | 288.0461 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.15796 | 285.9278 | 3 | 519441.0261 | 1660995.1497 | 2180436.1758 | 281.0692 | 289.2233 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.15796 | 285.9278 | 4 | 813489.7634 | 2214660.1996 | 3028149.963 | 282.4126 | 290.5046 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.15796 | 295.0019 | 1 | 172672.8236 | 559421.0187 | 732093.8423 | 278.3963 | 296.1123 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.15796 | 295.0019 | 2 | 368703.0868 | 1118842.0374 | 1487545.1242 | 279.7537 | 297.2582 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.15796 | 295.0019 | 3 | 650971.393 | 1678263.0561 | 2329234.4491 | 281.1111 | 298.5349 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.15796 | 295.0019 | 4 | 1019477.7422 | 2237684.0748 | 3257161.817 | 282.4685 | 299.9424 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.15796 | 304.0759 | 1 | 194339.2471 | 539578.6852 | 733917.9324 | 278.3481 | 305.1927 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.15796 | 304.0759 | 2 | 414966.7494 | 1079157.3705 | 1494124.1199 | 279.6574 | 306.3496 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.15796 | 304.0759 | 3 | 732653.1634 | 1618736.0557 | 2351389.2192 | 280.9666 | 307.6541 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.15796 | 304.0759 | 4 | 1147398.4893 | 2158314.741 | 3305713.2303 | 282.2759 | 309.1063 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.15796 | 313.15 | 1 | 199321.9124 | 494138.0496 | 693459.962 | 278.2379 | 314.2087 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.15796 | 313.15 | 2 | 425606.0847 | 988276.0991 | 1413882.1838 | 279.4369 | 315.3085 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.15796 | 313.15 | 3 | 751437.6628 | 1482414.1487 | 2233851.8115 | 280.6359 | 316.5603 | 15000 | 15000 | 0 | 0
0.097947 | 277.0389 | 0.15796 | 313.15 | 4 | 1176816.6469 | 1976552.1983 | 3153368.8452 | 281.8349 | 317.964 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 285.9278 | 1 | 129831.1215 | 575077.9189 | 704909.0403 | 282.3262 | 286.9932 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 285.9278 | 2 | 277224.4888 | 1150155.8378 | 1427380.3265 | 283.7246 | 288.0851 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 285.9278 | 3 | 489459.4543 | 1725233.7566 | 2214693.2109 | 285.1231 | 289.2751 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 285.9278 | 4 | 766536.0179 | 2300311.6755 | 3066847.6934 | 286.5215 | 290.5631 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 295.0019 | 1 | 165809.9303 | 588416.578 | 754226.5083 | 282.3586 | 296.1459 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 295.0019 | 2 | 354048.9572 | 1176833.1561 | 1530882.1132 | 283.7895 | 297.3239 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 295.0019 | 3 | 625098.4901 | 1765249.7341 | 2390348.2242 | 285.2204 | 298.6276 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 295.0019 | 4 | 978958.5291 | 2353666.3121 | 3332624.8412 | 286.6512 | 300.0568 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 304.0759 | 1 | 189853.3856 | 576156.9349 | 766010.3205 | 282.3288 | 305.2416 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 304.0759 | 2 | 405388.2241 | 1152313.8699 | 1557702.094 | 283.7299 | 306.4463 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 304.0759 | 3 | 715741.5992 | 1728470.8048 | 2444212.4041 | 285.1309 | 307.7953 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 304.0759 | 4 | 1120913.5109 | 2304627.7398 | 3425541.2507 | 286.532 | 309.2886 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 313.15 | 1 | 198601.6037 | 538298.9896 | 736900.5933 | 282.2368 | 314.275 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 313.15 | 2 | 424068.0311 | 1076597.9793 | 1500666.0104 | 283.5458 | 315.441 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 313.15 | 3 | 748722.1204 | 1614896.9689 | 2363619.0894 | 284.8548 | 316.7584 | 15000 | 15000 | 0 | 0
0.097947 | 280.9278 | 0.15796 | 313.15 | 4 | 1172563.8717 | 2153195.9585 | 3325759.8302 | 286.1638 | 318.2272 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 285.9278 | 1 | 125805.3361 | 580449.5948 | 706254.931 | 286.2308 | 286.9952 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 285.9278 | 2 | 268628.3505 | 1160899.1897 | 1429527.5402 | 287.6449 | 288.0884 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 285.9278 | 3 | 474282.3637 | 1741348.7845 | 2215631.1482 | 289.0591 | 289.2765 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 285.9278 | 4 | 742767.3758 | 2321798.3794 | 3064565.7552 | 290.4732 | 290.5596 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 295.0019 | 1 | 161760.8624 | 601370.9444 | 763131.8068 | 286.2818 | 296.1594 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 295.0019 | 2 | 345403.1043 | 1202741.8887 | 1548144.993 | 287.7469 | 297.3501 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 295.0019 | 3 | 609833.625 | 1804112.8331 | 2413946.4581 | 289.212 | 298.6634 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 295.0019 | 4 | 955052.4245 | 2405483.7775 | 3360536.202 | 290.6771 | 300.0992 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 304.0759 | 1 | 186726.6056 | 596693.9917 | 783420.5973 | 286.2704 | 305.2681 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 304.0759 | 2 | 398711.7049 | 1193387.9833 | 1592099.6882 | 287.7241 | 306.4986 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 304.0759 | 3 | 703953.7321 | 1790081.975 | 2494035.707 | 289.1778 | 307.8711 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 304.0759 | 4 | 1102452.6871 | 2386775.9666 | 3489228.6537 | 290.6315 | 309.3855 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 313.15 | 1 | 197444.0128 | 566418.7367 | 763862.7495 | 286.1966 | 314.3161 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 313.15 | 2 | 421596.2621 | 1132837.4734 | 1554433.7355 | 287.5766 | 315.523 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 313.15 | 3 | 744358.0373 | 1699256.2101 | 2443614.2475 | 288.9565 | 316.8805 | 15000 | 15000 | 0 | 0
0.097947 | 284.8167 | 0.15796 | 313.15 | 4 | 1165729.3385 | 2265674.9468 | 3431404.2853 | 290.3365 | 318.3885 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 285.9278 | 1 | 126367.553 | 569780.0778 | 696147.6308 | 290.096 | 286.9799 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 285.9278 | 2 | 269828.8352 | 1139560.1557 | 1409388.9909 | 291.4864 | 288.0579 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 285.9278 | 3 | 476401.9045 | 1709340.2335 | 2185742.138 | 292.8769 | 289.2313 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 285.9278 | 4 | 746086.7608 | 2279120.3113 | 3025207.0722 | 294.2673 | 290.5001 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 295.0019 | 1 | 161688.568 | 598284.1177 | 759972.6857 | 290.1656 | 296.1546 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 295.0019 | 2 | 345248.7361 | 1196568.2354 | 1541816.9716 | 291.6255 | 297.3405 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 295.0019 | 3 | 609561.0771 | 1794852.3531 | 2404413.4302 | 293.0855 | 298.6489 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 295.0019 | 4 | 954625.5908 | 2393136.4708 | 3347762.0616 | 294.5455 | 300.0798 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 304.0759 | 1 | 186623.7504 | 601189.8554 | 787813.6058 | 290.1726 | 305.2748 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 304.0759 | 2 | 398492.0812 | 1202379.7107 | 1600871.792 | 291.6397 | 306.512 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 304.0759 | 3 | 703565.9709 | 1803569.5661 | 2507135.537 | 293.1068 | 307.8911 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 304.0759 | 4 | 1101845.4194 | 2404759.4215 | 3506604.8408 | 294.5739 | 309.412 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 313.15 | 1 | 198015.8779 | 578497.2908 | 776513.1687 | 290.1173 | 314.3354 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 313.15 | 2 | 422817.3485 | 1156994.5816 | 1579811.9301 | 291.529 | 315.5618 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 313.15 | 3 | 746513.9517 | 1735491.8724 | 2482005.8241 | 292.9407 | 316.9391 | 15000 | 15000 | 0 | 0
0.097947 | 288.7056 | 0.15796 | 313.15 | 4 | 1169105.6877 | 2313989.1632 | 3483094.8508 | 294.3524 | 318.4674 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation