## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'S': 225.0 ton, 2.23 COP liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 1f227b30-91a6-416b-855f-d431ecf4e404 |  | ✓
| data_timestamp | 2022-12-20T09:13Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'S' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 376802.3371 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.033905 | 277.0389 | 0.05327 | 285.9278 | 1 | 44264.3422 | 203945.2164 | 248209.5586 | 278.4685 | 287.0402 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05327 | 285.9278 | 2 | 97990.4935 | 407890.4329 | 505880.9264 | 279.8981 | 288.195 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05327 | 285.9278 | 3 | 180147.101 | 611835.6493 | 791982.7503 | 281.3277 | 289.4772 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05327 | 285.9278 | 4 | 290734.1646 | 815780.8657 | 1106515.0304 | 282.7573 | 290.8869 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05327 | 295.0019 | 1 | 50311.5414 | 191187.4551 | 241498.9966 | 278.3791 | 296.0881 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05327 | 295.0019 | 2 | 111377.5227 | 382374.9103 | 493752.4329 | 279.7192 | 297.2226 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05327 | 295.0019 | 3 | 204758.0036 | 573562.3654 | 778320.369 | 281.0594 | 298.5026 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05327 | 295.0019 | 4 | 330452.9843 | 764749.8205 | 1095202.8048 | 282.3995 | 299.9278 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05327 | 304.0759 | 1 | 49861.6813 | 174064.3725 | 223926.0538 | 278.259 | 305.0863 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05327 | 304.0759 | 2 | 110381.6417 | 348128.745 | 458510.3867 | 279.4792 | 306.1448 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05327 | 304.0759 | 3 | 202927.162 | 522193.1175 | 725120.2795 | 280.6993 | 307.3479 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05327 | 304.0759 | 4 | 327498.2423 | 696257.49 | 1023755.7323 | 281.9194 | 308.6954 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05327 | 313.15 | 1 | 43781.3322 | 152575.9685 | 196357.3007 | 278.1084 | 314.0389 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05327 | 313.15 | 2 | 96921.2268 | 305151.937 | 402073.1639 | 279.1779 | 314.9701 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05327 | 313.15 | 3 | 178181.3461 | 457727.9055 | 635909.2517 | 280.2474 | 316.0287 | 15000 | 15000 | 0 | 0
0.033905 | 277.0389 | 0.05327 | 313.15 | 4 | 287561.69 | 610303.8741 | 897865.5641 | 281.3169 | 317.2145 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 285.9278 | 1 | 43624.7937 | 222081.568 | 265706.3617 | 282.4879 | 287.1186 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 285.9278 | 2 | 96574.6886 | 444163.136 | 540737.8247 | 284.048 | 288.3512 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 285.9278 | 3 | 177544.2654 | 666244.7041 | 843788.9695 | 285.6081 | 289.7094 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 285.9278 | 4 | 286533.524 | 888326.2721 | 1174859.7961 | 287.1683 | 291.1932 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 295.0019 | 1 | 52415.2188 | 214273.1876 | 266688.4064 | 282.433 | 296.2014 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 295.0019 | 2 | 116034.553 | 428546.3751 | 544580.9282 | 283.9383 | 297.4512 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 295.0019 | 3 | 213319.5537 | 642819.5627 | 856139.1164 | 285.4436 | 298.8526 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 295.0019 | 4 | 344270.2208 | 857092.7503 | 1201362.9711 | 286.9488 | 300.4053 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 304.0759 | 1 | 54565.0997 | 202099.4858 | 256664.5855 | 282.3475 | 305.2341 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 304.0759 | 2 | 120793.8668 | 404198.9716 | 524992.8384 | 283.7673 | 306.4448 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 304.0759 | 3 | 222069.1431 | 606298.4574 | 828367.6004 | 285.187 | 307.8137 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 304.0759 | 4 | 358390.9285 | 808397.9431 | 1166788.8717 | 286.6068 | 309.3408 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 313.15 | 1 | 50575.2082 | 185560.4627 | 236135.6709 | 282.2313 | 314.2189 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 313.15 | 2 | 111961.2169 | 371120.9253 | 483082.1422 | 283.5349 | 315.3368 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 313.15 | 3 | 205831.0753 | 556681.388 | 762512.4633 | 284.8385 | 316.6018 | 15000 | 15000 | 0 | 0
0.033905 | 280.9278 | 0.05327 | 313.15 | 4 | 332184.7834 | 742241.8506 | 1074426.634 | 286.142 | 318.0138 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 285.9278 | 1 | 41666.3787 | 229100.5112 | 270766.8899 | 286.4291 | 287.1413 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 285.9278 | 2 | 92239.2339 | 458201.0225 | 550440.2563 | 288.0415 | 288.3947 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 285.9278 | 3 | 169573.9044 | 687301.5337 | 856875.4381 | 289.654 | 289.7681 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 285.9278 | 4 | 273670.3903 | 916402.0449 | 1190072.4353 | 291.2664 | 291.2614 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 295.0019 | 1 | 52515.7088 | 226241.5116 | 278757.2205 | 286.409 | 296.2556 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 295.0019 | 2 | 116257.0135 | 452483.0233 | 568740.0368 | 288.0013 | 297.5599 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 295.0019 | 3 | 213728.5282 | 678724.5349 | 892453.0631 | 289.5936 | 299.0159 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 295.0019 | 4 | 344930.2529 | 904966.0465 | 1249896.2994 | 291.1859 | 300.6236 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 304.0759 | 1 | 56849.2258 | 219017.1907 | 275866.4165 | 286.3581 | 305.3207 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 304.0759 | 2 | 125850.3667 | 438034.3814 | 563884.7481 | 287.8996 | 306.6203 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 304.0759 | 3 | 231365.0836 | 657051.5721 | 888416.6557 | 289.4411 | 308.0847 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 304.0759 | 4 | 373393.3764 | 876068.7628 | 1249462.1392 | 290.9825 | 309.7138 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 313.15 | 1 | 54801.9027 | 207427.5484 | 262229.4511 | 286.2766 | 314.3371 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 313.15 | 2 | 121318.0909 | 414855.0969 | 536173.1878 | 287.7365 | 315.5772 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 313.15 | 3 | 223032.8841 | 622282.6453 | 845315.5294 | 289.1964 | 316.9766 | 15000 | 15000 | 0 | 0
0.033905 | 284.8167 | 0.05327 | 313.15 | 4 | 359946.2821 | 829710.1937 | 1189656.4758 | 290.6563 | 318.5354 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 285.9278 | 1 | 39002.0622 | 225002.0461 | 264004.1082 | 290.2918 | 287.111 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 285.9278 | 2 | 86341.0848 | 450004.0921 | 536345.1769 | 291.878 | 288.3315 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 285.9278 | 3 | 158730.6642 | 675006.1382 | 833736.8024 | 293.4642 | 289.6644 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 285.9278 | 4 | 256170.8004 | 900008.1843 | 1156178.9847 | 295.0504 | 291.1095 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 295.0019 | 1 | 51246.5847 | 227092.4273 | 278339.012 | 290.3065 | 296.2538 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 295.0019 | 2 | 113447.4812 | 454184.8546 | 567632.3358 | 291.9075 | 297.5549 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 295.0019 | 3 | 208563.4444 | 681277.282 | 889840.7264 | 293.5084 | 299.0041 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 295.0019 | 4 | 336594.4745 | 908369.7093 | 1244964.1838 | 295.1094 | 300.6014 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 304.0759 | 1 | 57368.2409 | 224817.4872 | 282185.7281 | 290.2905 | 305.3492 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 304.0759 | 2 | 126999.3398 | 449634.9745 | 576634.3143 | 291.8754 | 306.6779 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 304.0759 | 3 | 233477.3719 | 674452.4617 | 907929.8336 | 293.4603 | 308.1727 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 304.0759 | 4 | 376802.3371 | 899269.949 | 1276072.2861 | 295.0452 | 309.8339 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 313.15 | 1 | 57136.205 | 218177.2258 | 275313.4309 | 290.2437 | 314.3963 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 313.15 | 2 | 126485.6689 | 436354.4517 | 562840.1206 | 291.7818 | 315.6979 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 313.15 | 3 | 232533.0321 | 654531.6775 | 887064.7096 | 293.3199 | 317.1656 | 15000 | 15000 | 0 | 0
0.033905 | 288.7056 | 0.05327 | 313.15 | 4 | 375278.2945 | 872708.9033 | 1247987.1979 | 294.858 | 318.7994 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation