## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'T': 350.0 ton, 2.09 COP liquid-cooled, centrifugal compressor chiller |  | ✓
| id | a633d3a8-b925-4bb9-a9f1-d0a3c3fcf701 |  | ✓
| data_timestamp | 2022-12-20T09:13Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'T' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 608129.1715 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.052741 | 277.0389 | 0.084587 | 285.9278 | 1 | 84457.3668 | 327352.5122 | 411809.879 | 278.514 | 287.0901 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.084587 | 285.9278 | 2 | 175313.7969 | 654705.0244 | 830018.8213 | 279.9891 | 288.2704 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.084587 | 285.9278 | 3 | 313999.1695 | 982057.5367 | 1296056.7061 | 281.4643 | 289.5858 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.084587 | 285.9278 | 4 | 500513.4846 | 1309410.0489 | 1809923.5335 | 282.9394 | 291.0362 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.084587 | 295.0019 | 1 | 94912.3563 | 304247.0246 | 399159.3809 | 278.4099 | 296.1325 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.084587 | 295.0019 | 2 | 197015.9168 | 608494.0492 | 805509.966 | 279.7809 | 297.2835 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.084587 | 295.0019 | 3 | 352869.1714 | 912741.0739 | 1265610.2453 | 281.1519 | 298.5867 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.084587 | 295.0019 | 4 | 562472.1202 | 1216988.0985 | 1779460.2186 | 282.5229 | 300.0422 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.084587 | 304.0759 | 1 | 93891.3321 | 273388.2051 | 367279.5372 | 278.2708 | 305.1196 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.084587 | 304.0759 | 2 | 194896.5087 | 546776.4102 | 741672.9189 | 279.5028 | 306.1835 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.084587 | 304.0759 | 3 | 349073.1645 | 820164.6153 | 1169237.7798 | 280.7347 | 307.3985 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.084587 | 304.0759 | 4 | 556421.2995 | 1093552.8204 | 1649974.1199 | 281.9667 | 308.7646 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.084587 | 313.15 | 1 | 82743.1679 | 234776.0536 | 317519.2215 | 278.0968 | 314.0552 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.084587 | 313.15 | 2 | 171755.5197 | 469552.1073 | 641307.627 | 279.1548 | 314.9783 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.084587 | 313.15 | 3 | 307626.0482 | 704328.1609 | 1011954.2091 | 280.2127 | 316.0349 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.084587 | 313.15 | 4 | 490354.7535 | 939104.2146 | 1429458.968 | 281.2707 | 317.2252 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 285.9278 | 1 | 82561.7472 | 352654.4891 | 435216.2363 | 282.5204 | 287.1561 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 285.9278 | 2 | 171378.9326 | 705308.9782 | 876687.9108 | 284.113 | 288.4022 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 285.9278 | 3 | 306951.5547 | 1057963.4673 | 1364915.022 | 285.7056 | 289.7801 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 285.9278 | 4 | 489279.6133 | 1410617.9564 | 1899897.5698 | 287.2982 | 291.2901 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 295.0019 | 1 | 97097.8819 | 336422.7538 | 433520.6356 | 282.4471 | 296.2298 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 295.0019 | 2 | 201552.5582 | 672845.5075 | 874398.0657 | 283.9664 | 297.4786 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 295.0019 | 3 | 360994.6108 | 1009268.2613 | 1370262.8721 | 285.4857 | 298.8832 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 295.0019 | 4 | 575424.0398 | 1345691.015 | 1921115.0548 | 287.005 | 300.4435 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 304.0759 | 1 | 100180.9512 | 312437.6865 | 412618.6376 | 282.3388 | 305.2484 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 304.0759 | 2 | 207952.2911 | 624875.373 | 832827.664 | 283.7498 | 306.4425 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 304.0759 | 3 | 372456.9762 | 937313.0595 | 1309770.0357 | 285.1607 | 307.7978 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 304.0759 | 4 | 593695.0067 | 1249750.7459 | 1843445.7527 | 286.5717 | 309.3144 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 313.15 | 1 | 92683.5652 | 280699.2873 | 373382.8525 | 282.1954 | 314.2145 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 313.15 | 2 | 192389.4662 | 561398.5746 | 753788.0408 | 283.4631 | 315.2989 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 313.15 | 3 | 344582.8776 | 842097.8619 | 1186680.7395 | 284.7307 | 316.533 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.084587 | 313.15 | 4 | 549263.7993 | 1122797.1491 | 1672060.9484 | 285.9984 | 317.9168 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 285.9278 | 1 | 79021.7554 | 361742.4153 | 440764.1707 | 286.4534 | 287.1718 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 285.9278 | 2 | 164030.7353 | 723484.8306 | 887515.5659 | 288.0901 | 288.4327 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 285.9278 | 3 | 293790.4236 | 1085227.2459 | 1379017.6696 | 289.7268 | 289.82 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 285.9278 | 4 | 468300.8204 | 1446969.6612 | 1915270.4817 | 291.3635 | 291.3335 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 295.0019 | 1 | 96376.3396 | 352384.4322 | 448760.7718 | 286.411 | 296.273 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 295.0019 | 2 | 200054.8048 | 704768.8644 | 904823.6692 | 288.0054 | 297.5648 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 295.0019 | 3 | 358312.0305 | 1057153.2967 | 1415465.3272 | 289.5998 | 299.0112 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 295.0019 | 4 | 571148.017 | 1409537.7289 | 1980685.7458 | 291.1941 | 300.6122 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 304.0759 | 1 | 102616.5929 | 335273.1172 | 437889.7101 | 286.3336 | 305.3203 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 304.0759 | 2 | 213008.1153 | 670546.2344 | 883554.3497 | 287.8506 | 306.5867 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 304.0759 | 3 | 381512.3082 | 1005819.3516 | 1387331.6598 | 289.3675 | 308.0182 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 304.0759 | 4 | 608129.1715 | 1341092.4688 | 1949221.6403 | 290.8844 | 309.6149 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 313.15 | 1 | 98138.8619 | 310408.4703 | 408547.3322 | 286.2211 | 314.3147 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 313.15 | 2 | 203713.3901 | 620816.9405 | 824530.3306 | 287.6256 | 315.5006 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 313.15 | 3 | 364864.8106 | 931225.4108 | 1296090.2213 | 289.03 | 316.8449 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.084587 | 313.15 | 4 | 581593.1235 | 1241633.881 | 1823227.0045 | 290.4344 | 318.3477 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 285.9278 | 1 | 74823.565 | 354616.2908 | 429439.8558 | 290.3127 | 287.1398 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 285.9278 | 2 | 155316.2711 | 709232.5817 | 864548.8527 | 291.9198 | 288.3679 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 285.9278 | 3 | 278182.2138 | 1063848.8725 | 1342031.0863 | 293.5269 | 289.7156 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 285.9278 | 4 | 443421.3931 | 1418465.1634 | 1861886.5565 | 295.134 | 291.1828 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 295.0019 | 1 | 93876.7932 | 352132.06 | 446008.8532 | 290.3014 | 296.2652 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 295.0019 | 2 | 194866.3294 | 704264.12 | 899130.4494 | 291.8973 | 297.5487 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 295.0019 | 3 | 349019.1113 | 1056396.18 | 1405415.2913 | 293.4931 | 298.9827 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 295.0019 | 4 | 556335.1389 | 1408528.24 | 1964863.3789 | 295.089 | 300.5674 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 304.0759 | 1 | 102470.2113 | 341894.4972 | 444364.7086 | 290.255 | 305.3387 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 304.0759 | 2 | 212704.2613 | 683788.9945 | 896493.2557 | 291.8045 | 306.6235 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 304.0759 | 3 | 380968.0845 | 1025683.4917 | 1406651.5762 | 293.3539 | 308.0731 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 304.0759 | 4 | 607261.681 | 1367577.9889 | 1974839.6699 | 294.9034 | 309.6877 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 313.15 | 1 | 100523.9023 | 323903.6025 | 424427.5049 | 290.1735 | 314.36 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 313.15 | 2 | 208664.1777 | 647807.2051 | 856471.3827 | 291.6414 | 315.5917 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 313.15 | 3 | 373732.0145 | 971710.8076 | 1345442.8222 | 293.1093 | 316.9856 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.084587 | 313.15 | 4 | 595727.4129 | 1295614.4102 | 1891341.8231 | 294.5773 | 318.5419 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation