## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'U': 450.0 ton, 2.06 COP liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 96794f1d-b863-48e9-bf41-ce6611d44098 |  | ✓
| data_timestamp | 2022-12-20T09:13Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'U' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 828702.2432 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.067809 | 277.0389 | 0.10936 | 285.9278 | 1 | 101446.9536 | 411645.8754 | 513092.829 | 278.4816 | 287.0479 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10936 | 285.9278 | 2 | 224656.3989 | 823291.7508 | 1047948.1496 | 279.9244 | 288.2156 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10936 | 285.9278 | 3 | 407730.7649 | 1234937.6262 | 1642668.3911 | 281.3671 | 289.514 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10936 | 285.9278 | 4 | 650670.0518 | 1646583.5016 | 2297253.5534 | 282.8099 | 290.943 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10936 | 295.0019 | 1 | 111189.6872 | 380113.3098 | 491302.997 | 278.3711 | 296.0783 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10936 | 295.0019 | 2 | 246231.8859 | 760226.6196 | 1006458.5055 | 279.7034 | 297.207 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10936 | 295.0019 | 3 | 446888.2956 | 1140339.9294 | 1587228.225 | 281.0356 | 298.4794 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10936 | 295.0019 | 4 | 713158.9163 | 1520453.2392 | 2233612.1556 | 282.3678 | 299.8956 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10936 | 304.0759 | 1 | 108750.9703 | 341804.723 | 450555.6933 | 278.2369 | 305.0663 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10936 | 304.0759 | 2 | 240831.2963 | 683609.4461 | 924440.7424 | 279.4348 | 306.1079 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10936 | 304.0759 | 3 | 437086.7207 | 1025414.1691 | 1462500.8898 | 280.6328 | 307.2905 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10936 | 304.0759 | 4 | 697517.2435 | 1367218.8922 | 2064736.1356 | 281.8308 | 308.6143 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10936 | 313.15 | 1 | 95956.7722 | 296720.1151 | 392676.8873 | 278.0788 | 314.0159 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10936 | 313.15 | 2 | 212498.2773 | 593440.2302 | 805938.5075 | 279.1188 | 314.9272 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10936 | 313.15 | 3 | 385664.8891 | 890160.3453 | 1275825.2344 | 280.1588 | 315.9634 | 15000 | 15000 | 0 | 0
0.067809 | 277.0389 | 0.10936 | 313.15 | 4 | 615456.6076 | 1186880.4604 | 1802337.068 | 281.1987 | 317.1244 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 285.9278 | 1 | 105256.7038 | 460386.8982 | 565643.6021 | 282.5449 | 287.1627 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 285.9278 | 2 | 233093.1703 | 920773.7964 | 1153866.9668 | 284.162 | 288.4468 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 285.9278 | 3 | 423042.7316 | 1381160.6947 | 1804203.4262 | 285.7791 | 289.8666 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 285.9278 | 4 | 675105.3876 | 1841547.5929 | 2516652.9805 | 287.3962 | 291.422 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 295.0019 | 1 | 120168.8342 | 435974.7395 | 556143.5737 | 282.4591 | 296.2203 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 295.0019 | 2 | 266116.3945 | 871949.479 | 1138065.8735 | 283.9905 | 297.4953 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 295.0019 | 3 | 482976.8556 | 1307924.2185 | 1790901.0741 | 285.5218 | 298.9257 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 295.0019 | 4 | 770750.2172 | 1743898.958 | 2514649.1752 | 287.0532 | 300.5114 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 304.0759 | 1 | 122331.8895 | 404786.5596 | 527118.4491 | 282.3496 | 305.2345 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 304.0759 | 2 | 270906.5257 | 809573.1192 | 1080479.6449 | 283.7714 | 306.4508 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 304.0759 | 3 | 491670.5044 | 1214359.6788 | 1706030.1833 | 285.1932 | 307.8258 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 304.0759 | 4 | 784623.8256 | 1619146.2384 | 2403770.0641 | 286.615 | 309.3595 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 313.15 | 1 | 113116.6067 | 366822.3585 | 479938.9653 | 282.2162 | 314.2083 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 313.15 | 2 | 250499.0895 | 733644.7171 | 984143.8066 | 283.5047 | 315.3202 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 313.15 | 3 | 454632.8789 | 1100467.0756 | 1555099.9545 | 284.7932 | 316.5792 | 15000 | 15000 | 0 | 0
0.067809 | 280.9278 | 0.10936 | 313.15 | 4 | 725517.975 | 1467289.4341 | 2192807.4091 | 286.0816 | 317.9854 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 285.9278 | 1 | 104512.4435 | 480562.5241 | 585074.9676 | 286.5078 | 287.2051 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 285.9278 | 2 | 231444.9902 | 961125.0482 | 1192570.0384 | 288.1989 | 288.5313 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 285.9278 | 3 | 420051.4358 | 1441687.5722 | 1861739.008 | 289.89 | 289.9922 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 285.9278 | 4 | 670331.7802 | 1922250.0963 | 2592581.8765 | 291.5812 | 291.5878 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 295.0019 | 1 | 122959.6296 | 463270.7722 | 586230.4018 | 286.4469 | 296.2863 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 295.0019 | 2 | 272296.6693 | 926541.5445 | 1198838.2138 | 288.0772 | 297.6285 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 295.0019 | 3 | 494193.4876 | 1389812.3167 | 1884005.8043 | 289.7075 | 299.1296 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 295.0019 | 4 | 788650.0845 | 1853083.0889 | 2641733.1734 | 291.3378 | 300.7898 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 304.0759 | 1 | 128654.9008 | 439202.9992 | 567857.9 | 286.3622 | 305.3241 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 304.0759 | 2 | 284908.9664 | 878405.9984 | 1163314.9648 | 287.9078 | 306.6329 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 304.0759 | 3 | 517083.6503 | 1317608.9976 | 1834692.6479 | 289.4534 | 308.1086 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 304.0759 | 4 | 825178.9526 | 1756811.9968 | 2581990.9494 | 290.999 | 309.7512 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 313.15 | 1 | 122513.7616 | 408359.205 | 530872.9666 | 286.2537 | 314.3206 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 313.15 | 2 | 271309.2853 | 816718.41 | 1088027.6953 | 287.6907 | 315.5492 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 313.15 | 3 | 492401.4762 | 1225077.615 | 1717479.0912 | 289.1278 | 316.9373 | 15000 | 15000 | 0 | 0
0.067809 | 284.8167 | 0.10936 | 313.15 | 4 | 785790.3342 | 1633436.82 | 2419227.1542 | 290.5648 | 318.4847 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 285.9278 | 1 | 100573.0676 | 472172.753 | 572745.8205 | 290.3699 | 287.1782 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 285.9278 | 2 | 222721.1599 | 944345.5059 | 1167066.6658 | 292.0343 | 288.4757 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 285.9278 | 3 | 404218.4837 | 1416518.2589 | 1820736.7425 | 293.6986 | 289.9027 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 285.9278 | 4 | 645065.0389 | 1888691.0118 | 2533756.0507 | 295.363 | 291.4594 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 295.0019 | 1 | 120983.6301 | 462001.408 | 582985.038 | 290.3341 | 296.2792 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 295.0019 | 2 | 267920.7771 | 924002.816 | 1191923.5931 | 291.9626 | 297.6133 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 295.0019 | 3 | 486251.6445 | 1386004.2239 | 1872255.8684 | 293.5911 | 299.1039 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 295.0019 | 4 | 775976.2322 | 1848005.6319 | 2623981.8641 | 295.2196 | 300.7509 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 304.0759 | 1 | 129204.2223 | 445054.0418 | 574258.2641 | 290.2743 | 305.3382 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 304.0759 | 2 | 286125.4505 | 890108.0836 | 1176233.5341 | 291.8431 | 306.6613 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 304.0759 | 3 | 519291.4574 | 1335162.1255 | 1854453.5829 | 293.4118 | 308.1521 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 304.0759 | 4 | 828702.2432 | 1780216.1673 | 2608918.4104 | 294.9806 | 309.8104 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 313.15 | 1 | 125695.1166 | 421330.6545 | 547025.771 | 290.1907 | 314.3563 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 313.15 | 2 | 278354.4624 | 842661.309 | 1121015.7714 | 291.6758 | 315.622 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 313.15 | 3 | 505187.8266 | 1263991.9635 | 1769179.7901 | 293.161 | 317.0513 | 15000 | 15000 | 0 | 0
0.067809 | 288.7056 | 0.10936 | 313.15 | 4 | 806195.2092 | 1685322.6179 | 2491517.8272 | 294.6461 | 318.6441 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation