## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'Y': 350.0 ton, 2.25 COP liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 8b0049db-1d50-48c3-b73d-939dde8a16fc |  | ✓
| data_timestamp | 2022-12-20T09:13Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'Y' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 602134.5404 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.052741 | 277.0389 | 0.082684 | 285.9278 | 1 | 159421.3051 | 303191.1415 | 462612.4466 | 278.4051 | 287.2635 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.082684 | 285.9278 | 2 | 215180.8544 | 606382.283 | 821563.1375 | 279.7714 | 288.3 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.082684 | 285.9278 | 3 | 302864.1951 | 909573.4245 | 1212437.6196 | 281.1376 | 289.4286 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.082684 | 285.9278 | 4 | 422471.327 | 1212764.566 | 1635235.893 | 282.5039 | 290.6494 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.082684 | 295.0019 | 1 | 186451.9073 | 296784.0164 | 483235.9237 | 278.3763 | 296.4021 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.082684 | 295.0019 | 2 | 251665.74 | 593568.0327 | 845233.7727 | 279.7136 | 297.4511 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.082684 | 295.0019 | 3 | 354216.187 | 890352.0491 | 1244568.2361 | 281.051 | 298.6083 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.082684 | 295.0019 | 4 | 494103.2483 | 1187136.0654 | 1681239.3137 | 282.3884 | 299.8736 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.082684 | 304.0759 | 1 | 208199.8476 | 284599.8988 | 492799.7464 | 278.3214 | 305.5085 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.082684 | 304.0759 | 2 | 281020.2881 | 569199.7976 | 850220.0857 | 279.6038 | 306.5476 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.082684 | 304.0759 | 3 | 395532.3237 | 853799.6964 | 1249332.02 | 280.8863 | 307.7078 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.082684 | 304.0759 | 4 | 551735.9542 | 1138399.5951 | 1690135.5493 | 282.1688 | 308.9893 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.082684 | 313.15 | 1 | 222842.3985 | 266638.7888 | 489481.1873 | 278.2404 | 314.5776 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.082684 | 313.15 | 2 | 300784.2502 | 533277.5776 | 834061.8278 | 279.442 | 315.5825 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.082684 | 313.15 | 3 | 423349.8378 | 799916.3664 | 1223266.2042 | 280.6435 | 316.7176 | 15000 | 15000 | 0 | 0
0.052741 | 277.0389 | 0.082684 | 313.15 | 4 | 590539.1613 | 1066555.1552 | 1657094.3165 | 281.845 | 317.9829 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 285.9278 | 1 | 156935.74 | 326700.5842 | 483636.3242 | 282.4032 | 287.3242 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 285.9278 | 2 | 211825.9326 | 653401.1684 | 865227.101 | 283.8786 | 288.426 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 285.9278 | 3 | 298142.1871 | 980101.7527 | 1278243.9398 | 285.354 | 289.6186 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 285.9278 | 4 | 415884.5036 | 1306802.3369 | 1722686.8405 | 286.8294 | 290.9019 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 295.0019 | 1 | 185371.6251 | 322226.3625 | 507597.9876 | 282.383 | 296.4727 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 295.0019 | 2 | 250207.6159 | 644452.7251 | 894660.341 | 283.8382 | 297.5943 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 295.0019 | 3 | 352163.8967 | 966679.0876 | 1318842.9844 | 285.2934 | 298.8235 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 295.0019 | 4 | 491240.4675 | 1288905.4502 | 1780145.9177 | 286.7486 | 300.1602 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 304.0759 | 1 | 209361.5092 | 311975.1484 | 521336.6577 | 282.3367 | 305.5915 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 304.0759 | 2 | 282588.2552 | 623950.2969 | 906538.5521 | 283.7456 | 306.7113 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 304.0759 | 3 | 397739.2164 | 935925.4453 | 1333664.6618 | 285.1545 | 307.953 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 304.0759 | 4 | 554814.3931 | 1247900.5938 | 1802714.9869 | 286.5634 | 309.3165 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 313.15 | 1 | 227217.9628 | 295946.9419 | 523164.9048 | 282.2643 | 314.6758 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 313.15 | 2 | 306690.2216 | 591893.8839 | 898584.1055 | 283.6008 | 315.7707 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 313.15 | 3 | 431662.4141 | 887840.8258 | 1319503.2399 | 284.9373 | 316.9983 | 15000 | 15000 | 0 | 0
0.052741 | 280.9278 | 0.082684 | 313.15 | 4 | 602134.5404 | 1183787.7678 | 1785922.3081 | 286.2738 | 318.3586 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 285.9278 | 1 | 155825.8979 | 337262.9865 | 493088.8843 | 286.3426 | 287.3515 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 285.9278 | 2 | 210327.9096 | 674525.9729 | 884853.8825 | 287.8686 | 288.4827 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 285.9278 | 3 | 296033.7397 | 1011788.9594 | 1307822.6991 | 289.3945 | 289.704 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 285.9278 | 4 | 412943.3881 | 1349051.9458 | 1761995.3339 | 290.9205 | 291.0154 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 295.0019 | 1 | 183908.6012 | 334721.6683 | 518630.2695 | 286.3311 | 296.5047 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 295.0019 | 2 | 248232.8816 | 669443.3365 | 917676.2181 | 287.8456 | 297.661 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 295.0019 | 3 | 349384.4843 | 1004165.0048 | 1353549.4891 | 289.36 | 298.9241 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 295.0019 | 4 | 487363.4095 | 1338886.673 | 1826250.0825 | 290.8745 | 300.2938 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 304.0759 | 1 | 208155.8513 | 326403.3576 | 534559.2089 | 286.2935 | 305.6299 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 304.0759 | 2 | 280960.9036 | 652806.7153 | 933767.6189 | 287.7703 | 306.7905 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 304.0759 | 3 | 395448.7407 | 979210.0729 | 1374658.8137 | 289.2471 | 308.0722 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 304.0759 | 4 | 551619.3627 | 1305613.4306 | 1857232.7933 | 290.7239 | 309.475 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 313.15 | 1 | 227015.5163 | 312308.0546 | 539323.5709 | 286.2297 | 314.7229 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 313.15 | 2 | 306416.9669 | 624616.1092 | 931033.0761 | 287.6427 | 315.8653 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 313.15 | 3 | 431277.8118 | 936924.1639 | 1368201.9756 | 289.0558 | 317.1403 | 15000 | 15000 | 0 | 0
0.052741 | 284.8167 | 0.082684 | 313.15 | 4 | 601598.0509 | 1249232.2185 | 1850830.2694 | 290.4688 | 318.5479 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 285.9278 | 1 | 157662.9876 | 334878.3482 | 492541.3358 | 290.2232 | 287.3499 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 285.9278 | 2 | 212807.5439 | 669756.6965 | 882564.2404 | 291.7409 | 288.4761 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 285.9278 | 3 | 299523.792 | 1004635.0447 | 1304158.8367 | 293.2586 | 289.6934 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 285.9278 | 4 | 417811.7319 | 1339513.393 | 1757325.1248 | 294.7762 | 291.0019 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 295.0019 | 1 | 184083.0124 | 334269.9335 | 518352.9459 | 290.2205 | 296.5039 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 295.0019 | 2 | 248468.2952 | 668539.867 | 917008.1622 | 291.7354 | 297.6591 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 295.0019 | 3 | 349715.8259 | 1002809.8006 | 1352525.6265 | 293.2503 | 298.9211 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 295.0019 | 4 | 487825.6045 | 1337079.7341 | 1824905.3386 | 294.7652 | 300.2899 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 304.0759 | 1 | 207052.0184 | 327884.5264 | 534936.5448 | 290.1915 | 305.631 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 304.0759 | 2 | 279470.9917 | 655769.0528 | 935240.0445 | 291.6775 | 306.7947 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 304.0759 | 3 | 393351.7095 | 983653.5791 | 1377005.2886 | 293.1635 | 308.079 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 304.0759 | 4 | 548694.1718 | 1311538.1055 | 1860232.2773 | 294.6494 | 309.4837 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 313.15 | 1 | 225153.1715 | 315722.1268 | 540875.2984 | 290.1364 | 314.7274 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 313.15 | 2 | 303903.2443 | 631444.2537 | 935347.498 | 291.5673 | 315.8779 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 313.15 | 3 | 427739.7806 | 947166.3805 | 1374906.1611 | 292.9981 | 317.1599 | 15000 | 15000 | 0 | 0
0.052741 | 288.7056 | 0.082684 | 313.15 | 4 | 596662.7804 | 1262888.5073 | 1859551.2877 | 294.429 | 318.5733 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation