## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'Z': 75.0 ton, 2.47 COP liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 5e82d941-e4e3-445b-adb0-6c04830b87e6 |  | ✓
| data_timestamp | 2022-12-20T09:13Z |  | ✓
| data_version | 1 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'Z' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| maximum_power | 112875.4136 | W
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Maximum input power at which the chiller operates reliably and continuously
Note on B30: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A31: Data group describing cooling performance over a range of conditions
Note on A32: Data group describing standby performance

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | evaporator_liquid_entering_temperature | condenser_liquid_leaving_temperature | evaporator_liquid_differential_pressure | condenser_liquid_differential_pressure | oil_cooler_heat | auxiliary_heat
m3/s | K | m3/s | K | - | W | W | W | K | K | Pa | Pa | W | W
0.011302 | 277.0389 | 0.017223 | 285.9278 | 1 | 32892.7608 | 67133.4534 | 100026.2142 | 278.4506 | 287.3144 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017223 | 285.9278 | 2 | 46185.2591 | 134266.9069 | 180452.1659 | 279.8624 | 288.4292 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017223 | 285.9278 | 3 | 65290.4634 | 201400.3603 | 266690.8237 | 281.2741 | 289.6247 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017223 | 285.9278 | 4 | 90208.3736 | 268533.8137 | 358742.1874 | 282.6859 | 290.9007 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017223 | 295.0019 | 1 | 36323.7875 | 63235.6235 | 99559.411 | 278.3687 | 296.3869 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017223 | 295.0019 | 2 | 51002.8194 | 126471.247 | 177474.0664 | 279.6985 | 297.4708 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017223 | 295.0019 | 3 | 72100.8776 | 189706.8705 | 261807.7481 | 281.0282 | 298.644 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017223 | 295.0019 | 4 | 99617.9621 | 252942.4939 | 352560.4561 | 282.358 | 299.9066 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017223 | 304.0759 | 1 | 37194.608 | 59511.5377 | 96706.1456 | 278.2904 | 305.4256 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017223 | 304.0759 | 2 | 52225.5525 | 119023.0753 | 171248.6279 | 279.5418 | 306.466 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017223 | 304.0759 | 3 | 73829.4121 | 178534.613 | 252364.0251 | 280.7933 | 307.5981 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017223 | 304.0759 | 4 | 102006.1866 | 238046.1507 | 340052.3373 | 282.0448 | 308.8219 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017223 | 313.15 | 1 | 35910.1049 | 55961.196 | 91871.3009 | 278.2157 | 314.4363 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017223 | 313.15 | 2 | 50421.961 | 111922.392 | 162344.3529 | 279.3925 | 315.4231 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017223 | 313.15 | 3 | 71279.7386 | 167883.588 | 239163.3266 | 280.5693 | 316.4987 | 15000 | 15000 | 0 | 0
0.011302 | 277.0389 | 0.017223 | 313.15 | 4 | 98483.4379 | 223844.784 | 322328.2218 | 281.7461 | 317.6631 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 285.9278 | 1 | 33115.9284 | 73386.5041 | 106502.4325 | 282.4744 | 287.4041 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 285.9278 | 2 | 46498.6124 | 146773.0083 | 193271.6206 | 284.021 | 288.6069 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 285.9278 | 3 | 65733.4398 | 220159.5124 | 285892.9522 | 285.5676 | 289.8909 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 285.9278 | 4 | 90820.4107 | 293546.0166 | 384366.4273 | 287.1142 | 291.2559 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 295.0019 | 1 | 37636.5045 | 70249.5804 | 107886.0849 | 282.4083 | 296.5027 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 295.0019 | 2 | 52846.0266 | 140499.1608 | 193345.1874 | 283.8888 | 297.6916 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 295.0019 | 3 | 74706.5543 | 210748.7413 | 285455.2955 | 285.3693 | 298.973 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 295.0019 | 4 | 103218.0875 | 280998.3217 | 384216.4092 | 286.8498 | 300.347 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 304.0759 | 1 | 39455.0183 | 67286.4008 | 106741.4192 | 282.3458 | 305.5657 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 304.0759 | 2 | 55399.4314 | 134572.8017 | 189972.2331 | 283.7639 | 306.7273 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 304.0759 | 3 | 78316.2121 | 201859.2025 | 280175.4146 | 285.1819 | 307.9862 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 304.0759 | 4 | 108205.3605 | 269145.6033 | 377350.9638 | 286.6 | 309.3424 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 313.15 | 1 | 38899.0352 | 64496.9654 | 103396.0006 | 282.287 | 314.5977 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 313.15 | 2 | 54618.7665 | 128993.9307 | 183612.6972 | 283.6463 | 315.7209 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 313.15 | 3 | 77212.6138 | 193490.8961 | 270703.5099 | 285.0056 | 316.9403 | 15000 | 15000 | 0 | 0
0.011302 | 280.9278 | 0.017223 | 313.15 | 4 | 106680.5771 | 257987.8615 | 364668.4386 | 286.3649 | 318.256 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 285.9278 | 1 | 32771.171 | 76085.3349 | 108856.506 | 286.4232 | 287.4368 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 285.9278 | 2 | 46014.5329 | 152170.6699 | 198185.2028 | 288.0296 | 288.675 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 285.9278 | 3 | 65049.1138 | 228256.0048 | 293305.1187 | 289.6361 | 289.9936 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 285.9278 | 4 | 89874.9138 | 304341.3398 | 394216.2536 | 291.2426 | 291.3924 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 295.0019 | 1 | 37979.3228 | 73709.3174 | 111688.6403 | 286.373 | 296.5556 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 295.0019 | 2 | 53327.3834 | 147418.6349 | 200746.0183 | 287.9293 | 297.7946 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 295.0019 | 3 | 75387.0313 | 221127.9523 | 296514.9836 | 289.4856 | 299.1269 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 295.0019 | 4 | 104158.2666 | 294837.2698 | 398995.5364 | 291.042 | 300.5526 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 304.0759 | 1 | 40467.258 | 71507.0441 | 111974.3021 | 286.3265 | 305.6387 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 304.0759 | 2 | 56820.7336 | 143014.0882 | 199834.8217 | 287.8363 | 306.8649 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 304.0759 | 3 | 80325.4566 | 214521.1322 | 294846.5888 | 289.3461 | 308.191 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 304.0759 | 4 | 110981.4271 | 286028.1763 | 397009.6034 | 290.856 | 309.6168 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 313.15 | 1 | 40485.2243 | 69478.5148 | 109963.7392 | 286.2837 | 314.6897 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 313.15 | 2 | 56845.9603 | 138957.0297 | 195802.99 | 287.7507 | 315.8916 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 313.15 | 3 | 80361.1187 | 208435.5445 | 288796.6633 | 289.2176 | 317.1936 | 15000 | 15000 | 0 | 0
0.011302 | 284.8167 | 0.017223 | 313.15 | 4 | 111030.6996 | 277914.0594 | 388944.759 | 290.6846 | 318.5959 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 285.9278 | 1 | 32224.5838 | 75229.9459 | 107454.5296 | 290.2966 | 287.4173 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 285.9278 | 2 | 45247.0609 | 150459.8917 | 195706.9526 | 291.8877 | 288.6407 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 285.9278 | 3 | 63964.1659 | 225689.8376 | 289654.0035 | 293.4787 | 289.943 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 285.9278 | 4 | 88375.8987 | 300919.7834 | 389295.6821 | 295.0698 | 291.3242 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 295.0019 | 1 | 37759.3699 | 73614.8346 | 111374.2045 | 290.2625 | 296.5513 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 295.0019 | 2 | 53018.5439 | 147229.6692 | 200248.2131 | 291.8194 | 297.7876 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 295.0019 | 3 | 74950.4359 | 220844.5037 | 295794.9396 | 293.3763 | 299.1169 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 295.0019 | 4 | 103555.0458 | 294459.3383 | 398014.3841 | 294.9332 | 300.5389 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 304.0759 | 1 | 40679.4866 | 72173.4674 | 112852.954 | 290.232 | 305.651 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 304.0759 | 2 | 57118.7272 | 144346.9349 | 201465.662 | 291.7584 | 306.8877 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 304.0759 | 3 | 80746.7196 | 216520.4023 | 297267.1219 | 293.2848 | 308.2247 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 304.0759 | 4 | 111563.4638 | 288693.8697 | 400257.3336 | 294.8112 | 309.6621 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 313.15 | 1 | 41157.864 | 70905.8444 | 112063.7085 | 290.2052 | 314.7191 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 313.15 | 2 | 57790.4247 | 141811.6889 | 199602.1135 | 291.7048 | 315.9448 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 313.15 | 3 | 81696.2745 | 212717.5333 | 294413.8078 | 293.2044 | 317.2723 | 15000 | 15000 | 0 | 0
0.011302 | 288.7056 | 0.017223 | 313.15 | 4 | 112875.4136 | 283623.3777 | 396498.7913 | 294.704 | 318.7016 | 15000 | 15000 | 0 | 0
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Entering evaporator liquid temperature
Note on J3: Leaving condenser liquid temperature
Note on K3: Pressure difference across the evaporator
Note on L3: Pressure difference across the condenser
Note on M3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on N3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation