## RS0002
RS0002: Unitary Cooling Air-Conditioning Equipment
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0002 |  | ✓
| schema_version | 1.0.0 |  | ✓
| description | Unitary System with Constant Efficiency |  | ✓
| id | bcf8b859-67a3-42f4-8f8d-4e57af1ccf22 |  | ✓
| data_timestamp | 2019-09-13T00:00Z |  | ✓
| data_version | 1 |  | ✓
| data_source | Committee
| disclaimer | Example data not to be used for simulation
| notes | An example representation that applies a constant COP of 3.1
description
description.product_information
| manufacturer | ABC HVAC
| model_number | U AB12
performance |  |  |  | ✓
| standby_power | 10 | W | ✓
| fan_position | BLOW_THROUGH
performance.dx_system_representation |  | $dx_system_representation
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Package manufacturer name
Note on B17: Package model number
Note on A18: Data group containing performance information
Note on B19: Continuous unit power draw regardless of fan or DX system operation
Note on B20: Position of the fan relative to the cooling coil
Note on A21: The corresponding Standard 205 direct expansion system representation

## dx_system_representation
performance.dx_system_representation
Data Group | Data Element | Value | Units | Required
performance.dx_system_representation.metadata |  |  |  | ✓
| schema_version | 1.0.0 |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0004 |  | ✓
| description | DX System with Constant Efficiency |  | ✓
| id | 123e4567-e89b-12d3-a456-426614174000 |  | ✓
| data_timestamp | 2020-05-07T00:00Z |  | ✓
| data_version | 1 |  | ✓
| disclaimer | Example data not to be used for simulation
| notes | An example representation that applies a constant COP of 3.1
performance.dx_system_representation.description
performance.dx_system_representation.description.product_information
| outdoor_unit_manufacturer | ABC HVAC
| outdoor_unit_model_number | DX AB12
| indoor_unit_manufacturer | ABC HVAC
| indoor_unit_model_number | DX AB12
| refrigerant | R-410A
| compressor_type | SCROLL
performance.dx_system_representation.performance |  |  |  | ✓
| compressor_speed_control_type | DISCRETE |  | ✓
| cycling_degradation_coefficient | 0.25 | - | ✓
performance.dx_system_representation.performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.dx_system_representation.performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: The version of the schema the data complies with
Note on B5: Data model name
Note on B6: Schema name or identifier
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Characterization of accuracy, limitations, and applicability of this data
Note on B12: Additional Information
Note on A13: Data group describing product and rating information
Note on A14: Data group describing product information
Note on B15: Outdoor unit manufacturer name
Note on B16: Outdoor unit model number
Note on B17: Indoor unit manufacturer name
Note on B18: Indoor unit model number
Note on B19: Refrigerant used
Note on B20: Type of compressor
Note on A21: Data group containing performance information
Note on B22: Method used to control different speeds of the compressor
Note on B23: Cycling degradation coefficient (C~D~) as described in AHRI 210/240
Note on A24: Data group describing cooling performance over a range of conditions
Note on A25: Data group describing standby performance

## performance_map_cooling
performance.dx_system_representation.performance.performance_map_cooling
grid_variables | [5 empty] | lookup_variables
outdoor_coil_entering_dry_bulb_temperature | indoor_coil_entering_relative_humidity | indoor_coil_entering_dry_bulb_temperature | indoor_coil_air_mass_flow_rate | compressor_sequence_number | ambient_absolute_air_pressure | gross_total_capacity | gross_sensible_capacity | gross_power
K | - | K | kg/s | - | Pa | W | W | W
283.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 42191.636 | 25314.9816 | 13610.2052
283.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 42191.636 | 25314.9816 | 13610.2052
283.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 56877.12 | 34126.272 | 18347.4581
283.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 56877.12 | 34126.272 | 18347.4581
283.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 62919.299 | 37751.5794 | 20296.5481
283.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 62919.299 | 37751.5794 | 20296.5481
283.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 102901.802 | 61741.0812 | 33194.1297
283.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 102901.802 | 61741.0812 | 33194.1297
283.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 42191.636 | 25314.9816 | 13610.2052
283.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 42191.636 | 25314.9816 | 13610.2052
283.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 56877.12 | 34126.272 | 18347.4581
283.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 56877.12 | 34126.272 | 18347.4581
283.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 62919.299 | 37751.5794 | 20296.5481
283.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 62919.299 | 37751.5794 | 20296.5481
283.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 102901.802 | 61741.0812 | 33194.1297
283.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 102901.802 | 61741.0812 | 33194.1297
283.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 42191.636 | 25314.9816 | 13610.2052
283.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 42191.636 | 25314.9816 | 13610.2052
283.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 56877.12 | 34126.272 | 18347.4581
283.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 56877.12 | 34126.272 | 18347.4581
283.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 62919.299 | 37751.5794 | 20296.5481
283.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 62919.299 | 37751.5794 | 20296.5481
283.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 102901.802 | 61741.0812 | 33194.1297
283.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 102901.802 | 61741.0812 | 33194.1297
283.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 42191.636 | 25314.9816 | 13610.2052
283.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 42191.636 | 25314.9816 | 13610.2052
283.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 56877.12 | 34126.272 | 18347.4581
283.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 56877.12 | 34126.272 | 18347.4581
283.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 62919.299 | 37751.5794 | 20296.5481
283.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 62919.299 | 37751.5794 | 20296.5481
283.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 102901.802 | 61741.0812 | 33194.1297
283.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 102901.802 | 61741.0812 | 33194.1297
323.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 30500.344 | 18300.2064 | 9838.8206
323.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 30500.344 | 18300.2064 | 9838.8206
323.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 44039.922 | 26423.9532 | 14206.4265
323.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 44039.922 | 26423.9532 | 14206.4265
323.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 39370.922 | 23622.5532 | 12700.2974
323.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 39370.922 | 23622.5532 | 12700.2974
323.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 66637.795 | 39982.677 | 21496.0629
323.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 66637.795 | 39982.677 | 21496.0629
323.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 30500.344 | 18300.2064 | 9838.8206
323.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 30500.344 | 18300.2064 | 9838.8206
323.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 44039.922 | 26423.9532 | 14206.4265
323.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 44039.922 | 26423.9532 | 14206.4265
323.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 39370.922 | 23622.5532 | 12700.2974
323.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 39370.922 | 23622.5532 | 12700.2974
323.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 66637.795 | 39982.677 | 21496.0629
323.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 66637.795 | 39982.677 | 21496.0629
323.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 30500.344 | 18300.2064 | 9838.8206
323.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 30500.344 | 18300.2064 | 9838.8206
323.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 44039.922 | 26423.9532 | 14206.4265
323.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 44039.922 | 26423.9532 | 14206.4265
323.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 39370.922 | 23622.5532 | 12700.2974
323.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 39370.922 | 23622.5532 | 12700.2974
323.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 66637.795 | 39982.677 | 21496.0629
323.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 66637.795 | 39982.677 | 21496.0629
323.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 30500.344 | 18300.2064 | 9838.8206
323.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 30500.344 | 18300.2064 | 9838.8206
323.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 44039.922 | 26423.9532 | 14206.4265
323.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 44039.922 | 26423.9532 | 14206.4265
323.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 39370.922 | 23622.5532 | 12700.2974
323.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 39370.922 | 23622.5532 | 12700.2974
323.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 66637.795 | 39982.677 | 21496.0629
323.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 66637.795 | 39982.677 | 21496.0629
Note on A2: Data group defining the grid variables for cooling performance
Note on G2: Data group defining the lookup variables for cooling performance
Note on A3: Dry bulb temperature of the air entering the outdoor coil
Note on B3: Relative humidity of the air entering the indoor coil
Note on C3: Dry bulb temperature of the air entering the indoor coil
Note on D3: Mass flow rate of air entering the indoor coil
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Ambient absolute air pressure
Note on G3: Total heat removed by the indoor coil
Note on H3: Sensible heat removed by the indoor coil
Note on I3: Gross power draw (of the outdoor unit)

## performance_map_standby
performance.dx_system_representation.performance.performance_map_standby
grid_variables | lookup_variables
outdoor_coil_environment_dry_bulb_temperature | gross_power
K | W
283.15 | 40
323.15 | 40
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the outdoor coil
Note on B3: Gross power draw (of the outdoor unit)